## 1) User Guide and Network Maps
User Guide
With this tool we aim to provide our customers with information on where there is spare capacity for new developments to connect to our network without triggering reinforcement work. To aid our customers in interpreting the information contained within this tool we have produced a user guide which can be found below. Please note that the data presented in this tool is based on high level analysis and as such may differ from the results of a formal connection application. If your proposed development falls within an area with limited network capacity please contact us to discuss a possible solution. We will always to work with customers to overcome network constraints whether this is through traditional reinforcement or smart network solutions.
Map Data
We now publish an interactive map on our website that contains the same information as contained within this tool.
Click here to access the map.
| Last Updated* | 2025-08-20
This version is 351 days old
* due to the infrequency of EHV plant replacement, switchgear ratings are checked quarterly
| Switchgear ratings checked | 2024-12-08
This version is 606 days old

## 2) 11 kV & 6.6 kV Connections
11 kV & 6.6 kV Connections
The results given by this tool are based on high level approximations only. It should also be noted that the network may have changed since the last time the data was updated. As such, the outcome of a formal application may differ from the results given by this tool. For further information on how to interpret the data contained within this workbook please refer to the user guide embedded within the first tab. Please note that the value of headroom quoted by this tool is based on total capacity available for new connections, the column beside it shows the maximum size of a single connection, based on the on-site primary switchgear rating, which can be much lower. To reflect this the 'Can Connect?' RAG value is derived using the lowest of these two values. It is normally not possible to accommodate a single connection of more than 7 MW at 11 kV or 6.6 kV, this is based on the typical load rating of items of plant such as circuit breakers, current transformers and cable terminations. It is possible that due to these addtional factors and the point of connection requested that the maximum connection size is lower than the values shown below.
Inputs | [18 empty] | Key
Easting |  | Enter Data | [5 empty] | Use the controls to the left to find the nearest primary substations to your site. The results will be displayed in the table below. When the desired site capacity and connection type are entered an estimate of available headroom and connection feasibility will be displayed. The results are based on both local constraints and constraints at the associated BSP. | [10 empty] | RAG | Limiting factor: Headroom |  | Limiting factor: Switchgear rating
Northing |  | Enter Data | [17 empty] | Capacity <90% of headroom |  | Suitable
Capacity (MW) |  | Enter Data | [17 empty] | Capacity >90% & < 100% of headroom |  | N/A
Connection Type |  | Enter Data | [17 empty] | Capacity >100% of headroom |  | Unsuitable
Distribution Network Capacity Capacity | [18 empty] | Transmission Constraints (App G)
No | Distance (km) | Primary Substation |  |  | BSP Group |  |  | BCA Group (GSP) |  |  | Primary Substation Location |  | Headroom (MW) | Max Single circuit connection (MW) |  | Can Connect? (RAG) | Can Connect? (RAG) | Limiting factor | Materiality Headroom (MW) | Fault Level Headroom (kA) | Transmission System Comment (see tab 6 for more details)
[11 empty] | Easting | Northing
1 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
2 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
3 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
4 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
5 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
6 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
7 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
8 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
9 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
10 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
Connection Types
Demand Firm |  |  |  |  | The connection of load which is secure for a first circuit outage.
Demand N-0 |  |  |  |  | The connection of load which can be actively constrained off under outage conditions.
Generation Synchronous (LV) |  |  |  |  | Generation such as diesel or gas turbines connected to the HV network through step up transformers.
Generation Synchronous (HV) |  |  |  |  | Generation such as diesel or gas turbines connected to the HV network directly i.e. without step up transformers.
Generation Inverter Based |  |  |  |  | Generation technologies connected by inverters this typically includes solar and wind generators .
Battery Energy Storage |  |  |  |  | Inverter connected battery energy storage schemes.

## 3) 33 kV Connections
33 kV Connections
The results given by this tool are based on high level approximations only. It should also be noted that the network may have changed since the last time the data was updated. As such, the outcome of a formal application may differ from the results given by this tool. For further information on how to interpret the data contained within this workbook please refer to the user guide embedded within the first tab.
Please note that the value of headroom quoted by this tool is based on total capacity available for new connections not the maximum size of a single connection which can be much lower. It is normally not possible to accommodate a single connection of more than 40 MW at 33 kV. This is based on the typical load rating of items of plant such as circuit breakers, current transformers and cable terminations.
Inputs | [11 empty] | Key
Easting |  | Enter Data | [5 empty] | Use the controls to the left to find the nearest BSP to your site. The results will be displayed in the table below. When the desired site capacity and connection type are entered an estimate of available headroom and connection feasibility will be displayed. It should be noted that the network assets surrounding your site may not be fed from the closest BSP. |  |  |  |  | Capacity <90% of headroom
Northing |  | Enter Data | [10 empty] | Capacity >90% & < 100% of headroom
Capacity (MW) |  | Enter Data | [10 empty] | Capacity >100% of headroom
Connection Type |  | Enter Data
Distribution Network Capacity Capacity | [11 empty] | Transmission Constraints (App G)
No | Distance (km) | BSP |  |  | BCA Group (GSP) |  |  | BSP Location |  | Headroom (MW) | Can Connect? (RAG) | Materiality Headroom (MW) | Fault Level Headroom (kA) | Transmission System Comment (see tab 6 for more details)
[8 empty] | Easting | Northing
1 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
2 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
3 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
4 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
5 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
6 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
7 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
8 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
9 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
10 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
Connection Types
Demand Firm |  |  |  |  | The connection of load which is secure for a first circuit outage.
Demand N-0 |  |  |  |  | The connection of load which can be actively constrained off under outage conditions.
Generation Synchronous (LV) |  |  |  |  | Generation such as diesel or gas turbines connected to the EHV network through step up transformers.
Generation Inverter Based |  |  |  |  | Generation technologies connected by inverters this typically includes solar and wind generators .
Battery Energy Storage |  |  |  |  | Inverter connected battery energy storage schemes.

## 4) Primary Headroom Data
Primary Substation Headroom
Primary Substation | Voltage (kV) | BSP Group |  | BCA Group (GSP) | Primary Substation Location |  | Individual Circuit Capacity |  | Demand Headroom (MW) |  | Generation Headroom N-0 -(MW) |  |  | Battery Storage Headroom N-0 -(MW)
[5 empty] | Easting | Northing | CB Rating | MVA | Firm | N-0 | Inverter Based | Synchronous - LV | Synchronous - HV
ALBION ST | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 367434 | 426087 | 400 | 4.5726 | 3.3041 | 13.4297 | 21.4846 | 3.749 | 2.7472 | 13.4297 | 0 | 0 | Offer signed 06/06/2025.
ALDERLEY | 11 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 385044 | 379026 | 400 | 7.621 | 7.7796 | 14.4696 | 8.008 | 1.9575 | 1.4344 | 8.008 | 1.4344 | 5.768 | Offer signed 11/03/2025
ALSTON | 11 | PENRITH & SHAP | PENRITH | HUTTON | 372125 | 546499 | 400 | 7.621 | 0 | 0.2888 | 2.9704 | 2.9704 | 2.9704 | 0.2888 | 3.2626 | 1.1073 | Offer signed 30/05/2025.
AMBLESIDE | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 337602 | 503506 | 400 | 7.621 | 0 | 4.9866 | 28.043 | 24.3899 | 17.5295 | 4.9866 | 0 | 0 | Offer signed 30/05/2025.
ANCOATS NORTH T11 & T12 | 6.6 | RED BANK | RED BANK | WHITEGATE | 385022 | 398830 | 400 | 4.5726 | 0 | 1.8213 | 30.4401 | 6.2106 | 4.5314 | 1.8213 | 4.8939 | 0.33304 | offer signed 25/04/2025
ANCOATS NORTH T14 | 6.6 | RED BANK | RED BANK | WHITEGATE | 385032 | 398840 | 400 | 4.5726 | 2.6507 | 7.4007 | 20.6324 | 20.6324 | 15.6013 | 7.4007 | 15.7536 | 7.6053 | offer signed 25/04/2025
ANNIE PIT | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 300011 | 527810 | 400 | 7.621 | 3.3032 | 8.8032 | 7 | 1.9575 | 1.4344 | 7 | 0 | 0 | Offer signed 30/05/2025.
ANSDELL | 6.6 | LYTHAM | LYTHAM | PENWORTHAM | 334416 | 428229 | 800 | 9.1452 | 6.3395 | 9.3395 | 20.488 | 9.4792 | 6.9163 | 9.3395 | 0 | 0 | Offer signed 30/05/2025.
ARDWICK | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 384753 | 397415 | 630 | 7.2019 | 0 | 1.6249 | 11.2179 | 1.9575 | 1.4344 | 1.6249 | 1.4344 | 0 | Offer signed 27/08/2024
ARNSIDE | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 346495 | 478180 | 400 | 7.621 | 0 | 4.9866 | 18.2259 | 18.2259 | 18.2259 | 4.9866 | 0 | 0 | Offer signed 30/05/2025.
ASHTON (GOLBORNE) | 6.6 | ORRELL | ORRELL | WASHWAY FARM / KIRKBY | 357056 | 400663 | 800 | 9.1452 | 0 | 6.4854 | 23.2144 | 9.0851 | 6.6288 | 6.4854 | 5.9845 | 2.5354 | #N/A
ASHTON (RIBBLE) | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 350275 | 430526 | 630 | 7.2019 | 1.2318 | 1.2318 | 4.97 | 1.9575 | 1.4344 | 1.2318 | 1.4344 | 0 | Offer signed 30/05/2025.
ASHTON ON MERSEY | 6.6 | SALE | SALE | CARRINGTON | 377188 | 392252 | 630 | 7.2019 | 8.8931 | 13.4587 | 28.6276 | 8.9051 | 6.4974 | 13.4587 | 6.5315 | 13.4847 | Offer signed 19/05/2025
ASHTON UNDER LYNE T11 & T12 | 6.6 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 393275 | 399319 | 630 | 7.2019 | 5.7604 | 9.8974 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 27/08/2024
ASHTON UNDER LYNE T13 | 6.6 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 393285 | 399329 | 630 | 7.2019 | 6.8413 | 11.5913 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 27/08/2024
ASHWOOD DALE | 6.6 | BUXTON | BUXTON | STALYBRIDGE | 406537 | 373050 | 630 | 7.2019 | 4.8797 | 4.8797 | 31.3492 | 10.1567 | 7.4106 | 4.8797 | 1.3561 | 10.6051 | Offer signed 27/08/2024
ASKAM | 11 | ULVERSTON | ULVERSTON | HARKER | 321558 | 477806 | 630 | 12.0031 | 3.1711 | 10.1511 | 9.4604 | 6.9121 | 4.9679 | 9.4604 | 6.4697 | 8.428 | Offer signed 30/05/2025.
ASKERTON CASTLE | 11 | - | - | HARKER | 354779 | 568913 | 800 | 15.242 | 0.92661 | 1.6266 | 3.1703 | 3.1703 | 3.1703 | 1.6266 | 3.9789 | 1.6295 | Offer signed 30/05/2025.
ASPATRIA | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 314417 | 542840 | 400 | 7.621 | 4.5706 | 6.5706 | 7 | 1.9575 | 1.4344 | 6.5706 | 0 | 0 | Offer signed 30/05/2025.
ATHERTON TOWN CENTRE | 11 | ATHERTON | ATHERTON | KEARSLEY | 367546 | 403338 | 800 | 15.242 | 7.154 | 11.3144 | 29.4172 | 4.8433 | 3.481 | 11.3144 | 3.7461 | 0 | Offer signed 24/12/2024
ATHLETIC ST | 6.6 | BURNLEY | BURNLEY | ROCHDALE | 385381 | 432208 | 400 | 4.5726 | 4.1643 | 7.6643 | 22.2341 | 13.1623 | 9.6036 | 7.6643 | 9.6723 | 7.1892 | Offer signed 06/06/2025.
AVENHAM | 6.6 | PRESTON EAST | PRESTON EAST | PENWORTHAM | 354028 | 429192 | 800 | 9.1452 | 8.3235 | 8.3235 | 11.2179 | 1.9575 | 1.4344 | 8.3235 | 1.4344 | 0 | Offer signed 30/05/2025.
BAGULEY | 11 | SALE | SALE | CARRINGTON | 380562 | 389035 | 400 | 7.621 | 4.9405 | 9.5775 | 30.0378 | 9.7499 | 7.0075 | 9.5775 | 7.6584 | 8.6278 | Offer signed 19/05/2025
BAMBER BRIDGE | 11 | RIBBLE | RIBBLE | PENWORTHAM | 356431 | 426698 | 630 | 12.0031 | 7.0899 | 11.2269 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 10.2623 | Offer signed 30/05/2025.
BARBARA ST | 6.6 | BOLTON | BOLTON | KEARSLEY | 370695 | 407609 | 630 | 7.2019 | 0 | 4.6283 | 11.2179 | 1.9575 | 1.4344 | 4.6283 | 1.4344 | 9.8525 | Offer signed 24/12/2024
BARROW | 11 | BARROW & SANDGATE | BARROW | HARKER | 319709 | 470489 | 630 | 12.0031 | 12.423 | 16.923 | 20.2861 | 9.8049 | 7.1468 | 16.923 | 8.0292 | 18.3194 | Offer signed 30/05/2025.
BARTON DOCK RD | 6.6 | BARTON | BARTON | CARRINGTON | 378864 | 395534 | 630 | 7.2019 | 1.6791 | 7.9291 | 11.2179 | 1.9575 | 1.4344 | 7.9291 | 1.4344 | 10.2441 | Offer signed 19/05/2025
BEDFORD | 11 | ATHERTON | ATHERTON | KEARSLEY | 366258 | 399876 | 800 | 15.242 | 5.0583 | 9.5583 | 28.6587 | 10.0417 | 7.2172 | 9.5583 | 7.2768 | 0 | Offer signed 24/12/2024
BELGRAVE | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 393008 | 403366 | 630 | 7.2019 | 7.5503 | 11.0503 | 22.9812 | 11.5599 | 8.4344 | 11.0503 | 9.5768 | 4.6017 | offer signed 25/04/2025
BENCHILL | 11 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 382454 | 388020 | 400 | 7.621 | 2.2533 | 9.4035 | 10.252 | 1.9575 | 1.4344 | 9.4035 | 1.4344 | 9.8921 | Offer signed 11/03/2025
BENTHAM | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 366887 | 470130 | 400 | 7.621 | 0 | 4.9866 | 6.8631 | 6.8631 | 6.8631 | 4.9866 | 0 | 0 | Offer signed 30/05/2025.
BISPHAM | 6.6 | BISPHAM | BISPHAM | PENWORTHAM | 331655 | 439667 | 630 | 7.2019 | 4.8338 | 9.4708 | 11.2179 | 1.9575 | 1.4344 | 9.4708 | 1.4344 | 10.1499 | Offer signed 30/05/2025.
BLACKBULL | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 353041 | 433005 | 630 | 7.2019 | 7.7012 | 11.8382 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 6.4123 | Offer signed 30/05/2025.
BLACKBURN | 6.6 | BLACKBURN | BLACKBURN | PENWORTHAM | 370584 | 429294 | 400 | 4.5726 | 3.0361 | 7.6731 | 30.4925 | 9.5961 | 7.0016 | 7.6731 | 6.1854 | 10.7604 | Offer signed 30/05/2025.
BLACKFRIARS | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 383030 | 399104 | 630 | 7.2019 | 0 | 0 | 7 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | Offer signed 24/12/2024
BLACKLEY | 6.6 | RED BANK | RED BANK | WHITEGATE | 383882 | 403258 | 630 | 7.2019 | 10.3952 | 15.0322 | 29.6234 | 13.1362 | 9.5845 | 15.0322 | 9.7958 | 15.68 | offer signed 25/04/2025
BLACKPOOL | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 330835 | 435308 | 630 | 7.2019 | 10.0656 | 17.8156 | 34.8269 | 8.637 | 6.3018 | 17.8156 | 6.7082 | 17.439 | Offer signed 30/05/2025.
BOLLINGTON | 11 | MACCLESFIELD | MACCLESFIELD | MACCLESFIELD | 393042 | 377873 | 630 | 12.0031 | 2.9004 | 5.204 | 11.2179 | 1.9575 | 1.4344 | 5.204 | 1.4344 | 0 | offer signed 25/04/2025
BOLTON BY BOWLAND | 11 | PADIHAM | PADIHAM | PADIHAM | 378320 | 449559 | 400 | 7.621 | 0.13732 | 4.6373 | 8.0509 | 8.0509 | 8.0509 | 4.6373 | 8.4802 | 3.8465 | Offer signed 19/05/2025.
BOLTON LE SANDS | 11 | LANCASTER | LANCASTER | HEYSHAM | 347707 | 467237 | 400 | 7.621 | 1.5831 | 1.5831 | 11.2179 | 1.9575 | 1.4344 | 1.5831 | 1.5151 | 5.0572 | Offer with ENW due to be signed 06/06/2025.
BOTANY BAY | 11 | LEYLAND | LEYLAND | PENWORTHAM | 359442 | 418850 | 630 | 12.0031 | 2.3335 | 10.3335 | 19.8952 | 19.8952 | 19.2172 | 10.3335 | 19.2177 | 9.8578 | Offer signed 30/05/2025.
BOW LANE | 11 | LEYLAND | LEYLAND | PENWORTHAM | 354895 | 422392 | 400 | 7.621 | 3.2216 | 7.8586 | 28.2411 | 6.154 | 4.423 | 7.8586 | 3.7567 | 5.6289 | Offer signed 30/05/2025.
BOWATERS | 11 | BARROW & SANDGATE | BARROW | HARKER | 319579 | 472480 | 400 | 7.621 | 13.1507 | 33.6507 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0.31765 | 2.6844 | Offer signed 30/05/2025.
BOWDON | 11 | ALTRINCHAM | ALTRINCHAM | CARRINGTON | 376743 | 386810 | 400 | 7.621 | 7.0123 | 11.6493 | 31.116 | 12.2476 | 8.8026 | 11.6493 | 8.9022 | 10.8219 | Offer signed 19/05/2025
BRADFORD | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 387613 | 397710 | 400 | 4.5726 | 2.7129 | 7.3499 | 11.2179 | 1.9575 | 1.4344 | 7.3499 | 1.4344 | 0 | Offer signed 27/08/2024
BRADSHAWGATE | 6.6 | BOLTON | BOLTON | KEARSLEY | 371891 | 408910 | 400 | 4.5726 | 4.6442 | 20.0523 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | Offer signed 24/12/2024
BRAMHALL | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 389440 | 386463 | 630 | 12.0031 | 5.5526 | 9.0526 | 23.23 | 12.6188 | 9.0694 | 9.0526 | 9.1136 | 8.37 | N/A
BRIDGEWATER | 6.6 | BLOOM ST | BLOOM ST | SOUTH MANCHESTER | 383543 | 397628 | 800 | 9.1452 | 0 | 4.7695 | 31.1793 | 13.2546 | 9.671 | 4.7695 | 9.8568 | 6.6125 | Offer signed 11/03/2025
BRINKSWAY | 6.6 | ADSWOOD | ADSWOOD | BREDBURY | 388434 | 389885 | 400 | 4.5726 | 8.8505 | 13.4875 | 29.828 | 12.9519 | 9.4501 | 13.4875 | 9.4256 | 12.706 | N/A
BROADHEATH | 11 | ALTRINCHAM | ALTRINCHAM | CARRINGTON | 376412 | 389026 | 400 | 7.621 | 12.4081 | 17.3081 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0.31765 | 2.6844 | Offer signed 19/05/2025
BROADWAY | 6.6 | LANCASTER | LANCASTER | HEYSHAM | 344792 | 464471 | 630 | 7.2019 | 1.5831 | 1.5831 | 11.2179 | 1.9575 | 1.4344 | 1.5831 | 1.5151 | 5.0572 | Offer with ENW due to be signed 06/06/2025.
BUCKSHAW | 11 | LEYLAND | LEYLAND | PENWORTHAM | 356748 | 421312 | 630 | 12.0031 | 9.9241 | 14.4241 | 28.5599 | 13.7188 | 9.8599 | 14.4241 | 9.8081 | 10.2615 | Offer signed 30/05/2025.
BURNLEY | 6.6 | BURNLEY | BURNLEY | ROCHDALE | 385569 | 434469 | 400 | 4.5726 | 16.8681 | 16.8681 | 14.763 | 5.2079 | 3.7998 | 14.763 | 3.8058 | 9.6649 | Offer signed 06/06/2025.
BURNLEY CENTRE | 6.6 | BURNLEY | BURNLEY | ROCHDALE | 384308 | 432288 | 630 | 7.2019 | 8.5335 | 8.5335 | 22.463 | 9.7351 | 7.103 | 8.5335 | 6.7909 | 5.3989 | Offer signed 06/06/2025.
BURNLEY NORTH | 6.6 | BURNLEY | BURNLEY | ROCHDALE | 384418 | 434168 | 630 | 7.2019 | 3.0342 | 11.2438 | 17.4329 | 17.4329 | 17.2572 | 11.2438 | 17.1739 | 8.8706 | Offer signed 06/06/2025.
BURROW BECK | 11 | LANCASTER | LANCASTER | HEYSHAM | 347903 | 458401 | 630 | 12.0031 | 0 | 0 | 7.7639 | 1.2783 | 0.91872 | 0 | 0.7451 | 5.0572 | Offer with ENW due to be signed 06/06/2025.
BURSCOUGH BRIDGE | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 344595 | 412486 | 630 | 12.0031 | 0.76792 | 0.76792 | 15.6502 | 8.7464 | 6.2862 | 0.76792 | 4.4683 | 2.8737 | Offer signed 30/05/2025.
BURY TOWN CENTRE | 6.6 | BURY | BURY | KEARSLEY | 380863 | 410807 | 400 | 4.5726 | 7.3412 | 11.4782 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 8.2958 | Offer signed 24/12/2024
BUSHELL ST | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 353809 | 430094 | 400 | 4.5726 | 6.0947 | 10.2347 | 11.2179 | 1.9575 | 1.4344 | 10.2347 | 1.4344 | 9.8954 | Offer signed 30/05/2025.
CAMPBELL ST | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 372937 | 406428 | 630 | 12.0031 | 0 | 8.1339 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 5.9733 | Offer signed 24/12/2024
CANNON ST | 6.6 | RED BANK | RED BANK | WHITEGATE | 384064 | 398635 | 400 | 4.5726 | 4.7518 | 26.6356 | 0.5637 | 0.091424 | 0.066705 | 0.5637 | 0.16545 | 1.3982 | offer signed 25/04/2025
CAPONTREE | 11 | CARLISLE | CARLISLE | HARKER | 352906 | 559671 | 400 | 7.621 | 14.7029 | 17.0399 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 30/05/2025.
CARLETON | 11 | EGREMONT | EGREMONT | HARKER | 308796 | 498305 | 630 | 12.0031 | 2.3061 | 4.8061 | 7.8535 | 7.8535 | 7.8535 | 4.8061 | 8.424 | 5.5206 | Offer signed 30/05/2025.
CARLISLE NORTH | 11 | - | - | HARKER | 338547 | 560280 | 630 | 12.0031 | 3.4968 | 21.8099 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 0.31765 | 1.6795 | Offer signed 30/05/2025.
CARR ST | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 376984 | 401329 | 400 | 7.621 | 0 | 14.0783 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 24/12/2024
CASTLETON | 6.6 | CASTLETON | CASTLETON | ROCHDALE | 388461 | 411290 | 630 | 7.2019 | 8.2876 | 12.9246 | 22.4265 | 3.6373 | 2.6538 | 12.9246 | 2.09 | 9.5109 | Offer signed 06/06/2025.
CATTERALL WATERWORKS | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 349381 | 442178 | 400 | 4.5726 | 0 | 0 | 9.6822 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | Offer signed 30/05/2025.
CECIL ST | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 331301 | 437023 | 630 | 7.2019 | 9.7849 | 14.9749 | 30.93 | 16.3781 | 11.9499 | 14.9749 | 12.1148 | 12.9781 | Offer signed 30/05/2025.
CENTRAL MANCHESTER | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 384852 | 397718 | 630 | 7.2019 | 0 | 7.725 | 11.2179 | 1.9575 | 1.4344 | 7.725 | 1.4344 | 0 | Offer signed 27/08/2024
CHADDERTON | 6.6 | CHADDERTON | CHADDERTON | WHITEGATE | 389161 | 403872 | 400 | 4.5726 | 7.1062 | 7.1062 | 26.9183 | 4.3658 | 3.1854 | 7.1062 | 1.3649 | 0 | offer signed 25/04/2025
CHAMBERHALL | 6.6 | BURY | BURY | KEARSLEY | 380280 | 411215 | 600 | 6.8589 | 4.613 | 9.933 | 11.2179 | 1.9575 | 1.4344 | 9.933 | 1.4344 | 8.4761 | Offer signed 24/12/2024
CHAPEL WHARF | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 383499 | 398634 | 630 | 7.2019 | 0 | 0 | 7 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | Offer signed 24/12/2024
CHASSEN RD | 6.6 | BARTON | BARTON | CARRINGTON | 375542 | 394453 | 630 | 7.2019 | 1.0893 | 11.9893 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | Offer signed 19/05/2025
CHATSWORTH ST | 11 | BARROW & SANDGATE | BARROW | HARKER | 319188 | 470003 | 800 | 15.242 | 6.2556 | 13.6556 | 29.96 | 9.8049 | 7.1849 | 13.6556 | 7.3076 | 14.6753 | Offer signed 30/05/2025.
CHEADLE HEATH | 6.6 | ADSWOOD | ADSWOOD | BREDBURY | 387062 | 389054 | 630 | 7.2019 | 6.0663 | 9.5663 | 20.9814 | 11.2566 | 8.2132 | 9.5663 | 8.0328 | 8.3048 | N/A
CHEADLE HULME | 11 | ADSWOOD | ADSWOOD | BREDBURY | 387386 | 386308 | 630 | 12.0031 | 7.1577 | 11.7947 | 30.94 | 12.9914 | 9.3371 | 11.7947 | 9.2691 | 12.9036 | N/A
CHEETHAM HILL | 6.6 | AGECROFT | AGECROFT | KEARSLEY | 383606 | 402218 | 400 | 4.5726 | 2.2567 | 2.2567 | 22.2495 | 15.2069 | 11.0953 | 2.2567 | 11.1639 | 2.7039 | Offer signed 24/12/2024
CHELFORD | 11 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 382184 | 373490 | 400 | 7.621 | 7.7796 | 14.4696 | 8.008 | 1.9575 | 1.4344 | 8.008 | 1.4344 | 5.768 | Offer signed 11/03/2025
CHESTER RD T11 & T12 | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 381030 | 396165 | 630 | 7.2019 | 0 | 4.2948 | 25.6308 | 9.3399 | 6.8147 | 4.2948 | 5.9831 | 2.9543 | Offer signed 11/03/2025
CHESTER RD T13 | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 381040 | 396175 | 630 | 7.2019 | 8.0071 | 13.2164 | 18.8764 | 18.8764 | 17.1166 | 13.2164 | 17.154 | 12.6129 | Offer signed 11/03/2025
CHORLEY SOUTH | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 358658 | 417041 | 800 | 15.242 | 0.76792 | 0.76792 | 24.192 | 13.3393 | 9.5872 | 0.76792 | 5.1053 | 5.0492 | Offer signed 30/05/2025.
CHORLTON | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 381411 | 393754 | 400 | 4.5726 | 2.2533 | 10.5919 | 10.252 | 1.9575 | 1.4344 | 10.252 | 1.4344 | 9.12 | Offer signed 11/03/2025
CHURCH | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 374687 | 428919 | 800 | 9.1452 | 5.2017 | 12.0017 | 13.899 | 13.899 | 13.899 | 12.0017 | 7.0436 | 11.2916 | Offer signed 19/05/2025.
CIRCLE SQ | 6.6 | Longsight | LONGSIGHT | BREDBURY | 384365 | 397285 | 600 | 6.8589 | 0 | 1.1309 | 24.3736 | 11.7622 | 8.582 | 1.1309
CLARENDON RD | 6.6 | BLACKBURN | BLACKBURN | PENWORTHAM | 369051 | 429883 | 400 | 4.5726 | 2.5947 | 7.2317 | 30.686 | 12.6181 | 9.2065 | 7.2317 | 2.9125 | 3.9899 | Offer signed 30/05/2025.
CLAUGHTON | 11 | LANCASTER | LANCASTER | HEYSHAM | 355872 | 466268 | 630 | 12.0031 | 0.85148 | 1.5831 | 8.1939 | 1.9575 | 1.4344 | 1.5831 | 1.5151 | 3.7068 | Offer with ENW due to be signed 06/06/2025.
BLACKBURN RD CLAYTON | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 374632 | 430529 | 630 | 7.2019 | 11.6124 | 19.2924 | 25.1053 | 10.7308 | 7.8295 | 19.2924 | 7.0436 | 19.3058 | Offer signed 19/05/2025.
CLEVELEYS | 6.6 | BISPHAM | BISPHAM | PENWORTHAM | 332286 | 443104 | 630 | 7.2019 | 5.0638 | 8.5638 | 11.2179 | 1.9575 | 1.4344 | 8.5638 | 1.4344 | 7.8631 | Offer signed 30/05/2025.
CLIFTON JUNCTION | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 379289 | 403073 | 630 | 12.0031 | 0 | 8.0004 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 4.7605 | Offer signed 24/12/2024
CLOVER HILL | 6.6 | NELSON | NELSON | PADIHAM | 386638 | 437064 | 630 | 7.2019 | 4.9506 | 18.8858 | 0 | 0 | 0 | 0 | 0 | 0 | Offer signed 19/05/2025.
COG LANE | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 382462 | 432232 | 800 | 9.1452 | 6.6328 | 17.0577 | 42.9095 | 8.539 | 6.2303 | 17.0577 | 1.845 | 13.1837 | Offer signed 19/05/2025.
CONISTON | 11 | ULVERSTON | ULVERSTON | HARKER | 329874 | 497641 | 400 | 7.621 | 0 | 1.0875 | 4.6538 | 4.6538 | 4.6538 | 1.0875 | 4.8516 | 1.4303 | Offer signed 30/05/2025.
COPSE RD | 6.6 | THORNTON | THORNTON | STANAH | 333013 | 446934 | 630 | 7.2019 | 5.3706 | 7.0076 | 22.6584 | 4.6408 | 3.3861 | 7.0076 | 2.296 | 3.1319 | offer signed 25/04/2025
COX GREEN | 11 | BOLTON | BOLTON | KEARSLEY | 371893 | 413641 | 630 | 12.0031 | 4.6442 | 9.5576 | 11.2179 | 1.9575 | 1.4344 | 9.5576 | 1.4344 | 8.1583 | Offer signed 24/12/2024
CRAGGS ROW | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 353740 | 430080 | 630 | 7.2019 | 5.7815 | 9.9215 | 11.2179 | 1.9575 | 1.4344 | 9.9215 | 1.4344 | 9.0804 | Offer signed 30/05/2025.
CROWN LANE | 11 | WESTHOUGHTON | WESTHOUGHTON | KEARSLEY | 362706 | 410859 | 400 | 7.621 | 4.8238 | 9.4608 | 31.7685 | 6.9189 | 4.9727 | 9.4608 | 0.088852 | 0 | Offer signed 24/12/2024
CULCHETH | 11 | GOLBORNE | GOLBORNE | BOLD | 365430 | 395366 | 400 | 7.621 | 0 | 0.66907 | 13.4825 | 11.63 | 8.5223 | 0.66907 | 0 | 0 | N/A
CUTACRE | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 369848 | 404515 | 630 | 12.0031 | 0 | 6.4941 | 7 | 1.9575 | 1.4344 | 6.4941 | 1.4344 | 7 | Offer signed 24/12/2024
DALTON | 11 | ULVERSTON | ULVERSTON | HARKER | 323582 | 474255 | 400 | 7.621 | 3.1711 | 10.6511 | 30.2025 | 15.5094 | 11.1469 | 10.6511 | 11.6712 | 8.928 | Offer signed 30/05/2025.
DEANSGATE | 6.6 | BLOOM ST | BLOOM ST | SOUTH MANCHESTER | 383463 | 398149 | 630 | 7.2019 | 0 | 8.7294 | 29.546 | 12.5418 | 9.1508 | 8.7294 | 9.1618 | 11.3246 | Offer signed 11/03/2025
DENTON EAST | 6.6 | DROYLSDEN | DROYLSDEN | STALYBRIDGE | 392394 | 395626 | 630 | 7.2019 | 10.6347 | 15.2717 | 0.74872 | 0.13065 | 0.095738 | 0.74872 | 1.4344 | 11.2179 | Offer signed 27/08/2024
DENTON WEST | 6.6 | DROYLSDEN | DROYLSDEN | STALYBRIDGE | 390380 | 395565 | 400 | 4.5726 | 7.0041 | 11.6411 | 0.74872 | 0.13065 | 0.095738 | 0.74872 | 1.4344 | 11.2179 | Offer signed 27/08/2024
DICKINSON ST T11 & T12 | 6.6 | Bloom St | BLOOM ST | SOUTH MANCHESTER | 384109 | 397722 | 800 | 9.1452 | 0 | 14.694 | 37.0726 | 12.4862 | 9.1103 | 14.694
DICKINSON ST T13 | 6.6 | Stuart Street | STUART ST | STALYBRIDGE | 384109 | 397722 | 800 | 9.1452 | 10.3474 | 24.3474 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 9.5067 | 5.4068 | Offer signed 27/08/2024
DIDSBURY | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 384792 | 391153 | 630 | 7.2019 | 2.2533 | 12.2919 | 10.252 | 1.9575 | 1.4344 | 10.252 | 1.4344 | 11.2179 | Offer signed 11/03/2025
DODGSON RD | 6.6 | PRESTON EAST | PRESTON EAST | PENWORTHAM | 355190 | 430397 | 400 | 4.5726 | 8.3235 | 8.3235 | 11.2179 | 1.9575 | 1.4344 | 8.3235 | 1.4344 | 0 | Offer signed 30/05/2025.
DOUGLAS ST | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 352220 | 429932 | 400 | 4.5726 | 7.346 | 14.006 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | Offer signed 30/05/2025.
DROYLSDEN EAST | 6.6 | DROYLSDEN | DROYLSDEN | STALYBRIDGE | 390532 | 398053 | 630 | 7.2019 | 7.4895 | 12.1295 | 0.74872 | 0.13065 | 0.095738 | 0.74872 | 1.4344 | 9.4097 | Offer signed 27/08/2024
DUKINFIELD | 6.6 | HYDE | HYDE | STALYBRIDGE | 394372 | 396438 | 400 | 4.5726 | 9.8907 | 15.5552 | 22.877 | 3.7103 | 2.7072 | 15.5552 | 2.6715 | 15.6217 | Offer signed 27/08/2024
DUMERS LANE | 11 | BURY | BURY | KEARSLEY | 380057 | 408141 | 400 | 7.621 | 6.4044 | 12.9044 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 7.2779 | Offer signed 24/12/2024
DUMPLINGTON | 11 | BARTON | BARTON | CARRINGTON | 376770 | 397157 | 800 | 15.242 | 13.1574 | 14.5574 | 6.9123 | 1.1381 | 0.81794 | 6.9123 | 0.99981 | 8.4492 | Offer signed 19/05/2025
EASTLANDS | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 386458 | 398693 | 800 | 9.1452 | 2.837 | 7.474 | 0 | 0 | 0 | 0 | 0 | 0 | Offer signed 27/08/2024
EASTON | 11 | - | - | HARKER | 343201 | 571738 | 800 | 15.242 | 0 | 0 | 2.5014 | 2.5014 | 2.5014 | 0 | 2.8786 | 0 | Offer signed 30/05/2025.
EGREMONT | 11 | EGREMONT | EGREMONT | HARKER | 301070 | 513074 | 400 | 7.621 | 2.6806 | 5.1806 | 19.8329 | 17.002 | 12.2197 | 5.1806 | 12.6319 | 4.995 | Offer signed 30/05/2025.
EMBLETON | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 315767 | 529389 | 630 | 12.0031 | 3.7531 | 14.7531 | 7 | 1.9575 | 1.4344 | 7 | 0 | 0 | Offer signed 30/05/2025.
EXCHANGE ST | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 369100 | 423028 | 800 | 9.1452 | 2.4355 | 5.9355 | 21.4846 | 3.749 | 2.7472 | 5.9355 | 0 | 0 | Offer signed 06/06/2025.
FAILSWORTH | 6.6 | CHADDERTON | CHADDERTON | WHITEGATE | 389631 | 401496 | 400 | 4.5726 | 7.1062 | 7.1062 | 28.0798 | 9.1092 | 6.6751 | 7.1062 | 1.3649 | 0 | offer signed 25/04/2025
FALLOWFIELD | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 385608 | 393881 | 400 | 4.5726 | 2.2533 | 8.0277 | 10.252 | 1.9575 | 1.4344 | 8.0277 | 1.4344 | 11.2006 | Offer signed 11/03/2025
FARNWORTH | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 373726 | 405532 | 800 | 15.242 | 0 | 13.5631 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 24/12/2024
FENISCOWLES | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 364660 | 425120 | 630 | 7.2019 | 3.0003 | 15.3003 | 18.5862 | 3.749 | 2.7472 | 15.3003 | 0 | 0 | Offer signed 06/06/2025.
FERODO | 11 | NEW MILLS | NEW MILLS | STALYBRIDGE | 405720 | 381338 | 630 | 12.0031 | 3.8546 | 14.8146 | 28.4985 | 15.8974 | 11.4258 | 14.8146 | 11.2192 | 5.6473 | Offer signed 27/08/2024
FLAT LANE | 11 | PADIHAM | NELSON | PADIHAM | 383248 | 456995 | 630 | 12.0031 | 0 | 5.29 | 10.8314 | 10.8314 | 10.8314 | 5.29 | 11.0501 | 4.4257 | Offer signed 19/05/2025.
FREDERICK RD | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 381697 | 399348 | 800 | 9.1452 | 0 | 0 | 7 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | Offer signed 24/12/2024
FUSEHILL | 11 | CARLISLE | CARLISLE | HARKER | 341042 | 555452 | 400 | 7.621 | 3.7009 | 10.2009 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 30/05/2025.
GALE | 6.6 | BELFIELD | BELFIELD | ROCHDALE | 389570 | 414943 | 400 | 4.5726 | 12.7975 | 17.4345 | 29.2305 | 12.1907 | 8.8946 | 17.4345 | 8.6697 | 0 | Offer signed 06/06/2025.
GARSTANG | 6.6 | THORNTON | THORNTON | STANAH | 348319 | 445221 | 630 | 7.2019 | 1.0033 | 1.0033 | 14.3446 | 10.4385 | 7.6492 | 1.0033 | 9.0987 | 0.2593 | offer signed 25/04/2025
GATLEY | 6.6 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 384242 | 388388 | 400 | 4.5726 | 1.5604 | 12.0604 | 8.008 | 1.9575 | 1.4344 | 8.008 | 1.4344 | 5.768 | Offer signed 11/03/2025
GIDLOW | 6.6 | WIGAN | WIGAN | KIRKBY | 357620 | 406662 | 400 | 4.5726 | 4.1079 | 8.7449 | 30.7035 | 13.514 | 9.8602 | 8.7449 | 8.9257 | 9.6892 | Offer signed 27/08/2024
GILLSROW | 11 | PENRITH & SHAP | PENRITH | HUTTON | 337117 | 526444 | 630 | 12.0031 | 0.75526 | 2.9553 | 7.9428 | 7.9428 | 7.9428 | 2.9553 | 7.4769 | 2.881 | Offer signed 30/05/2025.
GLAXO | 11 | ULVERSTON | ULVERSTON | HARKER | 330458 | 477825 | 400 | 7.621 | 8.3417 | 20.2917 | 11.341 | 1.8672 | 1.342 | 11.341 | 1.4212 | 12.0107 | Offer signed 30/05/2025.
GLOSSOP | 11 | HYDE | HYDE | STALYBRIDGE | 402300 | 394074 | 630 | 12.0031 | 9.0205 | 13.6575 | 30.2187 | 5.5025 | 4.0321 | 13.6575 | 5.4751 | 12.055 | Offer signed 27/08/2024
GOLBORNE T11 & T12 | 11 | GOLBORNE | GOLBORNE | BOLD | 360621 | 397766 | 800 | 15.242 | 7.9618 | 13.4618 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0 | 0 | N/A
GOWHOLE | 11 | NEW MILLS | NEW MILLS | STALYBRIDGE | 401104 | 383846 | 400 | 7.621 | 4.6602 | 4.6602 | 24.7724 | 8.8265 | 6.3437 | 4.6602 | 7.0494 | 5.6473 | Offer signed 27/08/2024
GRANE RD | 6.6 | ROSSENDALE | ROSSENDALE | PADIHAM | 378312 | 422726 | 400 | 4.5726 | 10.2903 | 15.3903 | 24.5658 | 6.4256 | 4.6883 | 15.3903 | 5.885 | 14.3872 | Offer signed 19/05/2025.
GRANGE | 11 | ULVERSTON | ULVERSTON | HARKER | 340240 | 478314 | 400 | 7.621 | 4.9843 | 10.9843 | 21.0377 | 21.0377 | 18.9348 | 10.9843 | 19.5311 | 10.7263 | Offer signed 30/05/2025.
GREAT HARWOOD | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 373765 | 431955 | 630 | 7.2019 | 10.5713 | 18.6913 | 18.2668 | 3.3946 | 2.4768 | 18.2668 | 1.1085 | 9.368 | Offer signed 19/05/2025.
GREEN LANE (ALTRINCHAM) | 11 | ALTRINCHAM | ALTRINCHAM | CARRINGTON | 378744 | 387772 | 400 | 7.621 | 6.4151 | 11.0521 | 31.082 | 15.6665 | 11.2598 | 11.0521 | 11.1508 | 10.8283 | Offer signed 19/05/2025
GREEN LANE (HAZEL GROVE) | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 391570 | 387132 | 400 | 7.621 | 1.1 | 5.737 | 31.3043 | 8.7907 | 6.318 | 5.737 | 5.6166 | 0.45951 | N/A
GREEN ST T11 | 6.6 | WIGAN | WIGAN | KIRKBY | 358235 | 404898 | 630 | 7.2019 | 2.5936 | 6.5936 | 18.7496 | 18.7496 | 17.6707 | 6.5936 | 4.1968 | 3.8848 | Offer signed 27/08/2024
GREEN ST T12 & T13 | 6.6 | WIGAN | WIGAN | KIRKBY | 358225 | 404888 | 630 | 7.2019 | 3.6086 | 9.1486 | 32.334 | 8.9093 | 6.5005 | 9.1486 | 5.7981 | 10.2071 | Offer signed 27/08/2024
GREENFIELD | 11 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 399322 | 404583 | 800 | 15.242 | 13.1685 | 17.6685 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 27/08/2024
GREENHILL | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 393262 | 404755 | 400 | 4.5726 | 14.1596 | 25.6143 | 61.0138 | 9.8956 | 7.2201 | 25.6143 | 6.8407 | 4.6017 | offer signed 25/04/2025
GRIFFIN | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 367171 | 427130 | 800 | 9.1452 | 3.3041 | 12.0373 | 21.4846 | 3.749 | 2.7472 | 12.0373 | 0 | 0 | Offer signed 06/06/2025.
HADFIELD | 11 | HYDE | HYDE | STALYBRIDGE | 401790 | 395876 | 400 | 7.621 | 11.0707 | 17.4582 | 7.6746 | 1.2636 | 0.90815 | 7.6746 | 0.83754 | 7.0779 | Offer signed 27/08/2024
HALL CROSS | 6.6 | PEEL | PEEL | PENWORTHAM | 342288 | 430650 | 630 | 7.2019 | 1.3796 | 4.2579 | 21.8282 | 10.3734 | 7.5687 | 4.2579 | 0 | 0 | Offer signed 30/05/2025.
HANDFORTH | 11 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 385958 | 383397 | 400 | 7.621 | 6.7054 | 11.3424 | 8.008 | 1.9575 | 1.4344 | 8.008 | 1.4344 | 5.768 | Offer signed 11/03/2025
HANGING BRIDGE | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 346186 | 417486 | 630 | 12.0031 | 0.76792 | 0.76792 | 11.1668 | 11.1668 | 11.1668 | 0.76792 | 5.1053 | 5.1053 | Offer signed 30/05/2025.
HAREHOLME | 6.6 | ROSSENDALE | ROSSENDALE | PADIHAM | 382535 | 422283 | 800 | 9.1452 | 8.2232 | 12.8602 | 29.5331 | 12.6687 | 9.2434 | 12.8602 | 9.5452 | 9.9239 | Offer signed 19/05/2025.
HARPURHEY | 6.6 | RED BANK | RED BANK | WHITEGATE | 385907 | 402469 | 400 | 4.5726 | 10.8498 | 15.4898 | 30.096 | 12.3604 | 9.0185 | 15.4898 | 9.1946 | 15.552 | offer signed 25/04/2025
HARWOOD | 11 | BOLTON | BOLTON | KEARSLEY | 374043 | 410941 | 400 | 7.621 | 1.9387 | 6.2387 | 11.2179 | 1.9575 | 1.4344 | 6.2387 | 1.4344 | 7.187 | Offer signed 24/12/2024
HATTERSLEY | 11 | HYDE | HYDE | STALYBRIDGE | 398419 | 395120 | 800 | 15.242 | 0 | 0 | 15.3048 | 4.7076 | 3.3834 | 0 | 3.4214 | 6.4802 | Offer signed 27/08/2024
HAVERTHWAITE | 11 | ULVERSTON | ULVERSTON | HARKER | 334234 | 483827 | 630 | 12.0031 | 4.6691 | 7.1691 | 13.0313 | 13.0313 | 13.0313 | 7.1691 | 13.0026 | 6.7952 | Offer signed 30/05/2025.
HAWK GREEN | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 395915 | 387138 | 630 | 12.0031 | 12.5909 | 17.0909 | 30.012 | 16.9291 | 12.1673 | 17.0909 | 12.0132 | 15.4515 | N/A
HAYDOCK | 11 | GOLBORNE | GOLBORNE | BOLD | 357489 | 397336 | 630 | 12.0031 | 3.675 | 11.7479 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0 | 0 | N/A
HDA NO1 | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 301743 | 524532 | 400 | 7.621 | 13.9779 | 20.1979 | 3.8254 | 0.62982 | 0.45267 | 3.8254 | 0 | 0 | Offer signed 30/05/2025.
HDA NO2 | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 301429 | 525527 | 630 | 12.0031 | 13.9779 | 20.1979 | 7 | 1.9575 | 1.4344 | 7 | 0 | 0 | Offer signed 30/05/2025.
HEADY HILL | 6.6 | CASTLETON | CASTLETON | ROCHDALE | 384370 | 410583 | 400 | 4.5726 | 7 | 10.5 | 22.919 | 10.078 | 7.3532 | 10.5 | 7.0425 | 7.7035 | Offer signed 06/06/2025.
HEAP BRIDGE | 6.6 | BURY | BURY | KEARSLEY | 382793 | 410428 | 400 | 4.5726 | 6.8636 | 6.8636 | 7.09 | 1.9575 | 1.4344 | 6.8636 | 1.4344 | 2.695 | Offer signed 24/12/2024
HEASANDFORD | 6.6 | BURNLEY | BURNLEY | ROCHDALE | 385349 | 433821 | 400 | 4.5726 | 8.6745 | 17.8845 | 29.2282 | 9.0582 | 6.6091 | 17.8845 | 0 | 0 | Offer signed 06/06/2025.
HEATON MOOR | 6.6 | VERNON PARK | VERNON PARK | BREDBURY | 387623 | 391345 | 630 | 7.2019 | 1.1685 | 1.1685 | 29.5497 | 9.7233 | 7.0944 | 1.1685 | 7.1221 | 0 | N/A
HEATON NORRIS | 6.6 | VERNON PARK | VERNON PARK | BREDBURY | 388860 | 391967 | 400 | 4.5726 | 1.1685 | 1.1685 | 24.1427 | 4.7323 | 3.4528 | 1.1685 | 3.0681 | 0 | N/A
HELWITH BRIDGE | 11 | PADIHAM | PADIHAM | PADIHAM | 381025 | 469428 | 630 | 12.0031 | 0 | 7.8845 | 12.5457 | 12.5457 | 12.5457 | 7.8845 | 13.2972 | 8.3367 | Offer signed 19/05/2025.
HENSINGHAM | 11 | EGREMONT | EGREMONT | HARKER | 298465 | 517239 | 630 | 12.0031 | 13.8842 | 18.0212 | 24.8375 | 12.1136 | 8.7063 | 18.0212 | 9.101 | 17.1039 | Offer signed 30/05/2025.
HEYROD | 6.6 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 397310 | 399981 | 600 | 6.8589 | 9.0174 | 13.6544 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 27/08/2024
HEYSIDE | 6.6 | ROYTON | ROYTON | WHITEGATE | 393433 | 407129 | 400 | 4.5726 | 4.0744 | 14.564 | 0 | 0 | 0 | 0 | 0 | 0 | offer signed 25/04/2025
HEYWOOD | 6.6 | CASTLETON | CASTLETON | ROCHDALE | 385429 | 410369 | 630 | 7.2019 | 5.2236 | 7.2978 | 16.361 | 2.6535 | 1.9361 | 7.2978 | 1.2885 | 0 | Offer signed 06/06/2025.
HIGHER MILL | 6.6 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 385731 | 388090 | 400 | 4.5726 | 4.5549 | 12.0549 | 8.008 | 1.9575 | 1.4344 | 8.008 | 1.4344 | 5.768 | Offer signed 11/03/2025
HIGHER WALTON | 11 | LEYLAND | LEYLAND | PENWORTHAM | 358020 | 427270 | 400 | 7.621 | 3.1244 | 7.7614 | 22.8687 | 5.4258 | 3.8996 | 7.7614 | 3.7037 | 4.126 | Offer signed 30/05/2025.
HILL TOP T11 & T12 | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 373466 | 403748 | 400 | 7.621 | 0 | 6.0298 | 7 | 1.9575 | 1.4344 | 6.0298 | 1.4344 | 7 | Offer signed 24/12/2024
HILL TOP T13 | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 373476 | 403758 | 400 | 7.621 | 0 | 0.6094 | 6.1239 | 1.9575 | 1.4344 | 0.6094 | 1.4344 | 0.95096 | Offer signed 24/12/2024
HINDLEY GREEN | 11 | ATHERTON | ATHERTON | KEARSLEY | 363389 | 403254 | 630 | 12.0031 | 6.504 | 11.3144 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0.31765 | 0 | Offer signed 24/12/2024
HOLLINWOOD | 6.6 | CHADDERTON | CHADDERTON | WHITEGATE | 390287 | 402592 | 630 | 7.2019 | 7.1062 | 7.1062 | 27.0457 | 7.3597 | 5.3698 | 7.1062 | 1.3649 | 0 | offer signed 25/04/2025
HOLME RD | 11 | RIBBLE | RIBBLE | PENWORTHAM | 352311 | 429141 | 400 | 7.621 | 7.6426 | 11.7796 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | Offer signed 30/05/2025.
HOLT ST | 11 | BURY | BURY | KEARSLEY | 378620 | 416362 | 630 | 12.0031 | 4.911 | 8.411 | 11.2179 | 1.9575 | 1.4344 | 8.411 | 1.4344 | 6.5258 | Offer signed 24/12/2024
HURST | 6.6 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 394658 | 400360 | 630 | 7.2019 | 6.1773 | 9.6773 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 27/08/2024
HUTTON END | 11 | PENRITH & SHAP | PENRITH | HUTTON | 345810 | 538827 | 630 | 12.0031 | 10.228 | 17.9247 | 20.1869 | 20.1869 | 16.4971 | 17.9247 | 17.2503 | 13.3736 | Offer signed 30/05/2025.
HYDE | 6.6 | HYDE | HYDE | STALYBRIDGE | 395215 | 395126 | 630 | 7.2019 | 6.0507 | 10.6877 | 31.5333 | 5.5025 | 4.0321 | 10.6877 | 5.4751 | 11.4433 | Offer signed 27/08/2024
HYNDBURN RD | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 375688 | 428877 | 800 | 9.1452 | 4.9013 | 17.2013 | 29.528 | 13.5627 | 9.8957 | 17.2013 | 7.0436 | 17.6125 | Offer signed 19/05/2025.
INDIA ST | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 369485 | 421865 | 400 | 4.5726 | 3.3041 | 18.2793 | 21.4846 | 3.749 | 2.7472 | 18.2793 | 0 | 0 | Offer signed 06/06/2025.
INGLETON | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 368913 | 472337 | 630 | 12.0031 | 0 | 4.9866 | 12.571 | 12.571 | 12.571 | 4.9866 | 0 | 0 | Offer signed 30/05/2025.
IRLAM | 6.6 | CARRINGTON BSP | CARRINGTON BSP | CARRINGTON | 371680 | 393360 | 1250 | 14.2894 | 2.595 | 6.735 | 11.2179 | 1.9575 | 1.4344 | 6.735 | 1.4344 | 4.4053 | Offer signed 19/05/2025
JAMES ST | 11 | CARLISLE | CARLISLE | HARKER | 340034 | 555418 | 630 | 12.0031 | 5.1976 | 9.3346 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 30/05/2025.
KAY ST | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 373863 | 427594 | 630 | 7.2019 | 13.7162 | 17.8532 | 28.7026 | 13.3438 | 9.736 | 17.8532 | 7.0436 | 16.5205 | Offer signed 19/05/2025.
KENDAL | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 351915 | 491858 | 400 | 7.621 | 0 | 4.9866 | 28.1086 | 9.3279 | 6.7042 | 4.9866 | 0 | 0 | Offer signed 30/05/2025.
KESWICK | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 327022 | 523784 | 400 | 7.621 | 5.4573 | 7.9573 | 7 | 1.9575 | 1.4344 | 7 | 0 | 0 | Offer signed 30/05/2025.
KINGSWAY | 11 | BELFIELD | BELFIELD | ROCHDALE | 391636 | 411724 | 630 | 12.0031 | 20.2509 | 28.3165 | 46.9796 | 8.1389 | 5.8496 | 28.3165 | 1.6009 | 0 | Offer signed 06/06/2025.
KINKRY HILL | 11 | - | - | HARKER | 350800 | 575111 | 800 | 15.242 | 0.78604 | 2.286 | 3.1482 | 3.1482 | 3.1482 | 2.286 | 3.1954 | 2.3112 | Offer signed 30/05/2025.
KIRKBY LONSDALE | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 359833 | 478813 | 400 | 7.621 | 0 | 4.9866 | 13.064 | 13.064 | 13.064 | 4.9866 | 0 | 0 | Offer signed 30/05/2025.
KIRKBY MOOR | 11 | ULVERSTON | ULVERSTON | HARKER | 326099 | 483011 | 1250 | 23.8157 | 2.2497 | 5.7497 | 2.6498 | 2.6498 | 2.6498 | 2.6498 | 2.8987 | 2.8987 | Offer signed 30/05/2025.
KIRKBY STEPHEN | 11 | PENRITH & SHAP | PENRITH | HUTTON | 376579 | 509136 | 800 | 15.242 | 9.707 | 12.2786 | 18.2988 | 18.2988 | 18.2988 | 12.2786 | 19.5904 | 10.2783 | Offer signed 30/05/2025.
KIRKBY THORE | 11 | PENRITH & SHAP | PENRITH | HUTTON | 364439 | 526672 | 630 | 12.0031 | 4.3762 | 15.6262 | 30.0186 | 24.0694 | 17.2991 | 15.6262 | 18.6543 | 13.2545 | Offer signed 30/05/2025.
KIRKHALL LANE | 11 | ATHERTON | ATHERTON | KEARSLEY | 365510 | 401069 | 400 | 7.621 | 3.7309 | 6.0809 | 20.9284 | 11.3788 | 8.1782 | 6.0809 | 8.0695 | 0 | Offer signed 24/12/2024
KITT GREEN | 6.6 | ORRELL | ORRELL | KIRKBY | 354934 | 405497 | 400 | 4.5726 | 0 | 11.5881 | 31.455 | 12.7156 | 9.2776 | 11.5881 | 9.0797 | 10.8837 | Offer signed 27/08/2024
KNOTT MILL | 6.6 | BLOOM ST | BLOOM ST | SOUTH MANCHESTER | 383136 | 397725 | 800 | 9.1452 | 0 | 0.42268 | 29.6802 | 6.9329 | 5.0584 | 0.42268 | 4.9077 | 0 | Offer signed 11/03/2025
LAMBERHEAD | 6.6 | ORRELL | ORRELL | KIRKBY | 355516 | 404030 | 630 | 7.2019 | 0 | 14.25 | 22.9643 | 9.926 | 7.2423 | 14.25 | 7.0795 | 15.6051 | Offer signed 27/08/2024
LANCASTER | 11 | LANCASTER | LANCASTER | HEYSHAM | 348644 | 463628 | 630 | 12.0031 | 1.3152 | 1.5831 | 11.2179 | 1.9575 | 1.4344 | 1.5831 | 1.5151 | 5.0572 | Offer with ENW due to be signed 06/06/2025.
LANGLEY | 11 | CHADDERTON | CHADDERTON | WHITEGATE | 386421 | 406330 | 400 | 7.621 | 2.8029 | 7.1062 | 30.767 | 9.1092 | 6.6751 | 7.1062 | 1.3649 | 0 | offer signed 25/04/2025
LANGROYD RD | 6.6 | NELSON | NELSON | PADIHAM | 389077 | 440584 | 400 | 4.5726 | 4.9506 | 14.636 | 0 | 0 | 0 | 0 | 0 | 0 | Offer signed 19/05/2025.
LEIGH | 11 | ATHERTON | ATHERTON | KEARSLEY | 365863 | 399907 | 800 | 15.242 | 3.9483 | 11.3144 | 19.4736 | 19.4736 | 19.4736 | 11.3144 | 19.6186 | 0 | Offer signed 24/12/2024
LEVENSHULME | 6.6 | LONGSIGHT | LONGSIGHT | BREDBURY | 387494 | 394155 | 400 | 4.5726 | 0 | 1.1309 | 24.1017 | 13.7733 | 10.0494 | 1.1309 | 10.1941 | 6.1719 | N/A
LEYLAND NATIONAL | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 301973 | 525948 | 400 | 7.621 | 14.2059 | 21.7602 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0 | 0 | Offer signed 30/05/2025.
LITTLE HULTON | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 372024 | 403826 | 630 | 12.0031 | 0 | 4.4798 | 7 | 1.9575 | 1.4344 | 4.4798 | 1.4344 | 4.4466 | Offer signed 24/12/2024
LITTLE SALKELD | 11 | PENRITH & SHAP | PENRITH | HUTTON | 356221 | 537513 | 400 | 7.621 | 2.6317 | 5.0248 | 15.5468 | 15.5468 | 15.5468 | 5.0248 | 16.5605 | 4.0762 | Offer signed 30/05/2025.
LITTLEBOROUGH | 6.6 | BELFIELD | BELFIELD | ROCHDALE | 393221 | 416124 | 400 | 4.5726 | 1.847 | 5.347 | 24.361 | 9.7822 | 7.1374 | 5.347 | 6.9929 | 0 | Offer signed 06/06/2025.
LONGFORD BRIDGE | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 380056 | 395083 | 800 | 9.1452 | 7.9112 | 12.5482 | 30.347 | 7.8159 | 5.7027 | 12.5482 | 5.7031 | 10.4658 | Offer signed 11/03/2025
LONGRIDGE | 6.6 | PRESTON EAST | PRESTON EAST | PENWORTHAM | 360581 | 437001 | 400 | 4.5726 | 8.3235 | 8.3235 | 11.2179 | 1.9575 | 1.4344 | 8.3235 | 1.4344 | 0 | Offer signed 30/05/2025.
LONGSIGHT | 6.6 | LONGSIGHT | LONGSIGHT | BREDBURY | 385535 | 396037 | 400 | 4.5726 | 0 | 1.1309 | 27.5509 | 5.5636 | 4.0594 | 1.1309 | 2.8907 | 9.1882 | N/A
LOSTOCK | 11 | WESTHOUGHTON | WESTHOUGHTON | KEARSLEY | 365293 | 409079 | 800 | 15.242 | 4.4357 | 10.4357 | 35.2852 | 5.8094 | 4.1754 | 10.4357 | 0.088852 | 0 | Offer signed 24/12/2024
LOWER DARWEN | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 369695 | 424981 | 800 | 9.1452 | 3.3041 | 17.6772 | 21.4846 | 3.749 | 2.7472 | 17.6772 | 0 | 0 | Offer signed 06/06/2025.
LYONS RD | 6.6 | BARTON | BARTON | CARRINGTON | 378253 | 397241 | 400 | 4.5726 | 0 | 1.2369 | 11.2179 | 1.9575 | 1.4344 | 1.2369 | 1.4344 | 10.6576 | Offer signed 19/05/2025
MANCHESTER UNIVERSITY | 6.6 | LONGSIGHT | LONGSIGHT | BREDBURY | 384762 | 396769 | 800 | 9.1452 | 0 | 1.0641 | 31.7708 | 10.425 | 7.6063 | 1.0641 | 7.4513 | 1.5496 | N/A
MARPLE | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 395671 | 388643 | 630 | 12.0031 | 0.01064 | 0.01064 | 6.1203 | 6.1203 | 6.1203 | 0.01064 | 7.1061 | 0 | N/A
MARTON | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 333341 | 433485 | 400 | 4.5726 | 8.4126 | 13.8152 | 24.4755 | 8.3912 | 6.1225 | 13.8152 | 6.5522 | 14.5624 | Offer signed 30/05/2025.
MARYPORT | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 303716 | 535313 | 630 | 12.0031 | 7.8843 | 17.1847 | 7 | 1.9575 | 1.4344 | 7 | 0 | 0 | Offer signed 30/05/2025.
MELLING | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 360144 | 471643 | 630 | 12.0031 | 0 | 3.5076 | 6 | 6 | 6 | 3.5076 | 0 | 0 | Offer signed 30/05/2025.
MERESIDE | 6.6 | PEEL | PEEL | PENWORTHAM | 334431 | 434843 | 630 | 7.2019 | 4.2579 | 4.2579 | 21.8282 | 12.8846 | 9.401 | 4.2579 | 0 | 0 | Offer signed 30/05/2025.
MIDDLETON JUNCTION | 11 | CHADDERTON | CHADDERTON | WHITEGATE | 388606 | 405292 | 630 | 12.0031 | 4.6028 | 7.1062 | 26.9049 | 4.4297 | 3.1837 | 7.1062 | 1.3649 | 0 | offer signed 25/04/2025
MIDWAY | 11 | EGREMONT | EGREMONT | HARKER | 304525 | 501993 | 630 | 12.0031 | 9.6272 | 12.1822 | 17.71 | 17.71 | 17.71 | 12.1822 | 18.0835 | 11.4916 | Offer signed 30/05/2025.
MILNROW | 6.6 | CASTLETON | CASTLETON | ROCHDALE | 392351 | 413056 | 400 | 4.5726 | 11.8036 | 16.4436 | 29.1338 | 10.1213 | 7.3848 | 16.4436 | 7.4802 | 14.0754 | Offer signed 06/06/2025.
MINTSFEET | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 351827 | 494315 | 400 | 7.621 | 0 | 4.9866 | 15.1484 | 2.4941 | 1.7925 | 4.9866 | 0 | 0 | Offer signed 30/05/2025.
MONSALL | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 386332 | 401003 | 630 | 7.2019 | 5.5654 | 15.0654 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 0 | Offer signed 27/08/2024
MONTON | 6.6 | BARTON | BARTON | CARRINGTON | 376321 | 399494 | 400 | 4.5726 | 4.3122 | 7.8122 | 11.2179 | 1.9575 | 1.4344 | 7.8122 | 1.4344 | 5.0297 | Offer signed 19/05/2025
MOORSIDE | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 349331 | 435746 | 630 | 7.2019 | 1.3385 | 4.8385 | 11.2179 | 1.9575 | 1.4344 | 4.8385 | 1.4344 | 8.9507 | Offer signed 30/05/2025.
MORTON PARK | 11 | CARLISLE | CARLISLE | HARKER | 337826 | 553939 | 1250 | 23.8157 | 6.7947 | 11.2325 | 1.8718 | 0.44197 | 0.31765 | 1.8718 | 0.31765 | 2.6844 | Offer signed 30/05/2025.
MOSLEY RD | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 379058 | 396289 | 630 | 7.2019 | 3.3131 | 6.7974 | 22.2899 | 9.1722 | 6.6923 | 6.7974 | 5.8695 | 0 | Offer signed 11/03/2025
MOSS LANE | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 380858 | 405856 | 400 | 7.621 | 0 | 5.1236 | 7 | 1.9575 | 1.4344 | 5.1236 | 1.4344 | 3.7702 | Offer signed 24/12/2024
MOSS NOOK PRIMARY | 11 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 384084 | 385010 | 800 | 15.242 | 10.2407 | 18.3384 | 8.008 | 1.9575 | 1.4344 | 8.008 | 1.4344 | 5.768 | Offer signed 11/03/2025
MOSS SIDE (Leyland) | 11 | LEYLAND | LEYLAND | PENWORTHAM | 352170 | 422970 | 400 | 7.621 | 3.1192 | 6.4332 | 27.4357 | 12.7753 | 9.1819 | 6.4332 | 9.1199 | 4.5253 | Offer signed 30/05/2025.
MOSS SIDE (Longsight) | 6.6 | LONGSIGHT | LONGSIGHT | BREDBURY | 384007 | 395893 | 400 | 4.5726 | 0 | 0.87234 | 34.7022 | 10.2965 | 7.5126 | 0.87234 | 7.5673 | 1.6732 | N/A
MOSSLEY | 11 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 397437 | 401979 | 400 | 7.621 | 10.433 | 15.07 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 27/08/2024
MOUNT ST | 6.6 | BARTON | BARTON | CARRINGTON | 376250 | 397574 | 400 | 4.5726 | 5.1397 | 9.7766 | 11.2179 | 1.9575 | 1.4344 | 9.7766 | 1.4344 | 8.7054 | Offer signed 19/05/2025
MUSGRAVE RD | 6.6 | BOLTON | BOLTON | KEARSLEY | 370045 | 409863 | 800 | 9.1452 | 4.6442 | 15.0286 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | Offer signed 24/12/2024
NELSON | 6.6 | NELSON | NELSON | PADIHAM | 386020 | 438507 | 400 | 4.5726 | 2.6922 | 6.8322 | 0 | 0 | 0 | 0 | 0 | 0 | Offer signed 19/05/2025.
NEW MOSTON | 6.6 | CHADDERTON | CHADDERTON | WHITEGATE | 388333 | 402657 | 630 | 7.2019 | 7.1062 | 7.1062 | 29.9265 | 9.1092 | 6.6751 | 7.1062 | 1.3649 | 0 | offer signed 25/04/2025
NEWBIGGIN ON LUNE | 11 | PENRITH & SHAP | PENRITH | HUTTON | 369770 | 505803 | 800 | 15.242 | 0.54668 | 2.0467 | 3.1289 | 3.1289 | 3.1289 | 2.0467 | 3.8322 | 2.0546 | Offer signed 30/05/2025.
NEWBY | 11 | PENRITH & SHAP | PENRITH | HUTTON | 360520 | 521151 | 400 | 7.621 | 0.86113 | 7.8611 | 14.9704 | 14.9704 | 14.9704 | 7.8611 | 15.0523 | 7.0631 | Offer signed 30/05/2025.
NEWTON | 11 | HYDE | HYDE | STALYBRIDGE | 396385 | 396464 | 400 | 7.621 | 9.5828 | 14.5828 | 18.5374 | 5.5025 | 4.0321 | 14.5828 | 1.511 | 1.511 | Offer signed 27/08/2024
NEWTON HEATH | 6.6 | CHADDERTON | CHADDERTON | WHITEGATE | 388030 | 400511 | 400 | 4.5726 | 0.70343 | 0.70343 | 12.1464 | 9.1092 | 6.6751 | 0.70343 | 1.3649 | 0 | offer signed 25/04/2025
NEWTON LE WILLOWS | 11 | GOLBORNE | GOLBORNE | BOLD | 357891 | 395944 | 630 | 12.0031 | 5.9012 | 10.0382 | 26.8438 | 11.1538 | 8.0165 | 10.0382 | 0 | 0 | N/A
NEWTONGATE T11 & T12 | 11 | PENRITH & SHAP | PENRITH | HUTTON | 349973 | 530340 | 630 | 12.0031 | 3.6118 | 7.6118 | 32.3339 | 6.6973 | 4.8135 | 7.6118 | 3.841 | 8.6565 | Offer signed 30/05/2025.
NEWTONGATE T13 | 11 | PENRITH & SHAP | PENRITH | HUTTON | 349973 | 530340 | 630 | 12.0031 | 1.1708 | 5.9208 | 20.0079 | 20.0079 | 19.3467 | 5.9208 | 14.4183 | 10.2752 | Offer signed 30/05/2025.
NORBRECK | 6.6 | BISPHAM | BISPHAM | PENWORTHAM | 331831 | 441463 | 400 | 4.5726 | 17.2283 | 23.2687 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | Offer signed 30/05/2025.
NORBURY | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 392447 | 385492 | 400 | 7.621 | 9.5318 | 15.8044 | 8.2926 | 1.3653 | 0.98128 | 8.2926 | 0.56343 | 4.7615 | N/A
NORTHENDEN | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 382555 | 390327 | 400 | 4.5726 | 2.2533 | 11.7351 | 10.252 | 1.9575 | 1.4344 | 10.252 | 1.4344 | 9.31 | Offer signed 11/03/2025
NWGB PARTINGTON | 6.6 | CARRINGTON BSP | CARRINGTON BSP | CARRINGTON | 372569 | 392079 | 400 | 4.5726 | 3.2832 | 8.2232 | 11.2179 | 1.9575 | 1.4344 | 8.2232 | 1.4344 | 10.0382 | Offer signed 19/05/2025
OFFERTON | 6.6 | VERNON PARK | VERNON PARK | BREDBURY | 391010 | 389489 | 400 | 4.5726 | 1.1685 | 1.1685 | 28.6097 | 12.6558 | 9.2341 | 1.1685 | 9.1327 | 0 | N/A
OPENSHAW | 6.6 | DROYLSDEN | DROYLSDEN | STALYBRIDGE | 388606 | 397346 | 630 | 7.2019 | 1.65 | 5.6137 | 0.74872 | 0.13065 | 0.095738 | 0.74872 | 1.4344 | 5.886 | Offer signed 27/08/2024
ORMSKIRK | 11 | SKELMERSDALE | SKELMERSDALE | WASHWAY FARM | 341294 | 408158 | 800 | 15.242 | 8.4153 | 13.0523 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 10.4513 | Offer signed 29/05/2024. Parrallel offer signed 27/08/2024
PADIHAM | 11 | PADIHAM | PADIHAM | PADIHAM | 378428 | 433238 | 400 | 7.621 | 16.9204 | 23.9204 | 7.9459 | 1.3082 | 0.94025 | 7.9459 | 0.84345 | 7.1279 | Offer signed 19/05/2025.
PEEL ST | 11 | PADIHAM | PADIHAM | PADIHAM | 374463 | 441514 | 630 | 12.0031 | 0 | 9.491 | 19.7529 | 19.7529 | 19.7529 | 9.491 | 19.6031 | 8.983 | Offer signed 19/05/2025.
PENDLETON | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 381161 | 398842 | 400 | 4.5726 | 0 | 0 | 7 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | Offer signed 24/12/2024
PETTERIL BANK | 11 | CARLISLE | CARLISLE | HARKER | 341768 | 553686 | 400 | 7.621 | 8.3847 | 12.5217 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 30/05/2025.
PHILLIPS LANE | 6.6 | NELSON | NELSON | PADIHAM | 387571 | 439522 | 800 | 9.1452 | 1.0902 | 10.0902 | 0 | 0 | 0 | 0 | 0 | 0 | Offer signed 19/05/2025.
PICCADILLY | 6.6 | BLOOM ST | BLOOM ST | SOUTH MANCHESTER | 384427 | 398261 | 400 | 4.5726 | 0 | 9.5911 | 30.1358 | 8.5392 | 6.2304 | 9.5911 | 6.0414 | 15.0117 | Offer signed 11/03/2025
PIMBO | 11 | SKELMERSDALE | SKELMERSDALE | WASHWAY FARM | 349148 | 404549 | 400 | 7.621 | 9.5722 | 19.48 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 10.4513 | Offer signed 29/05/2024. Parrallel offer signed 27/08/2024
PIRELLI | 11 | CARLISLE | CARLISLE | HARKER | 339059 | 553548 | 400 | 7.621 | 6.2477 | 10.6855 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 1.4344 | 7 | Offer signed 30/05/2025.
PORTWOOD | 6.6 | VERNON PARK | VERNON PARK | BREDBURY | 389826 | 390619 | 400 | 4.5726 | 1.1685 | 1.1685 | 28.3238 | 9.353 | 6.8242 | 1.1685 | 6.7371 | 0 | N/A
POULTON | 6.6 | BISPHAM | BISPHAM | PENWORTHAM | 335679 | 439130 | 800 | 9.1452 | 7.5974 | 9.5774 | 11.2179 | 1.9575 | 1.4344 | 9.5774 | 1.4344 | 6.9765 | Offer signed 30/05/2025.
POYNTON | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 392096 | 383493 | 630 | 12.0031 | 7.4219 | 10.9219 | 22.616 | 13.2503 | 9.5233 | 10.9219 | 9.4181 | 10.8112 | N/A
PREESALL | 11 | THORNTON | THORNTON | STANAH | 336965 | 446547 | 800 | 15.242 | 12.8862 | 17.3862 | 23.2987 | 10.4385 | 7.6492 | 17.3862 | 9.0987 | 15.8281 | offer signed 25/04/2025
PRESTON EAST | 6.6 | PRESTON EAST | PRESTON EAST | PENWORTHAM | 356777 | 432926 | 630 | 7.2019 | 8.3235 | 8.3235 | 2.6918 | 0.43658 | 0.31854 | 2.6918 | 1.4344 | 0 | Offer signed 30/05/2025.
PRESTON OLD RD | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 332562 | 434929 | 800 | 9.1452 | 11.0951 | 15.7321 | 30.0255 | 11.8009 | 8.6102 | 15.7321 | 8.77 | 17.138 | Offer signed 30/05/2025.
PRESTWICH | 6.6 | AGECROFT | AGECROFT | KEARSLEY | 381392 | 404001 | 400 | 4.5726 | 6.0987 | 10.7357 | 31.527 | 7.9688 | 5.8143 | 10.7357 | 5.8553 | 6.3816 | Offer signed 24/12/2024
PRINGLE ST | 6.6 | BLACKBURN | BLACKBURN | PENWORTHAM | 369088 | 427387 | 400 | 4.5726 | 4.2941 | 11.8541 | 29.7848 | 12.542 | 9.151 | 11.8541 | 8.8549 | 17.2513 | Offer signed 30/05/2025.
PRINNY HILL | 6.6 | ROSSENDALE | ROSSENDALE | PADIHAM | 378328 | 423395 | 630 | 7.2019 | 10.2903 | 15.3903 | 24.5658 | 11.1878 | 8.1629 | 15.3903 | 9.5083 | 14.3872 | Offer signed 19/05/2025.
QUEENS PARK | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 385893 | 400645 | 400 | 4.5726 | 0 | 0.8332 | 11.2179 | 1.9575 | 1.4344 | 0.8332 | 1.4344 | 0 | Offer signed 27/08/2024
RADCLIFFE | 11 | - | - | KEARSLEY | 377524 | 406160 | 400 | 7.621 | 4.3505 | 4.7505 | 44.9335 | 11.7825 | 8.4683 | 4.7505 | 8.7443 | 5.7413 | Offer signed 24/12/2024
RANDAL ST | 6.6 | BLACKBURN | BLACKBURN | PENWORTHAM | 368092 | 428515 | 630 | 7.2019 | 4.8458 | 17.5458 | 32.4488 | 12.803 | 9.3414 | 17.5458 | 8.8192 | 17.3639 | Offer signed 30/05/2025.
RAWTENSTALL RD | 6.6 | ROSSENDALE | ROSSENDALE | PADIHAM | 379395 | 422143 | 630 | 7.2019 | 10.476 | 15.113 | 30.533 | 15.9244 | 11.6189 | 15.113 | 11.7382 | 14.2835 | Offer signed 19/05/2025.
REDDISH VALE | 6.6 | VERNON PARK | VERNON PARK | BREDBURY | 390147 | 393309 | 800 | 9.1452 | 1.1685 | 1.1685 | 29.6625 | 10.0665 | 7.3448 | 1.1685 | 7.0914 | 0 | N/A
RIBBLESDALE T13 & T14 | 11 | PADIHAM | PADIHAM | PADIHAM | 374759 | 443587 | 800 | 15.242 | 1.2757 | 4.0257 | 22.4738 | 16.4266 | 11.8061 | 4.0257 | 11.8923 | 1.683 | Offer signed 19/05/2025.
RIBBLETON | 6.6 | PRESTON EAST | PRESTON EAST | PENWORTHAM | 356730 | 431506 | 630 | 7.2019 | 8.3235 | 8.3235 | 11.2179 | 1.9575 | 1.4344 | 8.3235 | 1.4344 | 0 | Offer signed 30/05/2025.
RINGLEY | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 376120 | 405531 | 630 | 12.0031 | 0 | 14.5751 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 24/12/2024
RISLEY | 11 | - | - | BOLD | 365181 | 392989 | 400 | 7.621 | 0 | 9.7744 | 8.8484 | 1.4568 | 1.047 | 8.8484 | 1.2626 | 4.1747 | N/A
ROBERT HALL ST | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 381359 | 397718 | 400 | 4.5726 | 0 | 0 | 7 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | Offer signed 24/12/2024
ROCHDALE CENTRAL | 6.6 | ROCHDALE CENTRAL | ROCHDALE CENTRAL | ROCHDALE | 389111 | 413393 | 630 | 7.2019 | 22.8493 | 35.8493 | 2.6918 | 0.43658 | 0.31854 | 2.6918 | 0.31848 | 2.6914 | Offer signed 06/06/2025.
ROMAN RD | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 369058 | 426505 | 630 | 7.2019 | 3.3041 | 11.5072 | 21.4846 | 3.749 | 2.7472 | 11.5072 | 0 | 0 | Offer signed 06/06/2025.
ROMILEY | 11 | VERNON PARK | VERNON PARK | BREDBURY | 393626 | 390716 | 400 | 7.621 | 1.1685 | 1.1685 | 22.273 | 11.0271 | 7.9254 | 1.1685 | 7.5834 | 0 | N/A
ROSSALL | 6.6 | THORNTON | THORNTON | STANAH | 331916 | 445505 | 400 | 4.5726 | 1.5191 | 5.0191 | 0 | 0 | 0 | 0 | 0 | 0 | offer signed 25/04/2025
ROYTON | 6.6 | ROYTON | ROYTON | WHITEGATE | 392426 | 407533 | 800 | 9.1452 | 4.0744 | 14.1144 | 0 | 0 | 0 | 0 | 0 | 0 | offer signed 25/04/2025
SALE | 6.6 | SALE | SALE | CARRINGTON | 378952 | 392177 | 630 | 7.2019 | 8.8931 | 13.4587 | 29.8145 | 8.4673 | 6.178 | 13.4587 | 6.5677 | 14.7385 | Offer signed 19/05/2025
SALE MOOR | 6.6 | SALE | SALE | CARRINGTON | 379671 | 391133 | 400 | 4.5726 | 2.1161 | 2.1161 | 11.6729 | 11.6729 | 11.6729 | 2.1161 | 12.01 | 1.3941 | Offer signed 19/05/2025
SALFORD QUAYS | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 380334 | 397555 | 800 | 9.1452 | 0 | 0 | 7 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | Offer signed 24/12/2024
SAMLESBURY ENTERPRISE ZONE | 11 | BLACKBURN |  | PENWORTHAM | 363416 | 431248 | 630 | 12 | 18.8886 | 25.5133 | 27.5361 | 17.9694 | 12.9149 | 25.5133
SANDGATE | 11 | BARROW & SANDGATE | BARROW | HARKER | 321492 | 468870 | 630 | 12.0031 | 9.064 | 13.564 | 29.4377 | 9.8049 | 7.119 | 13.564 | 7.2924 | 14.3266 | Offer signed 30/05/2025.
SCARISBRICK | 11 | SKELMERSDALE | SKELMERSDALE | WASHWAY FARM | 338069 | 412086 | 400 | 7.621 | 2.2304 | 3.7304 | 6.1578 | 1.9575 | 1.4344 | 3.7304 | 1.4344 | 3.6656 | Offer signed 29/05/2024. Parrallel offer signed 27/08/2024
SEBERGHAM | 11 | CARLISLE | CARLISLE | HARKER | 335344 | 542653 | 630 | 12.0031 | 0 | 0 | 1.9335 | 1.9335 | 1.4344 | 0 | 1.4344 | 1.1732 | Offer signed 30/05/2025.
SEDBERGH | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 365151 | 491747 | 400 | 7.621 | 0 | 4.9866 | 18.5687 | 18.5687 | 18.5687 | 4.9866 | 0 | 0 | Offer signed 30/05/2025.
SELSMIRE | 11 | PENRITH & SHAP | PENRITH | HUTTON | 361018 | 507505 | 630 | 12.0031 | 1.1003 | 1.1003 | 4.3655 | 4.3655 | 4.3655 | 1.1003 | 4.9054 | 1.1883 | Offer signed 30/05/2025.
SETTLE | 11 | PADIHAM | PADIHAM | PADIHAM | 381588 | 463721 | 630 | 12.0031 | 0.40057 | 7.9006 | 13.7375 | 13.7375 | 13.7375 | 7.9006 | 13.3716 | 7.6618 | Offer signed 19/05/2025.
SEVEN STARS | 11 | LEYLAND | LEYLAND | PENWORTHAM | 352653 | 421636 | 800 | 15.242 | 0.79316 | 7.1432 | 31.5788 | 26.4225 | 18.9904 | 7.1432 | 18.9995 | 5.2353 | Offer signed 30/05/2025.
SHANNON ST SOUTH | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 330806 | 435291 | 630 | 7.2019 | 3.6821 | 9.3806 | 31.88 | 10.8491 | 7.9158 | 9.3806 | 8.0106 | 5.397 | Offer signed 30/05/2025.
SHAP | 11 | PENRITH & SHAP | PENRITH | HUTTON | 356910 | 513357 | 400 | 7.621 | 3.2686 | 6.0686 | 13.1101 | 13.1101 | 13.1101 | 6.0686 | 12.2325 | 7.0318 | Offer signed 30/05/2025.
SHAW | 6.6 | ROYTON | ROYTON | WHITEGATE | 394298 | 409450 | 800 | 9.1452 | 4.0744 | 15.4911 | 0 | 0 | 0 | 0 | 0 | 0 | offer signed 25/04/2025
Siddick | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 300289 | 530805 | 630 | 12.0031 | 17.4263 | 23.9263 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0 | 0 | Offer signed 30/05/2025.
SILLOTH | 11 | CARLISLE | CARLISLE | HARKER | 311307 | 553464 | 400 | 7.621 | 16.1589 | 38.5649 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 30/05/2025.
SKELMERSDALE | 11 | SKELMERSDALE | SKELMERSDALE | WASHWAY FARM | 347198 | 407434 | 630 | 12.0031 | 5.4323 | 10.3555 | 11.2179 | 1.936 | 1.3915 | 10.3555 | 1.3976 | 7.809 | Offer signed 29/05/2024. Parrallel offer signed 27/08/2024
SKELTON C | 11 | PENRITH & SHAP | PENRITH | HUTTON | 342672 | 538337 | 630 | 12.0031 | 10.228 | 17.9247 | 28.9975 | 23.8623 | 17.1503 | 17.9247 | 17.7881 | 13.3736 | Offer signed 30/05/2025.
SLIPWAY | 11 | EGREMONT | EGREMONT | HARKER | 297180 | 518183 | 400 | 7.621 | 4.6554 | 6.6554 | 16.7408 | 16.7408 | 12.1706 | 6.6554 | 12.7115 | 7.3459 | Offer signed 30/05/2025.
SNIPE | 6.6 | DROYLSDEN | DROYLSDEN | STALYBRIDGE | 391844 | 398322 | 800 | 9.1452 | 6.572 | 11.212 | 0.74872 | 0.13065 | 0.095738 | 0.74872 | 1.4344 | 11.2179 | Offer signed 27/08/2024
S.E. MACCLESFIELD | 11 | MACCLESFIELD | MACCLESFIELD | MACCLESFIELD | 392001 | 372504 | 630 | 12.0031 | 8.8674 | 9.605 | 11.2179 | 1.9575 | 1.4344 | 9.605 | 1.4344 | 0 | offer signed 25/04/2025
SOUTH PARK | 11 | LYTHAM | LYTHAM | PENWORTHAM | 336410 | 427512 | 400 | 7.621 | 14.4484 | 17.3158 | 29.4139 | 11.4576 | 8.2348 | 17.3158 | 0 | 0 | Offer signed 30/05/2025.
S.W. MACCLESFIELD | 11 | MACCLESFIELD | MACCLESFIELD | MACCLESFIELD | 390968 | 373004 | 400 | 7.621 | 2.07 | 6.207 | 11.2179 | 1.9575 | 1.4344 | 6.207 | 1.4344 | 0 | offer signed 25/04/2025
SPA RD | 6.6 | BOLTON | BOLTON | KEARSLEY | 371065 | 409109 | 400 | 4.5726 | 4.1696 | 4.1696 | 11.2179 | 1.9575 | 1.4344 | 4.1696 | 1.4344 | 5.2215 | Offer signed 24/12/2024
SPADEADAM 132/11KV | 11 | - | - | HARKER | 361282 | 570359 | 1250 | 23.8157 | 26.9071 | 34.0526 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 0.31765 | 1.6795 | Offer signed 30/05/2025.
SPOTLAND | 6.6 | ROCHDALE CENTRAL | ROCHDALE CENTRAL | ROCHDALE | 387882 | 414309 | 630 | 7.2019 | 7.7721 | 11.2721 | 22.5461 | 13.1771 | 9.6144 | 11.2721 | 4.1691 | 9.6296 | Offer signed 06/06/2025.
SPRING COTTAGE | 6.6 | NELSON | NELSON | PADIHAM | 385446 | 437481 | 400 | 4.5726 | 3.4211 | 17.2011 | 0 | 0 | 0 | 0 | 0 | 0 | Offer signed 19/05/2025.
SPRING GARDEN ST 11kV | 11 | LANCASTER | LANCASTER | HEYSHAM | 347661 | 461494 | 800 | 15.242 | 1.5831 | 1.5831 | 11.2179 | 1.9575 | 1.4344 | 1.5831 | 1.5151 | 5.0572 | Offer with ENW due to be signed 06/06/2025.
SPRING GARDEN ST 6.6KV | 6.6 | LANCASTER | LANCASTER | HEYSHAM | 347651 | 461484 | 800 | 9.1452 | 1.5831 | 1.5831 | 11.2179 | 1.9575 | 1.4344 | 1.5831 | 1.5151 | 5.0572 | Offer with ENW due to be signed 06/06/2025.
SQUIRES GATE | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 332037 | 432063 | 400 | 4.5726 | 5.2193 | 9.8193 | 16.8524 | 2.7332 | 1.9942 | 9.8193 | 2.1114 | 6.2955 | Offer signed 30/05/2025.
ST ANNES | 6.6 | LYTHAM | LYTHAM | PENWORTHAM | 331716 | 429849 | 630 | 7.2019 | 10.3973 | 13.8973 | 22.251 | 9.7438 | 7.1094 | 13.8973 | 0 | 0 | Offer signed 30/05/2025.
ST JOHNS | 6.6 | Frederick Road | FREDERICK RD | KEARSLEY | 383100 | 398078 | 600 | 6.8589 | 0 | 0 | 7 | 1.9575 | 1.4344 | 0
ST MARYS | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 392582 | 405316 | 630 | 7.2019 | 10.8651 | 15.5021 | 29.5844 | 10.5784 | 7.7183 | 15.5021 | 7.7148 | 4.6017 | offer signed 25/04/2025
ST MARYS ST | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 354932 | 429640 | 400 | 4.5726 | 5.8868 | 9.3868 | 11.2179 | 1.9575 | 1.4344 | 9.3868 | 1.4344 | 10.0664 | Offer signed 30/05/2025.
ST THOMAS RD | 6.6 | LYTHAM | LYTHAM | PENWORTHAM | 332713 | 428643 | 400 | 4.5726 | 14.0369 | 17.3158 | 28.6623 | 12.8926 | 9.4068 | 17.3158 | 0 | 0 | Offer signed 30/05/2025.
STAINBURN | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 302535 | 529330 | 630 | 12.0031 | 9.2484 | 11.7484 | 7 | 1.9575 | 1.4344 | 7 | 0 | 0 | Offer signed 30/05/2025.
STANDISH | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 356139 | 410059 | 630 | 12.0031 | 0.76792 | 0.76792 | 15.2795 | 2.5157 | 1.8081 | 0.76792 | 1.9914 | 1.9914 | Offer signed 30/05/2025.
STRANGEWAYS | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 383780 | 399743 | 400 | 4.5726 | 0 | 0 | 7 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | Offer signed 24/12/2024
STRAWBERRY BANK | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 376338 | 429396 | 630 | 7.2019 | 5.2782 | 9.6934 | 20.7427 | 3.3642 | 2.4546 | 9.6934 | 2.4384 | 6.5078 | Offer signed 19/05/2025.
STUART ST | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 387190 | 398835 | 600 | 6.8589 | 6.3991 | 13.3991 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 0 | Offer signed 27/08/2024
STUBBINS | 11 | ROSSENDALE | ROSSENDALE | PADIHAM | 379112 | 418005 | 400 | 7.621 | 6.8206 | 23.8206 | 26.4541 | 4.3555 | 3.1304 | 23.8206 | 2.782 | 23.5098 | Offer signed 19/05/2025.
SWINTON | 11 | AGECROFT | AGECROFT | KEARSLEY | 378367 | 401718 | 800 | 15.242 | 10.5687 | 18.1608 | 30.2421 | 14.9405 | 10.738 | 18.1608 | 10.853 | 18.1986 | Offer signed 24/12/2024
TAME VALLEY | 6.6 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 395148 | 398108 | 630 | 7.2019 | 5.8983 | 10.5353 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 27/08/2024
TARDY GATE | 11 | RIBBLE | RIBBLE | PENWORTHAM | 353958 | 426066 | 400 | 7.621 | 9.2273 | 13.3643 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 9.065 | Offer signed 30/05/2025.
TARLETON | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 344741 | 422417 | 400 | 7.621 | 0.76792 | 0.76792 | 19.0437 | 7.4537 | 5.3571 | 0.76792 | 0.31765 | 2.6844 | Offer signed 30/05/2025.
THE HEIGHT | 6.6 | AGECROFT | AGECROFT | KEARSLEY | 379792 | 400497 | 400 | 4.5726 | 3.93 | 14.63 | 29.6311 | 9.9147 | 7.2341 | 14.63 | 7.3789 | 14.5981 | Offer signed 24/12/2024
THORLEY LN | 11 | MOSS NOOK |  | SOUTH MANCHESTER | 381374 | 386134 | 630 | 12 | 10.2407 | 35.4407 | 8.008 | 1.9575 | 1.4344 | 8.008
THORNTON | 11 | BISPHAM | BISPHAM | PENWORTHAM | 334207 | 442111 | 630 | 12.0031 | 9.1378 | 12.2748 | 11.2179 | 1.9575 | 1.411 | 11.2179 | 0.31765 | 2.6844 | Offer signed 30/05/2025.
TOWNLEY ST | 11 | CHADDERTON | CHADDERTON | WHITEGATE | 387242 | 405960 | 400 | 7.621 | 7.1062 | 7.1062 | 33.2516 | 9.1092 | 6.6226 | 7.1062 | 1.3649 | 0 | offer signed 25/04/2025
TRAFFORD | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 380714 | 396551 | 630 | 7.2019 | 1.9978 | 8.9978 | 22.5072 | 7.7079 | 5.6239 | 8.9978 | 5.7122 | 14.3365 | Offer signed 11/03/2025
TRAFFORD PARK NORTH | 6.6 | BARTON | BARTON | CARRINGTON | 378738 | 397694 | 630 | 7.2019 | 1.3294 | 6.5794 | 2.6918 | 0.43658 | 0.31854 | 2.6918 | 0.31848 | 2.6914 | Offer signed 19/05/2025
TRIMPELL | 11 | - | - | HEYSHAM | 341861 | 458979 | 630 | 12.0031 | 20.2475 | 20.2475 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 0.31765 | 1.6795 | Offer with ENW due to be signed 06/06/2025.
TRINITY | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 382649 | 398230 | 630 | 7.2019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Offer signed 24/12/2024
TULKETH | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 352393 | 431036 | 400 | 4.5726 | 9.5519 | 13.6889 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 8.4618 | Offer signed 30/05/2025.
ULVERSTON | 11 | ULVERSTON | ULVERSTON | HARKER | 327495 | 477808 | 630 | 12.0031 | 4.8133 | 7.8133 | 15.0691 | 10.1731 | 7.3116 | 7.8133 | 7.6223 | 7.75 | Offer signed 30/05/2025.
UNION RD | 6.6 | BOLTON | BOLTON | KEARSLEY | 372174 | 410598 | 630 | 7.2019 | 1.9994 | 6.6364 | 11.2179 | 1.9575 | 1.4344 | 6.6364 | 1.4344 | 9.7198 | Offer signed 24/12/2024
UPHOLLAND | 11 | ORRELL | ORRELL | KIRKBY | 352531 | 404369 | 630 | 12.0031 | 0 | 7.7914 | 22.9884 | 11.4429 | 8.2242 | 7.7914 | 8.1328 | 6.6945 | Offer signed 27/08/2024
URMSTON | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 377117 | 395709 | 400 | 4.5726 | 9.2314 | 13.8684 | 29.3029 | 7.9091 | 5.7707 | 13.8684 | 5.7691 | 14.4783 | Offer signed 11/03/2025
VICTORIA PARK | 6.6 | LONGSIGHT | LONGSIGHT | BREDBURY | 385373 | 395948 | 630 | 7.2019 | 0 | 1.1309 | 28.1638 | 8.265 | 6.0304 | 1.1309 | 4.6312 | 4.9475 | N/A
WARBRECK | 6.6 | BISPHAM | BISPHAM | PENWORTHAM | 331775 | 438420 | 630 | 7.2019 | 7.5578 | 11.0578 | 11.2179 | 1.9575 | 1.4344 | 11.0578 | 1.4344 | 10.9371 | Offer signed 30/05/2025.
WARDLEWORTH | 6.6 | BELFIELD | BELFIELD | ROCHDALE | 390339 | 414050 | 630 | 7.2019 | 7.9415 | 12.5785 | 30.316 | 7.9586 | 5.8068 | 12.5785 | 5.5739 | 0 | Offer signed 06/06/2025.
WARTON | 6.6 | PEEL | PEEL | PENWORTHAM | 341290 | 428540 | 1250 | 14.2894 | 3.8745 | 4.2579 | 21.8282 | 12.6437 | 9.2252 | 4.2579 | 0 | 0 | Offer signed 30/05/2025.
WATERHEAD | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 394942 | 405940 | 400 | 4.5726 | 15.0413 | 20.1052 | 29.1545 | 13.0571 | 9.5268 | 20.1052 | 9.344 | 4.6017 | offer signed 25/04/2025
WATERSWALLOWS | 11 | BUXTON | BUXTON | STALYBRIDGE | 407734 | 375459 | 630 | 12.0031 | 4.8797 | 4.8797 | 29.478 | 12.4383 | 8.9397 | 4.8797 | 1.3561 | 10.6051 | Offer signed 27/08/2024
WEASTE | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 378751 | 398897 | 800 | 9.1452 | 0 | 0 | 7 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | Offer signed 24/12/2024
WERNETH | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 391273 | 403453 | 630 | 7.2019 | 14.0728 | 18.7098 | 29.951 | 12.7139 | 9.2764 | 18.7098 | 8.8768 | 4.6017 | offer signed 25/04/2025
WESLEY PLACE BACUP | 6.6 | ROSSENDALE | ROSSENDALE | PADIHAM | 386475 | 422130 | 400 | 4.5726 | 12.6855 | 17.3225 | 29.5181 | 13.4927 | 9.8446 | 17.3225 | 10.1945 | 7.7239 | Offer signed 19/05/2025.
WEST DIDSBURY | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 383306 | 392514 | 630 | 7.2019 | 2.2533 | 11.7063 | 10.252 | 1.9575 | 1.4344 | 10.252 | 1.4344 | 8.6933 | Offer signed 11/03/2025
WESTGATE | 6.6 | LANCASTER | LANCASTER | HEYSHAM | 343077 | 463204 | 630 | 7.2019 | 1.5831 | 1.5831 | 11.2179 | 1.9575 | 1.4344 | 1.5831 | 1.5151 | 5.0572 | Offer with ENW due to be signed 06/06/2025.
WESTHOUGHTON | 11 | WESTHOUGHTON | WESTHOUGHTON | KEARSLEY | 365831 | 407025 | 400 | 7.621 | 0.022228 | 4.6592 | 11.3623 | 1.8707 | 1.3445 | 4.6592 | 0.088852 | 0 | Offer signed 24/12/2024
WESTLINTON | 11 | CARLISLE | CARLISLE | HARKER | 339551 | 564489 | 630 | 12.0031 | 3.4021 | 5.9021 | 7 | 1.9575 | 1.4344 | 5.9021 | 1.4344 | 7 | Offer signed 30/05/2025.
WHALLEY | 11 | PADIHAM | PADIHAM | PADIHAM | 373376 | 436176 | 630 | 12.0031 | 10.5045 | 15.1415 | 25.709 | 8.3738 | 6.0184 | 15.1415 | 5.5392 | 11.0853 | Offer signed 19/05/2025.
WHALLEY RANGE | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 382923 | 394645 | 630 | 7.2019 | 2.2533 | 13.2298 | 10.252 | 1.9575 | 1.4344 | 10.252 | 1.4344 | 10.576 | Offer signed 11/03/2025
WHASSET | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 350648 | 481468 | 630 | 12.0031 | 0 | 4.9866 | 21.3127 | 19.359 | 13.9137 | 4.9866 | 0 | 0 | Offer signed 30/05/2025.
WHITTLE LE WOODS | 11 | LEYLAND | LEYLAND | PENWORTHAM | 357874 | 421203 | 630 | 12.0031 | 5.7686 | 9.2686 | 23.423 | 14.5177 | 10.4341 | 9.2686 | 10.3146 | 9.0214 | Offer signed 30/05/2025.
WHITWORTH | 6.6 | ROCHDALE CENTRAL | ROCHDALE CENTRAL | ROCHDALE | 388779 | 419157 | 630 | 7.2 | 5.0377 | 6.5377 | 9.9573 | 4.6205 | 3.3712 | 6.5377 | 3.1391 | 5.9064 | Offer signed 06/06/2025.
WIGTON | 11 | CARLISLE | CARLISLE | HARKER | 325814 | 549933 | 400 | 7.621 | 2.939 | 7.076 | 4.0463 | 1.9575 | 1.4344 | 4.0463 | 1.4344 | 0.21045 | Offer signed 30/05/2025.
WILLOW HEY | 11 | SKELMERSDALE | SKELMERSDALE | WASHWAY FARM | 347779 | 406066 | 400 | 7.621 | 10.1494 | 14.7864 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 9.682 | Offer signed 29/05/2024. Parrallel offer signed 27/08/2024
WILLOWBANK | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 391885 | 406064 | 630 | 7.2019 | 2.0566 | 7.0938 | 25.394 | 13.0332 | 9.5094 | 7.0938 | 9.2635 | 4.6017 | offer signed 25/04/2025
WILLOWHOLME | 11 | CARLISLE | CARLISLE | HARKER | 338653 | 556688 | 630 | 12.0031 | 5.1928 | 9.3298 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer signed 30/05/2025.
WILMSLOW | 11 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 384710 | 381286 | 630 | 12.0031 | 4.1703 | 7.6703 | 8.008 | 1.9575 | 1.4344 | 7.6703 | 1.4344 | 5.768 | Offer signed 11/03/2025
WINDERMERE | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 341657 | 498418 | 630 | 12.0031 | 0 | 4.9866 | 30.663 | 20.0262 | 14.3932 | 4.9866 | 0 | 0 | Offer signed 30/05/2025.
WINIFRED RD | 6.6 | ADSWOOD | ADSWOOD | BREDBURY | 389971 | 388470 | 630 | 7.2019 | 3.8991 | 7.3991 | 17.5235 | 6.8228 | 4.9781 | 7.3991 | 2.1791 | 7.5047 | N/A
WITHINGTON | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 384841 | 392774 | 630 | 7.2019 | 2.2533 | 6.4616 | 10.252 | 1.9575 | 1.4344 | 6.4616 | 1.4344 | 6.0832 | Offer signed 11/03/2025
WITHYFOLD DRIVE | 11 | MACCLESFIELD | MACCLESFIELD | MACCLESFIELD | 392132 | 374352 | 400 | 7.621 | 9.605 | 9.605 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0.31765 | 0 | offer signed 25/04/2025
WOODBINE ST | 6.6 | CASTLETON | CASTLETON | ROCHDALE | 390519 | 412388 | 800 | 9.1452 | 5.4618 | 8.9618 | 24.115 | 14.3537 | 10.4729 | 8.9618 | 10.5673 | 8.8316 | Offer signed 06/06/2025.
WOODFIELD RD | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 358258 | 418014 | 400 | 7.621 | 0.76792 | 0.76792 | 30.5968 | 14.0659 | 10.1094 | 0.76792 | 5.1053 | 5.1053 | Offer signed 30/05/2025.
WOODHILL LANE | 6.6 | LANCASTER | LANCASTER | HEYSHAM | 343294 | 463785 | 400 | 4.5726 | 1.5831 | 1.5831 | 11.2179 | 1.9575 | 1.4344 | 1.5831 | 1.5151 | 2.7595 | Offer with ENW due to be signed 06/06/2025.
WOODHOUSE PARK | 11 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 382132 | 386340 | 630 | 12.0031 | 1.3433 | 4.8433 | 8.008 | 1.9575 | 1.4344 | 4.8433 | 1.4344 | 0.86929 | Offer signed 11/03/2025
WOODLEY | 11 | VERNON PARK | VERNON PARK | BREDBURY | 393116 | 392019 | 400 | 7.621 | 1.1685 | 1.1685 | 10.6844 | 1.7591 | 1.2643 | 1.1685 | 1.0921 | 0 | N/A
WOOLFOLD | 11 | BURY | BURY | KEARSLEY | 378874 | 411666 | 630 | 12.0031 | 10.9628 | 14.9628 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | Offer signed 24/12/2024
WORDSWORTH ST | 6.6 | BOLTON | BOLTON | KEARSLEY | 370709 | 410873 | 400 | 4.5726 | 4.6442 | 14.7833 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | Offer signed 24/12/2024
WORSLEY MESNES | 6.6 | WIGAN | WIGAN | KIRKBY | 357435 | 403977 | 630 | 7.2019 | 5.5348 | 12.9603 | 25.914 | 12.0535 | 8.7945 | 12.9603 | 7.7377 | 8.7753 | Offer signed 27/08/2024
WRIGHTINGTON | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 353466 | 413290 | 400 | 7.621 | 0.76792 | 0.76792 | 30.2323 | 15.3275 | 11.0162 | 0.76792 | 5.1053 | 5.1053 | Offer signed 30/05/2025.
YEALAND | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 351537 | 475934 | 630 | 12.0031 | 0 | 4.9866 | 12.6034 | 12.6034 | 12.6034 | 4.9866 | 0 | 0 | Offer signed 30/05/2025.

## 5) BSP Headroom Data
BSP Headroom
BSP | Voltage (kV) | BCA Group (GSP) | BSP Coordinates |  | Demand Headroom (MW) |  | Generation Headroom - N-0 -(MW) |  | Battery Storage Headroom N-0 -(MW)
|  |  | Easting | Northing | Firm | Non Firm | Inverter Based | Synchronous
ADSWOOD | 33 | BREDBURY | 389188 | 388310 | 34.5937 | 52.5937 | 140.8044 | 46.0296 | 52.5937 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.39156%2C-2.16403z=20?hl=en | N/A
AGECROFT | 33 | KEARSLEY | 380345 | 401831 | 10.5687 | 22.5687 | 91.0187 | 27.7562 | 22.5687 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.51279%2C-2.29754z=20?hl=en | Offer signed 24/12/2024
ALTRINCHAM | 33 | CARRINGTON | 376380 | 389012 | 37.0559 | 55.0559 | 148.5916 | 49.4726 | 55.0559 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.39778%2C-2.35667z=20?hl=en | Offer signed 19/05/2025
ATHERTON | 33 | KEARSLEY | 366150 | 402088 | 11.3144 | 11.3144 | 123.6442 | 27.7637 | 11.3144 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.51405%2C-2.51233z=20?hl=en | Offer signed 24/12/2024
BARROW | 33 | HARKER | 319709 | 470489 | 38.9701 | 66.6016 | 53.4488 | 9.6965 | 53.4488 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.12391%2C-3.23018z=20?hl=en | Offer signed 30/05/2025.
BARTON | 33 | CARRINGTON | 376758 | 397174 | 28.5038 | 50.4209 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.47087%2C-2.35076z=20?hl=en | Offer signed 19/05/2025
BELFIELD | 33 | ROCHDALE | 391033 | 413945 | 28.3165 | 28.3165 | 56.6931 | 23.3845 | 28.3165 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.62216%2C-2.13727z=20?hl=en | Offer signed 06/06/2025.
BISPHAM | 33 | PENWORTHAM | 332328 | 439711 | 33.5828 | 33.5828 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.84897%2C-3.04054z=20?hl=en | Offer signed 30/05/2025.
BLACKBURN | 33 | PENWORTHAM | 370584 | 429294 | 27.0387 | 27.0387 | 76.5024 | 44.4544 | 27.0387 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.7592%2C-2.44764z=20?hl=en | Offer signed 30/05/2025.
BLACKPOOL | 33 | PENWORTHAM | 330835 | 435308 | 33.1562 | 33.9962 | 125.5107 | 35.4721 | 33.9962 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.80944%2C-3.05179z=20?hl=en | Offer signed 30/05/2025.
BLOOM ST | 33 | SOUTH MANCHESTER | 384221 | 397717 | 0 | 36.0944 | 152.4184 | 48.3248 | 36.0944 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.47593%2C-2.23943z=20?hl=en | Offer signed 11/03/2025
BOLTON | 33 | KEARSLEY | 372255 | 410566 | 4.6442 | 32.6442 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.59102%2C-2.42059z=20?hl=en | Offer signed 24/12/2024
BURNLEY | 33 | ROCHDALE | 385569 | 434469 | 61.594 | 61.594 | 80.8895 | 28.9482 | 61.594 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.80624%2C-2.22125z=20?hl=en | Offer signed 06/06/2025.
BURY | 33 | KEARSLEY | 380272 | 411184 | 25.5868 | 25.5868 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.5967%2C-2.29975z=20?hl=en | Offer signed 24/12/2024
BUXTON | 33 | STALYBRIDGE | 407769 | 375476 | 4.8797 | 4.8797 | 85.0845 | 44.9195 | 4.8797 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.27596%2C-1.885z=20?hl=en | Offer signed 27/08/2024
CARLISLE | 33 | HARKER | 338655 | 556583 | 19.5339 | 40.7339 | 6.7308 | 1.9358 | 6.7308 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.8993%2C-2.9589z=20?hl=en | Offer signed 30/05/2025.
CARRINGTON BSP | 33 | CARRINGTON | 373110 | 393020 | 10.1771 | 31.1771 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.43349%2C-2.40648z=20?hl=en | Offer signed 19/05/2025
CASTLETON | 33 | ROCHDALE | 388461 | 411290 | 39.4244 | 39.4244 | 99.6769 | 37.9363 | 39.4244 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.59783%2C-2.17663z=20?hl=en | Offer signed 06/06/2025.
CHADDERTON | 33 | WHITEGATE | 389137 | 403821 | 7.1062 | 7.1062 | 49.6561 | 9.0084 | 7.1062 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.53127%2C-2.16481z=20?hl=en | offer signed 25/04/2025
DROYLSDEN | 33 | STALYBRIDGE | 390140 | 398146 | 37.4038 | 37.4038 | 0.7122 | 0.1292 | 0.7122 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.4802%2C-2.14954z=20?hl=en | Offer signed 27/08/2024
EGREMONT | 33 | HARKER | 301070 | 513074 | 41.4738 | 41.4738 | 41.8213 | 34.4792 | 41.4738 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.50354%2C-3.52919z=20?hl=en | Offer signed 30/05/2025.
FREDERICK RD | 33 | KEARSLEY | 381795 | 399250 | 0 | 0 | 6.7308 | 1.9358 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.49066%2C-2.27698z=20?hl=en | Offer signed 24/12/2024
GOLBORNE | 33 | BOLD | 360607 | 397690 | 26.7279 | 45.2287 | 63.3976 | 11.5013 | 45.2287 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.47498%2C-2.59493z=20?hl=en | N/A
GREENHILL | 33 | WHITEGATE | 393262 | 404755 | 25.6143 | 25.6143 | 88.1994 | 29.7717 | 25.6143 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.53936%2C-2.10308z=20?hl=en | offer signed 25/04/2025
HAZEL GROVE | 33 | BREDBURY | 391313 | 386877 | 41.5832 | 59.5832 | 131.0538 | 37.3058 | 59.5832 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.37854%2C-2.1319z=20?hl=en | N/A
HARTSHEAD-HEYROD | 33 | STALYBRIDGE | 397322 | 399942 | 26.7933 | 88.7933 | 6.7308 | 1.9358 | 6.7308 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.49638%2C-2.04169z=20?hl=en | Offer signed 27/08/2024
HUNCOAT | 33 | PADIHAM | 377997 | 431083 | 46.3931 | 60.1931 | 67.1658 | 21.3062 | 60.1931 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.77521%2C-2.33688z=20?hl=en | Offer signed 19/05/2025.
HYDE | 33 | STALYBRIDGE | 395522 | 395647 | 30.4942 | 30.4942 | 29.9951 | 5.4416 | 29.9951 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.45264%2C-2.07376z=20?hl=en | Offer signed 27/08/2024
KEARSLEY LOCAL | 33 | KEARSLEY | 376355 | 404783 | 0 | 33.0877 | 6.7308 | 1.9358 | 6.7308 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.53905%2C-2.35884z=20?hl=en | Offer signed 24/12/2024
KENDAL (PARKSIDE RD) | 33 | HUTTON | 351915 | 491858 | 0 | 4.9866 | 93.8515 | 25.9319 | 4.9866 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.31969%2C-2.74168z=20?hl=en | Offer signed 30/05/2025.
LANCASTER | 33 | HEYSHAM | 348644 | 463628 | 1.5831 | 1.5831 | 10.6707 | 1.9358 | 1.5831 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.06622%2C-2.78639z=20?hl=en | Offer with ENW due to be signed 06/06/2025.
LEYLAND | 33 | PENWORTHAM | 354121 | 423373 | 12.928 | 27.892 | 126.0207 | 32.9155 | 27.892 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.70478%2C-2.69663z=20?hl=en | Offer signed 30/05/2025.
LONGSIGHT | 33 | BREDBURY | 385592 | 396016 | 0 | 1.1309 | 148.6419 | 39.0296 | 1.1309 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.46086%2C-2.21901z=20?hl=en | N/A
LOWER DARWEN | 33 | ROCHDALE | 369695 | 424981 | 3.3041 | 53.3041 | 20.4366 | 3.7075 | 20.4366 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.72038%2C-2.45999z=20?hl=en | Offer signed 06/06/2025.
LYTHAM | 33 | PENWORTHAM | 335361 | 429316 | 17.3158 | 17.3158 | 42.9626 | 40.7898 | 17.3158 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.75633%2C-2.98215z=20?hl=en | Offer signed 30/05/2025.
MACCLESFIELD | 33 | MACCLESFIELD | 392047 | 374564 | 9.605 | 9.605 | 10.6707 | 1.9358 | 9.605 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.26811%2C-2.12063z=20?hl=en | offer signed 25/04/2025
MOSS NOOK | 33 | SOUTH MANCHESTER | 384073 | 385068 | 10.2407 | 35.4407 | 7.7 | 1.9358 | 7.7 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.36201%2C-2.2408z=20?hl=en | Offer signed 11/03/2025
NELSON | 33 | PADIHAM | 385989 | 438643 | 4.9506 | 26.3634 | 0 | 0 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.84299%2C-2.214z=20?hl=en | Offer signed 19/05/2025.
NEW MILLS | 33 | STALYBRIDGE | 401141 | 383916 | 16.6353 | 16.6353 | 46.8568 | 46.8568 | 16.6353 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.35237%2C-1.9844z=20?hl=en | Offer signed 27/08/2024
ORRELL | 33 | KIRKBY | 352784 | 404565 | 0 | 56.6328 | 126.8713 | 52.9212 | 56.6328 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.5356%2C-2.71374z=20?hl=en | Offer signed 27/08/2024
PADIHAM | 33 | PADIHAM | 378571 | 433224 | 26.0082 | 57.5082 | 136.3037 | 30.0792 | 57.5082 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.79502%2C-2.32919z=20?hl=en | Offer signed 19/05/2025.
PEEL | 33 | PENWORTHAM | 335644 | 432080 | 4.2579 | 4.2579 | 21.8282 | 21.8282 | 4.2579 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.78114%2C-2.9776z=20?hl=en | Offer signed 30/05/2025.
PENRITH | 33 | HUTTON | 349996 | 530398 | 17.9247 | 17.9247 | 37.1451 | 28.1451 | 17.9247 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.66637%2C-2.77723z=20?hl=en | Offer signed 30/05/2025.
PRESTON EAST | 33 | PENWORTHAM | 356774 | 432942 | 8.3235 | 8.3235 | 10.6707 | 1.9358 | 8.3235 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.79104%2C-2.6584z=20?hl=en | Offer signed 30/05/2025.
RED BANK | 33 | WHITEGATE | 384542 | 399276 | 19.4478 | 37.4478 | 154.2706 | 32.7792 | 37.4478 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.49001%2C-2.23427z=20?hl=en | offer signed 25/04/2025
RIBBLE | 33 | PENWORTHAM | 351794 | 429241 | 74.2156 | 110.2156 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.75725%2C-2.73184z=20?hl=en | Offer signed 30/05/2025.
ROCHDALE CENTRAL | 33 | ROCHDALE | 389111 | 413393 | 48.3811 | 60.7184 | 95.5596 | 40.6973 | 60.7184 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.61653%2C-2.16602z=20?hl=en | Offer signed 06/06/2025.
ROSSENDALE | 33 | PADIHAM | 380261 | 422010 | 35.5304 | 53.3264 | 105.5461 | 53.6429 | 53.3264 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.69402%2C-2.30041z=20?hl=en | Offer signed 19/05/2025.
ROYTON | 33 | WHITEGATE | 392426 | 407533 | 4.0744 | 70.4872 | 0 | 0 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.56464%2C-2.11572z=20?hl=en | offer signed 25/04/2025
SALE | 33 | CARRINGTON | 378726 | 392892 | 8.8931 | 13.4587 | 78.2744 | 48.5664 | 13.4587 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.42581%2C-2.31835z=20?hl=en | Offer signed 19/05/2025
SANDGATE | 33 | HARKER | 321492 | 468870 | 38.9701 | 66.6016 | 110.9878 | 20.135 | 66.6016 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.10982%2C-3.20288z=20?hl=en | Offer signed 30/05/2025.
SHAP | 33 | HUTTON | 356910 | 513357 | 17.9247 | 17.9247 | 37.1451 | 37.1451 | 17.9247 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.51358%2C-2.66756z=20?hl=en | Offer signed 30/05/2025.
SIDDICK | 33 | HARKER | 300332 | 530823 | 24.5012 | 78.5548 | 6.7308 | 1.9358 | 6.7308 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.64948%2C-3.51144z=20?hl=en | Offer signed 30/05/2025.
SKELMERSDALE | 33 | WASHWAY FARM | 347172 | 407455 | 19.48 | 19.48 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.56076%2C-2.79859z=20?hl=en | Offer signed 29/05/2024. Parrallel offer signed 27/08/2024
STAINBURN | 33 | HARKER | 302535 | 529330 | 24.5012 | 78.5548 | 6.7308 | 1.9358 | 6.7308 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.66252%2C-3.54717z=20?hl=en | Offer signed 30/05/2025.
STRETFORD | 33 | SOUTH MANCHESTER | 380069 | 395104 | 12.004 | 46.6437 | 135.2178 | 33.7504 | 46.6437 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.4523%2C-2.30113z=20?hl=en | Offer signed 11/03/2025
STUART ST | 33 | STALYBRIDGE | 387247 | 398875 | 57.7972 | 120.7972 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.48612%2C-2.19476z=20?hl=en | Offer signed 27/08/2024
THORNTON | 33 | STANAH | 334559 | 443368 | 22.2933 | 34.2933 | 23.2987 | 10.323 | 23.2987 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.8709%2C-3.00229z=20?hl=en | offer signed 25/04/2025
ULVERSTON | 33 | HARKER | 327495 | 477808 | 53.4892 | 53.4892 | 60.7195 | 25.5535 | 53.4892 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.1907%2C-3.11215z=20?hl=en | Offer signed 30/05/2025.
VERNON PARK | 33 | BREDBURY | 391131 | 390929 | 1.1685 | 1.1685 | 83.6745 | 16.0407 | 1.1685 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.41552%2C-2.13492z=20?hl=en | N/A
WEST DIDSBURY | 33 | SOUTH MANCHESTER | 382900 | 393269 | 2.2533 | 38.7533 | 9.8577 | 1.9358 | 9.8577 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.42927%2C-2.25292z=20?hl=en | Offer signed 11/03/2025
WESTHOUGHTON | 33 | KEARSLEY | 365831 | 407025 | 26.4539 | 26.4539 | 87.4461 | 24.9562 | 26.4539 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.55846%2C-2.51787z=20?hl=en | Offer signed 24/12/2024
WIGAN | 33 | KIRKBY | 358343 | 404626 | 5.5348 | 44.5348 | 115.2618 | 62.4571 | 44.5348 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.53645%2C-2.62967z=20?hl=en | Offer signed 27/08/2024
WRIGHTINGTON | 33 | PENWORTHAM | 354460 | 413610 | 0.76792 | 0.76792 | 80.7309 | 22.527 | 0.76792 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.61411%2C-2.70439z=20?hl=en | Offer signed 30/05/2025.

## 6) GSP Demand Headroom Data (hidden)
GSP Headroom
Substation | GSP | Voltage (kV) | GSP Group | GSP Coordinates |  | Demand Headroom (MVA) |  | Battery Storage Headroom N-0 -(MW)
|  |  |  | Easting | Northing | Firm (non inverter based) | Non Firm (inverter based)
Bold GSP (132) | BOLD | 132 | BOLD | 353959 | 393258 | -139.0585 | -139.0585 | -99.1396 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.39156%2C-2.16403z=20?hl=en
Bredbury (132) | BREDBURY | 132 | BREDBURY | 391365 | 390944 | 130.6602 | 146.7402 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.51279%2C-2.29754z=20?hl=en
Carrington GSP (132) | CARRINGTON | 132 | CARRINGTON | 372952 | 393301 | -48.4123 | 104.5877 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.53127%2C-2.16481z=20?hl=en
Harker / Hutton GSP (132) | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | 132 | HARKER / HUTTON | 338285 | 561159 | -654.416 | -654.416 | -1393.5411 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.4802%2C-2.14954z=20?hl=en
Heysham GSP (132) | HEYSHAM | 132 | HEYSHAM | 341889 | 460007 | 328.4761 | 328.4761 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.50354%2C-3.52919z=20?hl=en
Kearsley GSP (132) | KEARSLEY | 132 | KEARSLEY | 376283 | 404800 | -9.6464 | 127.5736 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.53905%2C-2.35884z=20?hl=en
Padiham (132) | PADIHAM | 132 | PADIHAM | 378522 | 433196 | -252.3064 | -252.3064 | -271.5158 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.31969%2C-2.74168z=20?hl=en
Penwortham East / Rochdale SGT 1 GSP (132) | PENWORTHAM EAST/ROCHDALE | 132 | PENWORTHAM EAST / ROCHDALE | 350213 | 428032 | 323.9712 | 342.7212 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.06622%2C-2.78639z=20?hl=en
Penwortham West / Stanah GSP (132) | PENWORTHAM WEST/STANAH | 132 | PENWORTHAM WEST / STANAH | 350200 | 428029 | 234.1023 | 234.1023 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.70478%2C-2.69663z=20?hl=en
Rochdale GSP (132) | ROCHDALE | 132 | ROCHDALE | 385789 | 413832 | 131.1469 | 131.1469 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.46086%2C-2.21901z=20?hl=en
South Manchester GSP (132) | SOUTH MANCHESTER | 132 | SOUTH MANCHESTER | 381823 | 391734 | 187.0908 | 187.0908 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.72038%2C-2.45999z=20?hl=en
Stalybridge GSP (132) | STALYBRIDGE | 132 | STALYBRIDGE | 397172 | 399496 | 77.1566 | 174.0566 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.75633%2C-2.98215z=20?hl=en
Washway Farm / Kirkby GSP (132) | Washway Farm GSP / Kirkby GSP GROUP | 132 | WASHWAY FARM / KIRKBY | 345822 | 407637 | -106.5126 | -106.5126 | -15.7832 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.26811%2C-2.12063z=20?hl=en
Whitegate GSP (132) | WHITEGATE | 132 | WHITEGATE | 389202 | 403745 | 175.4843 | 279.2843 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.36201%2C-2.2408z=20?hl=en

## 7)Transmission Capacity - App G
Appendix G Summary
GSP / Site |  | Capacity of Connected & Contracted Connections (MW) |  |  |  | Materiality Headroom (Part 5) (MW) | Materiality Status | Capacity in Project Progression / Modification Application | Total Aggregated Developer Capacity Limit(MW) | Transmission FL Headroom (kA) | Project Progression Update
|  | Part 1 | Part 2 | Part 3 | Part 4
BOLD* | BOLD | 25.1 | 50.4 | 0 | 0 | N/A | B | N/A | 75.5 | 0 | N/A
BREDBURY | BREDBURY | 10.1 | 134.1 | 0 | 282.6 | 0 | C | 0 | 424.8 | 3 | N/A
CARRINGTON | CARRINGTON | 105 | 94 | 0 | 4 | 0 | C | 0 | 203 | 5.13 | Offer signed 19/05/2025
HARKER | HARKER | 765.4 | 40 | 0 | 916.8 | 0 | D | 0 | 1785.2 | 0 | Offer signed 30/05/2025.
HUTTON | HUTTON | 47.9 | 48 | 0 | 139 | 0 | D | 0 | 239.9 | 0 | Offer signed 30/05/2025.
HEYSHAM | HEYSHAM | 292.6 | 0 | 75 | 21.5 | 0 | C | 24 | 423.1 | 0 | Offer with ENW due to be signed 06/06/2025.
KEARSLEY | KEARSLEY | 57.9 | 229.7 | 11 | 35 | 0 | C | 0 | 368.6 | 3 | Offer signed 24/12/2024
KIRKBY | KIRKBY | 6 | 86.3 | 0 | 80.9 | 0 | D | 0 | 233.3 | 3 | Offer signed 27/08/2024
MACCLESFIELD | MACCLESFIELD | 27.9 | 20 | 0 | 7.5 | 0 | C | 0 | 65.4 | 2.57 | offer signed 25/04/2025
PADIHAM | PADIHAM | 35.5 | 128.1 | 149.9 | 193.9 | 0 | D | 0 | 555.4 | TBC | Offer signed 19/05/2025.
PENWORTHAM | PENWORTHAM | 187.9 | 497.1 | 67.6 | 109.2 | 0 | D | 0 | 1109.8 | 3 | Offer signed 30/05/2025.
ROCHDALE | ROCHDALE | 204.1 | 179.1 | 35 | 376.2 | 0 | C | 0 | 639.5 | 1.92 | Offer signed 06/06/2025.
SOUTH MANCHESTER | SOUTH MANCHESTER | 22.2 | 81.3 | 0 | 649.7 | 0 | C | 0 | 753.2 | 0 | Offer signed 11/03/2025
STALYBRIDGE | STALYBRIDGE | 28.3 | 226.8 | 0 | 50 | 0 | C | 0 | 345.1 | 0.591 | Offer signed 27/08/2024
STANAH | STANAH | 195.9 | 142 | 0 | 50 | 0 | C | 0 | 387.9 | 3.01 | offer signed 25/04/2025
WASHWAY FARM | WASHWAY FARM | 7.9 | 101.2 | 0 | 2 | 0 | D | 0 | 161 | 3 | Offer signed 29/05/2024. Parrallel offer signed 27/08/2024
WHITEGATE | WHITEGATE | 32 | 198.3 | 0 | 126.9 | 0 | C | 0 | 380 | 3.09 | offer signed 25/04/2025
Process |  |  | Parts 1 - 5 |  |  |  |  | Materiality Status
The Appendix G process aims to improve on the Statement of Works process by reducing timescales and facilitating greater transparency to the customer. Seventeen of ENWLs twenty GSPs have already converted to the Appendix G process and work is in progress to convert the three remaining sites. The above table summarises the Appendix G results of the GSPs which have already been converted from the Statement of Works process. Sites marked with an asterisk (*) are connected to the transmission network through the distribution network operated by SP Energy Networks. Appendix G submissions for these sites are made by SP Energy Networks on behalf of Electricity North West. For Further information on how to interpret the information presented in this table please refer to the user guide embedded within the first tab of this workbook. |  |  | Appendix G consists of 5 parts: • Part 1 – Existing power stations already connected to our network. • Part 2 – Power stations connected or contracted to connect to our network for which site specific requirements will apply e.g. power factor and controllability. • Part 3 – Power stations connected or contracted to connect to our network for which interim restrictions on availability will apply. Site specific requirements e.g. power factor and controllability, will also apply. • Part 4 – Power stations contracted to connect to our network which are unable to connect until transmission works have been completed. • Part 5 – Materiality headroom. This is a figure, determined by the transmission system operator, representing the available thermal capacity at the transmission system interface before a Modification Application is triggered. |  |  |  |  | To aid understanding we have given each GSP a materiality status. The three status are: A. The latest Appendix G return indicates that there is spare transmission system capacity at this location. B. There is insufficient capacity to accommodate any further sites without undertaking transmission system work. To identify the scope of these works a Modification Application will be required. C. There is insufficient capacity to accommodate any further connections without undertaking work on the transmission system. These works have already been identified and there are sites in project progression. New sites may still require a new Modification Application. D. There is insufficient capacity to accommodate any further connections without undertaking work on the transmission system. These works have already been identified and there are sites in project progression. New GSPs have now been trigged by the latest Project progression return by ESO.