## 1) User Guide and Network Maps
User Guide
With this tool we aim to provide our customers with information on where there is spare capacity for new developments to connect to our network without triggering reinforcement work. To aid our customers in interpreting the information contained within this tool we have produced a user guide which can be found below. Please note that the data presented in this tool is based on high level analysis and as such may differ from the results of a formal connection application. If your proposed development falls within an area with limited network capacity please contact us to discuss a possible solution. We will always to work with customers to overcome network constraints whether this is through traditional reinforcement or smart network solutions.
Map Data
We now publish an interactive map on our website that contains the same information as contained within this tool.
Click here to access the map.
| Last Updated* | 2024-06-27
This version is 1 day old
* due to the infrequency of EHV plant replacement, switchgear ratings are checked quarterly
| Switchgear ratings checked | 2023-12-04
This version is 206 days old

## 2) 11 kV & 6.6 kV Connections
11 kV & 6.6 kV Connections
The results given by this tool are based on high level approximations only. It should also be noted that the network may have changed since the last time the data was updated. As such, the outcome of a formal application may differ from the results given by this tool. For further information on how to interpret the data contained within this workbook please refer to the user guide embedded within the first tab. Please note that the value of headroom quoted by this tool is based on total capacity available for new connections, the column beside it shows the maximum size of a single connection, based on the on-site primary switchgear rating, which can be much lower. To reflect this the 'Can Connect?' RAG value is derived using the lowest of these two values. It is normally not possible to accommodate a single connection of more than 7 MW at 11 kV or 6.6 kV, this is based on the typical load rating of items of plant such as circuit breakers, current transformers and cable terminations. It is possible that due to these addtional factors and the point of connection requested that the maximum connection size is lower than the values shown below.
Inputs | [18 empty] | Key
Easting |  | Enter Data | [5 empty] | Use the controls to the left to find the nearest primary substations to your site. The results will be displayed in the table below. When the desired site capacity and connection type are entered an estimate of available headroom and connection feasibility will be displayed. The results are based on both local constraints and constraints at the associated BSP. | [10 empty] | RAG | Limiting factor: Headroom |  | Limiting factor: Switchgear rating
Northing |  | Enter Data | [17 empty] | Capacity <90% of headroom |  | Suitable
Capacity (MW) |  | Enter Data | [17 empty] | Capacity >90% & < 100% of headroom |  | N/A
Connection Type |  | Enter Data | [17 empty] | Capacity >100% of headroom |  | Unsuitable
Distribution Network Capacity Capacity | [18 empty] | Transmission Constraints (App G)
No | Distance (km) | Primary Substation |  |  | BSP Group |  |  | BCA Group (GSP) |  |  | Primary Substation Location |  | Headroom (MW) | Max Single circuit connection (MW) |  | Can Connect? (RAG) | Can Connect? (RAG) | Limiting factor | Materiality Headroom (MW) | Fault Level Headroom (kA) | Transmission System Comment (see tab 6 for more details)
[11 empty] | Easting | Northing
1 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
2 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
3 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
4 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
5 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
6 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
7 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
8 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
9 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
10 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
Connection Types
Demand Firm |  |  |  |  | The connection of load which is secure for a first circuit outage.
Demand N-0 |  |  |  |  | The connection of load which can be actively constrained off under outage conditions.
Generation Synchronous (LV) |  |  |  |  | Generation such as diesel or gas turbines connected to the HV network through step up transformers.
Generation Synchronous (HV) |  |  |  |  | Generation such as diesel or gas turbines connected to the HV network directly i.e. without step up transformers.
Generation Inverter Based |  |  |  |  | Generation technologies connected by inverters this typically includes solar and wind generators .
Battery Energy Storage |  |  |  |  | Inverter connected battery energy storage schemes.

## 3) 33 kV Connections
33 kV Connections
The results given by this tool are based on high level approximations only. It should also be noted that the network may have changed since the last time the data was updated. As such, the outcome of a formal application may differ from the results given by this tool. For further information on how to interpret the data contained within this workbook please refer to the user guide embedded within the first tab.
Please note that the value of headroom quoted by this tool is based on total capacity available for new connections not the maximum size of a single connection which can be much lower. It is normally not possible to accommodate a single connection of more than 40 MW at 33 kV. This is based on the typical load rating of items of plant such as circuit breakers, current transformers and cable terminations.
Inputs | [11 empty] | Key
Easting |  | Enter Data | [5 empty] | Use the controls to the left to find the nearest BSP to your site. The results will be displayed in the table below. When the desired site capacity and connection type are entered an estimate of available headroom and connection feasibility will be displayed. It should be noted that the network assets surrounding your site may not be fed from the closest BSP. |  |  |  |  | Capacity <90% of headroom
Northing |  | Enter Data | [10 empty] | Capacity >90% & < 100% of headroom
Capacity (MW) |  | Enter Data | [10 empty] | Capacity >100% of headroom
Connection Type |  | Enter Data
Distribution Network Capacity Capacity | [11 empty] | Transmission Constraints (App G)
No | Distance (km) | BSP |  |  | BCA Group (GSP) |  |  | BSP Location |  | Headroom (MW) | Can Connect? (RAG) | Materiality Headroom (MW) | Fault Level Headroom (kA) | Transmission System Comment (see tab 6 for more details)
[8 empty] | Easting | Northing
1 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
2 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
3 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
4 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
5 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
6 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
7 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
8 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
9 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
10 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
Connection Types
Demand Firm |  |  |  |  | The connection of load which is secure for a first circuit outage.
Demand N-0 |  |  |  |  | The connection of load which can be actively constrained off under outage conditions.
Generation Synchronous (LV) |  |  |  |  | Generation such as diesel or gas turbines connected to the EHV network through step up transformers.
Generation Inverter Based |  |  |  |  | Generation technologies connected by inverters this typically includes solar and wind generators .
Battery Energy Storage |  |  |  |  | Inverter connected battery energy storage schemes.

## 4) Primary Headroom Data
Primary Substation Headroom
Primary Substation | Voltage (kV) | BSP Group |  | BCA Group (GSP) | Primary Substation Location |  | Individual Circuit Capacity |  | Demand Headroom (MW) |  | Generation Headroom N-0 -(MW) |  |  | Battery Storage Headroom N-0 -(MW)
[5 empty] | Easting | Northing | CB Rating | MVA | Firm | N-0 | Inverter Based | Synchronous - LV | Synchronous - HV
ALBION ST | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 367434 | 426087 | 400 | 4.5726 | 0 | 11.5168 | 27.4154 | 4.7839 | 3.5056 | 11.5168 | 0 | 0 | Offers with ENW, due to be signed 20/08/2024 .Another parrallel submission made, offer due 28/06/2024
ALDERLEY | 11 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 385044 | 379026 | 400 | 7.621 | 9.8756 | 16.5656 | 8.984 | 1.9575 | 1.4344 | 8.984 | 1.4344 | 5.768 | 2nd Step offer with ENW, due to signed 15/07/2024.Offer with ENW due to sign 30/08/2024.Another submission made, awaiting Clock start date.
ALSTON | 11 | PENRITH & SHAP | PENRITH | HUTTON | 372125 | 546499 | 400 | 7.621 | 0 | 0 | 3.3047 | 3.3047 | 3.3047 | 0 | 3.2626 | 1.1073 | 2nd step offer signed 29/05/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024
AMBLESIDE | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 337602 | 503506 | 400 | 7.621 | 0 | 9.6047 | 29.6287 | 24.968 | 17.945 | 9.6047 | 0 | 0 | 2nd step offer signed 29/05/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024
ANCOATS NORTH T11 & T12 | 6.6 | RED BANK | RED BANK | WHITEGATE | 385022 | 398830 | 400 | 4.5726 | 0 | 2.7139 | 32.3302 | 6.5666 | 4.7912 | 2.7139 | 4.8939 | 0.33304 | Offers with ENW, due to be signed 28/08/2024
ANCOATS NORTH T14 | 6.6 | RED BANK | RED BANK | WHITEGATE | 385032 | 398840 | 400 | 4.5726 | 5.8273 | 10.5773 | 19.2839 | 19.2839 | 15.7107 | 10.5773 | 15.7536 | 7.6053 | Offers with ENW, due to be signed 28/08/2024
ANNIE PIT | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 300011 | 527810 | 400 | 7.621 | 3.8444 | 9.3444 | 7 | 1.9575 | 1.4344 | 7 | 0 | 0 | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
ANSDELL | 6.6 | LYTHAM | LYTHAM | PENWORTHAM | 334416 | 428229 | 800 | 9.1452 | 5.2586 | 8.2586 | 21.7548 | 9.7694 | 7.1281 | 8.2586 | 0 | 0 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
ARDWICK | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 384753 | 397415 | 630 | 7.2019 | 0 | 5.0887 | 11.2179 | 1.9575 | 1.4344 | 5.0887 | 1.4344 | 0 | Offer with ENW ,due signing by 29/08/2024
ARNSIDE | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 346495 | 478180 | 400 | 7.621 | 0 | 9.6047 | 18.3845 | 18.3845 | 18.3845 | 9.6047 | 0 | 0 | 2nd step offer signed 29/05/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024
ASHTON (GOLBORNE) | 6.6 | ORRELL | ORRELL | WASHWAY FARM / KIRKBY | 357056 | 400663 | 800 | 9.1452 | 0 | 2.446 | 26.2485 | 8.2984 | 6.0548 | 2.446 | 5.9845 | 2.5354 | #N/A
ASHTON (RIBBLE) | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 350275 | 430526 | 630 | 7.2019 | 0.05585 | 0.05585 | 5.57 | 1.9575 | 1.4344 | 0.05585 | 1.4344 | 0 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
ASHTON ON MERSEY | 6.6 | SALE | SALE | CARRINGTON | 377188 | 392252 | 630 | 7.2019 | 9.5983 | 13.7383 | 28.8941 | 8.7366 | 6.3744 | 13.7383 | 6.5315 | 13.4847 | N/A
ASHTON UNDER LYNE T11 & T12 | 6.6 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 393275 | 399319 | 630 | 7.2019 | 5.1037 | 9.2407 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer with ENW ,due signing by 29/08/2024
ASHTON UNDER LYNE T13 | 6.6 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 393285 | 399329 | 630 | 7.2019 | 6.9141 | 11.6641 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer with ENW ,due signing by 29/08/2024
ASHWOOD DALE | 6.6 | BUXTON | BUXTON | STALYBRIDGE | 406537 | 373050 | 630 | 7.2019 | 4.7176 | 9.2255 | 31.4391 | 9.2649 | 6.7599 | 9.2255 | 1.3561 | 10.6051 | Offer with ENW ,due signing by 29/08/2024
ASKAM | 11 | ULVERSTON | ULVERSTON | HARKER | 321558 | 477806 | 630 | 12.0031 | 1.548 | 8.528 | 11.7207 | 6.6451 | 4.7759 | 8.528 | 6.4697 | 8.428 | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
ASKERTON CASTLE | 11 | - | - | HARKER | 354779 | 568913 | 800 | 15.242 | 0.92953 | 1.6295 | 3.9789 | 3.9789 | 3.9789 | 1.6295 | 3.9789 | 1.6295 | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
ASPATRIA | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 314417 | 542840 | 400 | 7.621 | 4.1682 | 6.1682 | 7 | 1.9575 | 1.4344 | 6.1682 | 0 | 0 | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
ATHERTON TOWN CENTRE | 11 | ATHERTON | ATHERTON | KEARSLEY | 367546 | 403338 | 800 | 15.242 | 0.72274 | 0.72274 | 29.5131 | 4.8591 | 3.4923 | 0.72274 | 3.7461 | 0 | PP submitted, awaiting clock start date
ATHLETIC ST | 6.6 | BURNLEY | BURNLEY | ROCHDALE | 385381 | 432208 | 400 | 4.5726 | 5.3292 | 8.8292 | 22.71 | 13.0108 | 9.493 | 8.8292 | 9.6723 | 7.1892 | Offers with ENW, due to be signed 20/08/2024 .Another parrallel submission made, offer due 28/06/2024
AVENHAM | 6.6 | PRESTON EAST | PRESTON EAST | PENWORTHAM | 354028 | 429192 | 800 | 9.1452 | 0.80659 | 0.80659 | 11.2179 | 1.9575 | 1.4344 | 0.80659 | 1.4344 | 0 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
BAGULEY | 11 | SALE | SALE | CARRINGTON | 380562 | 389035 | 400 | 7.621 | 3.6678 | 8.3048 | 30.0013 | 9.8974 | 7.1135 | 8.3048 | 7.6584 | 8.6278 | N/A
BAMBER BRIDGE | 11 | RIBBLE | RIBBLE | PENWORTHAM | 356431 | 426698 | 630 | 12.0031 | 4.8943 | 9.0313 | 11.2179 | 1.9575 | 1.4344 | 9.0313 | 1.4344 | 10.2623 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
BARBARA ST | 6.6 | BOLTON | BOLTON | KEARSLEY | 370695 | 407609 | 630 | 7.2019 | 0 | 3.0385 | 11.2179 | 1.9575 | 1.4344 | 3.0385 | 1.4344 | 9.8525 | PP submitted, awaiting clock start date
BARROW | 11 | BARROW & SANDGATE | BARROW | HARKER | 319709 | 470489 | 630 | 12.0031 | 13.8644 | 18.3644 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 8.0292 | 18.3194 | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
BARTON DOCK RD | 6.6 | BARTON | BARTON | CARRINGTON | 378864 | 395534 | 630 | 7.2019 | 3.5741 | 9.8241 | 11.2179 | 1.9575 | 1.4344 | 9.8241 | 1.4344 | 10.2441 | N/A
BEDFORD | 11 | ATHERTON | ATHERTON | KEARSLEY | 366258 | 399876 | 800 | 15.242 | 0.72274 | 0.72274 | 28.5003 | 10.2671 | 7.3791 | 0.72274 | 7.2768 | 0 | PP submitted, awaiting clock start date
BELGRAVE | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 393008 | 403366 | 630 | 7.2019 | 7.6335 | 11.1335 | 23.1258 | 11.1722 | 8.1515 | 11.1335 | 9.5768 | 4.6017 | Offers with ENW, due to be signed 28/08/2024
BENCHILL | 11 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 382454 | 388020 | 400 | 7.621 | 7.8921 | 9.8921 | 7.06 | 1.9575 | 1.4344 | 7.06 | 1.4344 | 9.8921 | 2nd Step offer with ENW, due to signed 15/07/2024.Offer with ENW due to sign 30/08/2024.Another submission made, awaiting Clock start date.
BENTHAM | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 366887 | 470130 | 400 | 7.621 | 0 | 5.2692 | 7.259 | 7.259 | 7.259 | 5.2692 | 0 | 0 | 2nd step offer signed 29/05/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024
BISPHAM | 6.6 | BISPHAM | BISPHAM | PENWORTHAM | 331655 | 439667 | 630 | 7.2019 | 5.6529 | 10.2899 | 11.2179 | 1.9575 | 1.4344 | 10.2899 | 1.4344 | 10.1499 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
BLACKBULL | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 353041 | 433005 | 630 | 7.2019 | 6.4702 | 10.6072 | 11.2179 | 1.9575 | 1.4344 | 10.6072 | 1.4344 | 6.4123 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
BLACKBURN | 6.6 | BLACKBURN | BLACKBURN | PENWORTHAM | 370584 | 429294 | 400 | 4.5726 | 7.4664 | 12.1034 | 31.3792 | 9.4773 | 6.9149 | 12.1034 | 6.1854 | 10.7604 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
BLACKFRIARS | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 383030 | 399104 | 630 | 7.2019 | 0 | 13.5457 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 0 | PP submitted, awaiting clock start date
BLACKLEY | 6.6 | RED BANK | RED BANK | WHITEGATE | 383882 | 403258 | 630 | 7.2019 | 10.143 | 14.78 | 30.3333 | 13.6523 | 9.9611 | 14.78 | 9.7958 | 15.68 | Offers with ENW, due to be signed 28/08/2024
BLACKPOOL | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 330835 | 435308 | 630 | 7.2019 | 11.6204 | 19.3704 | 33.7019 | 8.6436 | 6.3066 | 19.3704 | 6.7082 | 17.439 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
BOLLINGTON | 11 | MACCLESFIELD | MACCLESFIELD | MACCLESFIELD | 393042 | 377873 | 630 | 12.0031 | 0.50979 | 2.9321 | 11.2179 | 1.9575 | 1.4344 | 2.9321 | 1.4344 | 0 | N/A
BOLTON BY BOWLAND | 11 | PADIHAM | PADIHAM | PADIHAM | 378320 | 449559 | 400 | 7.621 | 0 | 4.3239 | 8.4802 | 8.4802 | 8.4802 | 4.3239 | 8.4802 | 3.8465 | Two parrallel 2nd step offer with ENW due to be signed 04/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Another parrallel submission clock started, offer due 28/08/2024
BOLTON LE SANDS | 11 | LANCASTER | LANCASTER | HEYSHAM | 347707 | 467237 | 400 | 7.621 | 4.2023 | 4.2023 | 11.2179 | 1.9575 | 1.4344 | 4.2023 | 1.5151 | 5.0572 | Offer with ENW, due to be signed 30/08/2024. Parrallel submission made, offer due 08/06/2024.Another parrallel submission made, awaiting clock start date.
BOTANY BAY | 11 | LEYLAND | LEYLAND | PENWORTHAM | 359442 | 418850 | 630 | 12.0031 | 2.3738 | 10.3738 | 20.5557 | 20.5557 | 19.2357 | 10.3738 | 19.2177 | 9.8578 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
BOW LANE | 11 | LEYLAND | LEYLAND | PENWORTHAM | 354895 | 422392 | 400 | 7.621 | 2.5751 | 7.2121 | 29.2513 | 6.4583 | 4.6417 | 7.2121 | 3.7567 | 5.6289 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
BOWATERS | 11 | BARROW & SANDGATE | BARROW | HARKER | 319579 | 472480 | 400 | 7.621 | 13.7079 | 34.2079 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0.31765 | 2.6844 | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
BOWDON | 11 | ALTRINCHAM | ALTRINCHAM | CARRINGTON | 376743 | 386810 | 400 | 7.621 | 5.7917 | 10.4287 | 32.4374 | 12.4895 | 8.9764 | 10.4287 | 8.9022 | 10.8219 | N/A
BRADFORD | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 387613 | 397710 | 400 | 4.5726 | 0 | 5.0887 | 11.2179 | 1.9575 | 1.4344 | 5.0887 | 1.4344 | 0 | Offer with ENW ,due signing by 29/08/2024
BRADSHAWGATE | 6.6 | BOLTON | BOLTON | KEARSLEY | 371891 | 408910 | 400 | 4.5726 | 8.9885 | 19.6285 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | PP submitted, awaiting clock start date
BRAMHALL | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 389440 | 386463 | 630 | 12.0031 | 3.8562 | 7.3562 | 24.6012 | 12.4696 | 8.9622 | 7.3562 | 9.1136 | 8.37 | 2nd step offer with ENW,due to be signed 06/06/2024.Parrallel submission offer with ENW, due to be signed 29/08/2024
BRIDGEWATER | 6.6 | BLOOM ST | BLOOM ST | SOUTH MANCHESTER | 383543 | 397628 | 800 | 9.1452 | 0 | 6.8645 | 30.3079 | 13.2109 | 9.6391 | 6.8645 | 9.8568 | 6.6125 | 2nd Step offer with ENW, due to signed 15/07/2024.Offer with ENW due to sign 30/08/2024.Another submission made, awaiting Clock start date.
BRINKSWAY | 6.6 | ADSWOOD | ADSWOOD | BREDBURY | 388434 | 389885 | 400 | 4.5726 | 4.9073 | 10.079 | 30.1118 | 12.7883 | 9.3307 | 10.079 | 9.4256 | 12.706 | 2nd step offer with ENW,due to be signed 06/06/2024.Parrallel submission offer with ENW, due to be signed 29/08/2024
BROADHEATH | 11 | ALTRINCHAM | ALTRINCHAM | CARRINGTON | 376412 | 389026 | 400 | 7.621 | 11.1799 | 16.405 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0.31765 | 2.6844 | N/A
BROADWAY | 6.6 | LANCASTER | LANCASTER | HEYSHAM | 344792 | 464471 | 630 | 7.2019 | 4.2023 | 4.2023 | 11.2179 | 1.9575 | 1.4344 | 4.2023 | 1.5151 | 5.0572 | Offer with ENW, due to be signed 30/08/2024. Parrallel submission made, offer due 08/06/2024.Another parrallel submission made, awaiting clock start date.
BUCKSHAW | 11 | LEYLAND | LEYLAND | PENWORTHAM | 356748 | 421312 | 630 | 12.0031 | 8.5411 | 13.0411 | 27.8355 | 13.9652 | 10.0371 | 13.0411 | 9.8081 | 10.2615 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
BURNLEY | 6.6 | BURNLEY | BURNLEY | ROCHDALE | 385569 | 434469 | 400 | 4.5726 | 16.2385 | 16.2385 | 15.2123 | 5.215 | 3.805 | 15.2123 | 3.8058 | 9.6649 | Offers with ENW, due to be signed 20/08/2024 .Another parrallel submission made, offer due 28/06/2024
BURNLEY CENTRE | 6.6 | BURNLEY | BURNLEY | ROCHDALE | 384308 | 432288 | 630 | 7.2019 | 9.7989 | 9.7989 | 23.2074 | 9.1759 | 6.695 | 9.7989 | 6.7909 | 5.3989 | Offers with ENW, due to be signed 20/08/2024 .Another parrallel submission made, offer due 28/06/2024
BURNLEY NORTH | 6.6 | BURNLEY | BURNLEY | ROCHDALE | 384418 | 434168 | 630 | 7.2019 | 0 | 8.8072 | 17.9015 | 17.9015 | 14.198 | 8.8072 | 17.1739 | 8.8706 | Offers with ENW, due to be signed 20/08/2024 .Another parrallel submission made, offer due 28/06/2024
BURROW BECK | 11 | LANCASTER | LANCASTER | HEYSHAM | 347903 | 458401 | 630 | 12.0031 | 0 | 2.2239 | 7.5787 | 1.2478 | 0.8968 | 2.2239 | 0.7451 | 5.0572 | Offer with ENW, due to be signed 30/08/2024. Parrallel submission made, offer due 08/06/2024.Another parrallel submission made, awaiting clock start date.
BURSCOUGH BRIDGE | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 344595 | 412486 | 630 | 12.0031 | 5.1319 | 5.7161 | 15.5363 | 8.6641 | 6.2271 | 5.7161 | 4.4683 | 2.8737 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
BURY TOWN CENTRE | 6.6 | BURY | BURY | KEARSLEY | 380863 | 410807 | 400 | 4.5726 | 7.037 | 11.174 | 11.2179 | 1.9575 | 1.4344 | 11.174 | 1.4344 | 8.2958 | PP submitted, awaiting clock start date
BUSHELL ST | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 353809 | 430094 | 400 | 4.5726 | 5.7554 | 9.8954 | 11.2179 | 1.9575 | 1.4344 | 9.8954 | 1.4344 | 9.8954 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
CAMPBELL ST | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 372937 | 406428 | 630 | 12.0031 | 0 | 8.4423 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 5.9733 | PP submitted, awaiting clock start date
CANNON ST | 6.6 | RED BANK | RED BANK | WHITEGATE | 384064 | 398635 | 400 | 4.5726 | 6.6045 | 27.6045 | 2.3178 | 0.37591 | 0.27427 | 2.3178 | 0.16545 | 1.3982 | Offers with ENW, due to be signed 28/08/2024
CAPONTREE | 11 | CARLISLE | CARLISLE | HARKER | 352906 | 559671 | 400 | 7.621 | 14.6493 | 17.6283 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
CARLETON | 11 | EGREMONT | EGREMONT | HARKER | 308796 | 498305 | 630 | 12.0031 | 3.0533 | 5.5533 | 8.424 | 8.424 | 8.424 | 5.5533 | 8.424 | 5.5206 | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
CARLISLE NORTH | 11 | - | - | HARKER | 338547 | 560280 | 630 | 12.0031 | 2.5529 | 23.0529 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 0.31765 | 1.6795 | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
CARR ST | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 376984 | 401329 | 400 | 7.621 | 0 | 14.0701 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | PP submitted, awaiting clock start date
CASTLETON | 6.6 | CASTLETON | CASTLETON | ROCHDALE | 388461 | 411290 | 630 | 7.2019 | 5.6307 | 10.2677 | 21.456 | 3.4799 | 2.539 | 10.2677 | 2.09 | 9.5109 | Offers with ENW, due to be signed 20/08/2024 .Another parrallel submission made, offer due 28/06/2024
CATTERALL WATERWORKS | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 349381 | 442178 | 400 | 4.5726 | 0 | 0 | 9.5568 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
CECIL ST | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 331301 | 437023 | 630 | 7.2019 | 7.8891 | 13.0791 | 30.7725 | 16.1604 | 11.7911 | 13.0791 | 12.1148 | 12.9781 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
CENTRAL MANCHESTER | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 384852 | 397718 | 630 | 7.2019 | 0 | 5.0887 | 11.2179 | 1.9575 | 1.4344 | 5.0887 | 1.4344 | 0 | Offer with ENW ,due signing by 29/08/2024
CHADDERTON | 6.6 | CHADDERTON | CHADDERTON | WHITEGATE | 389161 | 403872 | 400 | 4.5726 | 0 | 0 | 28.609 | 4.64 | 3.3854 | 0 | 1.3649 | 0 | Offers with ENW, due to be signed 28/08/2024
CHAMBERHALL | 6.6 | BURY | BURY | KEARSLEY | 380280 | 411215 | 600 | 6.8589 | 3.517 | 8.837 | 11.2179 | 1.9575 | 1.4344 | 8.837 | 1.4344 | 8.4761 | PP submitted, awaiting clock start date
CHAPEL WHARF | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 383499 | 398634 | 630 | 7.2019 | 0 | 12.5943 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 0 | PP submitted, awaiting clock start date
CHASSEN RD | 6.6 | BARTON | BARTON | CARRINGTON | 375542 | 394453 | 630 | 7.2019 | 1.9942 | 12.8942 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | N/A
CHATSWORTH ST | 11 | BARROW & SANDGATE | BARROW | HARKER | 319188 | 470003 | 800 | 15.242 | 7.7147 | 15.1147 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 7.3076 | 14.6753 | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
CHEADLE HEATH | 6.6 | ADSWOOD | ADSWOOD | BREDBURY | 387062 | 389054 | 630 | 7.2019 | 4.9776 | 8.4776 | 22.4112 | 10.8557 | 7.9206 | 8.4776 | 8.0328 | 8.3048 | 2nd step offer with ENW,due to be signed 06/06/2024.Parrallel submission offer with ENW, due to be signed 29/08/2024
CHEADLE HULME | 11 | ADSWOOD | ADSWOOD | BREDBURY | 387386 | 386308 | 630 | 12.0031 | 7.144 | 11.781 | 31.3411 | 12.9619 | 9.316 | 11.781 | 9.2691 | 12.9036 | 2nd step offer with ENW,due to be signed 06/06/2024.Parrallel submission offer with ENW, due to be signed 29/08/2024
CHEETHAM HILL | 6.6 | AGECROFT | AGECROFT | KEARSLEY | 383606 | 402218 | 400 | 4.5726 | 2.8479 | 2.8479 | 22.1947 | 15.1094 | 11.0242 | 2.8479 | 11.1639 | 2.7039 | PP submitted, awaiting clock start date
CHELFORD | 11 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 382184 | 373490 | 400 | 7.621 | 9.8756 | 16.5656 | 8.968 | 1.9575 | 1.4344 | 8.968 | 1.4344 | 5.768 | 2nd Step offer with ENW, due to signed 15/07/2024.Offer with ENW due to sign 30/08/2024.Another submission made, awaiting Clock start date.
CHESTER RD T11 & T12 | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 381030 | 396165 | 630 | 7.2019 | 0.44411 | 5.4441 | 24.4081 | 8.2193 | 5.997 | 5.4441 | 5.9831 | 2.9543 | 2nd Step offer with ENW, due to signed 15/07/2024.Offer with ENW due to sign 30/08/2024.Another submission made, awaiting Clock start date.
CHESTER RD T13 | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 381040 | 396175 | 630 | 7.2019 | 4.1074 | 13.2137 | 18.6656 | 18.6656 | 17.1639 | 13.2137 | 17.154 | 12.6129 | 2nd Step offer with ENW, due to signed 15/07/2024.Offer with ENW due to sign 30/08/2024.Another submission made, awaiting Clock start date.
CHORLEY SOUTH | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 358658 | 417041 | 800 | 15.242 | 1.182 | 4.682 | 24.012 | 13.4049 | 9.6343 | 4.682 | 5.1053 | 5.0492 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
CHORLTON | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 381411 | 393754 | 400 | 4.5726 | 4.757 | 10.757 | 7.06 | 1.9575 | 1.4344 | 7.06 | 1.4344 | 9.12 | 2nd Step offer with ENW, due to signed 15/07/2024.Offer with ENW due to sign 30/08/2024.Another submission made, awaiting Clock start date.
CHURCH | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 374687 | 428919 | 800 | 9.1452 | 0.93241 | 11.9324 | 18.6892 | 18.6892 | 16.8754 | 11.9324 | 7.0436 | 11.2916 | Two parrallel 2nd step offer with ENW due to be signed 04/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Another parrallel submission clock started, offer due 28/08/2024
CLARENDON RD | 6.6 | BLACKBURN | BLACKBURN | PENWORTHAM | 369051 | 429883 | 400 | 4.5726 | 6.9961 | 11.6331 | 26.0405 | 6.698 | 4.8871 | 11.6331 | 2.9125 | 3.9899 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
CLAUGHTON | 11 | LANCASTER | LANCASTER | HEYSHAM | 355872 | 466268 | 630 | 12.0031 | 0.26281 | 3.7628 | 8.4614 | 1.9575 | 1.4344 | 3.7628 | 1.5151 | 3.7068 | Offer with ENW, due to be signed 30/08/2024. Parrallel submission made, offer due 08/06/2024.Another parrallel submission made, awaiting clock start date.
BLACKBURN RD CLAYTON | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 374632 | 430529 | 630 | 7.2019 | 11.6258 | 19.3058 | 27.6988 | 10.708 | 7.8129 | 19.3058 | 7.0436 | 19.3058 | Two parrallel 2nd step offer with ENW due to be signed 04/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Another parrallel submission clock started, offer due 28/08/2024
CLEVELEYS | 6.6 | BISPHAM | BISPHAM | PENWORTHAM | 332286 | 443104 | 630 | 7.2019 | 4.4479 | 7.9479 | 11.2179 | 1.9575 | 1.4344 | 7.9479 | 1.4344 | 7.8631 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
CLIFTON JUNCTION | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 379289 | 403073 | 630 | 12.0031 | 0 | 6.7153 | 7 | 1.9575 | 1.4344 | 6.7153 | 1.4344 | 4.7605 | PP submitted, awaiting clock start date
CLOVER HILL | 6.6 | NELSON | NELSON | PADIHAM | 386638 | 437064 | 630 | 7.2019 | 4.5373 | 18.1909 | 0 | 0 | 0 | 0 | 0 | 0 | Two parrallel 2nd step offer with ENW due to be signed 04/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Another parrallel submission clock started, offer due 28/08/2024
COG LANE | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 382462 | 432232 | 800 | 9.1452 | 5.6096 | 16.0345 | 43.3786 | 8.2693 | 6.0335 | 16.0345 | 1.845 | 13.1837 | Two parrallel 2nd step offer with ENW due to be signed 04/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Another parrallel submission clock started, offer due 28/08/2024
CONISTON | 11 | ULVERSTON | ULVERSTON | HARKER | 329874 | 497641 | 400 | 7.621 | 0 | 1.4343 | 4.8516 | 4.8516 | 4.8516 | 1.4343 | 4.8516 | 1.4303 | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
COPSE RD | 6.6 | THORNTON | THORNTON | STANAH | 333013 | 446934 | 630 | 7.2019 | 5.5405 | 7.1775 | 23.0632 | 4.9134 | 3.5849 | 7.1775 | 2.296 | 3.1319 | N/A
COX GREEN | 11 | BOLTON | BOLTON | KEARSLEY | 371893 | 413641 | 630 | 12.0031 | 4.2053 | 8.5053 | 11.2179 | 1.9575 | 1.4344 | 8.5053 | 1.4344 | 8.1583 | PP submitted, awaiting clock start date
CRAGGS ROW | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 353740 | 430080 | 630 | 7.2019 | 5.7554 | 9.8954 | 11.2179 | 1.9575 | 1.4344 | 9.8954 | 1.4344 | 9.0804 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
CROWN LANE | 11 | WESTHOUGHTON | WESTHOUGHTON | KEARSLEY | 362706 | 410859 | 400 | 7.621 | 2.415 | 7.052 | 32.4077 | 7.2306 | 5.1968 | 7.052 | 0.088852 | 0 | PP submitted, awaiting clock start date
CULCHETH | 11 | GOLBORNE | GOLBORNE | BOLD | 365430 | 395366 | 400 | 7.621 | 0 | 2.5533 | 13.5703 | 10.523 | 7.7111 | 2.5533 | 0 | 0 | N/A
CUTACRE | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 369848 | 404515 | 630 | 12.0031 | 0 | 9.939 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | PP submitted, awaiting clock start date
DALTON | 11 | ULVERSTON | ULVERSTON | HARKER | 323582 | 474255 | 400 | 7.621 | 1.548 | 9.028 | 32.4628 | 15.5023 | 11.1418 | 9.028 | 11.6712 | 8.928 | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
DEANSGATE | 6.6 | BLOOM ST | BLOOM ST | SOUTH MANCHESTER | 383463 | 398149 | 630 | 7.2019 | 0 | 12.5705 | 29.9539 | 12.5408 | 9.1501 | 12.5705 | 9.1618 | 11.3246 | 2nd Step offer with ENW, due to signed 15/07/2024.Offer with ENW due to sign 30/08/2024.Another submission made, awaiting Clock start date.
DENTON EAST | 6.6 | DROYLSDEN | DROYLSDEN | STALYBRIDGE | 392394 | 395626 | 630 | 7.2019 | 10.2163 | 14.8533 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | Offer with ENW ,due signing by 29/08/2024
DENTON WEST | 6.6 | DROYLSDEN | DROYLSDEN | STALYBRIDGE | 390380 | 395565 | 400 | 4.5726 | 5.9174 | 10.5544 | 11.2179 | 1.9575 | 1.4344 | 10.5544 | 1.4344 | 11.2179 | Offer with ENW ,due signing by 29/08/2024
DICKINSON ST | 6.6 | BLOOM ST | BLOOM ST | SOUTH MANCHESTER | 384109 | 397722 | 800 | 9.1452 | 0 | 3.8073 | 36.7251 | 12.4915 | 9.1141 | 3.8073 | 9.5067 | 5.4068 | 2nd Step offer with ENW, due to signed 15/07/2024.Offer with ENW due to sign 30/08/2024.Another submission made, awaiting Clock start date.
DIDSBURY | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 384792 | 391153 | 630 | 7.2019 | 8.3769 | 13.0139 | 7.06 | 1.9575 | 1.4344 | 7.06 | 1.4344 | 11.2179 | 2nd Step offer with ENW, due to signed 15/07/2024.Offer with ENW due to sign 30/08/2024.Another submission made, awaiting Clock start date.
DODGSON RD | 6.6 | PRESTON EAST | PRESTON EAST | PENWORTHAM | 355190 | 430397 | 400 | 4.5726 | 0.80659 | 0.80659 | 11.2179 | 1.9575 | 1.4344 | 0.80659 | 1.4344 | 0 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
DOUGLAS ST | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 352220 | 429932 | 400 | 4.5726 | 8.492 | 15.152 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
DROYLSDEN EAST | 6.6 | DROYLSDEN | DROYLSDEN | STALYBRIDGE | 390532 | 398053 | 630 | 7.2019 | 6.2684 | 10.9054 | 11.2179 | 1.9575 | 1.4344 | 10.9054 | 1.4344 | 9.4097 | Offer with ENW ,due signing by 29/08/2024
DUKINFIELD | 6.6 | HYDE | HYDE | STALYBRIDGE | 394372 | 396438 | 400 | 4.5726 | 10.0255 | 14.6625 | 23.8018 | 3.8603 | 2.8166 | 14.6625 | 2.6715 | 15.6217 | Offer with ENW ,due signing by 29/08/2024
DUMERS LANE | 11 | BURY | BURY | KEARSLEY | 380057 | 408141 | 400 | 7.621 | 3.1823 | 9.6823 | 11.2179 | 1.9575 | 1.4344 | 9.6823 | 1.4344 | 7.2779 | PP submitted, awaiting clock start date
DUMPLINGTON | 11 | BARTON | BARTON | CARRINGTON | 376770 | 397157 | 800 | 15.242 | 11.1196 | 12.5196 | 9.6557 | 1.5897 | 1.1426 | 9.6557 | 0.99981 | 8.4492 | N/A
EASTLANDS | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 386458 | 398693 | 800 | 9.1452 | 0 | 5.0887 | 0 | 0 | 0 | 0 | 0 | 0 | Offer with ENW ,due signing by 29/08/2024
EASTON | 11 | - | - | HARKER | 343201 | 571738 | 800 | 15.242 | 0 | 0.11433 | 2.8786 | 2.8786 | 2.8786 | 0.11433 | 2.8786 | 0 | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
EGREMONT | 11 | EGREMONT | EGREMONT | HARKER | 301070 | 513074 | 400 | 7.621 | 2.6834 | 5.1834 | 21.2377 | 17.0641 | 12.2643 | 5.1834 | 12.6319 | 4.995 | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
EMBLETON | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 315767 | 529389 | 630 | 12.0031 | 3.2201 | 14.2201 | 7 | 1.9575 | 1.4344 | 7 | 0 | 0 | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
EXCHANGE ST | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 369100 | 423028 | 800 | 9.1452 | 0 | 6.4001 | 23.5705 | 4.7839 | 3.5056 | 6.4001 | 0 | 0 | Offers with ENW, due to be signed 20/08/2024 .Another parrallel submission made, offer due 28/06/2024
FAILSWORTH | 6.6 | CHADDERTON | CHADDERTON | WHITEGATE | 389631 | 401496 | 400 | 4.5726 | 0 | 0 | 28.9569 | 9.3479 | 6.8205 | 0 | 1.3649 | 0 | Offers with ENW, due to be signed 28/08/2024
FALLOWFIELD | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 385608 | 393881 | 400 | 4.5726 | 6.6582 | 11.2952 | 7.06 | 1.9575 | 1.4344 | 7.06 | 1.4344 | 11.2006 | 2nd Step offer with ENW, due to signed 15/07/2024.Offer with ENW due to sign 30/08/2024.Another submission made, awaiting Clock start date.
FARNWORTH | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 373726 | 405532 | 800 | 15.242 | 0 | 9.9316 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | PP submitted, awaiting clock start date
FENISCOWLES | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 364660 | 425120 | 630 | 7.2019 | 0 | 14.0561 | 19.0252 | 4.7839 | 3.5056 | 14.0561 | 0 | 0 | Offers with ENW, due to be signed 20/08/2024 .Another parrallel submission made, offer due 28/06/2024
FERODO | 11 | NEW MILLS | NEW MILLS | STALYBRIDGE | 405720 | 381338 | 630 | 12.0031 | 1.2618 | 8.6091 | 30.4491 | 15.8424 | 11.3862 | 8.6091 | 11.2192 | 5.6473 | Offer with ENW ,due signing by 29/08/2024
FLAT LANE | 11 | PADIHAM | NELSON | PADIHAM | 383248 | 456995 | 630 | 12.0031 | 0 | 5.0323 | 11.0501 | 11.0501 | 11.0501 | 5.0323 | 11.0501 | 4.4257 | Two parrallel 2nd step offer with ENW due to be signed 04/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Another parrallel submission clock started, offer due 28/08/2024
FREDERICK RD | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 381697 | 399348 | 800 | 9.1452 | 0 | 11.074 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 0 | PP submitted, awaiting clock start date
FUSEHILL | 11 | CARLISLE | CARLISLE | HARKER | 341042 | 555452 | 400 | 7.621 | 2.9169 | 9.4169 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
GALE | 6.6 | BELFIELD | BELFIELD | ROCHDALE | 389570 | 414943 | 400 | 4.5726 | 11.9053 | 11.9053 | 30.4947 | 12.282 | 8.9613 | 11.9053 | 8.6697 | 0 | Offers with ENW, due to be signed 20/08/2024 .Another parrallel submission made, offer due 28/06/2024
GARSTANG | 6.6 | THORNTON | THORNTON | STANAH | 348319 | 445221 | 630 | 7.2019 | 1.1719 | 1.1719 | 14.6333 | 9.213 | 6.7511 | 1.1719 | 9.0987 | 0.2593 | N/A
GATLEY | 6.6 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 384242 | 388388 | 400 | 4.5726 | 1.4591 | 11.9591 | 8.968 | 1.9575 | 1.4344 | 8.968 | 1.4344 | 5.768 | 2nd Step offer with ENW, due to signed 15/07/2024.Offer with ENW due to sign 30/08/2024.Another submission made, awaiting Clock start date.
GIDLOW | 6.6 | WIGAN | WIGAN | KIRKBY | 357620 | 406662 | 400 | 4.5726 | 2.1518 | 6.7888 | 32.1414 | 12.1124 | 8.8375 | 6.7888 | 8.9257 | 9.6892 | 2nd step offer with ENW,due to be signed 04/06/2024 .Parrallel submission offer with ENW, due to be signed 29/08/2024
GILLSROW | 11 | PENRITH & SHAP | PENRITH | HUTTON | 337117 | 526444 | 630 | 12.0031 | 0 | 0 | 7.5611 | 7.5611 | 7.5611 | 0 | 7.4769 | 2.881 | 2nd step offer signed 29/05/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024
GLAXO | 11 | ULVERSTON | ULVERSTON | HARKER | 330458 | 477825 | 400 | 7.621 | 6.2572 | 18.2072 | 10.1516 | 1.6714 | 1.2013 | 10.1516 | 1.4212 | 12.0107 | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
GLOSSOP | 11 | HYDE | HYDE | STALYBRIDGE | 402300 | 394074 | 630 | 12.0031 | 8.1084 | 12.7454 | 31.2376 | 5.5172 | 4.043 | 12.7454 | 5.4751 | 12.055 | Offer with ENW ,due signing by 29/08/2024
GOLBORNE | 11 | GOLBORNE | GOLBORNE | BOLD | 360621 | 397766 | 800 | 15.242 | 0.65483 | 6.1548 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0 | 0 | N/A
GOWHOLE | 11 | NEW MILLS | NEW MILLS | STALYBRIDGE | 401104 | 383846 | 400 | 7.621 | 4.6141 | 8.6091 | 29.9812 | 10.3707 | 7.4536 | 8.6091 | 7.0494 | 5.6473 | Offer with ENW ,due signing by 29/08/2024
GRANE RD | 6.6 | ROSSENDALE | ROSSENDALE | PADIHAM | 378312 | 422726 | 400 | 4.5726 | 9.2872 | 14.3872 | 24.7332 | 7.1187 | 5.194 | 14.3872 | 5.885 | 14.3872 | Two parrallel 2nd step offer with ENW due to be signed 04/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Another parrallel submission clock started, offer due 28/08/2024
GRANGE | 11 | ULVERSTON | ULVERSTON | HARKER | 340240 | 478314 | 400 | 7.621 | 4.5683 | 10.5683 | 21.0097 | 21.0097 | 19.1881 | 10.5683 | 19.5311 | 10.7263 | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
GREAT HARWOOD | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 373765 | 431955 | 630 | 7.2019 | 8.8093 | 16.9293 | 19.4454 | 3.3934 | 2.4759 | 16.9293 | 1.1085 | 9.368 | Two parrallel 2nd step offer with ENW due to be signed 04/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Another parrallel submission clock started, offer due 28/08/2024
GREEN LANE (ALTRINCHAM) | 11 | ALTRINCHAM | ALTRINCHAM | CARRINGTON | 378744 | 387772 | 400 | 7.621 | 5.5419 | 10.1789 | 32.2668 | 15.7277 | 11.3038 | 10.1789 | 11.1508 | 10.8283 | N/A
GREEN LANE (HAZEL GROVE) | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 391570 | 387132 | 400 | 7.621 | 0 | 3.9671 | 33.5043 | 7.5382 | 5.4178 | 3.9671 | 5.6166 | 0.45951 | 2nd step offer with ENW,due to be signed 06/06/2024.Parrallel submission offer with ENW, due to be signed 29/08/2024
GREEN ST T11 | 6.6 | WIGAN | WIGAN | KIRKBY | 358235 | 404898 | 630 | 7.2019 | 0 | 3.9418 | 21.3921 | 9.1254 | 6.6581 | 3.9418 | 4.1968 | 3.8848 | 2nd step offer with ENW,due to be signed 04/06/2024 .Parrallel submission offer with ENW, due to be signed 29/08/2024
GREEN ST T12 & T13 | 6.6 | WIGAN | WIGAN | KIRKBY | 358225 | 404888 | 630 | 7.2019 | 3.0793 | 10.1549 | 32.3774 | 7.5217 | 5.488 | 10.1549 | 5.7981 | 10.2071 | 2nd step offer with ENW,due to be signed 04/06/2024 .Parrallel submission offer with ENW, due to be signed 29/08/2024
GREENFIELD | 11 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 399322 | 404583 | 800 | 15.242 | 12.5334 | 17.0334 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer with ENW ,due signing by 29/08/2024
GREENHILL | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 393262 | 404755 | 400 | 4.5726 | 15.4142 | 24.4519 | 55.5263 | 9.7225 | 7.0938 | 24.4519 | 6.8407 | 4.6017 | Offers with ENW, due to be signed 28/08/2024
GRIFFIN | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 367171 | 427130 | 800 | 9.1452 | 0 | 12.8037 | 27.4154 | 4.7839 | 3.5056 | 12.8037 | 0 | 0 | Offers with ENW, due to be signed 20/08/2024 .Another parrallel submission made, offer due 28/06/2024
HADFIELD | 11 | HYDE | HYDE | STALYBRIDGE | 401790 | 395876 | 400 | 7.621 | 11.5694 | 16.2897 | 8.3992 | 1.3829 | 0.99389 | 8.3992 | 0.83754 | 7.0779 | Offer with ENW ,due signing by 29/08/2024
HALL CROSS | 6.6 | PEEL | PEEL | PENWORTHAM | 342288 | 430650 | 630 | 7.2019 | 0 | 0 | 21.3624 | 10.5731 | 7.7144 | 0 | 0 | 0 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
HANDFORTH | 11 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 385958 | 383397 | 400 | 7.621 | 8.1935 | 12.8305 | 8.968 | 1.9575 | 1.4344 | 8.968 | 1.4344 | 5.768 | 2nd Step offer with ENW, due to signed 15/07/2024.Offer with ENW due to sign 30/08/2024.Another submission made, awaiting Clock start date.
HANGING BRIDGE | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 346186 | 417486 | 630 | 12.0031 | 1.4276 | 5.4276 | 10.8975 | 10.8975 | 10.8975 | 5.4276 | 5.1053 | 5.1053 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
HAREHOLME | 6.6 | ROSSENDALE | ROSSENDALE | PADIHAM | 382535 | 422283 | 800 | 9.1452 | 5.7899 | 10.4269 | 31.6811 | 12.5714 | 9.1725 | 10.4269 | 9.5452 | 9.9239 | Two parrallel 2nd step offer with ENW due to be signed 04/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Another parrallel submission clock started, offer due 28/08/2024
HARPURHEY | 6.6 | RED BANK | RED BANK | WHITEGATE | 385907 | 402469 | 400 | 4.5726 | 10.61 | 15.25 | 30.4539 | 12.8105 | 9.3469 | 15.25 | 9.1946 | 15.552 | Offers with ENW, due to be signed 28/08/2024
HARWOOD | 11 | BOLTON | BOLTON | KEARSLEY | 374043 | 410941 | 400 | 7.621 | 2.82 | 7.12 | 11.2179 | 1.9575 | 1.4344 | 7.12 | 1.4344 | 7.187 | PP submitted, awaiting clock start date
HATTERSLEY | 11 | HYDE | HYDE | STALYBRIDGE | 398419 | 395120 | 800 | 15.242 | 0.10576 | 3.6058 | 15.8004 | 5.2022 | 3.7389 | 3.6058 | 3.4214 | 6.4802 | Offer with ENW ,due signing by 29/08/2024
HAVERTHWAITE | 11 | ULVERSTON | ULVERSTON | HARKER | 334234 | 483827 | 630 | 12.0031 | 4.2472 | 6.7472 | 13.0026 | 13.0026 | 13.0026 | 6.7472 | 13.0026 | 6.7952 | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
HAWK GREEN | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 395915 | 387138 | 630 | 12.0031 | 11.2315 | 15.7315 | 30.5328 | 16.8201 | 12.0889 | 15.7315 | 12.0132 | 15.4515 | 2nd step offer with ENW,due to be signed 06/06/2024.Parrallel submission offer with ENW, due to be signed 29/08/2024
HAYDOCK | 11 | GOLBORNE | GOLBORNE | BOLD | 357489 | 397336 | 630 | 12.0031 | 7.9181 | 13.4181 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0 | 0 | N/A
HDA NO1 | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 301743 | 524532 | 400 | 7.621 | 13.1069 | 19.3269 | 2.7254 | 0.44872 | 0.3225 | 2.7254 | 0 | 0 | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
HDA NO2 | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 301429 | 525527 | 630 | 12.0031 | 13.1069 | 19.3269 | 7 | 1.9575 | 1.4344 | 7 | 0 | 0 | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
HEADY HILL | 6.6 | CASTLETON | CASTLETON | ROCHDALE | 384370 | 410583 | 400 | 4.5726 | 4.0459 | 7.5459 | 24.7522 | 9.9451 | 7.2562 | 7.5459 | 7.0425 | 7.7035 | Offers with ENW, due to be signed 20/08/2024 .Another parrallel submission made, offer due 28/06/2024
HEAP BRIDGE | 6.6 | BURY | BURY | KEARSLEY | 382793 | 410428 | 400 | 4.5726 | 5.417 | 5.417 | 5.4729 | 1.9575 | 1.4344 | 5.417 | 1.4344 | 2.695 | PP submitted, awaiting clock start date
HEASANDFORD | 6.6 | BURNLEY | BURNLEY | ROCHDALE | 385349 | 433821 | 400 | 4.5726 | 8.2144 | 17.4244 | 29.9937 | 8.3984 | 6.1277 | 17.4244 | 0 | 0 | Offers with ENW, due to be signed 20/08/2024 .Another parrallel submission made, offer due 28/06/2024
HEATON MOOR | 6.6 | VERNON PARK | VERNON PARK | BREDBURY | 387623 | 391345 | 630 | 7.2019 | 0 | 0 | 31.1274 | 9.589 | 6.9964 | 0 | 7.1221 | 0 | 2nd step offer with ENW,due to be signed 06/06/2024.Parrallel submission offer with ENW, due to be signed 29/08/2024
HEATON NORRIS | 6.6 | VERNON PARK | VERNON PARK | BREDBURY | 388860 | 391967 | 400 | 4.5726 | 0 | 0 | 28.1192 | 4.7012 | 3.4301 | 0 | 3.0681 | 0 | 2nd step offer with ENW,due to be signed 06/06/2024.Parrallel submission offer with ENW, due to be signed 29/08/2024
HELWITH BRIDGE | 11 | PADIHAM | PADIHAM | PADIHAM | 381025 | 469428 | 630 | 12.0031 | 0.47386 | 8.4739 | 13.2972 | 13.2972 | 13.2972 | 8.4739 | 13.2972 | 8.3367 | Two parrallel 2nd step offer with ENW due to be signed 04/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Another parrallel submission clock started, offer due 28/08/2024
HENSINGHAM | 11 | EGREMONT | EGREMONT | HARKER | 298465 | 517239 | 630 | 12.0031 | 11.7789 | 15.9159 | 25.8852 | 11.8051 | 8.4846 | 15.9159 | 9.101 | 17.1039 | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
HEYROD | 6.6 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 397310 | 399981 | 600 | 6.8589 | 9.6561 | 14.2931 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer with ENW ,due signing by 29/08/2024
HEYSIDE | 6.6 | ROYTON | ROYTON | WHITEGATE | 393433 | 407129 | 400 | 4.5726 | 10.1531 | 14.7901 | 0 | 0 | 0 | 0 | 0 | 0 | Offers with ENW, due to be signed 28/08/2024
HEYWOOD | 6.6 | CASTLETON | CASTLETON | ROCHDALE | 385429 | 410369 | 630 | 7.2019 | 6.1713 | 7.3025 | 18.088 | 2.9336 | 2.1405 | 7.3025 | 1.2885 | 0 | Offers with ENW, due to be signed 20/08/2024 .Another parrallel submission made, offer due 28/06/2024
HIGHER MILL | 6.6 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 385731 | 388090 | 400 | 4.5726 | 4.7901 | 12.2901 | 8.968 | 1.9575 | 1.4344 | 8.968 | 1.4344 | 5.768 | 2nd Step offer with ENW, due to signed 15/07/2024.Offer with ENW due to sign 30/08/2024.Another submission made, awaiting Clock start date.
HIGHER WALTON | 11 | LEYLAND | LEYLAND | PENWORTHAM | 358020 | 427270 | 400 | 7.621 | 3.0994 | 7.7364 | 21.3152 | 5.661 | 4.0687 | 7.7364 | 3.7037 | 4.126 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
HILL TOP T11 & T12 | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 373466 | 403748 | 400 | 7.621 | 0 | 8.6482 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | PP submitted, awaiting clock start date
HILL TOP T13 | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 373476 | 403758 | 400 | 7.621 | 0 | 0 | 7 | 1.9575 | 1.4344 | 0 | 1.4344 | 0.95096 | PP submitted, awaiting clock start date
HINDLEY GREEN | 11 | ATHERTON | ATHERTON | KEARSLEY | 363389 | 403254 | 630 | 12.0031 | 0.72274 | 0.72274 | 2.6844 | 0.44197 | 0.31765 | 0.72274 | 0.31765 | 0 | PP submitted, awaiting clock start date
HOLLINWOOD | 6.6 | CHADDERTON | CHADDERTON | WHITEGATE | 390287 | 402592 | 630 | 7.2019 | 0 | 0 | 26.6633 | 7.127 | 5.2001 | 0 | 1.3649 | 0 | Offers with ENW, due to be signed 28/08/2024
HOLME RD | 11 | RIBBLE | RIBBLE | PENWORTHAM | 352311 | 429141 | 400 | 7.621 | 6.819 | 10.956 | 11.2179 | 1.9575 | 1.4344 | 10.956 | 1.4344 | 11.2179 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
HOLT ST | 11 | BURY | BURY | KEARSLEY | 378620 | 416362 | 630 | 12.0031 | 3.397 | 6.897 | 11.2179 | 1.9575 | 1.4344 | 6.897 | 1.4344 | 6.5258 | PP submitted, awaiting clock start date
HURST | 6.6 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 394658 | 400360 | 630 | 7.2019 | 5.5232 | 9.0232 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer with ENW ,due signing by 29/08/2024
HUTTON END | 11 | PENRITH & SHAP | PENRITH | HUTTON | 345810 | 538827 | 630 | 12.0031 | 0 | 0 | 21.6275 | 20.5893 | 15.0875 | 0 | 17.2503 | 13.3736 | 2nd step offer signed 29/05/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024
HYDE | 6.6 | HYDE | HYDE | STALYBRIDGE | 395215 | 395126 | 630 | 7.2019 | 6.5327 | 11.1697 | 31.4548 | 5.5172 | 4.043 | 11.1697 | 5.4751 | 11.4433 | Offer with ENW ,due signing by 29/08/2024
HYNDBURN RD | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 375688 | 428877 | 800 | 9.1452 | 4.2125 | 16.5125 | 29.3612 | 13.3717 | 9.7563 | 16.5125 | 7.0436 | 17.6125 | Two parrallel 2nd step offer with ENW due to be signed 04/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Another parrallel submission clock started, offer due 28/08/2024
INDIA ST | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 369485 | 421865 | 400 | 4.5726 | 0 | 16.0968 | 27.4154 | 4.7839 | 3.5056 | 16.0968 | 0 | 0 | Offers with ENW, due to be signed 20/08/2024 .Another parrallel submission made, offer due 28/06/2024
INGLETON | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 368913 | 472337 | 630 | 12.0031 | 0 | 9.6047 | 12.6981 | 12.6981 | 12.6981 | 9.6047 | 0 | 0 | 2nd step offer signed 29/05/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024
IRLAM | 6.6 | CARRINGTON BSP | CARRINGTON BSP | CARRINGTON | 371680 | 393360 | 1250 | 14.2894 | 2.4609 | 6.6009 | 11.2179 | 1.9575 | 1.4344 | 6.6009 | 1.4344 | 4.4053 | N/A
JAMES ST | 11 | CARLISLE | CARLISLE | HARKER | 340034 | 555418 | 630 | 12.0031 | 7.0226 | 11.1596 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
KAY ST | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 373863 | 427594 | 630 | 7.2019 | 13.3013 | 17.4383 | 29.8132 | 13.4182 | 9.7903 | 17.4383 | 7.0436 | 16.5205 | Two parrallel 2nd step offer with ENW due to be signed 04/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Another parrallel submission clock started, offer due 28/08/2024
KENDAL | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 351915 | 491858 | 400 | 7.621 | 0 | 8.0652 | 28.0218 | 9.5151 | 6.8387 | 8.0652 | 0 | 0 | 2nd step offer signed 29/05/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024
KESWICK | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 327022 | 523784 | 400 | 7.621 | 3.2709 | 5.7709 | 7 | 1.9575 | 1.4344 | 5.7709 | 0 | 0 | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
KINGSWAY | 11 | BELFIELD | BELFIELD | ROCHDALE | 391636 | 411724 | 630 | 12.0031 | 11.9053 | 11.9053 | 45.8137 | 8.1077 | 5.8272 | 11.9053 | 1.6009 | 0 | Offers with ENW, due to be signed 20/08/2024 .Another parrallel submission made, offer due 28/06/2024
KINKRY HILL | 11 | - | - | HARKER | 350800 | 575111 | 800 | 15.242 | 0.81619 | 2.3162 | 3.1954 | 3.1954 | 3.1954 | 2.3162 | 3.1954 | 2.3112 | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
KIRKBY LONSDALE | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 359833 | 478813 | 400 | 7.621 | 0 | 6.1447 | 13.7662 | 13.7662 | 13.7662 | 6.1447 | 0 | 0 | 2nd step offer signed 29/05/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024
KIRKBY MOOR | 11 | ULVERSTON | ULVERSTON | HARKER | 326099 | 483011 | 1250 | 23.8157 | 2.2241 | 5.7241 | 3.4566 | 3.4566 | 3.4566 | 3.4566 | 2.8987 | 2.8987 | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
KIRKBY STEPHEN | 11 | PENRITH & SHAP | PENRITH | HUTTON | 376579 | 509136 | 800 | 15.242 | 0 | 0 | 19.5904 | 19.5904 | 15.0875 | 0 | 19.5904 | 10.2783 | 2nd step offer signed 29/05/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024
KIRKBY THORE | 11 | PENRITH & SHAP | PENRITH | HUTTON | 364439 | 526672 | 630 | 12.0031 | 0 | 0 | 29.4281 | 20.5893 | 15.0875 | 0 | 18.6543 | 13.2545 | 2nd step offer signed 29/05/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024
KIRKHALL LANE | 11 | ATHERTON | ATHERTON | KEARSLEY | 365510 | 401069 | 400 | 7.621 | 0.72274 | 0.72274 | 19.9589 | 11.6063 | 8.3417 | 0.72274 | 8.0695 | 0 | PP submitted, awaiting clock start date
KITT GREEN | 6.6 | ORRELL | ORRELL | KIRKBY | 354934 | 405497 | 400 | 4.5726 | 0 | 11.2981 | 31.9515 | 12.4733 | 9.1009 | 11.2981 | 9.0797 | 10.8837 | 2nd step offer with ENW,due to be signed 04/06/2024 .Parrallel submission offer with ENW, due to be signed 29/08/2024
KNOTT MILL | 6.6 | BLOOM ST | BLOOM ST | SOUTH MANCHESTER | 383136 | 397725 | 800 | 9.1452 | 0 | 0 | 31.367 | 6.9764 | 5.0902 | 0 | 4.9077 | 0 | 2nd Step offer with ENW, due to signed 15/07/2024.Offer with ENW due to sign 30/08/2024.Another submission made, awaiting Clock start date.
LAMBERHEAD | 6.6 | ORRELL | ORRELL | KIRKBY | 355516 | 404030 | 630 | 7.2019 | 0 | 15.2431 | 24.478 | 9.4669 | 6.9073 | 15.2431 | 7.0795 | 15.6051 | 2nd step offer with ENW,due to be signed 04/06/2024 .Parrallel submission offer with ENW, due to be signed 29/08/2024
LANCASTER | 11 | LANCASTER | LANCASTER | HEYSHAM | 348644 | 463628 | 630 | 12.0031 | 2.9515 | 4.2023 | 11.2179 | 1.9575 | 1.4344 | 4.2023 | 1.5151 | 5.0572 | Offer with ENW, due to be signed 30/08/2024. Parrallel submission made, offer due 08/06/2024.Another parrallel submission made, awaiting clock start date.
LANGLEY | 11 | CHADDERTON | CHADDERTON | WHITEGATE | 386421 | 406330 | 400 | 7.621 | 0 | 0 | 33.1798 | 9.5875 | 7.0256 | 0 | 1.3649 | 0 | Offers with ENW, due to be signed 28/08/2024
LANGROYD RD | 6.6 | NELSON | NELSON | PADIHAM | 389077 | 440584 | 400 | 4.5726 | 4.5373 | 15.0656 | 0 | 0 | 0 | 0 | 0 | 0 | Two parrallel 2nd step offer with ENW due to be signed 04/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Another parrallel submission clock started, offer due 28/08/2024
LEIGH | 11 | ATHERTON | ATHERTON | KEARSLEY | 365863 | 399907 | 800 | 15.242 | 0.72274 | 0.72274 | 19.6186 | 19.6186 | 19.6186 | 0.72274 | 19.6186 | 0 | PP submitted, awaiting clock start date
LEVENSHULME | 6.6 | LONGSIGHT | LONGSIGHT | BREDBURY | 387494 | 394155 | 400 | 4.5726 | 2.6719 | 6.1719 | 25.4427 | 13.5742 | 9.9041 | 6.1719 | 10.1941 | 6.1719 | 2nd step offer with ENW,due to be signed 06/06/2024.Parrallel submission offer with ENW, due to be signed 29/08/2024
LEYLAND NATIONAL | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 301973 | 525948 | 400 | 7.621 | 13.7639 | 21.549 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0 | 0 | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
LITTLE HULTON | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 372024 | 403826 | 630 | 12.0031 | 0 | 4.291 | 7 | 1.9575 | 1.4344 | 4.291 | 1.4344 | 4.4466 | PP submitted, awaiting clock start date
LITTLE SALKELD | 11 | PENRITH & SHAP | PENRITH | HUTTON | 356221 | 537513 | 400 | 7.621 | 0 | 0 | 16.5605 | 16.5605 | 15.0875 | 0 | 16.5605 | 4.0762 | 2nd step offer signed 29/05/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024
LITTLEBOROUGH | 6.6 | BELFIELD | BELFIELD | ROCHDALE | 393221 | 416124 | 400 | 4.5726 | 2.0518 | 5.5518 | 25.0991 | 10.2023 | 7.4439 | 5.5518 | 6.9929 | 0 | Offers with ENW, due to be signed 20/08/2024 .Another parrallel submission made, offer due 28/06/2024
LONGFORD BRIDGE | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 380056 | 395083 | 800 | 9.1452 | 4.1074 | 12.5286 | 31.2344 | 7.8311 | 5.7138 | 12.5286 | 5.7031 | 10.4658 | 2nd Step offer with ENW, due to signed 15/07/2024.Offer with ENW due to sign 30/08/2024.Another submission made, awaiting Clock start date.
LONGRIDGE | 6.6 | PRESTON EAST | PRESTON EAST | PENWORTHAM | 360581 | 437001 | 400 | 4.5726 | 0.80659 | 0.80659 | 11.2179 | 1.9575 | 1.4344 | 0.80659 | 1.4344 | 0 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
LONGSIGHT | 6.6 | LONGSIGHT | LONGSIGHT | BREDBURY | 385535 | 396037 | 400 | 4.5726 | 2.748 | 6.885 | 27.2475 | 5.3317 | 3.8902 | 6.885 | 2.8907 | 9.1882 | 2nd step offer with ENW,due to be signed 06/06/2024.Parrallel submission offer with ENW, due to be signed 29/08/2024
LOSTOCK | 11 | WESTHOUGHTON | WESTHOUGHTON | KEARSLEY | 365293 | 409079 | 800 | 15.242 | 4.4575 | 10.4575 | 36.6557 | 6.0351 | 4.3375 | 10.4575 | 0.088852 | 0 | PP submitted, awaiting clock start date
LOWER DARWEN | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 369695 | 424981 | 800 | 9.1452 | 0 | 15.861 | 27.4154 | 4.7839 | 3.5056 | 15.861 | 0 | 0 | Offers with ENW, due to be signed 20/08/2024 .Another parrallel submission made, offer due 28/06/2024
LYONS RD | 6.6 | BARTON | BARTON | CARRINGTON | 378253 | 397241 | 400 | 4.5726 | 6.0836 | 10.7206 | 11.2179 | 1.9575 | 1.4344 | 10.7206 | 1.4344 | 10.6576 | N/A
MANCHESTER UNIVERSITY | 6.6 | LONGSIGHT | LONGSIGHT | BREDBURY | 384762 | 396769 | 800 | 9.1452 | 0 | 1.3096 | 30.0909 | 10.2224 | 7.4586 | 1.3096 | 7.4513 | 1.5496 | 2nd step offer with ENW,due to be signed 06/06/2024.Parrallel submission offer with ENW, due to be signed 29/08/2024
MARPLE | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 395671 | 388643 | 630 | 12.0031 | 0.050606 | 0.050606 | 7.1061 | 7.1061 | 7.1061 | 0.050606 | 7.1061 | 0 | 2nd step offer with ENW,due to be signed 06/06/2024.Parrallel submission offer with ENW, due to be signed 29/08/2024
MARTON | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 333341 | 433485 | 400 | 4.5726 | 10.4104 | 15.0104 | 24.6386 | 8.3702 | 6.1071 | 15.0104 | 6.5522 | 14.5624 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
MARYPORT | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 303716 | 535313 | 630 | 12.0031 | 8.8797 | 17.6033 | 7 | 1.9575 | 1.4344 | 7 | 0 | 0 | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
MELLING | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 360144 | 471643 | 630 | 12.0031 | 0 | 3.3394 | 7.1573 | 7.1573 | 7.1573 | 3.3394 | 0 | 0 | 2nd step offer signed 29/05/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024
MERESIDE | 6.6 | PEEL | PEEL | PENWORTHAM | 334431 | 434843 | 630 | 7.2019 | 0 | 0 | 21.3624 | 13.096 | 9.5552 | 0 | 0 | 0 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
MIDDLETON JUNCTION | 11 | CHADDERTON | CHADDERTON | WHITEGATE | 388606 | 405292 | 630 | 12.0031 | 0 | 0 | 26.673 | 4.3915 | 3.1563 | 0 | 1.3649 | 0 | Offers with ENW, due to be signed 28/08/2024
MIDWAY | 11 | EGREMONT | EGREMONT | HARKER | 304525 | 501993 | 630 | 12.0031 | 8.8058 | 11.6056 | 18.7067 | 18.7067 | 17.715 | 11.6056 | 18.0835 | 11.4916 | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
MILNROW | 6.6 | CASTLETON | CASTLETON | ROCHDALE | 392351 | 413056 | 400 | 4.5726 | 10.2974 | 14.9374 | 30.1883 | 10.2347 | 7.4675 | 14.9374 | 7.4802 | 14.0754 | Offers with ENW, due to be signed 20/08/2024 .Another parrallel submission made, offer due 28/06/2024
MINTSFEET | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 351827 | 494315 | 400 | 7.621 | 0 | 5.796 | 16.7754 | 2.7619 | 1.9851 | 5.796 | 0 | 0 | 2nd step offer signed 29/05/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024
MONSALL | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 386332 | 401003 | 630 | 7.2019 | 0 | 5.0887 | 11.2179 | 1.9575 | 1.4344 | 5.0887 | 1.4344 | 0 | Offer with ENW ,due signing by 29/08/2024
MONTON | 6.6 | BARTON | BARTON | CARRINGTON | 376321 | 399494 | 400 | 4.5726 | 3.0849 | 6.5849 | 11.2179 | 1.9575 | 1.4344 | 6.5849 | 1.4344 | 5.0297 | N/A
MOORSIDE | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 349331 | 435746 | 630 | 7.2019 | 2.3562 | 5.8562 | 11.2179 | 1.9575 | 1.4344 | 5.8562 | 1.4344 | 8.9507 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
MORTON PARK | 11 | CARLISLE | CARLISLE | HARKER | 337826 | 553939 | 1250 | 23.8157 | 8.3041 | 12.1041 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0.31765 | 2.6844 | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
MOSLEY RD | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 379058 | 396289 | 630 | 7.2019 | 1.1196 | 4.6196 | 23.7167 | 8.9634 | 6.5399 | 4.6196 | 5.8695 | 0 | 2nd Step offer with ENW, due to signed 15/07/2024.Offer with ENW due to sign 30/08/2024.Another submission made, awaiting Clock start date.
MOSS LANE | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 380858 | 405856 | 400 | 7.621 | 0 | 3.0612 | 7 | 1.9575 | 1.4344 | 3.0612 | 1.4344 | 3.7702 | PP submitted, awaiting clock start date
MOSS NOOK PRIMARY | 11 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 384084 | 385010 | 800 | 15.242 | 15.7694 | 22.3167 | 8.968 | 1.9575 | 1.4344 | 8.968 | 1.4344 | 5.768 | 2nd Step offer with ENW, due to signed 15/07/2024.Offer with ENW due to sign 30/08/2024.Another submission made, awaiting Clock start date.
MOSS SIDE (Leyland) | 11 | LEYLAND | LEYLAND | PENWORTHAM | 352170 | 422970 | 400 | 7.621 | 3.3845 | 6.6985 | 27.9116 | 13.2553 | 9.5269 | 6.6985 | 9.1199 | 4.5253 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
MOSS SIDE (Longsight) | 6.6 | LONGSIGHT | LONGSIGHT | BREDBURY | 384007 | 395893 | 400 | 4.5726 | 0 | 2.8462 | 31.5971 | 9.9438 | 7.2552 | 2.8462 | 7.5673 | 1.6732 | 2nd step offer with ENW,due to be signed 06/06/2024.Parrallel submission offer with ENW, due to be signed 29/08/2024
MOSSLEY | 11 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 397437 | 401979 | 400 | 7.621 | 9.2836 | 13.9206 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer with ENW ,due signing by 29/08/2024
MOUNT ST | 6.6 | BARTON | BARTON | CARRINGTON | 376250 | 397574 | 400 | 4.5726 | 1.1513 | 5.7882 | 11.2179 | 1.9575 | 1.4344 | 5.7882 | 1.4344 | 8.7054 | N/A
MUSGRAVE RD | 6.6 | BOLTON | BOLTON | KEARSLEY | 370045 | 409863 | 800 | 9.1452 | 8.588 | 14.208 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | PP submitted, awaiting clock start date
NELSON | 6.6 | NELSON | NELSON | PADIHAM | 386020 | 438507 | 400 | 4.5726 | 2.0202 | 6.1602 | 0 | 0 | 0 | 0 | 0 | 0 | Two parrallel 2nd step offer with ENW due to be signed 04/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Another parrallel submission clock started, offer due 28/08/2024
NEW MOSTON | 6.6 | CHADDERTON | CHADDERTON | WHITEGATE | 388333 | 402657 | 630 | 7.2019 | 0 | 0 | 31.0839 | 9.5875 | 7.0256 | 0 | 1.3649 | 0 | Offers with ENW, due to be signed 28/08/2024
NEWBIGGIN ON LUNE | 11 | PENRITH & SHAP | PENRITH | HUTTON | 369770 | 505803 | 800 | 15.242 | 0 | 0 | 3.8322 | 3.8322 | 3.8322 | 0 | 3.8322 | 2.0546 | 2nd step offer signed 29/05/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024
NEWBY | 11 | PENRITH & SHAP | PENRITH | HUTTON | 360520 | 521151 | 400 | 7.621 | 0 | 0 | 15.0523 | 15.0523 | 15.0523 | 0 | 15.0523 | 7.0631 | 2nd step offer signed 29/05/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024
NEWTON | 11 | HYDE | HYDE | STALYBRIDGE | 396385 | 396464 | 400 | 7.621 | 9.8163 | 15.5743 | 8.0566 | 5.5172 | 4.043 | 8.0566 | 1.511 | 1.511 | Offer with ENW ,due signing by 29/08/2024
NEWTON HEATH | 6.6 | CHADDERTON | CHADDERTON | WHITEGATE | 388030 | 400511 | 400 | 4.5726 | 0 | 0 | 12.0025 | 9.5875 | 7.0256 | 0 | 1.3649 | 0 | Offers with ENW, due to be signed 28/08/2024
NEWTON LE WILLOWS | 11 | GOLBORNE | GOLBORNE | BOLD | 357891 | 395944 | 630 | 12.0031 | 8.8291 | 12.9661 | 28.3704 | 10.523 | 7.7111 | 12.9661 | 0 | 0 | N/A
NEWTONGATE T11 & T12 | 11 | PENRITH & SHAP | PENRITH | HUTTON | 349973 | 530340 | 630 | 12.0031 | 0 | 0 | 30.418 | 5.0081 | 3.5994 | 0 | 3.841 | 8.6565 | 2nd step offer signed 29/05/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024
NEWTONGATE T13 | 11 | PENRITH & SHAP | PENRITH | HUTTON | 349973 | 530340 | 630 | 12.0031 | 0 | 0 | 16.5236 | 16.5236 | 15.0875 | 0 | 14.4183 | 10.2752 | 2nd step offer signed 29/05/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024
NORBRECK | 6.6 | BISPHAM | BISPHAM | PENWORTHAM | 331831 | 441463 | 400 | 4.5726 | 17.3747 | 22.8902 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
NORBURY | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 392447 | 385492 | 400 | 7.621 | 11.082 | 15.719 | 5.3623 | 0.88286 | 0.63453 | 5.3623 | 0.56343 | 4.7615 | 2nd step offer with ENW,due to be signed 06/06/2024.Parrallel submission offer with ENW, due to be signed 29/08/2024
NORTHENDEN | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 382555 | 390327 | 400 | 4.5726 | 6.4031 | 9.9031 | 7.06 | 1.9575 | 1.4344 | 7.06 | 1.4344 | 9.31 | 2nd Step offer with ENW, due to signed 15/07/2024.Offer with ENW due to sign 30/08/2024.Another submission made, awaiting Clock start date.
NWGB PARTINGTON | 6.6 | CARRINGTON BSP | CARRINGTON BSP | CARRINGTON | 372569 | 392079 | 400 | 4.5726 | 5.6786 | 10.6186 | 11.2179 | 1.9575 | 1.4344 | 10.6186 | 1.4344 | 10.0382 | N/A
OFFERTON | 6.6 | VERNON PARK | VERNON PARK | BREDBURY | 391010 | 389489 | 400 | 4.5726 | 0 | 0 | 30.5974 | 12.4032 | 9.0497 | 0 | 9.1327 | 0 | 2nd step offer with ENW,due to be signed 06/06/2024.Parrallel submission offer with ENW, due to be signed 29/08/2024
OPENSHAW | 6.6 | DROYLSDEN | DROYLSDEN | STALYBRIDGE | 388606 | 397346 | 630 | 7.2019 | 2.7832 | 6.2832 | 11.2179 | 1.9575 | 1.4344 | 6.2832 | 1.4344 | 5.886 | Offer with ENW ,due signing by 29/08/2024
ORMSKIRK | 11 | SKELMERSDALE | SKELMERSDALE | WASHWAY FARM | 341294 | 408158 | 800 | 15.242 | 7.867 | 12.504 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 10.4513 | Offer e signed 29/05/2024. Parrallel submission offer with ENW, due to be signed 29/08/2024
PADIHAM | 11 | PADIHAM | PADIHAM | PADIHAM | 378428 | 433238 | 400 | 7.621 | 8.5652 | 20.5537 | 6.0139 | 0.99015 | 0.71164 | 6.0139 | 0.84345 | 7.1279 | Two parrallel 2nd step offer with ENW due to be signed 04/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Another parrallel submission clock started, offer due 28/08/2024
PEEL ST | 11 | PADIHAM | PADIHAM | PADIHAM | 374463 | 441514 | 630 | 12.0031 | 0 | 7.847 | 19.6031 | 19.6031 | 19.1207 | 7.847 | 19.6031 | 8.983 | Two parrallel 2nd step offer with ENW due to be signed 04/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Another parrallel submission clock started, offer due 28/08/2024
PENDLETON | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 381161 | 398842 | 400 | 4.5726 | 0 | 12.3234 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 0 | PP submitted, awaiting clock start date
PETTERIL BANK | 11 | CARLISLE | CARLISLE | HARKER | 341768 | 553686 | 400 | 7.621 | 8.0087 | 12.1457 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
PHILLIPS LANE | 6.6 | NELSON | NELSON | PADIHAM | 387571 | 439522 | 800 | 9.1452 | 2.2154 | 11.2154 | 0 | 0 | 0 | 0 | 0 | 0 | Two parrallel 2nd step offer with ENW due to be signed 04/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Another parrallel submission clock started, offer due 28/08/2024
PICCADILLY | 6.6 | BLOOM ST | BLOOM ST | SOUTH MANCHESTER | 384427 | 398261 | 400 | 4.5726 | 0 | 15.8973 | 29.5281 | 8.4273 | 6.1488 | 15.8973 | 6.0414 | 15.0117 | 2nd Step offer with ENW, due to signed 15/07/2024.Offer with ENW due to sign 30/08/2024.Another submission made, awaiting Clock start date.
PIMBO | 11 | SKELMERSDALE | SKELMERSDALE | WASHWAY FARM | 349148 | 404549 | 400 | 7.621 | 9.103 | 21.3547 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 10.4513 | Offer e signed 29/05/2024. Parrallel submission offer with ENW, due to be signed 29/08/2024
PIRELLI | 11 | CARLISLE | CARLISLE | HARKER | 339059 | 553548 | 400 | 7.621 | 7.7571 | 11.5571 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
PORTWOOD | 6.6 | VERNON PARK | VERNON PARK | BREDBURY | 389826 | 390619 | 400 | 4.5726 | 0 | 0 | 31.2648 | 9.3241 | 6.8031 | 0 | 6.7371 | 0 | 2nd step offer with ENW,due to be signed 06/06/2024.Parrallel submission offer with ENW, due to be signed 29/08/2024
POULTON | 6.6 | BISPHAM | BISPHAM | PENWORTHAM | 335679 | 439130 | 800 | 9.1452 | 9.1761 | 11.1561 | 11.2179 | 1.9575 | 1.4344 | 11.1561 | 1.4344 | 6.9765 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
POYNTON | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 392096 | 383493 | 630 | 12.0031 | 7.3552 | 10.8552 | 23.6228 | 13.091 | 9.4087 | 10.8552 | 9.4181 | 10.8112 | 2nd step offer with ENW,due to be signed 06/06/2024.Parrallel submission offer with ENW, due to be signed 29/08/2024
PREESALL | 11 | THORNTON | THORNTON | STANAH | 336965 | 446547 | 800 | 15.242 | 10.9341 | 15.4341 | 26.8965 | 9.213 | 6.7511 | 15.4341 | 9.0987 | 15.8281 | N/A
PRESTON EAST | 6.6 | PRESTON EAST | PRESTON EAST | PENWORTHAM | 356777 | 432926 | 630 | 7.2019 | 0.80659 | 0.80659 | 2.6918 | 0.43658 | 0.31854 | 0.80659 | 1.4344 | 0 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
PRESTON OLD RD | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 332562 | 434929 | 800 | 9.1452 | 11.301 | 15.938 | 30.2268 | 11.5687 | 8.4409 | 15.938 | 8.77 | 17.138 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
PRESTWICH | 6.6 | AGECROFT | AGECROFT | KEARSLEY | 381392 | 404001 | 400 | 4.5726 | 4.0826 | 8.7196 | 32.1779 | 7.8191 | 5.705 | 8.7196 | 5.8553 | 6.3816 | PP submitted, awaiting clock start date
PRINGLE ST | 6.6 | BLACKBURN | BLACKBURN | PENWORTHAM | 369088 | 427387 | 400 | 4.5726 | 8.6473 | 16.2073 | 30.2531 | 12.4167 | 9.0595 | 16.2073 | 8.8549 | 17.2513 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
PRINNY HILL | 6.6 | ROSSENDALE | ROSSENDALE | PADIHAM | 378328 | 423395 | 630 | 7.2019 | 9.2872 | 14.3872 | 24.7332 | 12.0467 | 8.7896 | 14.3872 | 9.5083 | 14.3872 | Two parrallel 2nd step offer with ENW due to be signed 04/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Another parrallel submission clock started, offer due 28/08/2024
QUEENS PARK | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 385893 | 400645 | 400 | 4.5726 | 0 | 0.80934 | 11.2179 | 1.9575 | 1.4344 | 0.80934 | 1.4344 | 0 | Offer with ENW ,due signing by 29/08/2024
RADCLIFFE | 11 | - | - | KEARSLEY | 377524 | 406160 | 400 | 7.621 | 7.6451 | 8.0451 | 43.9949 | 11.9216 | 8.5683 | 8.0451 | 8.7443 | 5.7413 | PP submitted, awaiting clock start date
RANDAL ST | 6.6 | BLACKBURN | BLACKBURN | PENWORTHAM | 368092 | 428515 | 630 | 7.2019 | 5.4637 | 18.1637 | 34.9192 | 13.1052 | 9.5619 | 18.1637 | 8.8192 | 17.3639 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
RAWTENSTALL RD | 6.6 | ROSSENDALE | ROSSENDALE | PADIHAM | 379395 | 422143 | 630 | 7.2019 | 10.3085 | 14.9455 | 30.169 | 15.73 | 11.477 | 14.9455 | 11.7382 | 14.2835 | Two parrallel 2nd step offer with ENW due to be signed 04/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Another parrallel submission clock started, offer due 28/08/2024
REDDISH VALE | 6.6 | VERNON PARK | VERNON PARK | BREDBURY | 390147 | 393309 | 800 | 9.1452 | 0 | 0 | 30.3545 | 9.729 | 7.0985 | 0 | 7.0914 | 0 | 2nd step offer with ENW,due to be signed 06/06/2024.Parrallel submission offer with ENW, due to be signed 29/08/2024
RIBBLESDALE T13 & RIBBLESDALE T14 | 11 | PADIHAM | PADIHAM | PADIHAM | 374759 | 443587 | 800 | 15.242 | 0 | 1.5478 | 22.1282 | 16.4821 | 11.846 | 1.5478 | 11.8923 | 1.683 | Two parrallel 2nd step offer with ENW due to be signed 04/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Another parrallel submission clock started, offer due 28/08/2024
RIBBLETON | 6.6 | PRESTON EAST | PRESTON EAST | PENWORTHAM | 356730 | 431506 | 630 | 7.2019 | 0.80659 | 0.80659 | 11.2179 | 1.9575 | 1.4344 | 0.80659 | 1.4344 | 0 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
RINGLEY | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 376120 | 405531 | 630 | 12.0031 | 0 | 9.303 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | PP submitted, awaiting clock start date
RISLEY | 11 | - | - | BOLD | 365181 | 392989 | 400 | 7.621 | 0 | 10.1525 | 8.7189 | 1.4355 | 1.0317 | 8.7189 | 1.2626 | 4.1747 | N/A
ROBERT HALL ST | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 381359 | 397718 | 400 | 4.5726 | 0 | 10.0784 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 0 | PP submitted, awaiting clock start date
ROCHDALE CENTRAL | 6.6 | ROCHDALE CENTRAL | ROCHDALE CENTRAL | ROCHDALE | 389111 | 413393 | 630 | 7.2019 | 17.4155 | 30.4155 | 2.6918 | 0.43658 | 0.31854 | 2.6918 | 0.31848 | 2.6914 | Offers with ENW, due to be signed 20/08/2024 .Another parrallel submission made, offer due 28/06/2024
ROMAN RD | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 369058 | 426505 | 630 | 7.2019 | 0 | 14.7322 | 27.4154 | 4.7839 | 3.5056 | 14.7322 | 0 | 0 | Offers with ENW, due to be signed 20/08/2024 .Another parrallel submission made, offer due 28/06/2024
ROMILEY | 11 | VERNON PARK | VERNON PARK | BREDBURY | 393626 | 390716 | 400 | 7.621 | 0 | 0 | 24.0007 | 10.8328 | 7.7857 | 0 | 7.5834 | 0 | 2nd step offer with ENW,due to be signed 06/06/2024.Parrallel submission offer with ENW, due to be signed 29/08/2024
ROSSALL | 6.6 | THORNTON | THORNTON | STANAH | 331916 | 445505 | 400 | 4.5726 | 0 | 3.109 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
ROYTON | 6.6 | ROYTON | ROYTON | WHITEGATE | 392426 | 407533 | 800 | 9.1452 | 10.6239 | 15.2609 | 0 | 0 | 0 | 0 | 0 | 0 | Offers with ENW, due to be signed 28/08/2024
SALE | 6.6 | SALE | SALE | CARRINGTON | 378952 | 392177 | 630 | 7.2019 | 11.4457 | 16.0857 | 31.0489 | 8.3079 | 6.0616 | 16.0857 | 6.5677 | 14.7385 | N/A
SALE MOOR | 6.6 | SALE | SALE | CARRINGTON | 379671 | 391133 | 400 | 4.5726 | 1.5401 | 1.5401 | 12.01 | 12.01 | 12.01 | 1.5401 | 12.01 | 1.3941 | N/A
SALFORD QUAYS | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 380334 | 397555 | 800 | 9.1452 | 0 | 13.5457 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 0 | PP submitted, awaiting clock start date
SAMLESBURY ENTERPRISE ZONE | 11 | BLACKBURN |  | PENWORTHAM | 363416 | 431248 | 630 | 12 | 11.68 | 16.18 | 30.3 | 18.2981 | 13.1512 | 16.18
SANDGATE | 11 | BARROW & SANDGATE | BARROW | HARKER | 321492 | 468870 | 630 | 12.0031 | 8.0044 | 12.5044 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 7.2924 | 14.3266 | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
SCARISBRICK | 11 | SKELMERSDALE | SKELMERSDALE | WASHWAY FARM | 338069 | 412086 | 400 | 7.621 | 2.1832 | 3.6832 | 6.4667 | 1.9575 | 1.4344 | 3.6832 | 1.4344 | 3.6656 | Offer e signed 29/05/2024. Parrallel submission offer with ENW, due to be signed 29/08/2024
SEBERGHAM | 11 | CARLISLE | CARLISLE | HARKER | 335344 | 542653 | 630 | 12.0031 | 0 | 0.47418 | 1.9438 | 1.9438 | 1.4344 | 0.47418 | 1.4344 | 1.1732 | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
SEDBERGH | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 365151 | 491747 | 400 | 7.621 | 0 | 9.6047 | 19.5532 | 19.5532 | 19.3689 | 9.6047 | 0 | 0 | 2nd step offer signed 29/05/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024
SELSMIRE | 11 | PENRITH & SHAP | PENRITH | HUTTON | 361018 | 507505 | 630 | 12.0031 | 0 | 0 | 4.9054 | 4.9054 | 4.9054 | 0 | 4.9054 | 1.1883 | 2nd step offer signed 29/05/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024
SETTLE | 11 | PADIHAM | PADIHAM | PADIHAM | 381588 | 463721 | 630 | 12.0031 | 0.62381 | 8.1238 | 13.3716 | 13.3716 | 13.3716 | 8.1238 | 13.3716 | 7.6618 | Two parrallel 2nd step offer with ENW due to be signed 04/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Another parrallel submission clock started, offer due 28/08/2024
SEVEN STARS | 11 | LEYLAND | LEYLAND | PENWORTHAM | 352653 | 421636 | 800 | 15.242 | 1.0585 | 7.4085 | 32.0548 | 26.6004 | 19.1182 | 7.4085 | 18.9995 | 5.2353 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
SHANNON ST SOUTH | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 330806 | 435291 | 630 | 7.2019 | 4.417 | 9.917 | 32.1479 | 10.7617 | 7.852 | 9.917 | 8.0106 | 5.397 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
SHAP | 11 | PENRITH & SHAP | PENRITH | HUTTON | 356910 | 513357 | 400 | 7.621 | 0 | 0 | 12.2325 | 12.2325 | 12.2325 | 0 | 12.2325 | 7.0318 | 2nd step offer signed 29/05/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024
SHAW | 6.6 | ROYTON | ROYTON | WHITEGATE | 394298 | 409450 | 800 | 9.1452 | 9.6466 | 14.2836 | 0 | 0 | 0 | 0 | 0 | 0 | Offers with ENW, due to be signed 28/08/2024
Siddick | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 300289 | 530805 | 630 | 12.0031 | 17.154 | 23.7448 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0 | 0 | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
SILLOTH | 11 | CARLISLE | CARLISLE | HARKER | 311307 | 553464 | 400 | 7.621 | 19.1247 | 38.4633 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
SKELMERSDALE | 11 | SKELMERSDALE | SKELMERSDALE | WASHWAY FARM | 347198 | 407434 | 630 | 12.0031 | 4.0328 | 8.6698 | 11.2179 | 1.8968 | 1.3632 | 8.6698 | 1.3976 | 7.809 | Offer e signed 29/05/2024. Parrallel submission offer with ENW, due to be signed 29/08/2024
SKELTON C | 11 | PENRITH & SHAP | PENRITH | HUTTON | 342672 | 538337 | 630 | 12.0031 | 0 | 0 | 30.438 | 20.5893 | 15.0875 | 0 | 17.7881 | 13.3736 | 2nd step offer signed 29/05/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024
SLIPWAY | 11 | EGREMONT | EGREMONT | HARKER | 297180 | 518183 | 400 | 7.621 | 6.0039 | 8.0039 | 16.7034 | 16.4559 | 11.8272 | 8.0039 | 12.7115 | 7.3459 | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
SNIPE | 6.6 | DROYLSDEN | DROYLSDEN | STALYBRIDGE | 391844 | 398322 | 800 | 9.1452 | 6.865 | 11.502 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | Offer with ENW ,due signing by 29/08/2024
S.E. MACCLESFIELD | 11 | MACCLESFIELD | MACCLESFIELD | MACCLESFIELD | 392001 | 372504 | 630 | 12.0031 | 3.2009 | 3.2009 | 11.2179 | 1.9575 | 1.4344 | 3.2009 | 1.4344 | 0 | N/A
SOUTH PARK | 11 | LYTHAM | LYTHAM | PENWORTHAM | 336410 | 427512 | 400 | 7.621 | 14.2837 | 18.263 | 29.4531 | 11.5051 | 8.269 | 18.263 | 0 | 0 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
S.W. MACCLESFIELD | 11 | MACCLESFIELD | MACCLESFIELD | MACCLESFIELD | 390968 | 373004 | 400 | 7.621 | 2.9463 | 3.2009 | 11.2179 | 1.9575 | 1.4344 | 3.2009 | 1.4344 | 0 | N/A
SPA RD | 6.6 | BOLTON | BOLTON | KEARSLEY | 371065 | 409109 | 400 | 4.5726 | 6.1005 | 6.1005 | 11.2179 | 1.9575 | 1.4344 | 6.1005 | 1.4344 | 5.2215 | PP submitted, awaiting clock start date
SPADEADAM 132/11KV | 11 | - | - | HARKER | 361282 | 570359 | 1250 | 23.8157 | 25.6755 | 32.6755 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 0.31765 | 1.6795 | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
SPOTLAND | 6.6 | ROCHDALE CENTRAL | ROCHDALE CENTRAL | ROCHDALE | 387882 | 414309 | 630 | 7.2019 | 6.4756 | 9.9756 | 23.6188 | 13.2215 | 9.6467 | 9.9756 | 4.1691 | 9.6296 | Offers with ENW, due to be signed 20/08/2024 .Another parrallel submission made, offer due 28/06/2024
SPRING COTTAGE | 6.6 | NELSON | NELSON | PADIHAM | 385446 | 437481 | 400 | 4.5726 | 4.5373 | 19.3706 | 0 | 0 | 0 | 0 | 0 | 0 | Two parrallel 2nd step offer with ENW due to be signed 04/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Another parrallel submission clock started, offer due 28/08/2024
SPRING GARDEN ST 11kV | 11 | LANCASTER | LANCASTER | HEYSHAM | 347661 | 461494 | 800 | 15.242 | 4.2023 | 4.2023 | 11.2179 | 1.9575 | 1.4344 | 4.2023 | 1.5151 | 5.0572 | Offer with ENW, due to be signed 30/08/2024. Parrallel submission made, offer due 08/06/2024.Another parrallel submission made, awaiting clock start date.
SPRING GARDEN ST 6.6KV | 6.6 | LANCASTER | LANCASTER | HEYSHAM | 347651 | 461484 | 800 | 9.1452 | 4.2023 | 4.2023 | 11.2179 | 1.9575 | 1.4344 | 4.2023 | 1.5151 | 5.0572 | Offer with ENW, due to be signed 30/08/2024. Parrallel submission made, offer due 08/06/2024.Another parrallel submission made, awaiting clock start date.
SQUIRES GATE | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 332037 | 432063 | 400 | 4.5726 | 6.0985 | 10.6985 | 17.2189 | 2.7927 | 2.0376 | 10.6985 | 2.1114 | 6.2955 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
ST ANNES | 6.6 | LYTHAM | LYTHAM | PENWORTHAM | 331716 | 429849 | 630 | 7.2019 | 9.1032 | 12.6032 | 23.0658 | 9.7789 | 7.1349 | 12.6032 | 0 | 0 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
ST MARYS | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 392582 | 405316 | 630 | 7.2019 | 13.0703 | 17.7073 | 29.2752 | 10.4152 | 7.5992 | 17.7073 | 7.7148 | 4.6017 | Offers with ENW, due to be signed 28/08/2024
ST MARYS ST | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 354932 | 429640 | 400 | 4.5726 | 7.1664 | 10.6664 | 11.2179 | 1.9575 | 1.4344 | 10.6664 | 1.4344 | 10.0664 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
ST THOMAS RD | 6.6 | LYTHAM | LYTHAM | PENWORTHAM | 332713 | 428643 | 400 | 4.5726 | 13.7705 | 18.263 | 30.1228 | 12.9389 | 9.4406 | 18.263 | 0 | 0 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
STAINBURN | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 302535 | 529330 | 630 | 12.0031 | 8.2537 | 10.7537 | 7 | 1.9575 | 1.4344 | 7 | 0 | 0 | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
STANDISH | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 356139 | 410059 | 630 | 12.0031 | 5.2192 | 5.7161 | 20.7493 | 7.409 | 5.325 | 5.7161 | 1.9914 | 1.9914 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
STRANGEWAYS | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 383780 | 399743 | 400 | 4.5726 | 0 | 12.3035 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 0 | PP submitted, awaiting clock start date
STRAWBERRY BANK | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 376338 | 429396 | 630 | 7.2019 | 10.5712 | 14.7082 | 19.7068 | 3.1962 | 2.332 | 14.7082 | 2.4384 | 6.5078 | Two parrallel 2nd step offer with ENW due to be signed 04/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Another parrallel submission clock started, offer due 28/08/2024
STUART ST | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 387190 | 398835 | 600 | 6.8589 | 0 | 5.0887 | 11.2179 | 1.9575 | 1.4344 | 5.0887 | 1.4344 | 0 | Offer with ENW ,due signing by 29/08/2024
STUBBINS | 11 | ROSSENDALE | ROSSENDALE | PADIHAM | 379112 | 418005 | 400 | 7.621 | 9.7611 | 26.7611 | 26.3049 | 4.3309 | 3.1127 | 26.3049 | 2.782 | 23.5098 | Two parrallel 2nd step offer with ENW due to be signed 04/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Another parrallel submission clock started, offer due 28/08/2024
SWINTON | 11 | AGECROFT | AGECROFT | KEARSLEY | 378367 | 401718 | 800 | 15.242 | 9.4014 | 9.4014 | 30.2092 | 14.9945 | 10.7768 | 9.4014 | 10.853 | 18.1986 | PP submitted, awaiting clock start date
TAME VALLEY | 6.6 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 395148 | 398108 | 630 | 7.2019 | 7.1554 | 11.7924 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Offer with ENW ,due signing by 29/08/2024
TARDY GATE | 11 | RIBBLE | RIBBLE | PENWORTHAM | 353958 | 426066 | 400 | 7.621 | 9.522 | 13.659 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 9.065 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
TARLETON | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 344741 | 422417 | 400 | 7.621 | 4.4822 | 5.7161 | 20.8292 | 7.8812 | 5.6644 | 5.7161 | 0.31765 | 2.6844 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
THE HEIGHT | 6.6 | AGECROFT | AGECROFT | KEARSLEY | 379792 | 400497 | 400 | 4.5726 | 4.5365 | 9.4014 | 29.77 | 9.9814 | 7.2827 | 9.4014 | 7.3789 | 14.5981 | PP submitted, awaiting clock start date
THORLEY LN | 11 | MOSS NOOK |  | SOUTH MANCHESTER | 381374 | 386134 | 630 | 12 | 20.3911 | 26.4 | 8.968 | 1.9575 | 1.4344 | 8.968
THORNTON | 11 | BISPHAM | BISPHAM | PENWORTHAM | 334207 | 442111 | 630 | 12.0031 | 9.1242 | 12.2612 | 11.2179 | 1.9202 | 1.3801 | 11.2179 | 0.31765 | 2.6844 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
TOWNLEY ST | 11 | CHADDERTON | CHADDERTON | WHITEGATE | 387242 | 405960 | 400 | 7.621 | 0 | 0 | 33.4932 | 9.0484 | 6.5033 | 0 | 1.3649 | 0 | Offers with ENW, due to be signed 28/08/2024
TRAFFORD | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 380714 | 396551 | 630 | 7.2019 | 4.1074 | 13.0269 | 22.3705 | 7.8459 | 5.7246 | 13.0269 | 5.7122 | 14.3365 | 2nd Step offer with ENW, due to signed 15/07/2024.Offer with ENW due to sign 30/08/2024.Another submission made, awaiting Clock start date.
TRAFFORD PARK NORTH | 6.6 | BARTON | BARTON | CARRINGTON | 378738 | 397694 | 630 | 7.2019 | 6.2399 | 11.4899 | 2.6918 | 0.43658 | 0.31854 | 2.6918 | 0.31848 | 2.6914 | N/A
TRIMPELL | 11 | - | - | HEYSHAM | 341861 | 458979 | 630 | 12.0031 | 19.7099 | 19.7099 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 0.31765 | 1.6795 | Offer with ENW, due to be signed 30/08/2024. Parrallel submission made, offer due 08/06/2024.Another parrallel submission made, awaiting clock start date.
TRINITY | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 382649 | 398230 | 630 | 7.2019 | 0 | 13.5457 | 0 | 0 | 0 | 0 | 0 | 0 | PP submitted, awaiting clock start date
TULKETH | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 352393 | 431036 | 400 | 4.5726 | 5.9366 | 10.0736 | 11.2179 | 1.9575 | 1.4344 | 10.0736 | 1.4344 | 8.4618 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
ULVERSTON | 11 | ULVERSTON | ULVERSTON | HARKER | 327495 | 477808 | 630 | 12.0031 | 4.827 | 7.827 | 16.3552 | 10.3803 | 7.4605 | 7.827 | 7.6223 | 7.75 | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
UNION RD | 6.6 | BOLTON | BOLTON | KEARSLEY | 372174 | 410598 | 630 | 7.2019 | 1.9788 | 6.6158 | 11.2179 | 1.9575 | 1.4344 | 6.6158 | 1.4344 | 9.7198 | PP submitted, awaiting clock start date
UPHOLLAND | 11 | ORRELL | ORRELL | KIRKBY | 352531 | 404369 | 630 | 12.0031 | 0 | 6.8665 | 22.0084 | 11.0765 | 7.9609 | 6.8665 | 8.1328 | 6.6945 | 2nd step offer with ENW,due to be signed 04/06/2024 .Parrallel submission offer with ENW, due to be signed 29/08/2024
URMSTON | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 377117 | 395709 | 400 | 4.5726 | 4.1074 | 14.3001 | 28.9446 | 7.9004 | 5.7644 | 14.3001 | 5.7691 | 14.4783 | 2nd Step offer with ENW, due to signed 15/07/2024.Offer with ENW due to sign 30/08/2024.Another submission made, awaiting Clock start date.
VICTORIA PARK | 6.6 | LONGSIGHT | LONGSIGHT | BREDBURY | 385373 | 395948 | 630 | 7.2019 | 0 | 5.8957 | 25.5112 | 8.1201 | 5.9246 | 5.8957 | 4.6312 | 4.9475 | 2nd step offer with ENW,due to be signed 06/06/2024.Parrallel submission offer with ENW, due to be signed 29/08/2024
WARBRECK | 6.6 | BISPHAM | BISPHAM | PENWORTHAM | 331775 | 438420 | 630 | 7.2019 | 7.4371 | 10.9371 | 11.2179 | 1.9575 | 1.4344 | 10.9371 | 1.4344 | 10.9371 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
WARDLEWORTH | 6.6 | BELFIELD | BELFIELD | ROCHDALE | 390339 | 414050 | 630 | 7.2019 | 5.8835 | 10.5205 | 31.4551 | 7.8533 | 5.73 | 10.5205 | 5.5739 | 0 | Offers with ENW, due to be signed 20/08/2024 .Another parrallel submission made, offer due 28/06/2024
WARTON | 6.6 | PEEL | PEEL | PENWORTHAM | 341290 | 428540 | 1250 | 14.2894 | 0 | 0 | 21.3624 | 13.1775 | 9.6147 | 0 | 0 | 0 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
WATERHEAD | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 394942 | 405940 | 400 | 4.5726 | 14.6569 | 19.2939 | 29.365 | 12.6707 | 9.2449 | 19.2939 | 9.344 | 4.6017 | Offers with ENW, due to be signed 28/08/2024
WATERSWALLOWS | 11 | BUXTON | BUXTON | STALYBRIDGE | 407734 | 375459 | 630 | 12.0031 | 9.2255 | 9.2255 | 28.4979 | 11.3335 | 8.1456 | 9.2255 | 1.3561 | 10.6051 | Offer with ENW ,due signing by 29/08/2024
WEASTE | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 378751 | 398897 | 800 | 9.1452 | 0 | 9.1167 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 0 | PP submitted, awaiting clock start date
WERNETH | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 391273 | 403453 | 630 | 7.2019 | 13.7613 | 18.3983 | 30.177 | 12.1364 | 8.8551 | 18.3983 | 8.8768 | 4.6017 | Offers with ENW, due to be signed 28/08/2024
WESLEY PLACE BACUP | 6.6 | ROSSENDALE | ROSSENDALE | PADIHAM | 386475 | 422130 | 400 | 4.5726 | 5.15 | 9.787 | 30.2639 | 13.4866 | 9.8402 | 9.787 | 10.1945 | 7.7239 | Two parrallel 2nd step offer with ENW due to be signed 04/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Another parrallel submission clock started, offer due 28/08/2024
WEST DIDSBURY | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 383306 | 392514 | 630 | 7.2019 | 3.7903 | 10.7903 | 7.06 | 1.9575 | 1.4344 | 7.06 | 1.4344 | 8.6933 | 2nd Step offer with ENW, due to signed 15/07/2024.Offer with ENW due to sign 30/08/2024.Another submission made, awaiting Clock start date.
WESTGATE | 6.6 | LANCASTER | LANCASTER | HEYSHAM | 343077 | 463204 | 630 | 7.2019 | 4.2023 | 4.2023 | 11.2179 | 1.9575 | 1.4344 | 4.2023 | 1.5151 | 5.0572 | Offer with ENW, due to be signed 30/08/2024. Parrallel submission made, offer due 08/06/2024.Another parrallel submission made, awaiting clock start date.
WESTHOUGHTON | 11 | WESTHOUGHTON | WESTHOUGHTON | KEARSLEY | 365831 | 407025 | 400 | 7.621 | 0 | 4.5846 | 12.0984 | 1.9919 | 1.4316 | 4.5846 | 0.088852 | 0 | PP submitted, awaiting clock start date
WESTLINTON | 11 | CARLISLE | CARLISLE | HARKER | 339551 | 564489 | 630 | 12.0031 | 8.6863 | 11.8226 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
WHALLEY | 11 | PADIHAM | PADIHAM | PADIHAM | 373376 | 436176 | 630 | 12.0031 | 8.2517 | 12.8887 | 28.3048 | 8.1283 | 5.842 | 12.8887 | 5.5392 | 11.0853 | Two parrallel 2nd step offer with ENW due to be signed 04/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Another parrallel submission clock started, offer due 28/08/2024
WHALLEY RANGE | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 382923 | 394645 | 630 | 7.2019 | 2.5842 | 11.7212 | 7.06 | 1.9575 | 1.4344 | 7.06 | 1.4344 | 10.576 | 2nd Step offer with ENW, due to signed 15/07/2024.Offer with ENW due to sign 30/08/2024.Another submission made, awaiting Clock start date.
WHASSET | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 350648 | 481468 | 630 | 12.0031 | 0 | 5.5877 | 23.0587 | 20.1058 | 14.4504 | 5.5877 | 0 | 0 | 2nd step offer signed 29/05/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024
WHITTLE LE WOODS | 11 | LEYLAND | LEYLAND | PENWORTHAM | 357874 | 421203 | 630 | 12.0031 | 5.775 | 9.275 | 23.9575 | 14.6726 | 10.5455 | 9.275 | 10.3146 | 9.0214 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
WHITWORTH | 6.6 | ROCHDALE CENTRAL | ROCHDALE CENTRAL | ROCHDALE | 388779 | 419157 | 630 | 7.2 | 4.6744 | 6.1744 | 10.5081 | 4.4977 | 3.2817 | 6.1744 | 3.1391 | 5.9064 | Offers with ENW, due to be signed 20/08/2024 .Another parrallel submission made, offer due 28/06/2024
WIGTON | 11 | CARLISLE | CARLISLE | HARKER | 325814 | 549933 | 400 | 7.621 | 0 | 2.1577 | 7 | 1.9575 | 1.4344 | 2.1577 | 1.4344 | 0.21045 | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
WILLOW HEY | 11 | SKELMERSDALE | SKELMERSDALE | WASHWAY FARM | 347779 | 406066 | 400 | 7.621 | 8.5302 | 13.1672 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 9.682 | Offer e signed 29/05/2024. Parrallel submission offer with ENW, due to be signed 29/08/2024
WILLOWBANK | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 391885 | 406064 | 630 | 7.2019 | 1.5784 | 5.0784 | 25.3471 | 12.6152 | 9.2044 | 5.0784 | 9.2635 | 4.6017 | Offers with ENW, due to be signed 28/08/2024
WILLOWHOLME | 11 | CARLISLE | CARLISLE | HARKER | 338653 | 556688 | 630 | 12.0031 | 5.4542 | 9.5912 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
WILMSLOW | 11 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 384710 | 381286 | 630 | 12.0031 | 4.8885 | 8.3885 | 8.968 | 1.9575 | 1.4344 | 8.3885 | 1.4344 | 5.768 | 2nd Step offer with ENW, due to signed 15/07/2024.Offer with ENW due to sign 30/08/2024.Another submission made, awaiting Clock start date.
WINDERMERE | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 341657 | 498418 | 630 | 12.0031 | 0 | 9.6047 | 30.4268 | 21.0012 | 15.094 | 9.6047 | 0 | 0 | 2nd step offer signed 29/05/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024
WINIFRED RD | 6.6 | ADSWOOD | ADSWOOD | BREDBURY | 389971 | 388470 | 630 | 7.2019 | 5.4547 | 8.9547 | 18.0363 | 4.5581 | 3.3257 | 8.9547 | 2.1791 | 7.5047 | 2nd step offer with ENW,due to be signed 06/06/2024.Parrallel submission offer with ENW, due to be signed 29/08/2024
WITHINGTON | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 384841 | 392774 | 630 | 7.2019 | 2.7832 | 6.2832 | 7.06 | 1.9575 | 1.4344 | 6.2832 | 1.4344 | 6.0832 | 2nd Step offer with ENW, due to signed 15/07/2024.Offer with ENW due to sign 30/08/2024.Another submission made, awaiting Clock start date.
WITHYFOLD DRIVE | 11 | MACCLESFIELD | MACCLESFIELD | MACCLESFIELD | 392132 | 374352 | 400 | 7.621 | 3.2009 | 3.2009 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0.31765 | 0 | N/A
WOODBINE ST | 6.6 | CASTLETON | CASTLETON | ROCHDALE | 390519 | 412388 | 800 | 9.1452 | 5.6856 | 9.1856 | 24.1055 | 14.2958 | 10.4306 | 9.1856 | 10.5673 | 8.8316 | Offers with ENW, due to be signed 20/08/2024 .Another parrallel submission made, offer due 28/06/2024
WOODFIELD RD | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 358258 | 418014 | 400 | 7.621 | 4.6352 | 5.7161 | 30.8118 | 13.893 | 9.9852 | 5.7161 | 5.1053 | 5.1053 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
WOODHILL LANE | 6.6 | LANCASTER | LANCASTER | HEYSHAM | 343294 | 463785 | 400 | 4.5726 | 1.7595 | 2.7595 | 11.2179 | 1.9575 | 1.4344 | 2.7595 | 1.5151 | 2.7595 | Offer with ENW, due to be signed 30/08/2024. Parrallel submission made, offer due 08/06/2024.Another parrallel submission made, awaiting clock start date.
WOODHOUSE PARK | 11 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 382132 | 386340 | 630 | 12.0031 | 1.0021 | 4.5021 | 8.968 | 1.9575 | 1.4344 | 4.5021 | 1.4344 | 0.86929 | 2nd Step offer with ENW, due to signed 15/07/2024.Offer with ENW due to sign 30/08/2024.Another submission made, awaiting Clock start date.
WOODLEY | 11 | VERNON PARK | VERNON PARK | BREDBURY | 393116 | 392019 | 400 | 7.621 | 0 | 0 | 10.4869 | 1.7266 | 1.2409 | 0 | 1.0921 | 0 | 2nd step offer with ENW,due to be signed 06/06/2024.Parrallel submission offer with ENW, due to be signed 29/08/2024
WOOLFOLD | 11 | BURY | BURY | KEARSLEY | 378874 | 411666 | 630 | 12.0031 | 4.0454 | 8.0454 | 11.2179 | 1.9575 | 1.4344 | 8.0454 | 1.4344 | 11.2179 | PP submitted, awaiting clock start date
WORDSWORTH ST | 6.6 | BOLTON | BOLTON | KEARSLEY | 370709 | 410873 | 400 | 4.5726 | 8.8855 | 13.5225 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | PP submitted, awaiting clock start date
WORSLEY MESNES | 6.6 | WIGAN | WIGAN | KIRKBY | 357435 | 403977 | 630 | 7.2019 | 3.0793 | 12.0743 | 26.1692 | 10.7093 | 7.8138 | 12.0743 | 7.7377 | 8.7753 | 2nd step offer with ENW,due to be signed 04/06/2024 .Parrallel submission offer with ENW, due to be signed 29/08/2024
WRIGHTINGTON | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 353466 | 413290 | 400 | 7.621 | 5.7161 | 5.7161 | 30.4446 | 15.2646 | 10.971 | 5.7161 | 5.1053 | 5.1053 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
YEALAND | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 351537 | 475934 | 630 | 12.0031 | 0 | 6.5082 | 12.8478 | 12.8478 | 12.8478 | 6.5082 | 0 | 0 | 2nd step offer signed 29/05/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024

## 5) BSP Headroom Data
BSP Headroom
BSP | Voltage (kV) | BCA Group (GSP) | BSP Coordinates |  | Demand Headroom (MW) |  | Generation Headroom - N-0 -(MW) |  | Battery Storage Headroom N-0 -(MW)
|  |  | Easting | Northing | Firm | Non Firm | Inverter Based | Synchronous
ADSWOOD | 33 | BREDBURY | 389188 | 388310 | 53.4482 | 53.4482 | 123.5127 | 41.5496 | 53.4482 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.39156%2C-2.16403z=20?hl=en | 2nd step offer with ENW,due to be signed 06/06/2024.Parrallel submission offer with ENW, due to be signed 29/08/2024
AGECROFT | 33 | KEARSLEY | 380345 | 401831 | 9.4014 | 9.4014 | 72.377 | 22.7783 | 9.4014 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.51279%2C-2.29754z=20?hl=en | PP submitted, awaiting clock start date
ALTRINCHAM | 33 | CARRINGTON | 376380 | 389012 | 54.185 | 72.185 | 149.5819 | 48.1146 | 72.185 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.39778%2C-2.35667z=20?hl=en | N/A
ATHERTON | 33 | KEARSLEY | 366150 | 402088 | 0.72274 | 0.72274 | 119.9397 | 27.0664 | 0.72274 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.51405%2C-2.51233z=20?hl=en | PP submitted, awaiting clock start date
BARROW | 33 | HARKER | 319709 | 470489 | 36.124 | 36.124 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.12391%2C-3.23018z=20?hl=en | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
BARTON | 33 | CARRINGTON | 376758 | 397174 | 33.3759 | 55.3711 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.47087%2C-2.35076z=20?hl=en | N/A
BELFIELD | 33 | ROCHDALE | 391033 | 413945 | 11.9053 | 11.9053 | 54.6806 | 23.5987 | 11.9053 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.62216%2C-2.13727z=20?hl=en | Offers with ENW, due to be signed 20/08/2024 .Another parrallel submission made, offer due 28/06/2024
BISPHAM | 33 | PENWORTHAM | 332328 | 439711 | 38.1306 | 38.1306 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.84897%2C-3.04054z=20?hl=en | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
BLACKBURN | 33 | PENWORTHAM | 370584 | 429294 | 50.1487 | 50.1487 | 76.7657 | 41.5265 | 50.1487 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.7592%2C-2.44764z=20?hl=en | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
BLACKPOOL | 33 | PENWORTHAM | 330835 | 435308 | 38.4385 | 39.2785 | 119.4893 | 35.8009 | 39.2785 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.80944%2C-3.05179z=20?hl=en | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
BLOOM ST | 33 | SOUTH MANCHESTER | 384221 | 397717 | 0 | 31.33 | 152.6811 | 47.5518 | 31.33 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.47593%2C-2.23943z=20?hl=en | 2nd Step offer with ENW, due to signed 15/07/2024.Offer with ENW due to sign 30/08/2024.Another submission made, awaiting Clock start date.
BOLTON | 33 | KEARSLEY | 372255 | 410566 | 18.8531 | 31.5453 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.59102%2C-2.42059z=20?hl=en | PP submitted, awaiting clock start date
BURNLEY | 33 | ROCHDALE | 385569 | 434469 | 24.9052 | 24.9052 | 39.2068 | 19.1611 | 24.9052 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.80624%2C-2.22125z=20?hl=en | Offers with ENW, due to be signed 20/08/2024 .Another parrallel submission made, offer due 28/06/2024
BURY | 33 | KEARSLEY | 380272 | 411184 | 15.8614 | 15.8614 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.5967%2C-2.29975z=20?hl=en | PP submitted, awaiting clock start date
BUXTON | 33 | STALYBRIDGE | 407769 | 375476 | 9.2255 | 9.2255 | 63.2157 | 15.196 | 9.2255 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.27596%2C-1.885z=20?hl=en | Offer with ENW ,due signing by 29/08/2024
CARLISLE | 33 | HARKER | 338655 | 556583 | 25.3459 | 43.5459 | 6.7308 | 1.9358 | 6.7308 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.8993%2C-2.9589z=20?hl=en | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
CARRINGTON BSP | 33 | CARRINGTON | 373110 | 393020 | 13.835 | 34.835 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.43349%2C-2.40648z=20?hl=en | N/A
CASTLETON | 33 | ROCHDALE | 388461 | 411290 | 46.6734 | 46.6734 | 103.112 | 38.3398 | 46.6734 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.59783%2C-2.17663z=20?hl=en | Offers with ENW, due to be signed 20/08/2024 .Another parrallel submission made, offer due 28/06/2024
CHADDERTON | 33 | WHITEGATE | 389137 | 403821 | 0 | 0 | 52.2634 | 9.4814 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.53127%2C-2.16481z=20?hl=en | Offers with ENW, due to be signed 28/08/2024
DROYLSDEN | 33 | STALYBRIDGE | 390140 | 398146 | 35.7668 | 35.7668 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.4802%2C-2.14954z=20?hl=en | Offer with ENW ,due signing by 29/08/2024
EGREMONT | 33 | HARKER | 301070 | 513074 | 59.0019 | 59.0019 | 43.1189 | 37.3447 | 43.1189 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.50354%2C-3.52919z=20?hl=en | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
FREDERICK RD | 33 | KEARSLEY | 381795 | 399250 | 0 | 13.5457 | 6.7308 | 1.9358 | 6.7308 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.49066%2C-2.27698z=20?hl=en | PP submitted, awaiting clock start date
GOLBORNE | 33 | BOLD | 360607 | 397690 | 35.9964 | 53.9964 | 57.3634 | 10.4066 | 53.9964 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.47498%2C-2.59493z=20?hl=en | N/A
GREENHILL | 33 | WHITEGATE | 393262 | 404755 | 24.4519 | 24.4519 | 71.389 | 17.527 | 24.4519 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.53936%2C-2.10308z=20?hl=en | Offers with ENW, due to be signed 28/08/2024
HAZEL GROVE | 33 | BREDBURY | 391313 | 386877 | 39.5509 | 52.9909 | 132.2032 | 37.5478 | 52.9909 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.37854%2C-2.1319z=20?hl=en | 2nd step offer with ENW,due to be signed 06/06/2024.Parrallel submission offer with ENW, due to be signed 29/08/2024
HARTSHEAD-HEYROD | 33 | STALYBRIDGE | 397322 | 399942 | 30.5644 | 92.5644 | 6.7308 | 1.9358 | 6.7308 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.49638%2C-2.04169z=20?hl=en | Offer with ENW ,due signing by 29/08/2024
HUNCOAT | 33 | PADIHAM | 377997 | 431083 | 43.1782 | 61.1782 | 74.3197 | 22.7743 | 61.1782 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.77521%2C-2.33688z=20?hl=en | Two parrallel 2nd step offer with ENW due to be signed 04/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Another parrallel submission clock started, offer due 28/08/2024
HYDE | 33 | STALYBRIDGE | 395522 | 395647 | 30.4244 | 30.4244 | 30.0756 | 5.4562 | 30.0756 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.45264%2C-2.07376z=20?hl=en | Offer with ENW ,due signing by 29/08/2024
KEARSLEY LOCAL | 33 | KEARSLEY | 376355 | 404783 | 0 | 29.4406 | 6.7308 | 1.9358 | 6.7308 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.53905%2C-2.35884z=20?hl=en | PP submitted, awaiting clock start date
KENDAL (PARKSIDE RD) | 33 | HUTTON | 351915 | 491858 | 0 | 9.6047 | 108.9064 | 30.2814 | 9.6047 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.31969%2C-2.74168z=20?hl=en | 2nd step offer signed 29/05/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024
LANCASTER | 33 | HEYSHAM | 348644 | 463628 | 4.2023 | 4.2023 | 10.6707 | 1.9358 | 4.2023 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.06622%2C-2.78639z=20?hl=en | Offer with ENW, due to be signed 30/08/2024. Parrallel submission made, offer due 08/06/2024.Another parrallel submission made, awaiting clock start date.
LEYLAND | 33 | PENWORTHAM | 354121 | 423373 | 12.6266 | 27.5906 | 124.2442 | 32.3372 | 27.5906 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.70478%2C-2.69663z=20?hl=en | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
LONGSIGHT | 33 | BREDBURY | 385592 | 396016 | 6.3394 | 24.3394 | 149.1089 | 39.554 | 24.3394 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.46086%2C-2.21901z=20?hl=en | 2nd step offer with ENW,due to be signed 06/06/2024.Parrallel submission offer with ENW, due to be signed 29/08/2024
LOWER DARWEN | 33 | ROCHDALE | 369695 | 424981 | 0 | 44.725 | 26.078 | 4.731 | 26.078 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.72038%2C-2.45999z=20?hl=en | Offers with ENW, due to be signed 20/08/2024 .Another parrallel submission made, offer due 28/06/2024
LYTHAM | 33 | PENWORTHAM | 335361 | 429316 | 18.263 | 18.263 | 42.8677 | 40.742 | 18.263 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.75633%2C-2.98215z=20?hl=en | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
MACCLESFIELD | 33 | MACCLESFIELD | 392047 | 374564 | 3.2009 | 3.2009 | 10.6707 | 1.9358 | 3.2009 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.26811%2C-2.12063z=20?hl=en | N/A
MOSS NOOK | 33 | SOUTH MANCHESTER | 384073 | 385068 | 20.3911 | 45.5911 | 8.6231 | 1.9358 | 8.6231 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.36201%2C-2.2408z=20?hl=en | 2nd Step offer with ENW, due to signed 15/07/2024.Offer with ENW due to sign 30/08/2024.Another submission made, awaiting Clock start date.
NELSON | 33 | PADIHAM | 385989 | 438643 | 4.5373 | 25.9501 | 0 | 0 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.84299%2C-2.214z=20?hl=en | Two parrallel 2nd step offer with ENW due to be signed 04/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Another parrallel submission clock started, offer due 28/08/2024
NEW MILLS | 33 | STALYBRIDGE | 401141 | 383916 | 8.6091 | 8.6091 | 40.5615 | 40.5615 | 8.6091 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.35237%2C-1.9844z=20?hl=en | Offer with ENW ,due signing by 29/08/2024
ORRELL | 33 | KIRKBY | 352784 | 404565 | 0 | 22.2604 | 104.8901 | 42.7597 | 22.2604 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.5356%2C-2.71374z=20?hl=en | 2nd step offer with ENW,due to be signed 04/06/2024 .Parrallel submission offer with ENW, due to be signed 29/08/2024
PADIHAM | 33 | PADIHAM | 378571 | 433224 | 8.5652 | 27.427 | 123.9868 | 25.8044 | 27.427 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.79502%2C-2.32919z=20?hl=en | Two parrallel 2nd step offer with ENW due to be signed 04/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Another parrallel submission clock started, offer due 28/08/2024
PEEL | 33 | PENWORTHAM | 335644 | 432080 | 0 | 0 | 21.3624 | 21.3624 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.78114%2C-2.9776z=20?hl=en | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
PENRITH | 33 | HUTTON | 349996 | 530398 | 0 | 0 | 33.5447 | 20.3615 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.66637%2C-2.77723z=20?hl=en | 2nd step offer signed 29/05/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024
PRESTON EAST | 33 | PENWORTHAM | 356774 | 432942 | 0.80659 | 0.80659 | 10.6707 | 1.9358 | 0.80659 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.79104%2C-2.6584z=20?hl=en | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
RED BANK | 33 | WHITEGATE | 384542 | 399276 | 36.868 | 55.1643 | 145.8409 | 38.604 | 55.1643 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.49001%2C-2.23427z=20?hl=en | Offers with ENW, due to be signed 28/08/2024
RIBBLE | 33 | PENWORTHAM | 351794 | 429241 | 74.14 | 110.14 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.75725%2C-2.73184z=20?hl=en | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
ROCHDALE CENTRAL | 33 | ROCHDALE | 389111 | 413393 | 46.4311 | 58.4311 | 94.6521 | 40.273 | 58.4311 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.61653%2C-2.16602z=20?hl=en | Offers with ENW, due to be signed 20/08/2024 .Another parrallel submission made, offer due 28/06/2024
ROSSENDALE | 33 | PADIHAM | 380261 | 422010 | 34.2881 | 36.2864 | 96.7129 | 48.8792 | 36.2864 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.69402%2C-2.30041z=20?hl=en | Two parrallel 2nd step offer with ENW due to be signed 04/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Another parrallel submission clock started, offer due 28/08/2024
ROYTON | 33 | WHITEGATE | 392426 | 407533 | 17.853 | 94.8316 | 0 | 0 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.56464%2C-2.11572z=20?hl=en | Offers with ENW, due to be signed 28/08/2024
SALE | 33 | CARRINGTON | 378726 | 392892 | 24.5357 | 24.5357 | 78.4545 | 49.258 | 24.5357 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.42581%2C-2.31835z=20?hl=en | N/A
SANDGATE | 33 | HARKER | 321492 | 468870 | 36.124 | 36.124 | 50.9976 | 9.2518 | 36.124 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.10982%2C-3.20288z=20?hl=en | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
SHAP | 33 | HUTTON | 356910 | 513357 | 0 | 0 | 33.5447 | 33.5447 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.51358%2C-2.66756z=20?hl=en | 2nd step offer signed 29/05/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024
SIDDICK | 33 | HARKER | 300332 | 530823 | 39.9765 | 84.0765 | 6.7308 | 1.9358 | 6.7308 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.64948%2C-3.51144z=20?hl=en | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
SKELMERSDALE | 33 | WASHWAY FARM | 347172 | 407455 | 21.3547 | 21.3547 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.56076%2C-2.79859z=20?hl=en | Offer e signed 29/05/2024. Parrallel submission offer with ENW, due to be signed 29/08/2024
STAINBURN | 33 | HARKER | 302535 | 529330 | 39.9765 | 84.0765 | 6.7308 | 1.9358 | 6.7308 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.66252%2C-3.54717z=20?hl=en | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
STRETFORD | 33 | SOUTH MANCHESTER | 380069 | 395104 | 4.1074 | 50.7342 | 131.4503 | 32.7456 | 50.7342 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.4523%2C-2.30113z=20?hl=en | 2nd Step offer with ENW, due to signed 15/07/2024.Offer with ENW due to sign 30/08/2024.Another submission made, awaiting Clock start date.
STUART ST | 33 | STALYBRIDGE | 387247 | 398875 | 0 | 5.0887 | 10.6707 | 1.9358 | 5.0887 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.48612%2C-2.19476z=20?hl=en | Offer with ENW ,due signing by 29/08/2024
THORNTON | 33 | STANAH | 334559 | 443368 | 12.4713 | 24.4713 | 26.8965 | 9.1111 | 24.4713 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.8709%2C-3.00229z=20?hl=en | N/A
ULVERSTON | 33 | HARKER | 327495 | 477808 | 45.1293 | 45.1293 | 51.0849 | 26.6593 | 45.1293 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.1907%2C-3.11215z=20?hl=en | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
VERNON PARK | 33 | BREDBURY | 391131 | 390929 | 0 | 0 | 94.4527 | 18.6274 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.41552%2C-2.13492z=20?hl=en | 2nd step offer with ENW,due to be signed 06/06/2024.Parrallel submission offer with ENW, due to be signed 29/08/2024
WEST DIDSBURY | 33 | SOUTH MANCHESTER | 382900 | 393269 | 15.2158 | 51.7158 | 6.7885 | 1.9358 | 6.7885 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.42927%2C-2.25292z=20?hl=en | 2nd Step offer with ENW, due to signed 15/07/2024.Offer with ENW due to sign 30/08/2024.Another submission made, awaiting Clock start date.
WESTHOUGHTON | 33 | KEARSLEY | 365831 | 407025 | 22.8063 | 22.8063 | 88.0127 | 25.2584 | 22.8063 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.55846%2C-2.51787z=20?hl=en | PP submitted, awaiting clock start date
WIGAN | 33 | KIRKBY | 358343 | 404626 | 3.0793 | 42.0793 | 87.9264 | 34.0049 | 42.0793 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.53645%2C-2.62967z=20?hl=en | 2nd step offer with ENW,due to be signed 04/06/2024 .Parrallel submission offer with ENW, due to be signed 29/08/2024
WRIGHTINGTON | 33 | PENWORTHAM | 354460 | 413610 | 5.7161 | 5.7161 | 56.6211 | 22.6708 | 5.7161 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.61411%2C-2.70439z=20?hl=en | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date

## 6)Transmission Capacity - App G
Appendix G Summary
GSP / Site |  | Capacity of Connected & Contracted Connections (MW) |  |  |  | Materiality Headroom (Part 5) (MW) | Materiality Status | Capacity in Project Progression / Modification Application | Total Aggregated Developer Capacity Limit(MW) | Transmission FL Headroom (kA) | Project Progression Update
|  | Part 1 | Part 2 | Part 3 | Part 4
BOLD* | BOLD | 25.1 | 50.4 | 0 | 0 | 0 | B | N/A | 75.5 | 0 | N/A
BREDBURY | BREDBURY | 10.1 | 134.1 | 0 | 288.2 | 0 | C | 0 | 432.4 | 3 | 2nd step offer with ENW,due to be signed 06/06/2024.Parrallel submission offer with ENW, due to be signed 29/08/2024
CARRINGTON | CARRINGTON | 105 | 94 | 0 | 0 | 0 | B | 0 | 338 | 5.13 | N/A
HARKER | HARKER | 765.4 | 88 | 0 | 1081.6 | 0 | C | 164.4 | 1935 | 0 | 2nd step offer with ENW,due to be signed 18/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Anothe parrallel submission made, Offer due 28/08/2024.
HUTTON | HUTTON | 47.9 | 53 | 0 | 151 | 0 | C | 284.6 | 251.9 | 0 | 2nd step offer signed 29/05/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024
HEYSHAM | HEYSHAM | 292.6 | 0 | 109 | 21.5 | 0 | C | 199.8 | 423.1 | 0 | Offer with ENW, due to be signed 30/08/2024. Parrallel submission made, offer due 08/06/2024.Another parrallel submission made, awaiting clock start date.
KEARSLEY | KEARSLEY | 57.9 | 264.7 | 11 | 0 | 0 | C | 75 | 333.6 | 3 | PP submitted, awaiting clock start date
KIRKBY | KIRKBY | 6 | 146.4 | 0 | 180.7 | 0 | C | 120 | 333.1 | 3 | 2nd step offer with ENW,due to be signed 04/06/2024 .Parrallel submission offer with ENW, due to be signed 29/08/2024
MACCLESFIELD | MACCLESFIELD | 27.9 | 30 | 0 | 0 | 0 | B | 0 | 97.9 | 2.57 | N/A
PADIHAM | PADIHAM | 35.5 | 135.1 | 219.9 | 438.7 | 0 | C | 144.9 | 829.2 | 0.837 | Two parrallel 2nd step offer with ENW due to be signed 04/07/2024.Parrallel submission offer with ENW,due to be signed 28/08/2024.Another parrallel submission clock started, offer due 28/08/2024
PENWORTHAM | PENWORTHAM | 187.9 | 601.1 | 67.6 | 253.2 | 0 | C | 263.5 | 1109.8 | 9.21 | 2nd Step offer with ENW,due to be signed 03/07/2024.Parrallel submission offer with ENW, due to be signed 24/08/2024. Another parrallel submission made, awaiting clock start date
ROCHDALE | ROCHDALE | 204.1 | 221.5 | 47 | 134.3 | 0 | C | 172 | 606.9 | 1.92 | Offers with ENW, due to be signed 20/08/2024 .Another parrallel submission made, offer due 28/06/2024
SOUTH MANCHESTER | SOUTH MANCHESTER | 22.2 | 81.3 | 0 | 420.8 | 0 | C | 169.9 | 524.3 | 3 | 2nd Step offer with ENW, due to signed 15/07/2024.Offer with ENW due to sign 30/08/2024.Another submission made, awaiting Clock start date.
STALYBRIDGE | STALYBRIDGE | 58.3 | 236.8 | 0 | 70 | 0 | C | 0 | 365.1 | 0.591 | Offer with ENW ,due signing by 29/08/2024
STANAH | STANAH | 195.9 | 142 | 0 | 0 | 0 | B | 0 | 349.4 | 3.01 | N/A
WASHWAY FARM | WASHWAY FARM | 7.9 | 101.2 | 0 | 51.9 | 0 | C | 85 | 161 | 3 | Offer e signed 29/05/2024. Parrallel submission offer with ENW, due to be signed 29/08/2024
WHITEGATE | WHITEGATE | 32 | 219.8 | 0 | 128.2 | 0 | C | 0 | 380 | 3.09 | Offers with ENW, due to be signed 28/08/2024
Process |  |  | Parts 1 - 5 |  |  |  |  | Materiality Status
The Appendix G process aims to improve on the Statement of Works process by reducing timescales and facilitating greater transparency to the customer. Seventeen of ENWLs twenty GSPs have already converted to the Appendix G process and work is in progress to convert the three remaining sites. The above table summarises the Appendix G results of the GSPs which have already been converted from the Statement of Works process. Sites marked with an asterisk (*) are connected to the transmission network through the distribution network operated by SP Energy Networks. Appendix G submissions for these sites are made by SP Energy Networks on behalf of Electricity North West. For Further information on how to interpret the information presented in this table please refer to the user guide embedded within the first tab of this workbook. |  |  | Appendix G consists of 5 parts: • Part 1 – Existing power stations already connected to our network. • Part 2 – Power stations connected or contracted to connect to our network for which site specific requirements will apply e.g. power factor and controllability. • Part 3 – Power stations connected or contracted to connect to our network for which interim restrictions on availability will apply. Site specific requirements e.g. power factor and controllability, will also apply. • Part 4 – Power stations contracted to connect to our network which are unable to connect until transmission works have been completed. • Part 5 – Materiality headroom. This is a figure, determined by the transmission system operator, representing the available thermal capacity at the transmission system interface before a Modification Application is triggered. |  |  |  |  | To aid understanding we have given each GSP a materiality status. The three status are: A. The latest Appendix G return indicates that there is spare transmission system capacity at this location. B. There is insufficient capacity to accommodate any further sites without undertaking transmission system work. To identify the scope of these works a Modification Application will be required. C. There is insufficient capacity to accommodate any further connections without undertaking work on the transmission system. These works have already been identified and there are sites in project progression. New sites may still require a new Modification Application.