## Introduction
Network Headroom Report 2025 Data Workbook
This workbook is an accompaniment to our 2025 Network Headroom Report. It contains detailed datasets and interactive tools which allow our customers to understand headroom availability by Primary and Bulk Supply point, from a Demand and Generation point of view out to 2051.
The Data contained in this workbook is based on our 2024 DFES data and existing network. Please note the value of headroom is calculated from two reference points, Firm Capacity at sites now, and the anticipated Firm Capacity at sites at the end of RIIO-ED2 (2028) based on changes to firm capacity driven by anticipated investment outcomes. Results should only be used as an indication and will be updated upon the next refresh of the data in two years time.
CONTENTS
Section | Tab | Description
INTERACTIVE DATA TOOLS | Local Authority Look Up | List of all Primaries, BSPs and GSPs with a link to the local authrity in which they are located.
| Demand Headroom Summary Table | Select specific Primary or BSP to return overview of Demand Headroom 2024-2051
| Generation Headroom Summary Table | Select specific Primary or BSP and technology type to return overview of Generation Headroom 2024-2051
GROUP,BSP AND PRIMARY SUBSTATION DATASETS | Primary Headroom | All Primary data showing demand headroom by Scenario
| BSP Headroom | All BSP data showing demand headroom by Scenario
| Gen Primary Headroom | All Primary data showing generation headroom by Scenario
| Gen BSP Headroom | All BSP data showing generation headroom by Scenario
TRANSMISSION HEADROOM | Transmission Headroom | Transmission Headroom with earliest in service dates
Version
1
Published
May 2025

## User Guide
Network Headroom Report 2023 Data Workbook - User Guide
This workbook should be used in conjunction with the following documents - Network Development Report, Network Headroom Report and Network Development Methodology
To review demand headroom at any Primary or Bulk Supply Point on the ENWL network, the user can initially identify the location via "Tab 1 Local Authority Look Up" which highlights the local authority in which the specific site resides. Please note some sites cover more than one local authority. Next the user should move to "Tab 2 Demand Headroom Table", and using the drop down menu in cell D4 select the Primary Substation as required. This will then cause the look up to display results from all six scenarios out to 2051.The user should then progress to cell D26 and select the Bulk Supply Point indicated in cell D5 to get a picture and understanding of the BSP headroom availability. Alternatively should the user only be interested in BSP capacity then cell D26 can be used to simply select the required BSP location.
Capacity is quoted as either Firm or Non Firm. Firm capacity is defined at a two transformer site as the Long Term Emergency Rating of the remaining in service transformer for the loss of the other transfomer or the HV transfer capablity of a single transfomer site. Non firm is based on the 3 min Auto Switching rating of the transfomer or the HV transfer capablity of a single transformer site.
A similar process can then be followed using "Tab 3 Generation headroom table". The drop down menu in cell D3 allows the Primary Substation to be selected with the results from all scenarios out to 2051 displayed. Use of Cell D4 allows the selection of the specific technology type to be made, allowing for example either Synchronous or Battery Technology to be selected. The user should then progress to cell D20 and select the Bulk Supply Point indicated in cell D6 to get a picture and understanding of the BSP headroom availability. It is recommended to also match the technology type via cell D21. Alternatively should the user only be interested in BSP capacity then cell D20 can be used to simply select the appropriate BSP location along with the technology type selection in cell D21.
Negative values shown in red cells in the report workbook tabs indicate where there are shortfalls in the capacity of our existing network and show us where future network interventions may be required; this allows users to understand the influence of the various scenarios on available network headroom up to 2051. Negative values also show where interventions may be required to accommodate demand or generation forecast requirements, and these should not be interpreted as a barrier to specific requirements. Review of the Network Development Plan Document will likely show an investment route planned to alleviate any highlighted shortfall.

## 1 - Local Authority Look Up
Primary | Bulk Supply Point | Grid Supply Point | Local Authority | Combined Local Authority
Albion St | Lower Darwen | Penwortham East GSP / Rochdale SGT 1 GROUP | Blackburn with Darwen | Lancashire
Alderley & Chelford | Moss Nook | South Manchester GSP | Cheshire East | Greater Manchester
Alston | Penrith & Shap | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Eden | Cumbria
Ambleside | Kendal (Parkside Rd) | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | South Lakeland | Cumbria
Ancoats North T11 & T12 | Red Bank | Whitegate GSP | Manchester | Greater Manchester
Ancoats North T14 | Red Bank | Whitegate GSP | Manchester | Greater Manchester
Annie Pit | Stainburn & Siddick | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Allerdale | Cumbria
Ansdell | Lytham | Penwortham West GSP / Stanah GSP GROUP | Fylde | Lancashire
Ardwick | Stuart St | Stalybridge GSP | Manchester | Greater Manchester
Arnside | Kendal (Parkside Rd) | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Lancaster | Cumbria
Arnside | Kendal (Parkside Rd) | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | South Lakeland | Cumbria
Ashton (Golborne) | Golborne | Bold | St. Helens | Merseyside
Ashton (Golborne) | Golborne | Bold | Wigan | Greater Manchester
Ashton (Ribble) | Ribble | Penwortham East GSP / Rochdale SGT 1 GROUP | Fylde | Lancashire
Ashton (Ribble) | Ribble | Penwortham East GSP / Rochdale SGT 1 GROUP | Preston | Lancashire
Ashton On Mersey | Sale | Carrington ENWL SGTs 1B 2B 4 7 | Trafford | Greater Manchester
Ashton Under Lyne T11 & T12 | Hartshead-Heyrod | Stalybridge GSP | Oldham | Greater Manchester
Ashton Under Lyne T11 & T12 | Hartshead-Heyrod | Stalybridge GSP | Tameside | Greater Manchester
Ashton Under Lyne T13 | Hartshead-Heyrod | Stalybridge GSP | Tameside | Greater Manchester
Ashwood Dale | Buxton | Stalybridge GSP | High Peak | Derbyshire
Askam & Dalton | Ulverston | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Barrow-in-Furness | Cumbria
Askam & Dalton | Ulverston | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Copeland | Cumbria
Askam & Dalton | Ulverston | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | South Lakeland | Cumbria
Askerton Castle | Spadeadam 11/33kV | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Carlisle | Cumbria
Aspatria | Stainburn & Siddick | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Allerdale | Cumbria
Atherton Town Centre | Atherton | Kearsley 132 GSP | Bolton | Greater Manchester
Atherton Town Centre | Atherton | Kearsley 132 GSP | Wigan | Lancashire
Athletic St | Burnley | Rochdale SGTs 2 3 4 | Burnley | Lancashire
Avenham | Preston East | Penwortham East GSP / Rochdale SGT 1 GROUP | Preston | Lancashire
Baguley | Sale | Carrington ENWL SGTs 1B 2B 4 7 | Manchester | Greater Manchester
Baguley | Sale | Carrington ENWL SGTs 1B 2B 4 7 | Trafford | Greater Manchester
Bamber Bridge | Ribble | Penwortham East GSP / Rochdale SGT 1 GROUP | South Ribble | Lancashire
Barbara St | Bolton | Kearsley 132 GSP | Bolton | Greater Manchester
Barrow | Barrow & Sandgate | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Barrow-in-Furness | Cumbria
Barrow | Barrow & Sandgate | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | South Lakeland | Cumbria
Barton Dock Rd | Barton | Carrington ENWL SGTs 1B 2B 4 7 | Trafford | Greater Manchester
Bedford | Atherton | Kearsley 132 GSP | Salford | Greater Manchester
Bedford | Atherton | Kearsley 132 GSP | Warrington | Warrington
Bedford | Atherton | Kearsley 132 GSP | Wigan | Greater Manchester
Belgrave | Greenhill | Whitegate GSP | Oldham | Greater Manchester
Belgrave | Greenhill | Whitegate GSP | Tameside | Greater Manchester
Benchill | West Didsbury | South Manchester GSP | Manchester | Greater Manchester
Bentham | Kendal (Parkside Rd) | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Craven | Cumbria
Bentham | Kendal (Parkside Rd) | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Lancaster | Cumbria
Bispham | Bispham | Penwortham West GSP / Stanah GSP GROUP | Blackpool | Lancashire
Bispham | Bispham | Penwortham West GSP / Stanah GSP GROUP | Wyre | Lancashire
Blackbull | Ribble | Penwortham East GSP / Rochdale SGT 1 GROUP | Preston | Lancashire
Blackbull | Ribble | Penwortham East GSP / Rochdale SGT 1 GROUP | Wyre | Lancashire
Blackburn | Blackburn | Penwortham East GSP / Rochdale SGT 1 GROUP | Blackburn with Darwen | Lancashire
Blackburn | Blackburn | Penwortham East GSP / Rochdale SGT 1 GROUP | Hyndburn | Lancashire
Blackburn Rd Clayton | Huncoat | Padiham GSP | Hyndburn | Lancashire
Blackburn Rd Clayton | Huncoat | Padiham GSP | Ribble Valley | Lancashire
Blackfriars | Frederick Rd | Kearsley 132 GSP | Manchester | Greater Manchester
Blackfriars | Frederick Rd | Kearsley 132 GSP | Salford | Greater Manchester
Blackley | Red Bank | Whitegate GSP | Bury | Greater Manchester
Blackley | Red Bank | Whitegate GSP | Manchester | Greater Manchester
Blackpool | Blackpool | Penwortham West GSP / Stanah GSP GROUP | Blackpool | Lancashire
Bollington |  | Macclesfield 33 GSP | Cheshire East | Cheshire East
Bolton By Bowland | Padiham | Padiham GSP | Ribble Valley | Lancashire
Bolton Le Sands | Lancaster | Heysham GSP | Lancaster | Lancashire
Botany Bay | Leyland | Penwortham West GSP / Stanah GSP GROUP | Chorley | Lancashire
Bow Lane | Leyland | Penwortham West GSP / Stanah GSP GROUP | Chorley | Lancashire
Bow Lane | Leyland | Penwortham West GSP / Stanah GSP GROUP | South Ribble | Lancashire
Bowaters | Barrow & Sandgate | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Barrow-in-Furness | Cumbria
Bowdon | Altrincham | Carrington ENWL SGTs 1B 2B 4 7 | Cheshire East | Cheshire East
Bowdon | Altrincham | Carrington ENWL SGTs 1B 2B 4 7 | Trafford | Greater Manchester
Bradford | Stuart St | Stalybridge GSP | Manchester | Greater Manchester
Bradshawgate | Bolton | Kearsley 132 GSP | Bolton | Greater Manchester
Bramhall | Hazel Grove | Bredbury GSP | Stockport | Greater Manchester
Bridgewater | Bloom St | South Manchester GSP | Manchester | Greater Manchester
Brinksway | Adswood | Bredbury GSP | Stockport | Greater Manchester
Broadheath | Altrincham | Carrington ENWL SGTs 1B 2B 4 7 | Trafford | Greater Manchester
Broadway | Lancaster | Heysham GSP | Lancaster | Lancashire
Buckshaw | Leyland | Penwortham West GSP / Stanah GSP GROUP | Chorley | Lancashire
Buckshaw | Leyland | Penwortham West GSP / Stanah GSP GROUP | South Ribble | Lancashire
Burnley | Burnley | Rochdale SGTs 2 3 4 | Burnley | Lancashire
Burnley | Burnley | Rochdale SGTs 2 3 4 | Pendle | Lancashire
Burnley Centre | Burnley | Rochdale SGTs 2 3 4 | Burnley | Lancashire
Burnley North | Burnley | Rochdale SGTs 2 3 4 | Burnley | Lancashire
Burnley North | Burnley | Rochdale SGTs 2 3 4 | Pendle | Lancashire
Burrow Beck | Lancaster | Heysham GSP | Lancaster | Lancashire
Burrow Beck | Lancaster | Heysham GSP | Wyre | Lancashire
Burscough Bridge | Wrightington | Penwortham West GSP / Stanah GSP GROUP | West Lancashire | Lancashire
Bury Town Centre | Bury | Kearsley 132 GSP | Bury | Greater Manchester
Campbell St |  | Kearsley Local 33 GSP | Bolton | Greater Manchester
Cannon St | Red Bank | Whitegate GSP | Manchester | Greater Manchester
Capontree | Carlisle | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Carlisle | Cumbria
Carleton | Egremont | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Copeland | Cumbria
Carlisle North | Carlisle North | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Carlisle | Cumbria
Carr St |  | Kearsley Local 33 GSP | Salford | Greater Manchester
Castleton | Castleton | Rochdale SGTs 2 3 4 | Rochdale | Greater Manchester
Catterall Waterworks | Ribble | Penwortham East GSP / Rochdale SGT 1 GROUP | Wyre | Lancashire
Cecil St | Blackpool | Penwortham West GSP / Stanah GSP GROUP | Blackpool | Lancashire
Central Manchester | Stuart St | Stalybridge GSP | Manchester | Greater Manchester
Chadderton | Chadderton | Whitegate GSP | Oldham | Greater Manchester
Chamberhall | Bury | Kearsley 132 GSP | Bury | Greater Manchester
Chamberhall | Bury | Kearsley 132 GSP | Rochdale | Greater Manchester
Chamberhall | Bury | Kearsley 132 GSP | Rossendale | Lancashire
Chapel Wharf | Frederick Rd | Kearsley 132 GSP | Manchester | Greater Manchester
Chapel Wharf | Frederick Rd | Kearsley 132 GSP | Salford | Greater Manchester
Chassen Rd | Barton | Carrington ENWL SGTs 1B 2B 4 7 | Trafford | Greater Manchester
Chatsworth St | Barrow & Sandgate | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Barrow-in-Furness | Cumbria
Cheadle Heath | Adswood | Bredbury GSP | Stockport | Greater Manchester
Cheadle Hulme | Adswood | Bredbury GSP | Stockport | Greater Manchester
Cheetham Hill | Agecroft | Kearsley 132 GSP | Bury | Greater Manchester
Cheetham Hill | Agecroft | Kearsley 132 GSP | Manchester | Greater Manchester
Cheetham Hill | Agecroft | Kearsley 132 GSP | Salford | Greater Manchester
Chester Rd T11 & T12 | Stretford | South Manchester GSP | Trafford | Greater Manchester
Chester Rd T13 | Stretford | South Manchester GSP | Trafford | Greater Manchester
Chorley South | Wrightington | Penwortham West GSP / Stanah GSP GROUP | Chorley | Lancashire
Chorlton | West Didsbury | South Manchester GSP | Manchester | Greater Manchester
Chorlton | West Didsbury | South Manchester GSP | Trafford | Greater Manchester
Church | Huncoat | Padiham GSP | Hyndburn | Lancashire
Circle Sq | Longsight | Bredbury GSP | Manchester | Greater Manchester
Clarendon Rd | Blackburn | Penwortham East GSP / Rochdale SGT 1 GROUP | Blackburn with Darwen | Lancashire
Clarendon Rd | Blackburn | Penwortham East GSP / Rochdale SGT 1 GROUP | Hyndburn | Lancashire
Clarendon Rd | Blackburn | Penwortham East GSP / Rochdale SGT 1 GROUP | Ribble Valley | Lancashire
Claughton | Lancaster | Heysham GSP | Lancaster | Lancashire
Cleveleys | Bispham | Penwortham West GSP / Stanah GSP GROUP | Blackpool | Lancashire
Cleveleys | Bispham | Penwortham West GSP / Stanah GSP GROUP | Wyre | Lancashire
Clifton Junction |  | Kearsley Local 33 GSP | Salford | Greater Manchester
Clover Hill | Nelson | Padiham GSP | Burnley | Lancashire
Clover Hill | Nelson | Padiham GSP | Pendle | Lancashire
Cog Lane | Huncoat | Padiham GSP | Burnley | Lancashire
Coniston | Ulverston | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | South Lakeland | Cumbria
Copse Rd | Thornton | Penwortham West GSP / Stanah GSP GROUP | Wyre | Lancashire
Cox Green | Bolton | Kearsley 132 GSP | Blackburn with Darwen | Lancashire
Cox Green | Bolton | Kearsley 132 GSP | Bolton | Greater Manchester
Cox Green | Bolton | Kearsley 132 GSP | Chorley | Lancashire
Craggs Row & Bushell St | Preston East | Penwortham East GSP / Rochdale SGT 1 GROUP | Preston | Lancashire
Crown Lane | Westhoughton | Kearsley 132 GSP | Bolton | Greater Manchester
Crown Lane | Westhoughton | Kearsley 132 GSP | Chorley | Lancashire
Crown Lane | Westhoughton | Kearsley 132 GSP | Wigan | Greater Manchester
Culcheth | Golborne | Bold | Salford | Greater Manchester
Culcheth | Golborne | Bold | Warrington | Warrington
Culcheth | Golborne | Bold | Wigan | Greater Manchester
Cutacre |  | Kearsley Local 33 GSP | Bolton | Greater Manchester
Deansgate | Bloom St | South Manchester GSP | Manchester | Greater Manchester
Denton East | Droylsden | Stalybridge GSP | Tameside | Greater Manchester
Denton West | Droylsden | Stalybridge GSP | Manchester | Greater Manchester
Denton West | Droylsden | Stalybridge GSP | Tameside | Greater Manchester
Dickinson St T11 & T12 | Bloom St | South Manchester GSP | Manchester | Greater Manchester
Dickinson St T13 | Stuart St | Stalybridge GSP | Manchester | Greater Manchester
Didsbury | West Didsbury | South Manchester GSP | Manchester | Greater Manchester
Dodgson Rd | Preston East | Penwortham East GSP / Rochdale SGT 1 GROUP | Preston | Lancashire
Douglas St | Ribble | Penwortham East GSP / Rochdale SGT 1 GROUP | Preston | Lancashire
Droylsden East | Droylsden | Stalybridge GSP | Manchester | Greater Manchester
Droylsden East | Droylsden | Stalybridge GSP | Tameside | Greater Manchester
Dukinfield | Hyde | Stalybridge GSP | Tameside | Greater Manchester
Dumers Lane | Bury | Kearsley 132 GSP | Bury | Greater Manchester
Dumplington | Barton | Carrington ENWL SGTs 1B 2B 4 7 | Trafford | Greater Manchester
Eastlands | Stuart St | Stalybridge GSP | Manchester | Greater Manchester
Easton | Spadeadam 11/33kV | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Carlisle | Cumbria
Egremont | Egremont | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Copeland | Cumbria
Embleton | Stainburn & Siddick | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Allerdale | Cumbria
Exchange St | Lower Darwen | Penwortham East GSP / Rochdale SGT 1 GROUP | Blackburn with Darwen | Lancashire
Failsworth | Chadderton | Whitegate GSP | Manchester | Greater Manchester
Failsworth | Chadderton | Whitegate GSP | Oldham | Greater Manchester
Fallowfield | West Didsbury | South Manchester GSP | Manchester | Greater Manchester
Farnworth |  | Kearsley Local 33 GSP | Bolton | Greater Manchester
Feniscowles | Lower Darwen | Penwortham East GSP / Rochdale SGT 1 GROUP | Blackburn with Darwen | Lancashire
Ferodo | New Mills | Stalybridge GSP | High Peak | Derbyshire
Flat Lane | Padiham | Padiham GSP | Craven | Lancashire
Flat Lane | Padiham | Padiham GSP | Ribble Valley | Lancashire
Frederick Rd | Frederick Rd | Kearsley 132 GSP | Salford | Greater Manchester
Fusehill | Carlisle | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Carlisle | Cumbria
Gale | Belfield | Rochdale SGTs 2 3 4 | Rochdale | Greater Manchester
Gale | Belfield | Rochdale SGTs 2 3 4 | Rossendale | Lancashire
Garstang | Thornton | Penwortham West GSP / Stanah GSP GROUP | Lancaster | Lancashire
Garstang | Thornton | Penwortham West GSP / Stanah GSP GROUP | Preston | Lancashire
Garstang | Thornton | Penwortham West GSP / Stanah GSP GROUP | Wyre | Lancashire
Gatley | Moss Nook | South Manchester GSP | Manchester | Greater Manchester
Gatley | Moss Nook | South Manchester GSP | Stockport | Greater Manchester
Gidlow | Wigan | Washway Farm GSP / Kirkby GSP GROUP | Bolton | Greater Manchester
Gidlow | Wigan | Washway Farm GSP / Kirkby GSP GROUP | Wigan | Greater Manchester
Gidlow | Wigan | Washway Farm GSP / Kirkby GSP GROUP | Wigan | Greater Manchester
Gillsrow | Penrith & Shap | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Allerdale | Cumbria
Gillsrow | Penrith & Shap | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Eden | Cumbria
Glaxo | Ulverston | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | South Lakeland | Cumbria
Glossop | Hyde | Stalybridge GSP | High Peak | Derbyshire
Golborne | Golborne | Bold | St. Helens | Merseyside
Golborne | Golborne | Bold | Warrington | Warrington
Golborne | Golborne | Bold | Wigan | Greater Manchester
Gowhole | New Mills | Stalybridge GSP | Cheshire East | Cheshire East
Gowhole | New Mills | Stalybridge GSP | High Peak | Derbyshire
Gowhole | New Mills | Stalybridge GSP | Stockport | Greater Manchester
Grane Rd & Prinny Hill | Rossendale | Padiham GSP | Hyndburn | Lancashire
Grane Rd & Prinny Hill | Rossendale | Padiham GSP | Rossendale | Lancashire
Grange | Ulverston | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | South Lakeland | Cumbria
Great Harwood | Huncoat | Padiham GSP | Hyndburn | Lancashire
Great Harwood | Huncoat | Padiham GSP | Ribble Valley | Lancashire
Green Lane (Altrincham) | Altrincham | Carrington ENWL SGTs 1B 2B 4 7 | Trafford | Greater Manchester
Green Lane (Hazel Grove) | Hazel Grove | Bredbury GSP | Stockport | Greater Manchester
Green St T11 | Wigan | Washway Farm GSP / Kirkby GSP GROUP | Wigan | Greater Manchester
Green St T12 & T13 | Wigan | Washway Farm GSP / Kirkby GSP GROUP | Wigan | Greater Manchester
Greenfield | Hartshead-Heyrod | Stalybridge GSP | Oldham | Greater Manchester
Greenfield | Hartshead-Heyrod | Stalybridge GSP | Rochdale | Greater Manchester
Greenhill | Greenhill | Whitegate GSP | Oldham | Greater Manchester
Griffin | Lower Darwen | Penwortham East GSP / Rochdale SGT 1 GROUP | Blackburn with Darwen | Lancashire
Griffin | Lower Darwen | Penwortham East GSP / Rochdale SGT 1 GROUP | Ribble Valley | Lancashire
Griffin | Lower Darwen | Penwortham East GSP / Rochdale SGT 1 GROUP | South Ribble | Lancashire
Hadfield | Hyde | Stalybridge GSP | High Peak | Derbyshire
Hadfield | Hyde | Stalybridge GSP | Tameside | Greater Manchester
Hall Cross | Peel | Penwortham West GSP / Stanah GSP GROUP | Fylde | Lancashire
Handforth | Moss Nook | South Manchester GSP | Cheshire East | Cheshire East
Handforth | Moss Nook | South Manchester GSP | Stockport | Greater Manchester
Hanging Bridge | Wrightington | Penwortham West GSP / Stanah GSP GROUP | Chorley | Lancashire
Hanging Bridge | Wrightington | Penwortham West GSP / Stanah GSP GROUP | West Lancashire | Lancashire
Hareholme | Rossendale | Padiham GSP | Burnley | Lancashire
Hareholme | Rossendale | Padiham GSP | Rossendale | Lancashire
Harpurhey | Red Bank | Whitegate GSP | Manchester | Greater Manchester
Harwood | Bolton | Kearsley 132 GSP | Blackburn with Darwen | Lancashire
Harwood | Bolton | Kearsley 132 GSP | Bolton | Greater Manchester
Harwood | Bolton | Kearsley 132 GSP | Bury | Greater Manchester
Hattersley | Hyde | Stalybridge GSP | High Peak | Derbyshire
Hattersley | Hyde | Stalybridge GSP | Tameside | Greater Manchester
Haverthwaite | Ulverston | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | South Lakeland | Cumbria
Hawk Green | Hazel Grove | Bredbury GSP | Cheshire East | Cheshire East
Hawk Green | Hazel Grove | Bredbury GSP | High Peak | Derbyshire
Hawk Green | Hazel Grove | Bredbury GSP | Stockport | Greater Manchester
Haydock | Golborne | Bold | St. Helens | Merseyside
Haydock | Golborne | Bold | Wigan | Greater Manchester
HDA No1 & HDA No2 | Stainburn & Siddick | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Allerdale | Cumbria
HDA No1 & HDA No2 | Stainburn & Siddick | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Copeland | Cumbria
Heady Hill | Castleton | Rochdale SGTs 2 3 4 | Rochdale | Greater Manchester
Heap Bridge | Bury | Kearsley 132 GSP | Bury | Greater Manchester
Heap Bridge | Bury | Kearsley 132 GSP | Rochdale | Greater Manchester
Heasandford | Burnley | Rochdale SGTs 2 3 4 | Burnley | Lancashire
Heaton Moor | Vernon Park | Bredbury GSP | Manchester | Greater Manchester
Heaton Moor | Vernon Park | Bredbury GSP | Stockport | Greater Manchester
Heaton Norris | Vernon Park | Bredbury GSP | Manchester | Greater Manchester
Heaton Norris | Vernon Park | Bredbury GSP | Stockport | Greater Manchester
Helwith Bridge | Padiham | Padiham GSP | Craven | Lancashire
Hensingham | Egremont | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Copeland | Cumbria
Heyrod | Hartshead-Heyrod | Stalybridge GSP | Tameside | Greater Manchester
Heyside | Royton | Whitegate GSP | Oldham | Greater Manchester
Heywood | Castleton | Rochdale SGTs 2 3 4 | Bury | Greater Manchester
Heywood | Castleton | Rochdale SGTs 2 3 4 | Rochdale | Greater Manchester
Higher Mill | Moss Nook | South Manchester GSP | Manchester | Greater Manchester
Higher Mill | Moss Nook | South Manchester GSP | Stockport | Greater Manchester
Higher Walton | Leyland | Penwortham West GSP / Stanah GSP GROUP | Blackburn with Darwen | Lancashire
Higher Walton | Leyland | Penwortham West GSP / Stanah GSP GROUP | Chorley | Lancashire
Higher Walton | Leyland | Penwortham West GSP / Stanah GSP GROUP | Preston | Lancashire
Higher Walton | Leyland | Penwortham West GSP / Stanah GSP GROUP | South Ribble | Lancashire
Hill Top T11 & T12 |  | Kearsley Local 33 GSP | Bolton | Greater Manchester
Hill Top T11 & T12 |  | Kearsley Local 33 GSP | Salford | Greater Manchester
Hill Top T11 & T12 |  | Kearsley Local 33 GSP | Wigan | Greater Manchester
Hill Top T13 |  | Kearsley Local 33 GSP | Salford | Greater Manchester
Hill Top T13 |  | Kearsley Local 33 GSP | Wigan | Greater Manchester
Hindley Green | Atherton | Kearsley 132 GSP | Bolton | Greater Manchester
Hindley Green | Atherton | Kearsley 132 GSP | Wigan | Greater Manchester
Hollinwood | Chadderton | Whitegate GSP | Oldham | Greater Manchester
Holme Rd | Ribble | Penwortham East GSP / Rochdale SGT 1 GROUP | South Ribble | Lancashire
Holt St | Bury | Kearsley 132 GSP | Blackburn with Darwen | Lancashire
Holt St | Bury | Kearsley 132 GSP | Bury | Greater Manchester
Holt St | Bury | Kearsley 132 GSP | Rossendale | Lancashire
Hurst | Hartshead-Heyrod | Stalybridge GSP | Oldham | Greater Manchester
Hurst | Hartshead-Heyrod | Stalybridge GSP | Tameside | Greater Manchester
Hutton End & Skelton C | Penrith & Shap | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Allerdale | Cumbria
Hutton End & Skelton C | Penrith & Shap | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Carlisle | Cumbria
Hutton End & Skelton C | Penrith & Shap | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Eden | Cumbria
Hyde | Hyde | Stalybridge GSP | Stockport | Greater Manchester
Hyde | Hyde | Stalybridge GSP | Tameside | Greater Manchester
Hyndburn Rd | Huncoat | Padiham GSP | Hyndburn | Lancashire
Hyndburn Rd | Huncoat | Padiham GSP | Rossendale | Lancashire
India St | Lower Darwen | Penwortham East GSP / Rochdale SGT 1 GROUP | Blackburn with Darwen | Lancashire
Ingleton | Kendal (Parkside Rd) | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Craven | Cumbria
Irlam | Carrington BSP | Carrington ENWL SGTs 1B 2B 4 7 | Salford | Greater Manchester
Irlam | Carrington BSP | Carrington ENWL SGTs 1B 2B 4 7 | Trafford | Greater Manchester
Irlam | Carrington BSP | Carrington ENWL SGTs 1B 2B 4 7 | Warrington | Warrington
James St | Carlisle | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Carlisle | Cumbria
Kay St | Huncoat | Padiham GSP | Blackburn with Darwen | Lancashire
Kay St | Huncoat | Padiham GSP | Hyndburn | Lancashire
Kay St | Huncoat | Padiham GSP | Rossendale | Lancashire
Kendal | Kendal (Parkside Rd) | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | South Lakeland | Cumbria
Keswick | Stainburn & Siddick | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Allerdale | Cumbria
Keswick | Stainburn & Siddick | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Eden | Cumbria
Kingsway | Belfield | Rochdale SGTs 2 3 4 | Rochdale | Greater Manchester
Kinkry Hill | Spadeadam 11/33kV | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Carlisle | Cumbria
Kirkby Lonsdale | Kendal (Parkside Rd) | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Lancaster | Cumbria
Kirkby Lonsdale | Kendal (Parkside Rd) | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | South Lakeland | Cumbria
Kirkby Moor | Ulverston | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Copeland | Cumbria
Kirkby Moor | Ulverston | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | South Lakeland | Cumbria
Kirkby Stephen | Penrith & Shap | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Eden | Cumbria
Kirkby Stephen | Penrith & Shap | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Richmondshire | Cumbria
Kirkby Thore | Penrith & Shap | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Eden | Cumbria
Kirkhall Lane | Atherton | Kearsley 132 GSP | Wigan | Greater Manchester
Kitt Green | Orrell | Washway Farm GSP / Kirkby GSP GROUP | Wigan | Greater Manchester
Knott Mill | Bloom St | South Manchester GSP | Manchester | Greater Manchester
Knott Mill | Bloom St | South Manchester GSP | Salford | Greater Manchester
Knott Mill | Bloom St | South Manchester GSP | Trafford | Greater Manchester
Lamberhead | Orrell | Washway Farm GSP / Kirkby GSP GROUP | Wigan | Greater Manchester
Lancaster | Lancaster | Heysham GSP | Lancaster | Lancashire
Langley | Chadderton | Whitegate GSP | Rochdale | Greater Manchester
Langroyd Rd | Nelson | Padiham GSP | Pendle | Lancashire
Leigh | Atherton | Kearsley 132 GSP | Wigan | Greater Manchester
Levenshulme | Longsight | Bredbury GSP | Manchester | Greater Manchester
Leyland National | Stainburn & Siddick | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Allerdale | Cumbria
Little Hulton |  | Kearsley Local 33 GSP | Bolton | Greater Manchester
Little Hulton |  | Kearsley Local 33 GSP | Salford | Greater Manchester
Little Hulton |  | Kearsley Local 33 GSP | Wigan | Greater Manchester
Little Salkeld | Penrith & Shap | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Carlisle | Cumbria
Little Salkeld | Penrith & Shap | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Eden | Cumbria
Littleborough | Belfield | Rochdale SGTs 2 3 4 | Rochdale | Greater Manchester
Longford Bridge | Stretford | South Manchester GSP | Trafford | Greater Manchester
Longridge | Preston East | Penwortham East GSP / Rochdale SGT 1 GROUP | Preston | Lancashire
Longridge | Preston East | Penwortham East GSP / Rochdale SGT 1 GROUP | Ribble Valley | Lancashire
Longsight | Longsight | Bredbury GSP | Manchester | Greater Manchester
Lostock | Westhoughton | Kearsley 132 GSP | Bolton | Greater Manchester
Lostock | Westhoughton | Kearsley 132 GSP | Chorley | Lancashire
Lower Darwen | Lower Darwen | Penwortham East GSP / Rochdale SGT 1 GROUP | Blackburn with Darwen | Lancashire
Lower Darwen | Lower Darwen | Penwortham East GSP / Rochdale SGT 1 GROUP | Hyndburn | Lancashire
Lower Darwen | Lower Darwen | Penwortham East GSP / Rochdale SGT 1 GROUP | Rossendale | Lancashire
Lyons Rd | Barton | Carrington ENWL SGTs 1B 2B 4 7 | Trafford | Greater Manchester
Manchester University | Longsight | Bredbury GSP | Manchester | Greater Manchester
Marple | Hazel Grove | Bredbury GSP | Stockport | Greater Manchester
Marton | Blackpool | Penwortham West GSP / Stanah GSP GROUP | Blackpool | Lancashire
Marton | Blackpool | Penwortham West GSP / Stanah GSP GROUP | Fylde | Lancashire
Maryport | Stainburn & Siddick | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Allerdale | Cumbria
Melling | Kendal (Parkside Rd) | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Craven | Cumbria
Melling | Kendal (Parkside Rd) | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Lancaster | Cumbria
Melling | Kendal (Parkside Rd) | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | South Lakeland | Cumbria
Mereside | Peel | Penwortham West GSP / Stanah GSP GROUP | Blackpool | Lancashire
Mereside | Peel | Penwortham West GSP / Stanah GSP GROUP | Fylde | Lancashire
Mereside | Peel | Penwortham West GSP / Stanah GSP GROUP | Wyre | Lancashire
Middleton Junction | Chadderton | Whitegate GSP | Oldham | Greater Manchester
Middleton Junction | Chadderton | Whitegate GSP | Rochdale | Greater Manchester
Midway | Egremont | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Copeland | Cumbria
Milnrow | Castleton | Rochdale SGTs 2 3 4 | Rochdale | Greater Manchester
Mintsfeet | Kendal (Parkside Rd) | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | South Lakeland | Cumbria
Monsall | Stuart St | Stalybridge GSP | Manchester | Greater Manchester
Monton | Barton | Carrington ENWL SGTs 1B 2B 4 7 | Salford | Greater Manchester
Moorside | Ribble | Penwortham East GSP / Rochdale SGT 1 GROUP | Fylde | Lancashire
Moorside | Ribble | Penwortham East GSP / Rochdale SGT 1 GROUP | Preston | Lancashire
Moorside | Ribble | Penwortham East GSP / Rochdale SGT 1 GROUP | Ribble Valley | Lancashire
Moorside | Ribble | Penwortham East GSP / Rochdale SGT 1 GROUP | Wyre | Lancashire
Morton Park & Pirelli | Carlisle | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Allerdale | Cumbria
Morton Park & Pirelli | Carlisle | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Carlisle | Cumbria
Mosley Rd | Stretford | South Manchester GSP | Trafford | Greater Manchester
Moss Lane |  | Kearsley Local 33 GSP | Bury | Greater Manchester
Moss Lane |  | Kearsley Local 33 GSP | Rochdale | Greater Manchester
Moss Nook Primary | Moss Nook Primary | South Manchester GSP | Cheshire East | Cheshire East
Moss Nook Primary | Moss Nook Primary | South Manchester GSP | Manchester | Greater Manchester
Moss Nook Primary | Moss Nook Primary | South Manchester GSP | Stockport | Greater Manchester
Moss Side (Leyland) & Seven Stars | Leyland | Penwortham West GSP / Stanah GSP GROUP | Chorley | Lancashire
Moss Side (Leyland) & Seven Stars | Leyland | Penwortham West GSP / Stanah GSP GROUP | South Ribble | Lancashire
Moss Side (Longsight) | Longsight | Bredbury GSP | Manchester | Greater Manchester
Moss Side (Longsight) | Longsight | Bredbury GSP | Trafford | Greater Manchester
Mossley | Hartshead-Heyrod | Stalybridge GSP | Oldham | Greater Manchester
Mossley | Hartshead-Heyrod | Stalybridge GSP | Tameside | Greater Manchester
Mount St | Barton | Carrington ENWL SGTs 1B 2B 4 7 | Salford | Greater Manchester
Musgrave Rd | Bolton | Kearsley 132 GSP | Bolton | Greater Manchester
Nelson | Nelson | Padiham GSP | Pendle | Lancashire
New Moston | Chadderton | Whitegate GSP | Manchester | Greater Manchester
New Moston | Chadderton | Whitegate GSP | Oldham | Greater Manchester
Newbiggin on Lune | Penrith & Shap | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Eden | Cumbria
Newby | Penrith & Shap | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Eden | Cumbria
Newton | Hyde | Stalybridge GSP | Tameside | Greater Manchester
Newton Heath | Chadderton | Whitegate GSP | Manchester | Greater Manchester
Newton Heath | Chadderton | Whitegate GSP | Oldham | Greater Manchester
Newton Le Willows | Golborne | Bold | St. Helens | Merseyside
Newtongate T11 & T12 | Penrith & Shap | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Eden | Cumbria
Newtongate T13 | Penrith & Shap | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Eden | Cumbria
Norbreck | Bispham | Penwortham West GSP / Stanah GSP GROUP | Blackpool | Lancashire
Norbury | Hazel Grove | Bredbury GSP | Cheshire East | Cheshire East
Norbury | Hazel Grove | Bredbury GSP | Stockport | Greater Manchester
Northenden | West Didsbury | South Manchester GSP | Manchester | Greater Manchester
Northenden | West Didsbury | South Manchester GSP | Trafford | Greater Manchester
NWGB Partington | Carrington BSP | Carrington ENWL SGTs 1B 2B 4 7 | Trafford | Greater Manchester
Offerton | Vernon Park | Bredbury GSP | Stockport | Greater Manchester
Openshaw | Droylsden | Stalybridge GSP | Manchester | Greater Manchester
Openshaw | Droylsden | Stalybridge GSP | Tameside | Greater Manchester
Ormskirk | Skelmersdale | Washway Farm GSP / Kirkby GSP GROUP | West Lancashire | Lancashire
Padiham | Padiham | Padiham GSP | Burnley | Lancashire
Padiham | Padiham | Padiham GSP | Hyndburn | Lancashire
Padiham | Padiham | Padiham GSP | Pendle | Lancashire
Padiham | Padiham | Padiham GSP | Ribble Valley | Lancashire
Peel St & Ribblesdale T13 | Padiham | Padiham GSP | Pendle | Lancashire
Peel St & Ribblesdale T13 | Padiham | Padiham GSP | Ribble Valley | Lancashire
Pendleton | Frederick Rd | Kearsley 132 GSP | Salford | Greater Manchester
Petteril Bank | Carlisle | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Carlisle | Cumbria
Petteril Bank | Carlisle | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Eden | Cumbria
Phillips Lane | Nelson | Padiham GSP | Pendle | Lancashire
Piccadilly | Bloom St | South Manchester GSP | Manchester | Greater Manchester
Pimbo | Skelmersdale | Washway Farm GSP / Kirkby GSP GROUP | West Lancashire | Lancashire
Portwood | Vernon Park | Bredbury GSP | Stockport | Greater Manchester
Poulton | Bispham | Penwortham West GSP / Stanah GSP GROUP | Fylde | Lancashire
Poulton | Bispham | Penwortham West GSP / Stanah GSP GROUP | Wyre | Lancashire
Poynton | Hazel Grove | Bredbury GSP | Cheshire East | Cheshire East
Preesall | Thornton | Penwortham West GSP / Stanah GSP GROUP | Wyre | Lancashire
Preston East | Preston East | Penwortham East GSP / Rochdale SGT 1 GROUP | Preston | Lancashire
Preston East | Preston East | Penwortham East GSP / Rochdale SGT 1 GROUP | Ribble Valley | Lancashire
Preston Old Rd | Blackpool | Penwortham West GSP / Stanah GSP GROUP | Blackpool | Lancashire
Prestwich | Agecroft | Kearsley 132 GSP | Bury | Greater Manchester
Prestwich | Agecroft | Kearsley 132 GSP | Manchester | Greater Manchester
Prestwich | Agecroft | Kearsley 132 GSP | Salford | Greater Manchester
Pringle St | Blackburn | Penwortham East GSP / Rochdale SGT 1 GROUP | Blackburn with Darwen | Lancashire
Queens Park | Stuart St | Stalybridge GSP | Manchester | Greater Manchester
Radcliffe | Radcliffe | Kearsley 132 GSP | Bolton | Greater Manchester
Radcliffe | Radcliffe | Kearsley 132 GSP | Bury | Greater Manchester
Randal St | Blackburn | Penwortham East GSP / Rochdale SGT 1 GROUP | Blackburn with Darwen | Lancashire
Randal St | Blackburn | Penwortham East GSP / Rochdale SGT 1 GROUP | Ribble Valley | Lancashire
Rawtenstall Rd | Rossendale | Padiham GSP | Hyndburn | Lancashire
Rawtenstall Rd | Rossendale | Padiham GSP | Rossendale | Lancashire
Reddish Vale | Vernon Park | Bredbury GSP | Stockport | Greater Manchester
Reddish Vale | Vernon Park | Bredbury GSP | Tameside | Greater Manchester
Ribblesdale T14 | Padiham | Padiham GSP | Ribble Valley | Lancashire
Ribbleton | Preston East | Penwortham East GSP / Rochdale SGT 1 GROUP | Preston | Lancashire
Ringley |  | Kearsley Local 33 GSP | Bolton | Greater Manchester
Risley | Risley | Risley | Warrington | Warrington
Robert Hall St | Frederick Rd | Kearsley 132 GSP | Salford | Greater Manchester
Rochdale Central | Rochdale Central | Rochdale SGTs 2 3 4 | Rochdale | Greater Manchester
Roman Rd | Lower Darwen | Penwortham East GSP / Rochdale SGT 1 GROUP | Blackburn with Darwen | Lancashire
Romiley | Vernon Park | Bredbury GSP | Stockport | Greater Manchester
Rossall | Thornton | Penwortham West GSP / Stanah GSP GROUP | Wyre | Lancashire
Royton | Royton | Whitegate GSP | Oldham | Greater Manchester
S.E. Macclesfield |  | Macclesfield 33 GSP | Cheshire East | Cheshire East
S.E. Macclesfield |  | Macclesfield 33 GSP | Staffordshire Moorlands | Staffordshire
S.W. Macclesfield |  | Macclesfield 33 GSP | Cheshire East | Cheshire East
Sale | Sale | Carrington ENWL SGTs 1B 2B 4 7 | Trafford | Greater Manchester
Sale Moor | Sale | Carrington ENWL SGTs 1B 2B 4 7 | Trafford | Greater Manchester
Salford Quays | Frederick Rd | Kearsley 132 GSP | Salford | Greater Manchester
Sandgate | Barrow & Sandgate | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Barrow-in-Furness | Cumbria
Scarisbrick | Skelmersdale | Washway Farm GSP / Kirkby GSP GROUP | Sefton | Merseyside
Scarisbrick | Skelmersdale | Washway Farm GSP / Kirkby GSP GROUP | West Lancashire | Lancashire
Sebergham | Carlisle | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Allerdale | Cumbria
Sebergham | Carlisle | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Carlisle | Cumbria
Sebergham | Carlisle | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Eden | Cumbria
Sedbergh | Kendal (Parkside Rd) | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Richmondshire | Cumbria
Sedbergh | Kendal (Parkside Rd) | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | South Lakeland | Cumbria
Selsmire | Penrith & Shap | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Eden | Cumbria
Selsmire | Penrith & Shap | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | South Lakeland | Cumbria
Settle | Padiham | Padiham GSP | Craven | Lancashire
Shannon St South | Blackpool | Penwortham West GSP / Stanah GSP GROUP | Blackpool | Lancashire
Shap | Penrith & Shap | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Eden | Cumbria
Shaw | Royton | Whitegate GSP | Oldham | Greater Manchester
Shaw | Royton | Whitegate GSP | Rochdale | Greater Manchester
Siddick | Stainburn & Siddick | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Allerdale | Cumbria
Silloth | Carlisle | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Allerdale | Cumbria
Skelmersdale | Skelmersdale | Washway Farm GSP / Kirkby GSP GROUP | West Lancashire | Lancashire
Slipway | Egremont | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Copeland | Cumbria
Snipe | Droylsden | Stalybridge GSP | Tameside | Greater Manchester
South Park | Lytham | Penwortham West GSP / Stanah GSP GROUP | Fylde | Lancashire
Spa Rd | Bolton | Kearsley 132 GSP | Bolton | Greater Manchester
Spadeadam 132/11kV* | Spadeadam 132/11kV* | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Carlisle | Cumbria
Spadeadam 132/11kV* | Spadeadam 132/11kV* | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Northumberland | Cumbria
Spotland | Rochdale Central | Rochdale SGTs 2 3 4 | Rochdale | Greater Manchester
Spring Cottage | Nelson | Padiham GSP | Pendle | Lancashire
Spring Garden St 11kV | Lancaster | Heysham GSP | Lancaster | Lancashire
Spring Garden St 6.6kV | Lancaster | Heysham GSP | Lancaster | Lancashire
Squires Gate | Blackpool | Penwortham West GSP / Stanah GSP GROUP | Blackpool | Lancashire
Squires Gate | Blackpool | Penwortham West GSP / Stanah GSP GROUP | Fylde | Lancashire
St Annes | Lytham | Penwortham West GSP / Stanah GSP GROUP | Fylde | Lancashire
St Marys | Greenhill | Whitegate GSP | Oldham | Greater Manchester
St Marys St | Ribble | Penwortham East GSP / Rochdale SGT 1 GROUP | Preston | Lancashire
St Thomas Rd | Lytham | Penwortham West GSP / Stanah GSP GROUP | Fylde | Lancashire
Stainburn | Stainburn & Siddick | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Allerdale | Cumbria
Standish | Wrightington | Penwortham West GSP / Stanah GSP GROUP | Chorley | Lancashire
Standish | Wrightington | Penwortham West GSP / Stanah GSP GROUP | West Lancashire | Lancashire
Standish | Wrightington | Penwortham West GSP / Stanah GSP GROUP | Wigan | Lancashire
Strangeways | Red Bank | Whitegate GSP | Manchester | Greater Manchester
Strangeways | Red Bank | Whitegate GSP | Salford | Greater Manchester
Strawberry Bank | Huncoat | Padiham GSP | Hyndburn | Lancashire
Stuart St | Stuart St | Stalybridge GSP | Manchester | Greater Manchester
Stuart St | Stuart St | Stalybridge GSP | Tameside | Greater Manchester
Stubbins | Rossendale | Padiham GSP | Bury | Greater Manchester
Stubbins | Rossendale | Padiham GSP | Rossendale | Lancashire
Swinton | Agecroft | Kearsley 132 GSP | Salford | Greater Manchester
Tame Valley | Hartshead-Heyrod | Stalybridge GSP | Tameside | Greater Manchester
Tardy Gate | Ribble | Penwortham East GSP / Rochdale SGT 1 GROUP | South Ribble | Lancashire
Tarleton | Wrightington | Penwortham West GSP / Stanah GSP GROUP | Chorley | Lancashire
Tarleton | Wrightington | Penwortham West GSP / Stanah GSP GROUP | South Ribble | Lancashire
Tarleton | Wrightington | Penwortham West GSP / Stanah GSP GROUP | West Lancashire | Lancashire
The Height | Agecroft | Kearsley 132 GSP | Salford | Greater Manchester
Thornton | Bispham | Penwortham West GSP / Stanah GSP GROUP | Blackpool | Lancashire
Thornton | Bispham | Penwortham West GSP / Stanah GSP GROUP | Wyre | Lancashire
Townley St | Chadderton | Whitegate GSP | Rochdale | Greater Manchester
Trafford | Stretford | South Manchester GSP | Trafford | Greater Manchester
Trafford Park North | Barton | Carrington ENWL SGTs 1B 2B 4 7 | Trafford | Greater Manchester
Trimpell | Trimpell | Heysham GSP | Lancaster | Lancashire
Trinity | Frederick Rd | Kearsley 132 GSP | Manchester | Greater Manchester
Trinity | Frederick Rd | Kearsley 132 GSP | Salford | Greater Manchester
Tulketh | Ribble | Penwortham East GSP / Rochdale SGT 1 GROUP | Preston | Lancashire
Ulverston | Ulverston | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Barrow-in-Furness | Cumbria
Ulverston | Ulverston | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | South Lakeland | Cumbria
Union Rd | Bolton | Kearsley 132 GSP | Bolton | Greater Manchester
Upholland | Orrell | Washway Farm GSP / Kirkby GSP GROUP | St. Helens | Merseyside
Upholland | Orrell | Washway Farm GSP / Kirkby GSP GROUP | West Lancashire | Lancashire
Upholland | Orrell | Washway Farm GSP / Kirkby GSP GROUP | Wigan | Greater Manchester
Urmston | Stretford | South Manchester GSP | Trafford | Greater Manchester
Victoria Park | Longsight | Bredbury GSP | Manchester | Greater Manchester
Warbreck | Bispham | Penwortham West GSP / Stanah GSP GROUP | Blackpool | Lancashire
Warbreck | Bispham | Penwortham West GSP / Stanah GSP GROUP | Wyre | Lancashire
Wardleworth | Belfield | Rochdale SGTs 2 3 4 | Rochdale | Greater Manchester
Warton | Peel | Penwortham West GSP / Stanah GSP GROUP | Fylde | Lancashire
Waterhead | Greenhill | Whitegate GSP | Oldham | Greater Manchester
Waterswallows | Buxton | Stalybridge GSP | Derbyshire Dales | Derbyshire
Waterswallows | Buxton | Stalybridge GSP | High Peak | Derbyshire
Weaste | Frederick Rd | Kearsley 132 GSP | Salford | Greater Manchester
Werneth | Greenhill | Whitegate GSP | Oldham | Greater Manchester
Wesley Place Bacup | Rossendale | Padiham GSP | Rossendale | Lancashire
West Didsbury | West Didsbury | South Manchester GSP | Manchester | Greater Manchester
Westgate | Lancaster | Heysham GSP | Lancaster | Lancashire
Westhoughton | Westhoughton | Kearsley 132 GSP | Bolton | Greater Manchester
Westhoughton | Westhoughton | Kearsley 132 GSP | Salford | Greater Manchester
Westhoughton | Westhoughton | Kearsley 132 GSP | Wigan | Greater Manchester
Westlinton | Carlisle | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Carlisle | Cumbria
Whalley | Padiham | Padiham GSP | Pendle | Lancashire
Whalley | Padiham | Padiham GSP | Ribble Valley | Lancashire
Whalley Range | West Didsbury | South Manchester GSP | Manchester | Greater Manchester
Whalley Range | West Didsbury | South Manchester GSP | Trafford | Greater Manchester
Whasset | Kendal (Parkside Rd) | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | South Lakeland | Cumbria
Whittle Le Woods | Leyland | Penwortham West GSP / Stanah GSP GROUP | Chorley | Lancashire
Whittle Le Woods | Leyland | Penwortham West GSP / Stanah GSP GROUP | South Ribble | Lancashire
Whitworth | Rochdale Central | Rochdale SGTs 2 3 4 | Rossendale | Lancashire
Wigton | Carlisle | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Allerdale | Cumbria
Wigton | Carlisle | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Carlisle | Cumbria
Willow Hey | Skelmersdale | Washway Farm GSP / Kirkby GSP GROUP | West Lancashire | Lancashire
Willowbank | Greenhill | Whitegate GSP | Oldham | Greater Manchester
Willowbank | Greenhill | Whitegate GSP | Rochdale | Greater Manchester
Willowholme | Carlisle | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Carlisle | Cumbria
Wilmslow | Moss Nook | South Manchester GSP | Cheshire East | Cheshire East
Windermere | Kendal (Parkside Rd) | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | South Lakeland | Cumbria
Winifred Rd | Adswood | Bredbury GSP | Stockport | Greater Manchester
Withington | West Didsbury | South Manchester GSP | Manchester | Greater Manchester
Withyfold Drive |  | Macclesfield 33 GSP | Cheshire East | Cheshire East
Woodbine St | Castleton | Rochdale SGTs 2 3 4 | Rochdale | Greater Manchester
Woodfield Rd | Wrightington | Penwortham West GSP / Stanah GSP GROUP | Chorley | Lancashire
Woodhill Lane | Lancaster | Heysham GSP | Lancaster | Lancashire
Woodhouse Park | Moss Nook | South Manchester GSP | Manchester | Greater Manchester
Woodhouse Park | Moss Nook | South Manchester GSP | Stockport | Greater Manchester
Woodley | Vernon Park | Bredbury GSP | Stockport | Greater Manchester
Woolfold | Bury | Kearsley 132 GSP | Bury | Greater Manchester
Wordsworth St | Bolton | Kearsley 132 GSP | Bolton | Greater Manchester
Worsley Mesnes | Wigan | Washway Farm GSP / Kirkby GSP GROUP | Wigan | Greater Manchester
Wrightington | Wrightington | Penwortham West GSP / Stanah GSP GROUP | Chorley | Lancashire
Wrightington | Wrightington | Penwortham West GSP / Stanah GSP GROUP | West Lancashire | Lancashire
Wrightington | Wrightington | Penwortham West GSP / Stanah GSP GROUP | Wigan | Lancashire
Yealand | Kendal (Parkside Rd) | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | Lancaster | Cumbria
Yealand | Kendal (Parkside Rd) | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | South Lakeland | Cumbria

## 2 - Demand headroom table
Select Primary | Mintsfeet
BSP | KENDAL (PARKSIDE RD) | 5.9893 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2036 | 2039 | 2042 | 2046 | 2051
GSP | HUTTON
Grid Coordinates | Easting | Northing
| 351827 | 494315
Best View | Firm |  | 3.1835 | 0.84167 | 0.16966 | -0.14283 | -0.50723 | -0.92531 | -1.6604 | -2.0544 | -2.5303 | -3.2027 | -5.0713 | -11.5633 | -14.5038 | -20.0797 | -21.9053
| Non Firm |  | 9.1835 | 6.8417 | 6.1697 | 5.8572 | 5.4928 | 5.0747 | 4.3396 | 3.9456 | 3.4697 | 2.7973 | 0.92865 | -5.5633 | -8.5038 | -14.0797 | -16.1578
Counterfactual | Firm |  | 3.1835 | 2.3186 | 2.0185 | 1.739 | 1.4239 | 1.0007 | 0.45915 | -0.17035 | -0.60834 | -1.0321 | -2.3211 | -3.8342 | -4.9607 | -9.4802 | -10.2432
| Non Firm |  | 9.1835 | 8.3186 | 8.0185 | 7.739 | 7.4239 | 7.0007 | 6.4592 | 5.8297 | 5.3917 | 4.9679 | 3.6789 | 2.1658 | 1.0393 | -3.4802 | -4.1886
Electric Engagement | Firm |  | 3.1835 | 0.4977 | -0.23373 | -0.54674 | -0.90904 | -1.3227 | -2.0456 | -2.4332 | -3.137 | -3.4395 | -15.3872 | -18.2527 | -20.2046 | -21.2639 | -22.416
| Non Firm |  | 9.1835 | 6.4977 | 5.7663 | 5.4533 | 5.091 | 4.6773 | 3.9544 | 3.5668 | 2.863 | 2.5605 | -9.3872 | -12.2527 | -14.2046 | -15.2639 | -16.7702
Holistic Transition | Firm |  | 3.1835 | 1.3724 | 0.83414 | -4.2783 | -4.3022 | -4.8369 | -5.4585 | -6.2062 | -7.5358 | -8.6806 | -11.8321 | -14.1833 | -15.9806 | -16.7614 | -15.4757
| Non Firm |  | 9.1835 | 7.3724 | 6.8341 | 1.7217 | 1.6978 | 1.1631 | 0.54154 | -0.20623 | -1.5358 | -2.6806 | -5.8321 | -8.1833 | -9.9806 | -10.7614 | -9.7695
Hydrogen Evolution | Firm |  | 3.1835 | 1.8626 | 1.4028 | 1.1602 | 0.93349 | 0.645 | -0.010675 | -0.35205 | -0.80953 | -1.4897 | -2.7093 | -7.5204 | -8.7723 | -12.5472 | -12.3366
| Non Firm |  | 9.1835 | 7.8626 | 7.4028 | 7.1602 | 6.9335 | 6.645 | 5.9893 | 5.6479 | 5.1905 | 4.5103 | 3.2907 | -1.5204 | -2.7723 | -6.5472 | -6.4742
Accelerated Decarbonisation | Firm |  | 3.1835 | 0.2966 | -0.49146 | -5.6866 | -5.7809 | -6.3404 | -6.9751 | -7.7735 | -9.1368 | -10.3115 | -13.7705 | -16.5129 | -18.5752 | -19.5692 | -18.503
| Non Firm |  | 9.1835 | 6.2966 | 5.5085 | 0.31338 | 0.21908 | -0.34044 | -0.97513 | -1.7735 | -3.1368 | -4.3115 | -7.7705 | -10.5129 | -12.5752 | -13.5692 | -12.7482
RIIO-ED2 Comment (Based on Best View Headroom) |  |  | Firm Capacity exceeded in FY27. Capacity will be released upon the completion of a new RIIO-ED2 connections driven reinforcement project
Select BSP | Wigan
GSP | KIRKBY |  | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2036 | 2039 | 2042 | 2046 | 2051
Grid Coordinates | Easting | Northing
| 358343 | 404626
Best View | Firm |  | 18.2167 | 12.9383 | 11.324 | 10.3407 | 8.8927 | 35.3597 | 33.9128 | 32.5421 | 30.9277 | 29.3739 | 20.4081 | 6.772 | -5.3059 | -18.0252 | -29.2143
| Non Firm |  | 57.2167 | 51.9383 | 50.324 | 49.3407 | 47.8927 | 46.3597 | 44.9128 | 43.5421 | 41.9277 | 40.3739 | 31.4081 | 17.772 | 5.6941 | -7.0252 | -18.2143
Counterfactual | Firm |  | 18.2167 | 16.452 | 15.4927 | 14.7718 | 13.8705 | 40.8398 | 39.4971 | 37.7855 | 36.4256 | 35.0142 | 30.7113 | 26.2346 | 21.945 | 17.2393 | 13.9798
| Non Firm |  | 57.2167 | 55.452 | 54.4927 | 53.7718 | 52.8705 | 51.8398 | 50.4971 | 48.7855 | 47.4256 | 46.0142 | 41.7113 | 37.2346 | 32.945 | 28.2393 | 24.9798
Electric Engagement | Firm |  | 18.2167 | 12.2679 | 1.6446 | -8.1112 | -9.6608 | 16.7401 | 15.2738 | 13.887 | 12.5505 | 11.2991 | 4.1514 | -9.3972 | -20.7308 | -32.3592 | -42.2617
| Non Firm |  | 57.2167 | 51.2679 | 40.6446 | 30.8888 | 29.3392 | 27.7401 | 26.2738 | 24.887 | 23.5505 | 22.2991 | 15.1514 | 1.6028 | -9.7308 | -21.3592 | -31.2617
Holistic Transition | Firm |  | 18.2167 | 15.0224 | 5.098 | -4.5159 | -6.0122 | 20.3206 | 17.8905 | 12.8239 | 7.6602 | 2.5722 | -10.7716 | -23.5478 | -33.8782 | -40.3854 | -36.3455
| Non Firm |  | 57.2167 | 54.0224 | 44.098 | 34.4841 | 32.9878 | 31.3206 | 28.8905 | 23.8239 | 18.6602 | 13.5722 | 0.2284 | -12.5478 | -22.8782 | -29.3854 | -25.3455
Hydrogen Evolution | Firm |  | 18.2167 | 15.6177 | 14.7108 | 14.0855 | 13.3317 | 40.4258 | 39.3751 | 38.2109 | 36.6368 | 35.019 | 28.6548 | 21.6362 | 16.7438 | 12.7827 | 11.142
| Non Firm |  | 57.2167 | 54.6177 | 53.7108 | 53.0855 | 52.3317 | 51.4258 | 50.3751 | 49.2109 | 47.6368 | 46.019 | 39.6548 | 32.6362 | 27.7438 | 23.7827 | 22.142
Accelerated Decarbonisation | Firm |  | 18.2167 | 12.4419 | 1.6735 | -8.3627 | -10.2438 | 15.8351 | 13.1049 | 7.6292 | 2.2118 | -3.1362 | -17.3863 | -31.0461 | -42.2813 | -49.8663 | -47.0161
| Non Firm |  | 57.2167 | 51.4419 | 40.6735 | 30.6373 | 28.7562 | 26.8351 | 24.1049 | 18.6292 | 13.2118 | 7.8638 | -6.3863 | -20.0461 | -31.2813 | -38.8663 | -36.0161
RIIO-ED2 Comment (Based on Best View Headroom) |  |  | No comment

## 3 - Generation headroom table
Select Primary | MINTSFEET
Select Technology | Battery Storage
BSP | KENDAL (PARKSIDE RD) | HARKER / HUTTON
GSP | HARKER / HUTTON | HARKER / HUTTON
Grid Coordinates | Easting | Northing | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2036 | 2039 | 2042 | 2046 | 2051
| 351827 | 494315
Best View | Non Firm |  | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
Counterfactual | Non Firm |  | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
Electric Engagement | Non Firm |  | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
Holistic Transition | Non Firm |  | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
Hydrogen Evolution | Non Firm |  | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
Accelerated Decarbonisation | Non Firm |  | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
RIIO-ED2 Comment (Based on Best View Headroom) |  |  | No comment
Select BSP | VERNON PARK
Select Technology | Battery Storage
GSP | BREDBURY
Grid Coordinates | Easting | Northing | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2036 | 2039 | 2042 | 2046 | 2051
| 391131 | 390929
Best View | Non Firm |  | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
Counterfactual | Non Firm |  | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
Electric Engagement | Non Firm |  | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
Holistic Transition | Non Firm |  | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
Hydrogen Evolution | Non Firm |  | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
Accelerated Decarbonisation | Non Firm |  | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
RIIO-ED2 Comment (Based on Best View Headroom) |  |  | No comment

## 4 - Transmission headroom
Earliest in Service Dates (EISDs) for new applications to the transmission network - to accompany a DNO's Network Scenario Headroom Report
2025-04-22 | Transmission Owner's freeze date
Electricity North West Limited | DNO Licence area
NGET | Transmision Owner providing
2025-04-22 | Last update (version, date)
| Demand |  | Generation
GSPs in November 2022 LTDS | EISD | Under review at freeze date? | EISD | Under review at freeze date? | Comments (optional)
Bredbury | TBC | Under active review | 2037 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process/Connections Reform
Carrington | 2037 | Under active review | 2037 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process/Connections Reform
Harker | TBC | Under active review | 2037 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process/Connections Reform
Hutton | TBC | Under active review | 2037 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process/Connections Reform
Heysham | TBC | Under active review | 2037 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process/Connections Reform
Kearsley | TBC | Under active review | 2037 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process/Connections Reform
Kearsley Local | TBC | Under active review | 2037 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process/Connections Reform
Kirkby | TBC | Under active review | 2037 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process/Connections Reform
Macclesfield | TBC | Under active review | 2037 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process/Connections Reform
Padiham | TBC | Under active review | 2037 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process/Connections Reform
Penwortham | TBC | Under active review | 2037 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process/Connections Reform
Rochdale | TBC | Under active review | 2028 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process/Connections Reform
South Manchester | TBC | Under active review | 2037 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process/Connections Reform
Stalybridge | TBC | Under active review | 2037 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process/Connections Reform
Stanah | TBC | Under active review | 2037 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process/Connections Reform
Washway Farm | TBC | Under active review | 2037 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process/Connections Reform
Whitegate | TBC | Under active review | 2037 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process/Connections Reform
Links to additional public-domain information related to the EISDs, provided by the Transmission Owner
https://www.nationalgrid.com/electricity-transmission/connections/regional-customer-connections-update
Purpose
To indicate potential transmission constraints by 'Earliest in Service Date' per Grid Supply Point (GSP)
To accompany a DNO's Network Scenario Headroom Report of unused substation capacity at primary substations and Bulk Supply Points
To address stakeholder feedback that information in the Network Scenario Headroom Reports requires context of potential transmission restrictions to connecting at the distribution network.
Notes
1 | Earliest in service dates (EISDs) represent a snapshot of the Transmission Owner's view at the 'freeze date' of the earliest date for connection for NEW applications for demand and generation of significant size (>1MW)
For customers which already have accepted connections with a DNO, DNOs may already have agreed with transmission for earlier connection dates for demand and generation customers
2 | For storage, both the demand and generation EISDs may be relevant.
3 | Where an EISD has not been established for a GSP, this is shown as N/A.
There is likely to be some headroom for connection because there is no constraint yet defined with defined construction works affecting connnection, this is shown as "no date restriction identified".
4 | Where the tranmission owner is actively reviewing construction works and earliest in service dates for new applications may be revised e.g. due to an application for capacity affecting that GSP, this is shown as "under active review"
5 | The EISDs reflect both works at a Grid Supply Point and in wider tranmission network.
6 | Unlike the rest of the DNO Network Scenario Headroom Reports, this is a snapshot of current status based on connection applications, not a scenario based output.
7 | The list of GSPs includes at a minimum the GSPs associated with the primary substations and Bulk Supply Points in the DNO's last Long Term Development Statement Table 3. Future new GSPs may not be included.

## Primary Headroom
Click the scenario name to move directly to the associated results | Best View
Counterfactual
Electric Engagement
Holistic Transition
Hydrogen Evolution
Accelerated Decarbonisation
| Primary | Best View Firm Headroom MVA | [14 empty] | Best View Non Firm Headroom MVA | [14 empty] | Counterfactual Firm Headroom MVA | [14 empty] | Counterfactual Non Firm Headroom MVA | [14 empty] | Electric Engagement Firm Headroom MVA | [14 empty] | Electric Engagement Non Firm Headroom MVA | [14 empty] | Holistic Transition Firm Headroom MVA | [14 empty] | Holistic Transition Non Firm Headroom MVA | [14 empty] | Hydrogen Evolution Firm Headroom MVA | [14 empty] | Hydrogen Evolution Non Firm Headroom MVA | [14 empty] | Accelerated Decarbonisation Firm Headroom MVA | [14 empty] | Accelerated Decarbonisation Non Firm Headroom MVA
|  | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2036 | 2039 | 2042 | 2046 | 2051 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2036 | 2039 | 2042 | 2046 | 2051 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2036 | 2039 | 2042 | 2046 | 2051 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2036 | 2039 | 2042 | 2046 | 2051 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2036 | 2039 | 2042 | 2046 | 2051 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2036 | 2039 | 2042 | 2046 | 2051 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2036 | 2039 | 2042 | 2046 | 2051 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2036 | 2039 | 2042 | 2046 | 2051 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2036 | 2039 | 2042 | 2046 | 2051 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2036 | 2039 | 2042 | 2046 | 2051 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2036 | 2039 | 2042 | 2046 | 2051 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2036 | 2039 | 2042 | 2046 | 2051 | Easting | Northing | BSP | GSP | Comments (Based on Best View Headroom)
| Albion St | 10.5045 | 9.4911 | 9.1504 | 8.9648 | 8.6757 | 8.3854 | 8.1278 | 7.8872 | 7.5168 | 7.1483 | 5.1526 | 1.6246 | -0.95245 | -2.9658 | -4.1887 | 15.1415 | 14.1281 | 13.7874 | 13.6018 | 13.3127 | 13.0224 | 12.7648 | 12.5242 | 12.1538 | 11.7853 | 9.7896 | 6.2616 | 3.6845 | 1.6712 | 0.22468 | 10.5045 | 10.0541 | 9.8889 | 9.7888 | 9.6417 | 9.4708 | 9.2346 | 8.9214 | 8.6676 | 8.4024 | 7.415 | 5.9344 | 5.0991 | 4.1667 | 3.6852 | 15.1415 | 14.6911 | 14.5259 | 14.4258 | 14.2787 | 14.1078 | 13.8716 | 13.5584 | 13.3046 | 13.0394 | 12.052 | 10.5714 | 9.7361 | 8.8037 | 8.3949 | 10.5045 | 9.2831 | 8.8408 | 8.581 | 8.2131 | 7.841 | 7.4971 | 7.1201 | 6.6488 | 6.1646 | 3.2385 | -0.010536 | -1.903 | -3.2815 | -3.6138 | 15.1415 | 13.9201 | 13.4778 | 13.218 | 12.8501 | 12.478 | 12.1341 | 11.7571 | 11.2858 | 10.8016 | 7.8755 | 4.6265 | 2.734 | 1.3555 | 0.82445 | 10.5045 | 9.8527 | 9.4128 | 9.1934 | 8.8397 | 8.4624 | 7.7983 | 6.1504 | 5.0609 | 3.7787 | 0.84689 | -1.5253 | -2.9446 | -3.3774 | -2.2579 | 15.1415 | 14.4897 | 14.0498 | 13.8304 | 13.4767 | 13.0994 | 12.4353 | 10.7874 | 9.6979 | 8.4157 | 5.4839 | 3.1117 | 1.6924 | 1.2596 | 2.1395 | 10.5045 | 9.6609 | 9.3831 | 9.2656 | 9.1197 | 8.9467 | 8.7433 | 8.5222 | 8.2142 | 7.8285 | 6.5987 | 4.8246 | 3.6681 | 2.9507 | 2.5835 | 15.1415 | 14.2979 | 14.0201 | 13.9026 | 13.7567 | 13.5837 | 13.3803 | 13.1592 | 12.8512 | 12.4655 | 11.2357 | 9.4616 | 8.3051 | 7.5877 | 7.2481 | 10.5045 | 9.387 | 8.7989 | 8.4928 | 8.0591 | 7.6246 | 6.8656 | 5.108 | 3.9207 | 2.5447 | -0.64 | -3.2512 | -4.8623 | -5.5131 | -4.6656 | 15.1415 | 14.024 | 13.4359 | 13.1298 | 12.6961 | 12.2616 | 11.5026 | 9.745 | 8.5577 | 7.1817 | 3.997 | 1.3858 | -0.22525 | -0.8761 | -0.20873 | 367434 | 426087 | LOWER DARWEN | ROCHDALE
| Alderley & Chelford | 9.186 | 8.479 | 8.0072 | 7.6839 | 7.3204 | 6.9623 | 3.6885 | 3.4049 | 2.977 | 1.9169 | -0.11572 | -4.0155 | -6.6412 | -9.4015 | -11.7722 | 15.876 | 15.169 | 14.6972 | 14.3739 | 14.0104 | 13.6523 | 10.3785 | 10.0949 | 9.667 | 8.6069 | 6.5743 | 2.6745 | 0.048816 | -2.7115 | -5.184 | 9.186 | 8.8706 | 8.5309 | 8.2166 | 7.8507 | 7.4596 | 6.9824 | 6.3841 | 5.8211 | 4.5787 | 2.9366 | 1.3472 | -0.11881 | -1.7358 | -2.9184 | 15.876 | 15.5606 | 15.2209 | 14.9066 | 14.5407 | 14.1496 | 13.6724 | 13.0741 | 12.5111 | 11.2687 | 9.6266 | 8.0372 | 6.5712 | 4.9542 | 3.9694 | 9.186 | 8.4392 | 7.9918 | 7.7409 | 5.493 | 5.2351 | 2.1338 | 1.9635 | 1.7228 | 0.51161 | -1.8103 | -4.52 | -6.5299 | -8.3091 | -10.1643 | 15.876 | 15.1292 | 14.6818 | 14.4309 | 12.183 | 11.9251 | 8.8238 | 8.6535 | 8.4128 | 7.2016 | 4.8797 | 2.17 | 0.16014 | -1.6191 | -3.6685 | 9.186 | 8.9482 | 8.6712 | 8.4905 | 8.2313 | 7.2398 | 3.9287 | 3.0895 | 2.1416 | -0.029552 | -3.4493 | -6.1807 | -8.2625 | -9.5865 | -8.7486 | 15.876 | 15.6382 | 15.3612 | 15.1805 | 14.9213 | 13.9298 | 10.6187 | 9.7795 | 8.8316 | 6.6604 | 3.2407 | 0.50931 | -1.5725 | -2.8965 | -2.2476 | 9.186 | 8.8242 | 8.4926 | 8.2767 | 8.0621 | 7.8014 | 4.5722 | 4.3348 | 3.923 | 2.8535 | 1.5597 | -0.5493 | -2.0495 | -3.4099 | -4.1399 | 15.876 | 15.5142 | 15.1826 | 14.9667 | 14.7521 | 14.4914 | 11.2622 | 11.0248 | 10.613 | 9.5435 | 8.2497 | 6.1407 | 4.6405 | 3.2801 | 2.6241 | 9.186 | 8.5925 | 8.1182 | 7.7753 | 7.3757 | 6.3013 | 2.8906 | 1.8986 | 0.83854 | -1.4413 | -5.1704 | -8.1366 | -10.434 | -12.0049 | -11.4539 | 15.876 | 15.2825 | 14.8082 | 14.4653 | 14.0657 | 12.9913 | 9.5806 | 8.5886 | 7.5285 | 5.2487 | 1.5196 | -1.4466 | -3.744 | -5.3149 | -4.8887 | 385044 | 379026 | MOSS NOOK | SOUTH MANCHESTER
| Alston | -0.908 | -0.95579 | -1.0104 | -1.0539 | -1.1021 | 0.14772 | 0.10266 | 0.056672 | 0.010619 | -0.029692 | -0.24891 | -0.59988 | -0.88137 | -1.217 | -1.5354 | 0.392 | 0.34421 | 0.2896 | 0.24614 | 0.19791 | 0.14772 | 0.10266 | 0.056672 | 0.010619 | -0.029692 | -0.24891 | -0.59988 | -0.88137 | -1.217 | -1.5694 | -0.908 | -0.95869 | -1.0274 | -1.0919 | -1.1592 | 0.067329 | -0.030417 | -0.24094 | -0.28111 | -0.32087 | -0.43377 | -0.52822 | -0.59964 | -0.65756 | -0.74062 | 0.392 | 0.34131 | 0.27257 | 0.20808 | 0.1408 | 0.067329 | -0.030417 | -0.24094 | -0.28111 | -0.32087 | -0.43377 | -0.52822 | -0.59964 | -0.65756 | -0.72836 | -0.908 | -0.95948 | -1.0147 | -1.0584 | -1.1067 | 0.14313 | 0.097967 | 0.051992 | 0.0151 | -0.015359 | -0.2033 | -0.51902 | -0.76289 | -1.0605 | -1.315 | 0.392 | 0.34052 | 0.28529 | 0.24158 | 0.19331 | 0.14313 | 0.097967 | 0.051992 | 0.0151 | -0.015359 | -0.2033 | -0.51902 | -0.76289 | -1.0605 | -1.3602 | -0.908 | -0.93309 | -0.97108 | -1.0063 | -1.0403 | 0.21997 | 0.16358 | 0.049976 | -0.0709 | -0.18698 | -0.51438 | -0.91443 | -1.2354 | -1.3989 | -1.2005 | 0.392 | 0.36691 | 0.32892 | 0.29375 | 0.25971 | 0.21997 | 0.16358 | 0.049976 | -0.0709 | -0.18698 | -0.51438 | -0.91443 | -1.2354 | -1.3989 | -1.2474 | -0.908 | -0.94916 | -0.99839 | -1.0341 | -1.0646 | 0.20284 | 0.16668 | 0.12555 | 0.079662 | 0.03499 | -0.11452 | -0.28106 | -0.38888 | -0.48036 | -0.48844 | 0.392 | 0.35084 | 0.30161 | 0.26586 | 0.2354 | 0.20284 | 0.16668 | 0.12555 | 0.079662 | 0.03499 | -0.11452 | -0.28106 | -0.38888 | -0.48036 | -0.50279 | -0.908 | -0.95768 | -1.0161 | -1.0726 | -1.1271 | 0.11861 | 0.048154 | -0.086587 | -0.21539 | -0.33868 | -0.68223 | -1.0614 | -1.3941 | -1.5751 | -1.404 | 0.392 | 0.34232 | 0.28391 | 0.22742 | 0.17292 | 0.11861 | 0.048154 | -0.086587 | -0.21539 | -0.33868 | -0.68223 | -1.0614 | -1.3941 | -1.5751 | -1.4439 | 372125 | 546499 | PENRITH & SHAP | HUTTON | Firm Capacity marginally exceeded. Storm Arwen Reinforcement project in RIIO-ED2 will increase firm capacity
| Ambleside | 8.4559 | 7.8102 | 7.5772 | 7.4578 | 7.2858 | 7.1107 | 6.9672 | 6.8353 | 6.6797 | 6.5424 | 5.5086 | 3.6404 | 2.0714 | 0.45508 | -0.9769 | 17.6559 | 17.0102 | 16.7772 | 16.6578 | 16.4858 | 16.3107 | 16.1672 | 16.0353 | 15.8797 | 15.7424 | 14.7086 | 12.8404 | 11.2714 | 9.6551 | 8.1176 | 8.4559 | 8.0787 | 7.841 | 7.6455 | 7.4318 | 7.2136 | 6.9491 | 6.6279 | 6.4427 | 6.2578 | 5.7151 | 5.1823 | 4.6996 | 4.135 | 3.664 | 17.6559 | 17.2787 | 17.041 | 16.8455 | 16.6318 | 16.4136 | 16.1491 | 15.8279 | 15.6427 | 15.4578 | 14.9151 | 14.3823 | 13.8996 | 13.335 | 12.9321 | 8.4559 | 7.7373 | 7.5014 | 7.4054 | 7.2532 | 7.1001 | 6.9896 | 6.8918 | 6.8035 | 6.7153 | 5.8334 | 4.1132 | 2.6921 | 1.2738 | 0.093003 | 17.6559 | 16.9373 | 16.7014 | 16.6054 | 16.4532 | 16.3001 | 16.1896 | 16.0918 | 16.0035 | 15.9153 | 15.0334 | 13.3132 | 11.8921 | 10.4738 | 9.1446 | 8.4559 | 8.0378 | 7.8765 | 7.7828 | 7.6484 | 7.51 | 7.288 | 6.711 | 6.1058 | 5.4971 | 3.7651 | 2.1235 | 0.83547 | 0.085877 | 0.72532 | 17.6559 | 17.2378 | 17.0765 | 16.9828 | 16.8484 | 16.71 | 16.488 | 15.911 | 15.3058 | 14.6971 | 12.9651 | 11.3235 | 10.0355 | 9.2859 | 9.7724 | 8.4559 | 7.9275 | 7.7236 | 7.6255 | 7.5289 | 7.4385 | 7.3391 | 7.2113 | 7.0335 | 6.8561 | 6.2342 | 5.5149 | 5.0237 | 4.5389 | 4.3807 | 17.6559 | 17.1275 | 16.9236 | 16.8255 | 16.7289 | 16.6385 | 16.5391 | 16.4113 | 16.2335 | 16.0561 | 15.4342 | 14.7149 | 14.2237 | 13.7389 | 13.5484 | 8.4559 | 7.7432 | 7.4856 | 7.3328 | 7.1409 | 6.956 | 6.6801 | 6.0359 | 5.4014 | 4.7626 | 2.9339 | 1.2085 | -0.16545 | -1.0266 | -0.51559 | 17.6559 | 16.9432 | 16.6856 | 16.5328 | 16.3409 | 16.156 | 15.8801 | 15.2359 | 14.6014 | 13.9626 | 12.1339 | 10.4085 | 9.0345 | 8.1734 | 8.5601 | 337602 | 503506 | KENDAL (PARKSIDE RD) | HUTTON
| Ancoats North T11 & T12 | 5.8017 | 0.73894 | -0.69619 | -1.1379 | -1.5644 | -2.0118 | -2.4579 | -2.9309 | -3.502 | -4.0737 | -5.9095 | -7.8783 | -9.2547 | -10.7255 | -12.1823 | 9.9387 | 4.8759 | 3.4408 | 2.9991 | 2.5726 | 2.1252 | 1.6791 | 1.2061 | 0.63503 | 0.063265 | -1.7725 | -3.7413 | -5.1177 | -6.5885 | -7.8996 | 5.8017 | 4.4574 | 3.8517 | 3.4863 | 3.1403 | 2.777 | 2.3642 | 1.8356 | 1.2968 | 0.74301 | -0.85391 | -2.4455 | -3.8457 | -5.3794 | -6.7274 | 9.9387 | 8.5944 | 7.9887 | 7.6233 | 7.2773 | 6.914 | 6.5012 | 5.9726 | 5.4338 | 4.88 | 3.2831 | 1.6915 | 0.29134 | -1.2424 | -2.3485 | 5.8017 | -0.087053 | -1.8854 | -2.5223 | -3.1614 | -3.8292 | -4.4842 | -5.1841 | -5.7662 | -6.3904 | -8.4542 | -10.669 | -12.2086 | -13.7096 | -15.1459 | 9.9387 | 4.0499 | 2.2516 | 1.6147 | 0.97561 | 0.30782 | -0.34715 | -1.0471 | -1.6292 | -2.2534 | -4.3172 | -6.532 | -8.0716 | -9.5726 | -10.799 | 5.8017 | 1.6415 | 0.23058 | -0.35165 | -0.94979 | -1.5973 | -2.2669 | -3.0704 | -3.7721 | -4.5122 | -6.6753 | -8.7283 | -10.1291 | -11.375 | -12.4279 | 9.9387 | 5.7785 | 4.3676 | 3.7853 | 3.1872 | 2.5397 | 1.8701 | 1.0666 | 0.36488 | -0.37517 | -2.5383 | -4.5913 | -5.9921 | -7.238 | -8.0978 | 5.8017 | 3.3683 | 2.4882 | 2.0877 | 1.7226 | 1.3266 | 0.92666 | 0.49452 | -0.062672 | -0.63027 | -2.3242 | -3.9922 | -5.1439 | -6.2945 | -7.3822 | 9.9387 | 7.5053 | 6.6252 | 6.2247 | 5.8596 | 5.4636 | 5.0637 | 4.6315 | 4.0743 | 3.5067 | 1.8128 | 0.14484 | -1.0069 | -2.1575 | -3.0555 | 5.8017 | -0.7709 | -2.7195 | -3.3637 | -4.0171 | -4.6958 | -5.4052 | -6.2581 | -6.983 | -7.7488 | -10.0185 | -12.1513 | -13.6097 | -14.9387 | -16.147 | 9.9387 | 3.3661 | 1.4175 | 0.77325 | 0.11985 | -0.55879 | -1.2682 | -2.1211 | -2.846 | -3.6118 | -5.8815 | -8.0143 | -9.4727 | -10.8017 | -11.781 | 385022 | 398830 | RED BANK | WHITEGATE | Firm Capacity exceeded in FY26. HV transfers are available to Strangeways primary via existing feeders.
| Ancoats North T14 | 3.1847 | 1.6052 | 0.94647 | 0.61673 | 0.31133 | 0.00309 | -0.30163 | -0.61818 | -0.97594 | -1.3292 | -2.0079 | -2.809 | -3.4156 | -4.0306 | -4.5744 | 7.9347 | 6.3552 | 5.6965 | 5.3667 | 5.0613 | 4.7531 | 4.4484 | 4.1318 | 3.7741 | 3.4208 | 2.7421 | 1.941 | 1.3344 | 0.71938 | 0.18697 | 3.1847 | 2.74 | 2.4298 | 2.1959 | 1.9754 | 1.7304 | 1.4562 | 1.1373 | 0.9167 | 0.69483 | 0.067911 | -0.52921 | -1.0284 | -1.5858 | -2.1197 | 7.9347 | 7.49 | 7.1798 | 6.9459 | 6.7254 | 6.4804 | 6.2062 | 5.8873 | 5.6667 | 5.4448 | 4.8179 | 4.2208 | 3.7216 | 3.1642 | 2.7193 | 3.1847 | 1.3605 | 0.65124 | 0.31835 | 0.011518 | -0.29752 | -0.60181 | -0.91583 | -1.2396 | -1.5556 | -2.127 | -2.8157 | -3.3014 | -3.7368 | -4.0382 | 7.9347 | 6.1105 | 5.4012 | 5.0684 | 4.7615 | 4.4525 | 4.1482 | 3.8342 | 3.5104 | 3.1944 | 2.623 | 1.9343 | 1.4486 | 1.0132 | 0.6772 | 3.1847 | 1.9065 | 1.3369 | 1.0423 | 0.77196 | 0.49323 | 0.19236 | -0.1909 | -0.62087 | -1.0455 | -1.7861 | -2.4465 | -2.8979 | -3.1704 | -3.0632 | 7.9347 | 6.6565 | 6.0869 | 5.7923 | 5.522 | 5.2432 | 4.9424 | 4.5591 | 4.1291 | 3.7045 | 2.9639 | 2.3035 | 1.8521 | 1.5796 | 1.6477 | 3.1847 | 2.5096 | 2.0434 | 1.7296 | 1.449 | 1.1597 | 0.86339 | 0.55284 | 0.19743 | -0.15758 | -0.73188 | -1.2722 | -1.6366 | -1.9746 | -2.1712 | 7.9347 | 7.2596 | 6.7934 | 6.4796 | 6.199 | 5.9097 | 5.6134 | 5.3028 | 4.9474 | 4.5924 | 4.0181 | 3.4778 | 3.1134 | 2.7754 | 2.5973 | 3.1847 | 1.1522 | 0.39838 | 0.062863 | -0.24704 | -0.55683 | -0.88728 | -1.3106 | -1.7456 | -2.1741 | -2.9265 | -3.6023 | -4.0715 | -4.36 | -4.2794 | 7.9347 | 5.9022 | 5.1484 | 4.8129 | 4.503 | 4.1932 | 3.8627 | 3.4394 | 3.0044 | 2.5759 | 1.8235 | 1.1477 | 0.67845 | 0.38998 | 0.43851 | 385032 | 398840 | RED BANK | WHITEGATE
| Annie Pit | 5.2295 | 4.4575 | 3.7358 | 3.1401 | 2.4787 | 1.8082 | 1.1844 | 0.90377 | 0.58496 | 0.28912 | -1.4036 | -5.1342 | -8.3397 | -11.5042 | -14.2459 | 10.7295 | 9.9575 | 9.2358 | 8.6401 | 7.9787 | 7.3082 | 6.6844 | 6.4038 | 6.085 | 5.7891 | 4.0964 | 0.36582 | -2.8397 | -6.0042 | -9.0498 | 5.2295 | 4.9447 | 4.6828 | 4.4744 | 4.2788 | 4.0691 | 3.8107 | 3.4869 | 3.2414 | 2.9989 | 2.2915 | 1.6137 | 1.0074 | 0.36146 | -0.088794 | 10.7295 | 10.4447 | 10.1828 | 9.9744 | 9.7788 | 9.5691 | 9.3107 | 8.9869 | 8.7414 | 8.4989 | 7.7915 | 7.1137 | 6.5074 | 5.8615 | 5.4677 | 5.2295 | 4.3515 | 3.6118 | 3.0147 | 2.3541 | 1.6856 | 1.0642 | 0.7889 | 0.52642 | 0.29148 | -1.2262 | -4.5908 | -7.5865 | -10.454 | -12.8104 | 10.7295 | 9.8515 | 9.1118 | 8.5147 | 7.8541 | 7.1856 | 6.5642 | 6.2889 | 6.0264 | 5.7915 | 4.2738 | 0.90921 | -2.0865 | -4.954 | -7.6844 | 5.2295 | 4.6885 | 4.0534 | 3.496 | 2.8683 | 2.2083 | 1.3913 | 0.29892 | -1.0608 | -2.4307 | -6.122 | -9.5295 | -12.2701 | -13.693 | -11.9752 | 10.7295 | 10.1885 | 9.5534 | 8.996 | 8.3683 | 7.7083 | 6.8913 | 5.7989 | 4.4392 | 3.0693 | -0.62202 | -4.0295 | -6.7701 | -8.193 | -6.8545 | 5.2295 | 4.8676 | 4.2437 | 3.7235 | 3.2384 | 2.7435 | 2.2331 | 1.9963 | 1.6702 | 1.3412 | 0.49686 | -0.38463 | -0.94601 | -1.3674 | -1.2477 | 10.7295 | 10.3676 | 9.7437 | 9.2235 | 8.7384 | 8.2435 | 7.7331 | 7.4963 | 7.1702 | 6.8412 | 5.9969 | 5.1154 | 4.554 | 4.1326 | 4.1635 | 5.2295 | 4.3296 | 3.573 | 2.9382 | 2.2396 | 1.5383 | 0.68541 | -0.48561 | -1.9279 | -3.3326 | -7.1442 | -10.7008 | -13.6277 | -15.3172 | -13.9239 | 10.7295 | 9.8296 | 9.073 | 8.4382 | 7.7396 | 7.0383 | 6.1854 | 5.0144 | 3.5721 | 2.1674 | -1.6442 | -5.2008 | -8.1277 | -9.8172 | -8.7293 | 300011 | 527810 | STAINBURN & SIDDICK | HARKER
| Ansdell | 7.7663 | 6.929 | 6.6345 | 6.4668 | 6.2627 | 6.0608 | 5.8812 | 5.722 | 5.5195 | 5.3463 | 4.186 | 2.1454 | 0.50118 | -1.2257 | -2.754 | 10.7663 | 9.929 | 9.6345 | 9.4668 | 9.2627 | 9.0608 | 8.8812 | 8.722 | 8.5195 | 8.3463 | 7.186 | 5.1454 | 3.5012 | 1.7743 | 0.13579 | 7.7663 | 7.496 | 7.325 | 7.1691 | 6.9765 | 6.7935 | 6.5737 | 6.3037 | 6.0443 | 5.7837 | 5.0316 | 4.345 | 3.7498 | 3.1475 | 2.7514 | 10.7663 | 10.496 | 10.325 | 10.1691 | 9.9765 | 9.7935 | 9.5737 | 9.3037 | 9.0443 | 8.7837 | 8.0316 | 7.345 | 6.7498 | 6.1475 | 5.8111 | 7.7663 | 6.8296 | 6.5381 | 6.4088 | 6.246 | 6.0943 | 5.9849 | 5.9046 | 5.7919 | 5.6881 | 4.6973 | 2.795 | 1.3041 | -0.2166 | -1.5198 | 10.7663 | 9.8296 | 9.5381 | 9.4088 | 9.246 | 9.0943 | 8.9849 | 8.9046 | 8.7919 | 8.6881 | 7.6973 | 5.795 | 4.3041 | 2.7834 | 1.3795 | 7.7663 | 7.2264 | 7.0437 | 6.9519 | 6.8023 | 6.6315 | 6.3789 | 5.7788 | 5.1336 | 4.4919 | 2.6442 | 0.86651 | -0.51177 | -1.3696 | -0.68834 | 10.7663 | 10.2264 | 10.0437 | 9.9519 | 9.8023 | 9.6315 | 9.3789 | 8.7788 | 8.1336 | 7.4919 | 5.6442 | 3.8665 | 2.4882 | 1.6304 | 2.1576 | 7.7663 | 7.3698 | 7.1926 | 7.0913 | 6.9819 | 6.8607 | 6.7445 | 6.6346 | 6.4558 | 6.2853 | 5.7291 | 5.016 | 4.4692 | 3.9874 | 3.6059 | 10.7663 | 10.3698 | 10.1926 | 10.0913 | 9.9819 | 9.8607 | 9.7445 | 9.6346 | 9.4558 | 9.2853 | 8.7291 | 8.016 | 7.4692 | 6.9874 | 6.6653 | 7.7663 | 6.8143 | 6.4909 | 6.3107 | 6.0831 | 5.8547 | 5.5406 | 4.8567 | 4.1389 | 3.4269 | 1.3852 | -0.54326 | -2.0547 | -3.08 | -2.5977 | 10.7663 | 9.8143 | 9.4909 | 9.3107 | 9.0831 | 8.8547 | 8.5406 | 7.8567 | 7.1389 | 6.4269 | 4.3852 | 2.4567 | 0.94525 | -0.080044 | 0.2919 | 334416 | 428229 | LYTHAM | PENWORTHAM
| Ardwick | -0.6889 | -2.4602 | -3.6753 | -4.5671 | -5.4405 | 5.6816 | 5.0946 | 4.8817 | 4.5761 | 4.2833 | 3.1379 | 1.533 | 0.3438 | -0.69359 | -1.4104 | 4.3111 | 2.5398 | 1.3247 | 0.43287 | -0.44051 | 10.6816 | 10.0946 | 9.8817 | 9.5761 | 9.2833 | 8.1379 | 6.533 | 5.3438 | 4.3064 | 3.5082 | -0.6889 | -1.1069 | -1.4149 | -1.5976 | -1.7452 | 10.1025 | 9.9132 | 9.6562 | 9.3464 | 9.0338 | 8.1443 | 7.2036 | 6.35 | 5.4397 | 4.7851 | 4.3111 | 3.8931 | 3.5851 | 3.4024 | 3.2548 | 15.1025 | 14.9132 | 14.6562 | 14.3464 | 14.0338 | 13.1443 | 12.2036 | 11.35 | 10.4397 | 9.8897 | -0.6889 | -2.7215 | -4.0252 | -4.9735 | -5.9047 | 5.1554 | 4.5003 | 4.2137 | 3.8838 | 3.5697 | 2.2969 | 0.81245 | -0.098727 | -0.76665 | -0.93073 | 4.3111 | 2.2785 | 0.97485 | 0.026484 | -0.9047 | 10.1554 | 9.5003 | 9.2137 | 8.8838 | 8.5697 | 7.2969 | 5.8124 | 4.9013 | 4.2334 | 3.9791 | -0.6889 | -2.1599 | -3.3246 | -4.2348 | -5.1365 | 5.9397 | 5.2393 | 4.7363 | 4.1828 | 3.6581 | 2.1057 | 0.76874 | 0.042032 | -0.24539 | 0.13139 | 4.3111 | 2.8401 | 1.6754 | 0.76524 | -0.13652 | 10.9397 | 10.2393 | 9.7363 | 9.1828 | 8.6581 | 7.1057 | 5.7687 | 5.042 | 4.7546 | 5.0329 | -0.6889 | -1.7876 | -2.8506 | -3.7075 | -4.5182 | 6.6611 | 6.1139 | 5.9211 | 5.6078 | 5.2948 | 4.3614 | 3.4711 | 2.9213 | 2.4141 | 2.1829 | 4.3111 | 3.2124 | 2.1494 | 1.2925 | 0.48181 | 11.6611 | 11.1139 | 10.9211 | 10.6078 | 10.2948 | 9.3614 | 8.4711 | 7.9213 | 7.4141 | 7.1926 | -0.6889 | -2.8069 | -4.1385 | -5.0958 | -6.0396 | 5.0141 | 4.2947 | 3.7548 | 3.1844 | 2.6444 | 1.0122 | -0.45251 | -1.2519 | -1.5104 | -1.1072 | 4.3111 | 2.1931 | 0.86149 | -0.095842 | -1.0396 | 10.0141 | 9.2947 | 8.7548 | 8.1844 | 7.6444 | 6.0122 | 4.5475 | 3.7481 | 3.4896 | 3.8178 | 384753 | 397415 | STUART ST | STALYBRIDGE | Firm Capacity marginally exceeded. HV demand to be transferred off Ardwick onto surounding primaries.
| Arnside | 11.4244 | 11.3906 | 11.3424 | 11.3006 | 11.2286 | 11.1557 | 11.1014 | 11.0547 | 10.9898 | 10.9289 | 10.4339 | 9.6005 | 8.8638 | 8.133 | 7.4987 | 13.9244 | 13.8906 | 13.8424 | 13.8006 | 13.7286 | 13.6557 | 13.6014 | 13.5547 | 13.4898 | 13.4289 | 12.9339 | 12.1005 | 11.3638 | 10.633 | 9.9342 | 11.4244 | 11.3823 | 11.321 | 11.2593 | 11.1882 | 11.1209 | 11.0392 | 10.9448 | 10.8651 | 10.7851 | 10.5523 | 10.3407 | 10.1196 | 9.8613 | 9.6584 | 13.9244 | 13.8823 | 13.821 | 13.7593 | 13.6882 | 13.6209 | 13.5392 | 13.4448 | 13.3651 | 13.2851 | 13.0523 | 12.8407 | 12.6196 | 12.3613 | 12.1907 | 11.4244 | 11.3968 | 11.3561 | 11.3281 | 11.2697 | 11.2129 | 11.1805 | 11.1588 | 11.1132 | 11.0555 | 10.6232 | 9.8457 | 9.2052 | 8.5987 | 8.0573 | 13.9244 | 13.8968 | 13.8561 | 13.8281 | 13.7697 | 13.7129 | 13.6805 | 13.6588 | 13.6132 | 13.5555 | 13.1232 | 12.3457 | 11.7052 | 11.0987 | 10.4756 | 11.4244 | 11.4515 | 11.4283 | 11.3923 | 11.3359 | 11.2758 | 11.1763 | 10.9048 | 10.6193 | 10.3357 | 9.5278 | 8.7733 | 8.1762 | 7.8485 | 8.2314 | 13.9244 | 13.9515 | 13.9283 | 13.8923 | 13.8359 | 13.7758 | 13.6763 | 13.4048 | 13.1193 | 12.8357 | 12.0278 | 11.2733 | 10.6762 | 10.3485 | 10.6467 | 11.4244 | 11.3963 | 11.356 | 11.3268 | 11.2959 | 11.2683 | 11.2336 | 11.1755 | 11.0843 | 10.9918 | 10.6267 | 10.1999 | 9.8899 | 9.6116 | 9.5537 | 13.9244 | 13.8963 | 13.856 | 13.8268 | 13.7959 | 13.7683 | 13.7336 | 13.6755 | 13.5843 | 13.4918 | 13.1267 | 12.6999 | 12.3899 | 12.1116 | 12.0339 | 11.4244 | 11.4315 | 11.3822 | 11.3167 | 11.2331 | 11.1542 | 11.0331 | 10.7302 | 10.4229 | 10.1178 | 9.2443 | 8.4291 | 7.7721 | 7.3705 | 7.6719 | 13.9244 | 13.9315 | 13.8822 | 13.8167 | 13.7331 | 13.6542 | 13.5331 | 13.2302 | 12.9229 | 12.6178 | 11.7443 | 10.9291 | 10.2721 | 9.8705 | 10.1051 | 346495 | 478180 | KENDAL (PARKSIDE RD) | HUTTON
| Ashton (Golborne) | 7.6232 | 4.5274 | 3.1839 | 2.3793 | 1.4888 | 0.54634 | -0.1254 | -0.8868 | -1.8539 | -2.8874 | -6.9468 | -12.2885 | -16.3759 | -20.0764 | -22.7682 | 13.4232 | 10.3274 | 8.9839 | 8.1793 | 7.2888 | 6.3463 | 5.6746 | 4.9132 | 3.9461 | 2.9126 | -1.1468 | -6.4885 | -10.5759 | -14.2764 | -17.1365 | 7.6232 | 6.5893 | 6.106 | 5.7789 | 5.3919 | 4.921 | 4.3661 | 3.734 | 3.0309 | 2.2329 | -0.30433 | -3.2408 | -6.0643 | -9.2037 | -11.1416 | 13.4232 | 12.3893 | 11.906 | 11.5789 | 11.1919 | 10.721 | 10.1661 | 9.534 | 8.8309 | 8.0329 | 5.4957 | 2.5592 | -0.26435 | -3.4037 | -5.0958 | 7.6232 | 4.1313 | 2.748 | 2.0336 | 1.1832 | 0.30739 | -0.25475 | -0.85416 | -1.5575 | -2.3445 | -6.2468 | -12.8628 | -17.8785 | -22.1264 | -24.8495 | 13.4232 | 9.9313 | 8.548 | 7.8336 | 6.9832 | 6.1074 | 5.5453 | 4.9458 | 4.2425 | 3.4555 | -0.44681 | -7.0628 | -12.0785 | -16.3264 | -19.0393 | 7.6232 | 5.1839 | 4.0999 | 3.4036 | 2.5735 | 1.6019 | 0.69847 | -0.8009 | -2.4557 | -4.1755 | -9.386 | -14.2902 | -18.5842 | -21.6087 | -21.8008 | 13.4232 | 10.9839 | 9.8999 | 9.2036 | 8.3735 | 7.4019 | 6.4985 | 4.9991 | 3.3443 | 1.6245 | -3.586 | -8.4902 | -12.7842 | -15.8087 | -16.0542 | 7.6232 | 5.7881 | 4.8171 | 4.2158 | 3.6055 | 2.8692 | 2.3402 | 1.7601 | 0.97695 | 0.089858 | -2.8113 | -6.555 | -9.8726 | -12.4326 | -13.5751 | 13.4232 | 11.5881 | 10.6171 | 10.0158 | 9.4055 | 8.6692 | 8.1402 | 7.5601 | 6.7769 | 5.8899 | 2.9887 | -0.75503 | -4.0726 | -6.6326 | -7.6611 | 7.6232 | 3.7257 | 2.2222 | 1.3731 | 0.43184 | -0.5411 | -1.4152 | -2.944 | -4.6071 | -6.3486 | -11.738 | -17.2018 | -21.4068 | -24.2015 | -23.6926 | 13.4232 | 9.5257 | 8.0222 | 7.1731 | 6.2318 | 5.2589 | 4.3848 | 2.856 | 1.1929 | -0.54858 | -5.938 | -11.4018 | -15.6068 | -18.4015 | -18.0453 | 357056 | 400663 | GOLBORNE | BOLD
| Ashton (Ribble) | 3.321 | 2.4479 | 2.1934 | 1.6212 | 1.001 | 0.38074 | -0.22231 | -0.35701 | -0.53714 | -0.69783 | -1.6212 | -3.1667 | -4.441 | -5.6531 | -6.782 | 3.321 | 2.4479 | 2.1934 | 1.6212 | 1.001 | 0.38074 | -0.22231 | -0.35701 | -0.53714 | -0.69783 | -1.6212 | -3.1667 | -4.441 | -5.6531 | -6.8431 | 3.321 | 2.9582 | 2.8218 | 2.7323 | 2.6147 | 2.4806 | 2.3074 | 2.0864 | 1.8615 | 1.6362 | 0.9776 | 0.28777 | -0.39386 | -1.0632 | -1.4575 | 3.321 | 2.9582 | 2.8218 | 2.7323 | 2.6147 | 2.4806 | 2.3074 | 2.0864 | 1.8615 | 1.6362 | 0.9776 | 0.28777 | -0.39386 | -1.0632 | -1.3986 | 3.321 | 2.331 | 2.0721 | 1.5314 | 0.94493 | 0.36432 | -0.18505 | -0.25894 | -0.36824 | -0.47043 | -1.2267 | -2.7393 | -3.9174 | -5.0149 | -5.9415 | 3.321 | 2.331 | 2.0721 | 1.5314 | 0.94493 | 0.36432 | -0.18505 | -0.25894 | -0.36824 | -0.47043 | -1.2267 | -2.7393 | -3.9174 | -5.0149 | -6.0115 | 3.321 | 2.7423 | 2.5838 | 2.0651 | 1.4847 | 0.88416 | 0.23093 | -0.19601 | -0.66444 | -1.1322 | -2.482 | -3.7972 | -4.8127 | -5.3992 | -5.0055 | 3.321 | 2.7423 | 2.5838 | 2.0651 | 1.4847 | 0.88416 | 0.23093 | -0.19601 | -0.66444 | -1.1322 | -2.482 | -3.7972 | -4.8127 | -5.3992 | -5.083 | 3.321 | 2.6757 | 2.4918 | 1.9782 | 1.4572 | 0.91279 | 0.35302 | 0.24538 | 0.071652 | -0.096341 | -0.6579 | -1.4311 | -2.0281 | -2.5366 | -2.7534 | 3.321 | 2.6757 | 2.4918 | 1.9782 | 1.4572 | 0.91279 | 0.35302 | 0.24538 | 0.071652 | -0.096341 | -0.6579 | -1.4311 | -2.0281 | -2.5366 | -2.7508 | 3.321 | 2.2999 | 2.0096 | 1.4198 | 0.77627 | 0.13768 | -0.55995 | -1.0558 | -1.5803 | -2.1022 | -3.6076 | -5.0472 | -6.1719 | -6.8721 | -6.5687 | 3.321 | 2.2999 | 2.0096 | 1.4198 | 0.77627 | 0.13768 | -0.55995 | -1.0558 | -1.5803 | -2.1022 | -3.6076 | -5.0472 | -6.1719 | -6.8721 | -6.6382 | 350275 | 430526 | RIBBLE | PENWORTHAM
| Ashton On Mersey | 11.129 | 10.6093 | 10.3153 | 10.0796 | 9.7731 | 9.459 | 9.1655 | 8.9004 | 8.5998 | 8.3251 | 6.5337 | 3.9167 | 1.9528 | 0.15458 | -1.113 | 15.269 | 14.7493 | 14.4553 | 14.2196 | 13.9131 | 13.599 | 13.3055 | 13.0404 | 12.7398 | 12.4651 | 10.6737 | 8.0567 | 6.0928 | 4.2946 | 2.8968 | 11.129 | 10.933 | 10.776 | 10.6133 | 10.3962 | 10.17 | 9.8903 | 9.5583 | 9.2647 | 8.9605 | 8.0566 | 7.1884 | 6.3364 | 5.4328 | 4.7949 | 15.269 | 15.073 | 14.916 | 14.7533 | 14.5362 | 14.31 | 14.0303 | 13.6983 | 13.4047 | 13.1005 | 12.1966 | 11.3284 | 10.4764 | 9.5728 | 9.0388 | 11.129 | 10.4967 | 10.1311 | 9.8426 | 9.4205 | 8.9909 | 8.5943 | 8.2202 | 7.8141 | 7.3049 | 5.0863 | 2.355 | 0.46482 | -1.1068 | -1.6243 | 15.269 | 14.6367 | 14.2711 | 13.9826 | 13.5605 | 13.1309 | 12.7343 | 12.3602 | 11.9541 | 11.4449 | 9.2263 | 6.495 | 4.6048 | 3.0332 | 2.3783 | 11.129 | 10.8753 | 10.6253 | 10.3811 | 9.9706 | 9.5162 | 8.9555 | 8.0039 | 7.043 | 6.1102 | 3.5104 | 1.2859 | -0.22747 | -1.0431 | -0.42606 | 15.269 | 15.0153 | 14.7653 | 14.5211 | 14.1106 | 13.6562 | 13.0955 | 12.1439 | 11.183 | 10.2502 | 7.6504 | 5.4259 | 3.9125 | 3.0969 | 3.5675 | 11.129 | 10.8381 | 10.6421 | 10.498 | 10.3307 | 10.1294 | 9.9151 | 9.7027 | 9.419 | 9.1363 | 8.0376 | 6.7835 | 5.8875 | 5.0184 | 4.4469 | 15.269 | 14.9781 | 14.7821 | 14.638 | 14.4707 | 14.2694 | 14.0551 | 13.8427 | 13.559 | 13.2763 | 12.1776 | 10.9235 | 10.0275 | 9.1584 | 8.6526 | 11.129 | 10.637 | 10.2528 | 9.8969 | 9.3886 | 8.8739 | 8.2392 | 7.1779 | 6.1306 | 5.1128 | 2.2658 | -0.13158 | -1.7706 | -2.7179 | -2.289 | 15.269 | 14.777 | 14.3928 | 14.0369 | 13.5286 | 13.0139 | 12.3792 | 11.3179 | 10.2706 | 9.2528 | 6.4058 | 4.0084 | 2.3694 | 1.4221 | 1.7505 | 377188 | 392252 | SALE | CARRINGTON
| Ashton Under Lyne T11 & T12 | 7.0906 | 6.4277 | 6.0237 | 5.703 | 5.31 | 4.8956 | 4.4857 | 4.0677 | 3.6175 | 3.1854 | 1.1181 | -2.1948 | -4.77 | -7.208 | -8.8836 | 11.2276 | 10.5647 | 10.1607 | 9.84 | 9.447 | 9.0326 | 8.6227 | 8.2047 | 7.7545 | 7.3224 | 5.2551 | 1.9422 | -0.63303 | -3.071 | -4.9289 | 7.0906 | 6.8247 | 6.5889 | 6.3516 | 6.0675 | 5.7384 | 5.2253 | 4.5228 | 4.2745 | 3.9406 | 2.8027 | 1.6049 | 0.334 | -1.0466 | -1.9793 | 11.2276 | 10.9617 | 10.7259 | 10.4886 | 10.2045 | 9.8754 | 9.3623 | 8.6598 | 8.4115 | 8.0776 | 6.9397 | 5.7419 | 4.471 | 3.0904 | 2.3004 | 7.0906 | 6.2451 | 5.7022 | 5.2406 | 4.699 | 4.1253 | 3.5408 | 2.9356 | 2.332 | 1.7381 | -0.80198 | -3.8241 | -6.1067 | -8.0771 | -8.9659 | 11.2276 | 10.3821 | 9.8392 | 9.3776 | 8.836 | 8.2623 | 7.6778 | 7.0726 | 6.469 | 5.8751 | 3.335 | 0.3129 | -1.9697 | -3.9401 | -4.9344 | 7.0906 | 6.6444 | 6.2445 | 5.8721 | 5.3991 | 4.85 | 4.1361 | 2.9928 | 1.8602 | 0.77276 | -2.3355 | -5.0521 | -6.816 | -7.7986 | -7.3385 | 11.2276 | 10.7814 | 10.3815 | 10.0091 | 9.5361 | 8.987 | 8.2731 | 7.1298 | 5.9972 | 4.9098 | 1.8015 | -0.9151 | -2.679 | -3.6616 | -3.3245 | 7.0906 | 6.6739 | 6.3695 | 6.1448 | 5.9057 | 5.6105 | 5.2576 | 4.8711 | 4.4201 | 3.9616 | 2.4872 | 0.9936 | -0.36773 | -1.643 | -2.4026 | 11.2276 | 10.8109 | 10.5065 | 10.2818 | 10.0427 | 9.7475 | 9.3946 | 9.0081 | 8.5571 | 8.0986 | 6.6242 | 5.1306 | 3.7693 | 2.494 | 1.8224 | 7.0906 | 6.3763 | 5.8403 | 5.3575 | 4.7879 | 4.1965 | 3.4509 | 2.2249 | 1.0348 | -0.10509 | -3.4813 | -6.5772 | -8.5875 | -9.7415 | -9.5785 | 11.2276 | 10.5133 | 9.9773 | 9.4945 | 8.9249 | 8.3335 | 7.5879 | 6.3619 | 5.1718 | 4.0319 | 0.65575 | -2.4402 | -4.4505 | -5.6045 | -5.5 | 393275 | 399319 | HARTSHEAD-HEYROD | STALYBRIDGE
| Ashton Under Lyne T13 | 6.8413 | 6.5956 | 6.4997 | 6.4632 | 6.4118 | 6.3563 | 6.3062 | 6.2573 | 6.1822 | 6.1153 | 5.6021 | 4.6698 | 3.8853 | 3.0335 | 2.1821 | 11.5913 | 11.3456 | 11.2497 | 11.2132 | 11.1618 | 11.1063 | 11.0562 | 11.0073 | 10.9322 | 10.8653 | 10.3521 | 9.4198 | 8.6353 | 7.7835 | 6.8579 | 6.8413 | 6.7832 | 6.7185 | 6.6721 | 6.6251 | 6.5718 | 6.5004 | 6.4116 | 6.3242 | 6.2372 | 5.9787 | 5.7234 | 5.5011 | 5.2694 | 5.0918 | 11.5913 | 11.5332 | 11.4685 | 11.4221 | 11.3751 | 11.3218 | 11.2504 | 11.1616 | 11.0742 | 10.9872 | 10.7287 | 10.4734 | 10.2511 | 10.0194 | 9.8675 | 6.8413 | 6.5585 | 6.4553 | 6.4178 | 6.3659 | 6.31 | 6.2585 | 6.2092 | 6.1516 | 6.1041 | 5.6518 | 4.7915 | 4.0849 | 3.3393 | 2.6316 | 11.5913 | 11.3085 | 11.2053 | 11.1678 | 11.1159 | 11.06 | 11.0085 | 10.9592 | 10.9016 | 10.8541 | 10.4018 | 9.5415 | 8.8349 | 8.0893 | 7.2841 | 6.8413 | 6.7142 | 6.6571 | 6.6428 | 6.6085 | 6.5611 | 6.4541 | 6.1614 | 5.8508 | 5.551 | 4.6973 | 3.8025 | 3.043 | 2.5788 | 3.0294 | 11.5913 | 11.4642 | 11.4071 | 11.3928 | 11.3585 | 11.3111 | 11.2041 | 10.9114 | 10.6008 | 10.301 | 9.4473 | 8.5525 | 7.793 | 7.3288 | 7.6791 | 6.8413 | 6.7772 | 6.7294 | 6.7154 | 6.7062 | 6.6875 | 6.6548 | 6.6107 | 6.5296 | 6.4479 | 6.1726 | 5.8755 | 5.6686 | 5.4817 | 5.4651 | 11.5913 | 11.5272 | 11.4794 | 11.4654 | 11.4562 | 11.4375 | 11.4048 | 11.3607 | 11.2796 | 11.1979 | 10.9226 | 10.6255 | 10.4186 | 10.2317 | 10.1992 | 6.8413 | 6.5919 | 6.4893 | 6.4473 | 6.3882 | 6.3281 | 6.2109 | 5.8954 | 5.5711 | 5.2586 | 4.3746 | 3.5032 | 2.6672 | 2.0818 | 2.428 | 11.5913 | 11.3419 | 11.2393 | 11.1973 | 11.1382 | 11.0781 | 10.9609 | 10.6454 | 10.3211 | 10.0086 | 9.1246 | 8.2532 | 7.4172 | 6.8318 | 7.1019 | 393285 | 399329 | HARTSHEAD-HEYROD | STALYBRIDGE
| Ashwood Dale | 5.8691 | 5.3674 | 5.0953 | 4.8746 | 4.5488 | 4.1991 | 3.8608 | 3.5614 | 3.2777 | 3.014 | 1.241 | -1.6687 | -3.8631 | -5.9521 | -7.5212 | 13.1501 | 12.6484 | 12.3763 | 12.1556 | 11.8298 | 11.4801 | 11.1418 | 10.8424 | 10.5587 | 10.295 | 8.522 | 5.6123 | 3.4179 | 1.3289 | -0.42249 | 5.8691 | 5.584 | 5.3523 | 5.1273 | 4.8551 | 4.5976 | 4.2622 | 3.8283 | 3.5898 | 3.3426 | 2.5965 | 1.7956 | 1.004 | 0.10074 | -0.62533 | 13.1501 | 12.865 | 12.6333 | 12.4083 | 12.1361 | 11.8786 | 11.5432 | 11.1093 | 10.8708 | 10.6236 | 9.8775 | 9.0766 | 8.285 | 7.3817 | 6.7757 | 5.8691 | 5.2488 | 4.8807 | 4.5711 | 4.1478 | 3.6949 | 3.2618 | 2.8469 | 2.4676 | 2.0826 | -0.022753 | -2.9334 | -4.9042 | -6.493 | -7.1831 | 13.1501 | 12.5298 | 12.1617 | 11.8521 | 11.4288 | 10.9759 | 10.5428 | 10.1279 | 9.7486 | 9.3636 | 7.2582 | 4.3476 | 2.3768 | 0.78802 | -0.069161 | 5.8691 | 5.6549 | 5.385 | 5.1013 | 4.6879 | 4.2441 | 3.6583 | 2.574 | 1.5146 | 0.48692 | -2.4138 | -4.8598 | -6.321 | -6.8557 | -6.0616 | 13.1501 | 12.9359 | 12.666 | 12.3823 | 11.9689 | 11.5251 | 10.9393 | 9.855 | 8.7956 | 7.7679 | 4.8672 | 2.4212 | 0.95995 | 0.4253 | 1.0449 | 5.8691 | 5.5375 | 5.3152 | 5.1418 | 4.9323 | 4.7256 | 4.5038 | 4.2547 | 3.9635 | 3.6686 | 2.665 | 1.5844 | 0.83468 | 0.051309 | -0.52211 | 13.1501 | 12.8185 | 12.5962 | 12.4228 | 12.2133 | 12.0066 | 11.7848 | 11.5357 | 11.2445 | 10.9496 | 9.946 | 8.8654 | 8.1157 | 7.3323 | 6.8218 | 5.8691 | 5.4881 | 5.1303 | 4.7747 | 4.2908 | 3.7877 | 3.1262 | 1.9568 | 0.85946 | -0.20937 | -3.246 | -5.8068 | -7.4018 | -8.1093 | -7.5319 | 13.1501 | 12.7691 | 12.4113 | 12.0557 | 11.5718 | 11.0687 | 10.4072 | 9.2378 | 8.1405 | 7.0716 | 4.035 | 1.4742 | -0.12083 | -0.82834 | -0.37764 | 406537 | 373050 | BUXTON | STALYBRIDGE
| Askam & Dalton | 3.6349 | 3.4854 | 3.2371 | 3.0639 | 2.8898 | 2.7125 | 2.5549 | 2.3839 | 2.162 | 1.9642 | 0.15613 | -3.9042 | -7.3401 | -10.7487 | -13.4732 | 10.6149 | 10.4654 | 10.2171 | 10.0439 | 9.8698 | 9.6925 | 9.5349 | 9.3639 | 9.142 | 8.9442 | 7.1361 | 3.0758 | -0.36009 | -3.7687 | -6.8747 | 3.6349 | 3.469 | 3.1737 | 2.9271 | 2.6825 | 2.3946 | 2.0464 | 1.6414 | 1.4001 | 1.1612 | 0.48729 | -0.10465 | -0.80354 | -1.6391 | -2.3367 | 10.6149 | 10.449 | 10.1537 | 9.9071 | 9.6625 | 9.3746 | 9.0264 | 8.6214 | 8.3801 | 8.1412 | 7.4673 | 6.8753 | 6.1765 | 5.3409 | 4.7309 | 3.6349 | 3.4769 | 3.2279 | 3.0544 | 2.8821 | 2.7075 | 2.552 | 2.3854 | 2.2214 | 2.086 | 1.1482 | -2.5715 | -5.6926 | -8.7169 | -10.9976 | 10.6149 | 10.4569 | 10.2079 | 10.0344 | 9.8621 | 9.6875 | 9.532 | 9.3654 | 9.2014 | 9.066 | 8.1282 | 4.4085 | 1.2874 | -1.7369 | -4.4782 | 3.6349 | 3.66 | 3.5142 | 3.3514 | 3.267 | 3.148 | 2.9362 | 1.7374 | 0.39309 | -0.94375 | -4.7245 | -8.2368 | -11.0268 | -12.4876 | -10.3604 | 10.6149 | 10.64 | 10.4942 | 10.3314 | 10.247 | 10.128 | 9.9162 | 8.7174 | 7.3731 | 6.0363 | 2.2555 | -1.2568 | -4.0468 | -5.5076 | -3.8495 | 3.6349 | 3.5353 | 3.3313 | 3.2196 | 3.1479 | 3.044 | 2.9002 | 2.7228 | 2.4815 | 2.2443 | 1.4923 | 0.33998 | -0.51466 | -1.277 | -1.2706 | 10.6149 | 10.5153 | 10.3113 | 10.1996 | 10.1279 | 10.024 | 9.8802 | 9.7028 | 9.4615 | 9.2243 | 8.4723 | 7.32 | 6.4653 | 5.703 | 5.5815 | 3.6349 | 3.5665 | 3.3201 | 3.046 | 2.8585 | 2.6764 | 2.3945 | 0.97498 | -0.46425 | -1.8946 | -5.9535 | -9.7212 | -12.7753 | -14.5893 | -12.862 | 10.6149 | 10.5465 | 10.3001 | 10.026 | 9.8385 | 9.6564 | 9.3745 | 7.955 | 6.5158 | 5.0854 | 1.0265 | -2.7412 | -5.7953 | -7.6093 | -6.2627 | 321558 | 477806 | ULVERSTON | HARKER
| Askerton Castle | 0.92661 | 0.90895 | 0.87067 | 0.83116 | 0.78935 | 0.73665 | 0.67767 | 0.60558 | 0.53942 | 0.47756 | 0.29478 | 0.11723 | -0.0012506 | -0.076918 | -0.10531 | 1.6266 | 1.6089 | 1.5707 | 1.5312 | 1.4893 | 1.4367 | 1.3777 | 1.3056 | 1.2394 | 1.1776 | 0.99478 | 0.81723 | 0.69875 | 0.62308 | 0.59152 | 0.92661 | 0.91896 | 0.89791 | 0.88039 | 0.85914 | 0.78608 | 0.70085 | 0.60512 | 0.55407 | 0.50242 | 0.35554 | 0.23528 | 0.14538 | 0.076541 | 0.052941 | 1.6266 | 1.619 | 1.5979 | 1.5804 | 1.5591 | 1.4861 | 1.4009 | 1.3051 | 1.2541 | 1.2024 | 1.0555 | 0.93528 | 0.84538 | 0.77654 | 0.75438 | 0.92661 | 0.90524 | 0.862 | 0.81503 | 0.76415 | 0.69968 | 0.62637 | 0.53609 | 0.46226 | 0.39338 | 0.19074 | -0.0042201 | -0.13048 | -0.20386 | -0.21827 | 1.6266 | 1.6052 | 1.562 | 1.515 | 1.4641 | 1.3997 | 1.3264 | 1.2361 | 1.1623 | 1.0934 | 0.89074 | 0.69578 | 0.56952 | 0.49614 | 0.47547 | 0.92661 | 0.91954 | 0.89256 | 0.86617 | 0.83535 | 0.77972 | 0.71131 | 0.63457 | 0.57007 | 0.50805 | 0.3231 | 0.13392 | 0.01346 | -0.055276 | -0.033704 | 1.6266 | 1.6195 | 1.5926 | 1.5662 | 1.5354 | 1.4797 | 1.4113 | 1.3346 | 1.2701 | 1.208 | 1.0231 | 0.83392 | 0.71346 | 0.64472 | 0.65696 | 0.92661 | 0.91268 | 0.88364 | 0.85849 | 0.83292 | 0.79098 | 0.73362 | 0.67107 | 0.61318 | 0.55645 | 0.37951 | 0.19642 | 0.071388 | -0.025312 | -0.053698 | 1.6266 | 1.6127 | 1.5836 | 1.5585 | 1.5329 | 1.491 | 1.4336 | 1.3711 | 1.3132 | 1.2564 | 1.0795 | 0.89642 | 0.77139 | 0.67469 | 0.64452 | 0.92661 | 0.91018 | 0.87183 | 0.8316 | 0.7862 | 0.7327 | 0.6715 | 0.59246 | 0.52335 | 0.45813 | 0.277 | 0.11765 | 0.0066425 | -0.046267 | -0.00812 | 1.6266 | 1.6102 | 1.5718 | 1.5316 | 1.4862 | 1.4327 | 1.3715 | 1.2925 | 1.2233 | 1.1581 | 0.977 | 0.81765 | 0.70664 | 0.65373 | 0.68193 | 354779 | 568913 | - | HARKER
| Aspatria | 5.5882 | 5.3175 | 5.2314 | 5.1825 | 5.0623 | 4.9269 | 4.8073 | 4.692 | 4.5602 | 4.4473 | 3.5488 | 1.8562 | 0.25626 | -1.305 | -2.7412 | 7.5882 | 7.3175 | 7.2314 | 7.1825 | 7.0623 | 6.9269 | 6.8073 | 6.692 | 6.5602 | 6.4473 | 5.5488 | 3.8562 | 2.2563 | 0.69501 | -0.85361 | 5.5882 | 5.4533 | 5.3416 | 5.2206 | 5.067 | 4.9112 | 4.713 | 4.4054 | 4.2822 | 4.1598 | 3.7206 | 3.2568 | 2.8142 | 2.2711 | 1.7794 | 7.5882 | 7.4533 | 7.3416 | 7.2206 | 7.067 | 6.9112 | 6.713 | 6.4054 | 6.2822 | 6.1598 | 5.7206 | 5.2568 | 4.8142 | 4.2711 | 3.8655 | 5.5882 | 5.301 | 5.2234 | 5.1978 | 5.1027 | 4.9976 | 4.9222 | 4.8028 | 4.6899 | 4.5923 | 3.9068 | 2.398 | 0.88771 | -0.56628 | -1.8605 | 7.5882 | 7.301 | 7.2234 | 7.1978 | 7.1027 | 6.9976 | 6.9222 | 6.8028 | 6.6899 | 6.5923 | 5.9068 | 4.398 | 2.8877 | 1.4337 | 0.0031922 | 5.5882 | 5.528 | 5.5028 | 5.4628 | 5.3719 | 5.2681 | 5.0891 | 4.6128 | 4.1015 | 3.5901 | 1.8646 | 0.15657 | -1.1581 | -1.8898 | -1.2774 | 7.5882 | 7.528 | 7.5028 | 7.4628 | 7.3719 | 7.2681 | 7.0891 | 6.6128 | 6.1015 | 5.5901 | 3.8646 | 2.1566 | 0.84187 | 0.11018 | 0.58185 | 5.5882 | 5.4898 | 5.4415 | 5.4106 | 5.36 | 5.3095 | 5.2404 | 5.1353 | 4.9869 | 4.8373 | 4.2471 | 3.5251 | 3.0282 | 2.4554 | 2.1821 | 7.5882 | 7.4898 | 7.4415 | 7.4106 | 7.36 | 7.3095 | 7.2404 | 7.1353 | 6.9869 | 6.8373 | 6.2471 | 5.5251 | 5.0282 | 4.4554 | 4.1577 | 5.5882 | 5.4042 | 5.3143 | 5.218 | 5.0735 | 4.9287 | 4.7011 | 4.1634 | 3.6186 | 3.0729 | 1.2302 | -0.60896 | -2.0493 | -2.9294 | -2.4751 | 7.5882 | 7.4042 | 7.3143 | 7.218 | 7.0735 | 6.9287 | 6.7011 | 6.1634 | 5.6186 | 5.0729 | 3.2302 | 1.391 | -0.04931 | -0.92942 | -0.5814 | 314417 | 542840 | STAINBURN & SIDDICK | HARKER
| Atherton Town Centre | 8.6786 | 7.5283 | 7.1984 | 7.0375 | 6.4359 | 5.7879 | 5.168 | 4.5878 | 3.8634 | 3.054 | -1.3115 | -8.0167 | -13.4866 | -19.1396 | -24.3225 | 20.4386 | 19.2883 | 18.9584 | 18.7975 | 18.1959 | 17.5479 | 16.928 | 16.3478 | 15.6234 | 14.814 | 10.4485 | 3.7433 | -1.7266 | -7.3796 | -12.8754 | 8.6786 | 8.1448 | 7.9043 | 7.6922 | 7.3533 | 6.9535 | 6.3977 | 5.6579 | 5.1106 | 4.5484 | 2.3847 | 0.076853 | -2.0861 | -4.3189 | -5.7239 | 20.4386 | 19.9048 | 19.6643 | 19.4522 | 19.1133 | 18.7135 | 18.1577 | 17.4179 | 16.8706 | 16.3084 | 14.1447 | 11.8369 | 9.6739 | 7.4411 | 6.2484 | 8.6786 | 7.4132 | 7.1045 | 7.0261 | 6.0354 | 5.0177 | 4.0209 | 3.0759 | 2.0976 | 1.1564 | -3.2185 | -9.7258 | -15.0512 | -20.3327 | -24.7733 | 20.4386 | 19.1732 | 18.8645 | 18.7861 | 17.7954 | 16.7777 | 15.7809 | 14.8359 | 13.8576 | 12.9164 | 8.5415 | 2.0342 | -3.2912 | -8.5727 | -13.3298 | 8.6786 | 8.414 | 8.3581 | 8.359 | 7.382 | 6.3289 | 4.878 | 2.1578 | -0.64109 | -3.2817 | -10.0177 | -16.0372 | -20.9173 | -24.0175 | -22.218 | 20.4386 | 20.174 | 20.1181 | 20.119 | 19.142 | 18.0889 | 16.638 | 13.9178 | 11.1189 | 8.4783 | 1.7423 | -4.2772 | -9.1573 | -12.2575 | -10.8593 | 8.6786 | 7.9624 | 7.7939 | 7.7974 | 7.5334 | 7.1919 | 6.7697 | 6.2973 | 5.6795 | 4.9442 | 2.3776 | -0.33639 | -2.2213 | -3.8486 | -4.6308 | 20.4386 | 19.7224 | 19.5539 | 19.5574 | 19.2934 | 18.9519 | 18.5297 | 18.0573 | 17.4395 | 16.7042 | 14.1376 | 11.4236 | 9.5387 | 7.9114 | 7.1714 | 8.6786 | 7.8284 | 7.5078 | 7.3172 | 6.1656 | 4.9928 | 3.3926 | 0.47947 | -2.4465 | -5.2172 | -12.5298 | -19.0714 | -24.4514 | -28.1272 | -26.9449 | 20.4386 | 19.5884 | 19.2678 | 19.0772 | 17.9256 | 16.7528 | 15.1526 | 12.2395 | 9.3135 | 6.5428 | -0.76975 | -7.3114 | -12.6914 | -16.3672 | -15.4507 | 367546 | 403338 | ATHERTON | KEARSLEY
| Athletic St | 6.5085 | 4.9905 | 4.687 | 4.6331 | 4.4825 | 4.3032 | 4.0433 | 3.7909 | 3.4889 | 3.2187 | 1.5223 | -1.32 | -3.6573 | -5.9676 | -7.8309 | 10.0085 | 8.4905 | 8.187 | 8.1331 | 7.9825 | 7.8032 | 7.5433 | 7.2909 | 6.9889 | 6.7187 | 5.0223 | 2.18 | -0.1573 | -2.4676 | -4.5105 | 6.5085 | 5.9309 | 5.7626 | 5.6728 | 5.5384 | 5.3855 | 5.1797 | 4.9235 | 4.5979 | 4.2677 | 3.2946 | 2.4081 | 1.6261 | 0.87772 | 0.43529 | 10.0085 | 9.4309 | 9.2626 | 9.1728 | 9.0384 | 8.8855 | 8.6797 | 8.4235 | 8.0979 | 7.7677 | 6.7946 | 5.9081 | 5.1261 | 4.3777 | 3.9974 | 6.5085 | 4.7682 | 4.4458 | 4.4287 | 4.3181 | 4.1924 | 3.9935 | 3.8081 | 3.5912 | 3.3888 | 1.8888 | -0.79482 | -2.9964 | -5.1433 | -6.8185 | 10.0085 | 8.2682 | 7.9458 | 7.9287 | 7.8181 | 7.6924 | 7.4935 | 7.3081 | 7.0912 | 6.8888 | 5.3888 | 2.7052 | 0.50364 | -1.6433 | -3.5343 | 6.5085 | 5.5304 | 5.3695 | 5.3795 | 5.2706 | 5.1291 | 4.7828 | 3.8979 | 2.9746 | 2.0602 | -0.58325 | -3.117 | -5.1262 | -6.3153 | -5.3181 | 10.0085 | 9.0304 | 8.8695 | 8.8795 | 8.7706 | 8.6291 | 8.2828 | 7.3979 | 6.4746 | 5.5602 | 2.9167 | 0.38296 | -1.6262 | -2.8153 | -2.0423 | 6.5085 | 5.4945 | 5.3127 | 5.3307 | 5.324 | 5.289 | 5.1541 | 4.9496 | 4.6698 | 4.3941 | 3.4527 | 2.4274 | 1.7165 | 1.1185 | 0.96025 | 10.0085 | 8.9945 | 8.8127 | 8.8307 | 8.824 | 8.789 | 8.6541 | 8.4496 | 8.1698 | 7.8941 | 6.9527 | 5.9274 | 5.2165 | 4.6185 | 4.4341 | 6.5085 | 4.7579 | 4.3973 | 4.3222 | 4.1355 | 3.9006 | 3.4541 | 2.4659 | 1.4528 | 0.45293 | -2.4252 | -5.1261 | -7.3043 | -8.6964 | -7.9554 | 10.0085 | 8.2579 | 7.8973 | 7.8222 | 7.6355 | 7.4006 | 6.9541 | 5.9659 | 4.9528 | 3.9529 | 1.0748 | -1.6261 | -3.8043 | -5.1964 | -4.618 | 385381 | 432208 | BURNLEY | ROCHDALE
| Avenham | 13.786 | 13.2738 | 12.8727 | 12.2874 | 11.7009 | 11.1147 | 10.535 | 10.107 | 9.6639 | 9.2335 | 7.7233 | 5.9625 | 4.7481 | 4.0879 | 3.6469 | 18.386 | 17.8738 | 17.4727 | 16.8874 | 16.3009 | 15.7147 | 15.135 | 14.707 | 14.2639 | 13.8335 | 12.3233 | 10.5625 | 9.3481 | 8.6879 | 8.1912 | 13.786 | 13.5611 | 13.2918 | 13.0328 | 12.7649 | 12.4834 | 12.086 | 11.6212 | 11.4551 | 11.2896 | 10.8258 | 10.4051 | 10.0673 | 9.7096 | 9.4162 | 18.386 | 18.1611 | 17.8918 | 17.6328 | 17.3649 | 17.0834 | 16.686 | 16.2212 | 16.0551 | 15.8896 | 15.4258 | 15.0051 | 14.6673 | 14.3096 | 14.0562 | 13.786 | 13.1979 | 12.7525 | 12.1229 | 11.4902 | 10.8548 | 10.2208 | 9.7347 | 9.2577 | 8.7924 | 7.1843 | 5.4595 | 4.3656 | 3.9267 | 3.7943 | 18.386 | 17.7979 | 17.3525 | 16.7229 | 16.0902 | 15.4548 | 14.8208 | 14.3347 | 13.8577 | 13.3924 | 11.7843 | 10.0595 | 8.9656 | 8.5267 | 8.3312 | 13.786 | 13.3652 | 12.991 | 12.414 | 11.8294 | 11.2261 | 10.5757 | 9.9452 | 9.2939 | 8.6635 | 6.8706 | 5.279 | 4.3196 | 4.1198 | 4.3858 | 18.386 | 17.9652 | 17.591 | 17.014 | 16.4294 | 15.8261 | 15.1757 | 14.5452 | 13.8939 | 13.2635 | 11.4706 | 9.879 | 8.9196 | 8.7198 | 8.9158 | 13.786 | 13.4544 | 13.1028 | 12.5511 | 12.0146 | 11.4725 | 10.9185 | 10.5052 | 10.0626 | 9.6226 | 8.3046 | 7.0143 | 6.1677 | 5.832 | 5.694 | 18.386 | 18.0544 | 17.7028 | 17.1511 | 16.6146 | 16.0725 | 15.5185 | 15.1052 | 14.6626 | 14.2226 | 12.9046 | 11.6143 | 10.7677 | 10.432 | 10.2977 | 13.786 | 13.224 | 12.7786 | 12.1398 | 11.4971 | 10.8555 | 10.1691 | 9.4816 | 8.8095 | 8.1606 | 6.3277 | 4.7199 | 3.7419 | 3.5329 | 3.7426 | 18.386 | 17.824 | 17.3786 | 16.7398 | 16.0971 | 15.4555 | 14.7691 | 14.0816 | 13.4095 | 12.7606 | 10.9277 | 9.3199 | 8.3419 | 8.1329 | 8.288 | 354028 | 429192 | PRESTON EAST | PENWORTHAM
| Baguley | 6.5185 | 6.3165 | 6.0828 | 5.8083 | 5.3264 | 9.7901 | 9.1725 | 8.5786 | 7.7677 | 6.9534 | 4.0092 | 0.39789 | -2.178 | -4.2309 | -5.6821 | 11.1555 | 10.9535 | 10.7198 | 10.4453 | 9.9634 | 14.4271 | 13.8095 | 13.2156 | 12.4047 | 11.5904 | 8.6462 | 5.0349 | 2.459 | 0.40605 | -1.2081 | 6.5185 | 6.384 | 6.2631 | 6.133 | 5.939 | 10.7075 | 10.3585 | 9.9333 | 9.5187 | 9.0478 | 7.5136 | 5.751 | 4.0964 | 2.4262 | 1.4053 | 11.1555 | 11.021 | 10.9001 | 10.77 | 10.576 | 15.3445 | 14.9955 | 14.5703 | 14.1557 | 13.6848 | 12.1506 | 10.388 | 8.7334 | 7.0632 | 6.1797 | 6.5185 | 6.2499 | 5.946 | 5.6213 | 5.0909 | 9.5145 | 8.7063 | 7.9218 | 6.9316 | 5.9014 | 2.3862 | -1.2964 | -3.7412 | -5.5421 | -6.8712 | 11.1555 | 10.8869 | 10.583 | 10.2583 | 9.7279 | 14.1515 | 13.3433 | 12.5588 | 11.5686 | 10.5384 | 7.0232 | 3.3406 | 0.89583 | -0.90512 | -2.1979 | 6.5185 | 6.6561 | 6.4499 | 6.1467 | 5.6181 | 9.9883 | 8.9635 | 7.4553 | 5.9113 | 4.3768 | 0.40818 | -2.7017 | -4.552 | -5.2513 | -4.7341 | 11.1555 | 11.2931 | 11.0869 | 10.7837 | 10.2551 | 14.6253 | 13.6005 | 12.0923 | 10.5483 | 9.0138 | 5.0452 | 1.9353 | 0.084978 | -0.61434 | -0.10328 | 6.5185 | 6.3475 | 6.1677 | 6.023 | 5.8211 | 10.533 | 10.1132 | 9.6446 | 9.0449 | 8.28 | 6.047 | 3.8502 | 2.3107 | 1.0137 | 0.35534 | 11.1555 | 10.9845 | 10.8047 | 10.66 | 10.4581 | 15.17 | 14.7502 | 14.2816 | 13.6819 | 12.917 | 10.684 | 8.4872 | 6.9477 | 5.6507 | 5.0706 | 6.5185 | 6.593 | 6.2973 | 5.8895 | 5.2516 | 9.5761 | 8.4941 | 6.9044 | 5.3044 | 3.6962 | -0.53904 | -3.9348 | -6.0609 | -6.9929 | -6.4644 | 11.1555 | 11.23 | 10.9343 | 10.5265 | 9.8886 | 14.2131 | 13.1311 | 11.5414 | 9.9414 | 8.3332 | 4.098 | 0.70218 | -1.4239 | -2.3559 | -1.9654 | 380562 | 389035 | SALE | CARRINGTON
| Bamber Bridge | 10.3863 | 8.8882 | 7.2493 | 6.4746 | 5.6466 | 4.796 | 3.9222 | 3.0111 | 2.0226 | 1.6323 | -0.66155 | -4.0357 | -6.5991 | -9.0767 | -11.0932 | 14.5233 | 13.0252 | 11.3863 | 10.6116 | 9.7836 | 8.933 | 8.0592 | 7.1481 | 6.1596 | 5.7693 | 3.4754 | 0.10127 | -2.4621 | -4.9397 | -7.0487 | 10.3863 | 9.7073 | 9.4558 | 9.3306 | 9.1933 | 9.041 | 8.8097 | 8.4802 | 8.1906 | 7.766 | 6.2688 | 4.5973 | 2.9383 | 1.1758 | 0.060237 | 14.5233 | 13.8443 | 13.5928 | 13.4676 | 13.3303 | 13.178 | 12.9467 | 12.6172 | 12.3276 | 11.903 | 10.4058 | 8.7343 | 7.0753 | 5.3128 | 4.3561 | 10.3863 | 8.659 | 6.9817 | 6.209 | 5.3873 | 4.548 | 3.69 | 2.8048 | 1.8783 | 1.5516 | -0.21424 | -3.479 | -6.0863 | -8.5112 | -10.3294 | 14.5233 | 12.796 | 11.1187 | 10.346 | 9.5243 | 8.685 | 7.827 | 6.9418 | 6.0153 | 5.6886 | 3.9228 | 0.65796 | -1.9493 | -4.3742 | -6.3045 | 10.3863 | 9.324 | 7.7981 | 7.065 | 6.2627 | 5.4106 | 4.3958 | 2.9515 | 1.4487 | 0.54244 | -2.2312 | -5.3466 | -7.6271 | -9.1302 | -8.6478 | 14.5233 | 13.461 | 11.9351 | 11.202 | 10.3997 | 9.5476 | 8.5328 | 7.0885 | 5.5857 | 4.6794 | 1.9058 | -1.2096 | -3.4901 | -4.9932 | -4.6334 | 10.3863 | 9.152 | 7.591 | 6.8788 | 6.1569 | 5.3919 | 4.5727 | 3.7172 | 2.767 | 2.4023 | 1.0873 | -0.80952 | -2.0825 | -3.0425 | -3.4831 | 14.5233 | 13.289 | 11.728 | 11.0158 | 10.2939 | 9.5289 | 8.7097 | 7.8542 | 6.904 | 6.5393 | 5.2243 | 3.3275 | 2.0545 | 1.0945 | 0.68255 | 10.3863 | 8.6061 | 6.9069 | 6.1118 | 5.2598 | 4.3974 | 3.3865 | 1.9218 | 0.415 | -0.49362 | -3.562 | -6.9396 | -9.496 | -11.302 | -10.9688 | 14.5233 | 12.7431 | 11.0439 | 10.2488 | 9.3968 | 8.5344 | 7.5235 | 6.0588 | 4.552 | 3.6434 | 0.57498 | -2.8026 | -5.359 | -7.165 | -6.9229 | 356431 | 426698 | RIBBLE | PENWORTHAM
| Barbara St | 3.1163 | 1.5225 | 1.0093 | 0.77734 | 0.44216 | 0.080841 | -0.2696 | -0.6152 | -1.011 | -1.4009 | -3.4678 | -6.4245 | -8.6341 | -10.5085 | -11.6359 | 10.0163 | 8.4225 | 7.9093 | 7.6773 | 7.3422 | 6.9808 | 6.6304 | 6.2848 | 5.889 | 5.4991 | 3.4322 | 0.47546 | -1.7341 | -3.6085 | -4.9669 | 3.1163 | 2.5863 | 2.3637 | 2.2315 | 2.0542 | 1.8418 | 1.5711 | 1.2529 | 0.97275 | 0.67152 | -0.26953 | -1.2235 | -2.1404 | -3.068 | -3.6688 | 10.0163 | 9.4863 | 9.2637 | 9.1315 | 8.9542 | 8.7418 | 8.4711 | 8.1529 | 7.8727 | 7.5715 | 6.6305 | 5.6765 | 4.7596 | 3.832 | 3.3161 | 3.1163 | 1.1993 | 0.54191 | 0.21675 | -0.22012 | -0.68627 | -1.1315 | -1.5833 | -2.0548 | -2.5537 | -4.9405 | -7.9065 | -9.8695 | -11.2094 | -11.4019 | 10.0163 | 8.0993 | 7.4419 | 7.1168 | 6.6799 | 6.2137 | 5.7685 | 5.3167 | 4.8452 | 4.3463 | 1.9595 | -1.0065 | -2.9695 | -4.3094 | -4.7514 | 3.1163 | 1.947 | 1.4884 | 1.2275 | 0.82406 | 0.34713 | -0.27947 | -1.3919 | -2.4975 | -3.5873 | -6.6427 | -9.1006 | -10.5477 | -10.9281 | -9.7607 | 10.0163 | 8.847 | 8.3884 | 8.1275 | 7.7241 | 7.2471 | 6.6205 | 5.5081 | 4.4025 | 3.3127 | 0.25725 | -2.2006 | -3.6477 | -4.0281 | -3.1183 | 3.1163 | 2.1239 | 1.7847 | 1.6577 | 1.507 | 1.2974 | 1.0334 | 0.73328 | 0.35121 | -0.051857 | -1.4249 | -2.7854 | -3.7239 | -4.4989 | -4.7689 | 10.0163 | 9.0239 | 8.6847 | 8.5577 | 8.407 | 8.1974 | 7.9334 | 7.6333 | 7.2512 | 6.8481 | 5.4751 | 4.1146 | 3.1761 | 2.4011 | 2.131 | 3.1163 | 1.176 | 0.4782 | 0.10938 | -0.38626 | -0.90627 | -1.8789 | -3.3704 | -4.8318 | -6.2769 | -10.4301 | -13.9836 | -15.6315 | -16.2254 | -15.3115 | 10.0163 | 8.076 | 7.3782 | 7.0094 | 6.5137 | 5.9937 | 5.0211 | 3.5296 | 2.0682 | 0.62305 | -3.5301 | -7.0836 | -8.7315 | -9.3254 | -8.6107 | 370695 | 407609 | BOLTON | KEARSLEY
| Barrow | 10.423 | 10.3152 | 10.1347 | 9.979 | 9.7616 | 9.5541 | 9.4071 | 9.2966 | 9.1245 | 8.9778 | 7.2023 | 3.6788 | 0.63256 | -2.5589 | -5.053 | 10.423 | 10.3152 | 10.1347 | 9.979 | 9.7616 | 9.5541 | 9.4071 | 9.2966 | 9.1245 | 8.9778 | 7.2023 | 3.6788 | 0.63256 | -2.5589 | -5.3728 | 10.423 | 10.3017 | 10.1207 | 9.9562 | 9.7712 | 9.5745 | 9.332 | 9.0551 | 8.8132 | 8.5681 | 7.8634 | 7.2374 | 6.6546 | 6.0757 | 5.7008 | 10.423 | 10.3017 | 10.1207 | 9.9562 | 9.7712 | 9.5745 | 9.332 | 9.0551 | 8.8132 | 8.5681 | 7.8634 | 7.2374 | 6.6546 | 6.0757 | 5.7515 | 10.423 | 10.3397 | 10.1872 | 10.0802 | 9.9124 | 9.7625 | 9.6907 | 9.6674 | 9.6083 | 9.5502 | 8.0387 | 4.7643 | 1.9558 | -0.9506 | -3.1537 | 10.423 | 10.3397 | 10.1872 | 10.0802 | 9.9124 | 9.7625 | 9.6907 | 9.6674 | 9.6083 | 9.5502 | 8.0387 | 4.7643 | 1.9558 | -0.9506 | -3.528 | 10.423 | 10.4961 | 10.4091 | 10.315 | 10.1428 | 9.9553 | 9.5781 | 8.4487 | 7.2726 | 6.1021 | 2.7741 | -0.31725 | -2.8741 | -4.3773 | -2.6474 | 10.423 | 10.4961 | 10.4091 | 10.315 | 10.1428 | 9.9553 | 9.5781 | 8.4487 | 7.2726 | 6.1021 | 2.7741 | -0.31725 | -2.8741 | -4.3773 | -3.0237 | 10.423 | 10.3397 | 10.2056 | 10.1299 | 10.0709 | 9.9988 | 9.921 | 9.8463 | 9.6836 | 9.5231 | 8.9479 | 8.2849 | 7.7593 | 7.1657 | 6.8652 | 10.423 | 10.3397 | 10.2056 | 10.1299 | 10.0709 | 9.9988 | 9.921 | 9.8463 | 9.6836 | 9.5231 | 8.9479 | 8.2849 | 7.7593 | 7.1657 | 6.9159 | 10.423 | 10.4341 | 10.2577 | 10.0616 | 9.7966 | 9.5467 | 9.0989 | 7.8624 | 6.6058 | 5.3557 | 1.7858 | -1.5437 | -4.393 | -6.2478 | -4.9041 | 10.423 | 10.4341 | 10.2577 | 10.0616 | 9.7966 | 9.5467 | 9.0989 | 7.8624 | 6.6058 | 5.3557 | 1.7858 | -1.5437 | -4.393 | -6.2478 | -5.1956 | 319709 | 470489 | BARROW & SANDGATE | HARKER
| Barton Dock Rd | 3.5271 | 3.1396 | 2.8612 | 2.6026 | 2.3425 | 2.0589 | 1.7495 | 1.4015 | 0.95556 | -0.49572 | -2.9949 | -5.0189 | -6.4352 | -7.9333 | -9.2261 | 9.8271 | 9.4396 | 9.1612 | 8.9026 | 8.6425 | 8.3589 | 8.0495 | 7.7015 | 7.2556 | 5.8043 | 3.3051 | 1.2811 | -0.13525 | -1.6333 | -2.8344 | 3.5271 | 3.4383 | 3.2961 | 3.1966 | 3.1157 | 3.0208 | 2.8942 | 2.7253 | 2.4953 | 2.2506 | 0.53293 | -0.59893 | -1.5393 | -2.9182 | -3.9032 | 9.8271 | 9.7383 | 9.5961 | 9.4966 | 9.4157 | 9.3208 | 9.1942 | 9.0253 | 8.7953 | 8.5506 | 6.8329 | 5.7011 | 4.7607 | 3.3818 | 2.5353 | 3.5271 | 3.0975 | 2.8117 | 2.5555 | 2.3029 | 2.0325 | 1.7434 | 1.4257 | 1.0476 | -0.32011 | -2.8642 | -5.4952 | -6.8669 | -8.2429 | -9.252 | 9.8271 | 9.3975 | 9.1117 | 8.8555 | 8.6029 | 8.3325 | 8.0434 | 7.7257 | 7.3476 | 5.9799 | 3.4358 | 0.80482 | -0.56686 | -1.9429 | -2.9163 | 3.5271 | 3.2425 | 3.0017 | 2.7615 | 2.5156 | 1.999 | 0.61254 | -0.92843 | -2.3763 | -2.8873 | -4.5943 | -6.25 | -7.4744 | -8.5134 | -8.7694 | 9.8271 | 9.5425 | 9.3017 | 9.0615 | 8.8156 | 8.299 | 6.9125 | 5.3716 | 3.9237 | 3.4127 | 1.7057 | 0.049999 | -1.1744 | -2.2134 | -2.4388 | 3.5271 | 3.3572 | 3.1375 | 2.9087 | 2.6954 | 2.4537 | 2.1819 | 1.8799 | 1.4771 | 0.065281 | -2.1707 | -3.7211 | -4.7435 | -5.7605 | -6.4828 | 9.8271 | 9.6572 | 9.4375 | 9.2087 | 8.9954 | 8.7537 | 8.4819 | 8.1799 | 7.7771 | 6.3653 | 4.1293 | 2.5789 | 1.5565 | 0.53946 | -0.06868 | 3.5271 | 3.1016 | 2.8117 | 2.5462 | 2.283 | 1.77 | 0.40119 | -1.1173 | -2.5294 | -3.0158 | -4.7258 | -6.4874 | -7.8307 | -8.9533 | -9.2585 | 9.8271 | 9.4016 | 9.1117 | 8.8462 | 8.583 | 8.07 | 6.7012 | 5.1827 | 3.7706 | 3.2842 | 1.5742 | -0.18735 | -1.5307 | -2.6533 | -2.9169 | 378864 | 395534 | BARTON | CARRINGTON
| Bedford | 5.8188 | 5.4262 | 5.099 | 4.8258 | 4.4614 | 4.0701 | 3.625 | 3.1649 | 2.6335 | 2.1091 | -0.40889 | -4.5261 | -8.1497 | -11.985 | -15.367 | 10.3188 | 9.9262 | 9.599 | 9.3258 | 8.9614 | 8.5701 | 8.125 | 7.6649 | 7.1335 | 6.6091 | 4.0911 | -0.026105 | -3.6497 | -7.485 | -10.9981 | 5.8188 | 5.6173 | 5.3927 | 5.1311 | 4.7938 | 4.4188 | 3.9255 | 3.265 | 2.7777 | 2.284 | 0.75172 | -0.88934 | -2.4998 | -4.356 | -5.6886 | 10.3188 | 10.1173 | 9.8927 | 9.6311 | 9.2938 | 8.9188 | 8.4255 | 7.765 | 7.2777 | 6.784 | 5.2517 | 3.6107 | 2.0002 | 0.14399 | -0.98639 | 5.8188 | 5.3944 | 5.0611 | 4.788 | 4.4264 | 4.0405 | 3.601 | 3.1535 | 2.6894 | 2.2459 | -0.12754 | -3.8744 | -6.8839 | -10.2206 | -13.2679 | 10.3188 | 9.8944 | 9.5611 | 9.288 | 8.9264 | 8.5405 | 8.101 | 7.6535 | 7.1894 | 6.7459 | 4.3725 | 0.62556 | -2.3839 | -5.7206 | -8.9535 | 5.8188 | 5.7479 | 5.5373 | 5.3346 | 5.0236 | 4.6447 | 3.9913 | 2.6992 | 1.3661 | 0.050023 | -3.693 | -7.5043 | -10.5059 | -12.5168 | -11.6971 | 10.3188 | 10.2479 | 10.0373 | 9.8346 | 9.5236 | 9.1447 | 8.4913 | 7.1992 | 5.8661 | 4.55 | 0.80704 | -3.0043 | -6.0059 | -8.0168 | -7.3949 | 5.8188 | 5.6008 | 5.3525 | 5.1702 | 4.9725 | 4.726 | 4.364 | 3.9484 | 3.4231 | 2.8877 | 1.1836 | -0.62867 | -1.9463 | -3.4921 | -4.3 | 10.3188 | 10.1008 | 9.8525 | 9.6702 | 9.4725 | 9.226 | 8.864 | 8.4484 | 7.9231 | 7.3877 | 5.6836 | 3.8713 | 2.5537 | 1.0079 | 0.27899 | 5.8188 | 5.5999 | 5.2852 | 4.9835 | 4.5887 | 4.1815 | 3.5143 | 2.1627 | 0.78387 | -0.71008 | -4.9854 | -9.1068 | -12.5495 | -15.0522 | -14.6379 | 10.3188 | 10.0999 | 9.7852 | 9.4835 | 9.0887 | 8.6815 | 8.0143 | 6.6627 | 5.2839 | 3.7899 | -0.48538 | -4.6068 | -8.0495 | -10.5522 | -10.2473 | 366258 | 399876 | ATHERTON | KEARSLEY
| Belgrave | 8.4794 | 8.0734 | 7.8997 | 7.7459 | 7.4521 | 7.1339 | 6.8363 | 6.5861 | 6.3602 | 6.1511 | 4.6464 | 2.122 | 0.13149 | -1.6663 | -3.0809 | 11.9794 | 11.5734 | 11.3997 | 11.2459 | 10.9521 | 10.6339 | 10.3363 | 10.0861 | 9.8602 | 9.6511 | 8.1464 | 5.622 | 3.6315 | 1.8337 | 0.2719 | 8.4794 | 8.3104 | 8.217 | 8.1252 | 7.9867 | 7.8277 | 7.6135 | 7.3318 | 7.1457 | 6.9503 | 6.341 | 5.6876 | 5.0013 | 4.2025 | 3.5613 | 11.9794 | 11.8104 | 11.717 | 11.6252 | 11.4867 | 11.3277 | 11.1135 | 10.8318 | 10.6457 | 10.4503 | 9.841 | 9.1876 | 8.5013 | 7.7025 | 7.1748 | 8.4794 | 7.9608 | 7.7016 | 7.4677 | 7.0319 | 6.5689 | 6.1332 | 5.7284 | 5.3443 | 4.9621 | 3.1716 | 0.66947 | -1.0504 | -2.3913 | -3.0783 | 11.9794 | 11.4608 | 11.2016 | 10.9677 | 10.5319 | 10.0689 | 9.6332 | 9.2284 | 8.8443 | 8.4621 | 6.6716 | 4.1695 | 2.4496 | 1.1087 | 0.32338 | 8.4794 | 8.312 | 8.1345 | 7.9131 | 7.4703 | 6.9909 | 6.3992 | 5.3876 | 4.4092 | 3.4694 | 1.0061 | -1.061 | -2.3313 | -2.737 | -2.0671 | 11.9794 | 11.812 | 11.6345 | 11.4131 | 10.9703 | 10.4909 | 9.8992 | 8.8876 | 7.9092 | 6.9694 | 4.5061 | 2.439 | 1.1687 | 0.763 | 1.3235 | 8.4794 | 8.2352 | 8.1179 | 8.0358 | 7.9123 | 7.7609 | 7.576 | 7.3627 | 7.1198 | 6.8717 | 5.9922 | 4.9441 | 4.1224 | 3.2991 | 2.7143 | 11.9794 | 11.7352 | 11.6179 | 11.5358 | 11.4123 | 11.2609 | 11.076 | 10.8627 | 10.6198 | 10.3717 | 9.4922 | 8.4441 | 7.6224 | 6.7991 | 6.2861 | 8.4794 | 8.1508 | 7.8918 | 7.6058 | 7.1029 | 6.5798 | 5.9312 | 4.8485 | 3.8223 | 2.8329 | 0.19528 | -2.0103 | -3.4212 | -4.0043 | -3.513 | 11.9794 | 11.6508 | 11.3918 | 11.1058 | 10.6029 | 10.0798 | 9.4312 | 8.3485 | 7.3223 | 6.3329 | 3.6953 | 1.4897 | 0.078775 | -0.5043 | -0.11533 | 393008 | 403366 | GREENHILL | WHITEGATE
| Benchill | 7.8493 | 7.5842 | 7.2128 | 6.8748 | 6.4826 | 6.0865 | 5.4648 | 4.8815 | 4.2978 | 3.725 | 2.9567 | 2.1039 | 1.4585 | 0.9724 | 0.56017 | 9.8493 | 9.5842 | 9.2128 | 8.8748 | 8.4826 | 8.0865 | 7.4648 | 6.8815 | 6.2978 | 5.725 | 4.9567 | 4.1039 | 3.4585 | 2.9724 | 2.4866 | 7.8493 | 7.796 | 7.6563 | 7.5276 | 7.3943 | 7.26 | 7.0292 | 6.7835 | 6.5355 | 6.2852 | 5.9586 | 5.7353 | 5.5255 | 5.3077 | 5.1523 | 9.8493 | 9.796 | 9.6563 | 9.5276 | 9.3943 | 9.26 | 9.0292 | 8.7835 | 8.5355 | 8.2852 | 7.9586 | 7.7353 | 7.5255 | 7.3077 | 7.1768 | 7.8493 | 7.5254 | 7.1213 | 6.7601 | 6.344 | 5.9242 | 5.2815 | 4.6724 | 4.0728 | 3.4721 | 2.6428 | 1.8576 | 1.3591 | 1.0844 | 1.0568 | 9.8493 | 9.5254 | 9.1213 | 8.7601 | 8.344 | 7.9242 | 7.2815 | 6.6724 | 6.0728 | 5.4721 | 4.6428 | 3.8576 | 3.3591 | 3.0844 | 2.9662 | 7.8493 | 7.6598 | 7.2903 | 6.9345 | 6.5172 | 6.089 | 5.3927 | 4.5744 | 3.7609 | 2.9573 | 1.8763 | 1.2336 | 0.8807 | 0.90756 | 1.3437 | 9.8493 | 9.6598 | 9.2903 | 8.9345 | 8.5172 | 8.089 | 7.3927 | 6.5744 | 5.7609 | 4.9573 | 3.8763 | 3.2336 | 2.8807 | 2.9076 | 3.252 | 7.8493 | 7.762 | 7.4382 | 7.1393 | 6.8414 | 6.5388 | 5.9855 | 5.4269 | 4.8387 | 4.25 | 3.6999 | 3.3997 | 3.1997 | 3.0208 | 2.9538 | 9.8493 | 9.762 | 9.4382 | 9.1393 | 8.8414 | 8.5388 | 7.9855 | 7.4269 | 6.8387 | 6.25 | 5.6999 | 5.3997 | 5.1997 | 5.0208 | 4.9516 | 7.8493 | 7.5402 | 7.1266 | 6.7444 | 6.3032 | 5.8591 | 5.1436 | 4.2978 | 3.4633 | 2.6391 | 1.4981 | 0.8076 | 0.41071 | 0.38836 | 0.76529 | 9.8493 | 9.5402 | 9.1266 | 8.7444 | 8.3032 | 7.8591 | 7.1436 | 6.2978 | 5.4633 | 4.6391 | 3.4981 | 2.8076 | 2.4107 | 2.3884 | 2.6865 | 382454 | 388020 | WEST DIDSBURY | SOUTH MANCHESTER
| Bentham | 2.0518 | 2.0046 | 1.9346 | 1.8834 | 1.8247 | 1.7628 | 1.7088 | 1.6549 | 1.5927 | 1.5383 | 1.2239 | 0.70129 | 0.0038811 | -0.7298 | -1.4033 | 6.5518 | 6.5046 | 6.4346 | 6.3834 | 6.3247 | 6.2628 | 6.2088 | 6.1549 | 6.0927 | 6.0383 | 5.7239 | 5.2013 | 4.5039 | 3.7702 | 3.0392 | 2.0518 | 1.9864 | 1.8881 | 1.8002 | 1.7131 | 1.618 | 1.5032 | 1.3632 | 1.2901 | 1.2187 | 1.0156 | 0.82772 | 0.65941 | 0.4643 | 0.30338 | 6.5518 | 6.4864 | 6.3881 | 6.3002 | 6.2131 | 6.118 | 6.0032 | 5.8632 | 5.7901 | 5.7187 | 5.5156 | 5.3277 | 5.1594 | 4.9643 | 4.8279 | 2.0518 | 2.0028 | 1.9325 | 1.8807 | 1.8219 | 1.7601 | 1.7057 | 1.6518 | 1.6056 | 1.5687 | 1.3095 | 0.84935 | 0.35889 | -0.28577 | -0.85178 | 6.5518 | 6.5028 | 6.4325 | 6.3807 | 6.3219 | 6.2601 | 6.2057 | 6.1518 | 6.1056 | 6.0687 | 5.8095 | 5.3494 | 4.8589 | 4.2142 | 3.5712 | 2.0518 | 2.062 | 2.0171 | 1.9782 | 1.938 | 1.8923 | 1.8226 | 1.6635 | 1.4902 | 1.3232 | 0.69094 | -0.077282 | -0.67159 | -0.98811 | -0.63885 | 6.5518 | 6.562 | 6.5171 | 6.4782 | 6.438 | 6.3923 | 6.3226 | 6.1635 | 5.9902 | 5.8232 | 5.1909 | 4.4227 | 3.8284 | 3.5119 | 3.7823 | 2.0518 | 2.0105 | 1.9458 | 1.9036 | 1.871 | 1.8363 | 1.7952 | 1.7439 | 1.6762 | 1.6102 | 1.394 | 1.1552 | 0.99646 | 0.85496 | 0.8345 | 6.5518 | 6.5105 | 6.4458 | 6.4036 | 6.371 | 6.3363 | 6.2952 | 6.2439 | 6.1762 | 6.1102 | 5.894 | 5.6552 | 5.4965 | 5.355 | 5.3173 | 2.0518 | 2.0396 | 1.9705 | 1.9051 | 1.839 | 1.7736 | 1.6848 | 1.4983 | 1.3163 | 1.1415 | 0.44067 | -0.37058 | -1.0098 | -1.3876 | -1.11 | 6.5518 | 6.5396 | 6.4705 | 6.4051 | 6.339 | 6.2736 | 6.1848 | 5.9983 | 5.8163 | 5.6415 | 4.9407 | 4.1294 | 3.4902 | 3.1124 | 3.327 | 366887 | 470130 | KENDAL (PARKSIDE RD) | HUTTON
| Bispham | 6.9752 | 6.1629 | 6.0005 | 5.9556 | 5.8065 | 5.6317 | 5.4629 | 5.3226 | 5.1887 | 5.055 | 3.2647 | -0.35978 | -3.4204 | -6.7674 | -9.7234 | 11.6122 | 10.7999 | 10.6375 | 10.5926 | 10.4435 | 10.2687 | 10.0999 | 9.9596 | 9.8257 | 9.692 | 7.9017 | 4.2772 | 1.2166 | -2.1304 | -5.3214 | 6.9752 | 6.7338 | 6.5774 | 6.3955 | 6.1207 | 5.8294 | 5.4447 | 4.9809 | 4.7669 | 4.5473 | 3.8746 | 3.1023 | 2.3536 | 1.5636 | 0.98646 | 11.6122 | 11.3708 | 11.2144 | 11.0325 | 10.7577 | 10.4664 | 10.0817 | 9.6179 | 9.4039 | 9.1843 | 8.5116 | 7.7393 | 6.9906 | 6.2006 | 5.7069 | 6.9752 | 6.0706 | 5.9189 | 5.9216 | 5.825 | 5.7113 | 5.6319 | 5.5833 | 5.5441 | 5.5312 | 4.0721 | 0.71282 | -2.1234 | -5.2556 | -7.9916 | 11.6122 | 10.7076 | 10.5559 | 10.5586 | 10.462 | 10.3483 | 10.2689 | 10.2203 | 10.1811 | 10.1682 | 8.7091 | 5.3498 | 2.5136 | -0.61863 | -3.6394 | 6.9752 | 6.7257 | 6.7349 | 6.7662 | 6.6632 | 6.5157 | 6.163 | 5.0834 | 3.9538 | 2.835 | -0.41987 | -3.5964 | -6.1678 | -7.7636 | -6.4625 | 11.6122 | 11.3627 | 11.3719 | 11.4032 | 11.3002 | 11.1527 | 10.8 | 9.7204 | 8.5908 | 7.472 | 4.2171 | 1.0406 | -1.5308 | -3.1266 | -2.1131 | 6.9752 | 6.7732 | 6.7633 | 6.8047 | 6.7951 | 6.7614 | 6.7006 | 6.623 | 6.5072 | 6.3848 | 5.7487 | 4.8914 | 4.2889 | 3.6544 | 3.3263 | 11.6122 | 11.4102 | 11.4003 | 11.4417 | 11.4321 | 11.3984 | 11.3376 | 11.26 | 11.1442 | 11.0218 | 10.3857 | 9.5284 | 8.9259 | 8.2914 | 7.943 | 6.9752 | 6.288 | 6.1152 | 6.0098 | 5.7786 | 5.5353 | 5.0644 | 3.8345 | 2.6135 | 1.403 | -2.1566 | -5.5677 | -8.3431 | -10.1842 | -9.1886 | 11.6122 | 10.925 | 10.7522 | 10.6468 | 10.4156 | 10.1723 | 9.7014 | 8.4715 | 7.2505 | 6.04 | 2.4804 | -0.93071 | -3.7061 | -5.5472 | -4.7732 | 331655 | 439667 | BISPHAM | PENWORTHAM
| Blackbull | 9.3662 | 7.4593 | 6.8435 | 6.4251 | 5.9902 | 5.5367 | 5.0576 | 4.5412 | 3.965 | 3.4012 | 2.0618 | -0.15447 | -2.0513 | -4.0705 | -5.8087 | 13.5032 | 11.5963 | 10.9805 | 10.5621 | 10.1272 | 9.6737 | 9.1946 | 8.6782 | 8.102 | 7.5382 | 6.1988 | 3.9825 | 2.0857 | 0.066476 | -1.7643 | 9.3662 | 8.5624 | 8.4513 | 8.3342 | 8.1993 | 8.0318 | 7.81 | 7.529 | 7.2485 | 6.9491 | 6.0398 | 5.0543 | 4.0457 | 3.0017 | 2.3592 | 13.5032 | 12.6994 | 12.5883 | 12.4712 | 12.3363 | 12.1688 | 11.947 | 11.666 | 11.3855 | 11.0861 | 10.1768 | 9.1913 | 8.1827 | 7.1387 | 6.5864 | 9.3662 | 7.1729 | 6.5077 | 6.0887 | 5.6561 | 5.2073 | 4.7333 | 4.2278 | 3.6979 | 3.184 | 1.9834 | -0.050851 | -1.6255 | -3.192 | -4.4914 | 13.5032 | 11.3099 | 10.6447 | 10.2257 | 9.7931 | 9.3443 | 8.8703 | 8.3648 | 7.8349 | 7.321 | 6.1204 | 4.0861 | 2.5115 | 0.94499 | -0.49586 | 9.3662 | 7.9618 | 7.4842 | 7.1314 | 6.7471 | 6.311 | 5.6924 | 4.7413 | 3.7414 | 2.7522 | 0.73523 | -1.1863 | -2.6172 | -3.6092 | -2.97 | 13.5032 | 12.0988 | 11.6212 | 11.2684 | 10.8841 | 10.448 | 9.8294 | 8.8783 | 7.8784 | 6.8892 | 4.8722 | 2.9507 | 1.5198 | 0.52778 | 1.0207 | 9.3662 | 7.9882 | 7.5005 | 7.1414 | 6.7797 | 6.3683 | 5.9048 | 5.4163 | 4.862 | 4.3088 | 3.4603 | 2.4463 | 1.7854 | 1.2322 | 1.0433 | 13.5032 | 12.1252 | 11.6375 | 11.2784 | 10.9167 | 10.5053 | 10.0418 | 9.5533 | 8.999 | 8.4458 | 7.5973 | 6.5833 | 5.9224 | 5.3692 | 5.1649 | 9.3662 | 7.0584 | 6.3632 | 5.9322 | 5.4816 | 5.0221 | 4.4785 | 3.5113 | 2.4869 | 1.4768 | -0.77288 | -3.0276 | -4.7587 | -5.9286 | -5.4636 | 13.5032 | 11.1954 | 10.5002 | 10.0692 | 9.6186 | 9.1591 | 8.6155 | 7.6483 | 6.6239 | 5.6138 | 3.3641 | 1.1094 | -0.62173 | -1.7916 | -1.4356 | 353041 | 433005 | RIBBLE | PENWORTHAM
| Blackburn | 9.3319 | 7.6482 | 6.911 | 6.483 | 6.0031 | 5.4778 | 4.9148 | 4.5947 | 4.1496 | 3.5288 | 0.76826 | -2.4164 | -4.7589 | -6.8223 | -8.3842 | 13.9689 | 12.2852 | 11.548 | 11.12 | 10.6401 | 10.1148 | 9.5518 | 9.2317 | 8.7866 | 8.1658 | 5.4053 | 2.2206 | -0.12194 | -2.1853 | -3.8204 | 9.3319 | 8.8893 | 8.6813 | 8.5817 | 8.4885 | 8.3705 | 8.2056 | 7.9916 | 7.7391 | 7.4621 | 6.2843 | 4.6472 | 2.9591 | 1.1265 | -0.074474 | 13.9689 | 13.5263 | 13.3183 | 13.2187 | 13.1255 | 13.0075 | 12.8426 | 12.6286 | 12.3761 | 12.0991 | 10.9213 | 9.2842 | 7.5961 | 5.7635 | 4.7131 | 9.3319 | 7.3816 | 6.601 | 6.1793 | 5.7131 | 5.2114 | 4.6847 | 4.4175 | 4.0766 | 3.7037 | 1.1556 | -2.1356 | -4.5997 | -6.6106 | -7.9141 | 13.9689 | 12.0186 | 11.238 | 10.8163 | 10.3501 | 9.8484 | 9.3217 | 9.0545 | 8.7136 | 8.3407 | 5.7926 | 2.5014 | 0.03735 | -1.9736 | -3.4009 | 9.3319 | 8.0687 | 7.4343 | 7.0413 | 6.5919 | 6.083 | 5.4111 | 4.619 | 3.7237 | 2.6851 | -0.72092 | -3.667 | -5.7373 | -6.9391 | -6.4455 | 13.9689 | 12.7057 | 12.0713 | 11.6783 | 11.2289 | 10.72 | 10.0481 | 9.256 | 8.3607 | 7.3221 | 3.9161 | 0.96998 | -1.1003 | -2.3021 | -1.9424 | 9.3319 | 8.5132 | 7.9484 | 7.5711 | 7.1971 | 6.7756 | 6.284 | 6.0185 | 5.6213 | 5.1648 | 3.0298 | 0.93163 | -0.49654 | -1.5005 | -1.8142 | 13.9689 | 13.1502 | 12.5854 | 12.2081 | 11.8341 | 11.4126 | 10.921 | 10.6555 | 10.2583 | 9.8018 | 7.6668 | 5.5686 | 4.1405 | 3.1365 | 2.8324 | 9.3319 | 7.2419 | 6.4278 | 5.9913 | 5.5097 | 4.9995 | 4.3432 | 3.5607 | 2.7034 | 1.8152 | -1.4932 | -4.7308 | -7.1349 | -8.595 | -8.2606 | 13.9689 | 11.8789 | 11.0648 | 10.6283 | 10.1467 | 9.6365 | 8.9802 | 8.1977 | 7.3404 | 6.4522 | 3.1438 | -0.093753 | -2.4979 | -3.958 | -3.7239 | 370584 | 429294 | BLACKBURN | PENWORTHAM
| Blackburn Rd Clayton | 11.6124 | 10.922 | 10.6345 | 10.4289 | 10.1706 | 9.9109 | 9.6762 | 9.4422 | 9.1625 | 8.8813 | 7.3856 | 4.7527 | 2.7024 | 0.94376 | -0.075532 | 19.2924 | 18.602 | 18.3145 | 18.1089 | 17.8506 | 17.5909 | 17.3562 | 17.1222 | 16.8425 | 16.5613 | 15.0656 | 12.4327 | 10.3824 | 8.6238 | 7.382 | 11.6124 | 11.4749 | 11.3104 | 11.1748 | 11.0392 | 10.8834 | 10.6974 | 10.4792 | 10.3279 | 10.1691 | 9.5267 | 8.5363 | 7.6307 | 6.743 | 6.0983 | 19.2924 | 19.1549 | 18.9904 | 18.8548 | 18.7192 | 18.5634 | 18.3774 | 18.1592 | 18.0079 | 17.8491 | 17.2067 | 16.2163 | 15.3107 | 14.423 | 13.862 | 11.6124 | 10.7773 | 10.3473 | 10.0122 | 9.6363 | 9.2511 | 8.8816 | 8.5037 | 8.1072 | 7.7026 | 5.8401 | 3.5628 | 1.9316 | 0.56655 | 0.1704 | 19.2924 | 18.4573 | 18.0273 | 17.6922 | 17.3163 | 16.9311 | 16.5616 | 16.1837 | 15.7872 | 15.3826 | 13.5201 | 11.2428 | 9.6116 | 8.2465 | 7.7432 | 11.6124 | 11.0307 | 10.6517 | 10.3335 | 9.9695 | 9.5766 | 9.0635 | 8.172 | 7.2853 | 6.4295 | 3.8408 | 1.7055 | 0.38622 | -0.058237 | 0.89091 | 19.2924 | 18.7107 | 18.3317 | 18.0135 | 17.6495 | 17.2566 | 16.7435 | 15.852 | 14.9653 | 14.1095 | 11.5208 | 9.3855 | 8.0662 | 7.6218 | 8.361 | 11.6124 | 11.4201 | 11.2394 | 11.0738 | 10.9105 | 10.7319 | 10.535 | 10.3176 | 10.0394 | 9.7471 | 8.8075 | 7.808 | 6.7943 | 5.9282 | 5.5378 | 19.2924 | 19.1001 | 18.9194 | 18.7538 | 18.5905 | 18.4119 | 18.215 | 17.9976 | 17.7194 | 17.4271 | 16.4875 | 15.488 | 14.4743 | 13.6082 | 13.2496 | 11.6124 | 10.7077 | 10.2581 | 9.8995 | 9.5016 | 9.0971 | 8.5778 | 7.6624 | 6.7601 | 5.8892 | 3.3096 | 1.003 | -0.45316 | -1.2129 | -0.65998 | 19.2924 | 18.3877 | 17.9381 | 17.5795 | 17.1816 | 16.7771 | 16.2578 | 15.3424 | 14.4401 | 13.5692 | 10.9896 | 8.683 | 7.2268 | 6.4671 | 6.891 | 374632 | 430529 | HUNCOAT | PADIHAM
| Blackfriars | 5.6042 | 3.9948 | 2.8608 | 1.8141 | 0.65529 | 1.7545 | 0.66376 | -0.25875 | -1.1525 | -2.0283 | -4.4583 | -6.1446 | -7.4345 | -8.7666 | -10.0169 | 15.3042 | 13.6948 | 12.5608 | 11.5141 | 10.3553 | 9.2545 | 8.1638 | 7.2412 | 6.3475 | 5.4717 | 3.0417 | 1.3554 | 0.065482 | -1.2666 | -2.4384 | 5.6042 | 5.0304 | 4.6495 | 4.3505 | 4.032 | 5.9108 | 5.5396 | 5.085 | 4.7058 | 4.3219 | 3.2081 | 2.0894 | 1.1023 | -0.0075047 | -1.0489 | 15.3042 | 14.7304 | 14.3495 | 14.0505 | 13.732 | 13.4108 | 13.0396 | 12.585 | 12.2058 | 11.8219 | 10.7081 | 9.5894 | 8.6023 | 7.4925 | 6.6411 | 5.6042 | 3.741 | 2.5187 | 1.4317 | 0.22122 | 1.263 | 0.1315 | -0.8453 | -1.7581 | -2.6846 | -5.2698 | -7.0101 | -8.2371 | -9.4313 | -10.4362 | 15.3042 | 13.441 | 12.2187 | 11.1317 | 9.9212 | 8.763 | 7.6315 | 6.6547 | 5.7419 | 4.8154 | 2.2302 | 0.48987 | -0.73707 | -1.9313 | -2.8416 | 5.6042 | 4.3207 | 3.2378 | 2.1862 | 1.0026 | 2.0655 | 0.90008 | -0.27458 | -1.393 | -2.514 | -5.3129 | -6.8802 | -7.9309 | -8.7646 | -9.2664 | 15.3042 | 14.0207 | 12.9378 | 11.8862 | 10.7026 | 9.5655 | 8.4001 | 7.2254 | 6.107 | 4.986 | 2.1871 | 0.61983 | -0.43092 | -1.2646 | -1.6808 | 5.6042 | 4.7384 | 3.7659 | 2.7434 | 1.633 | 2.7806 | 1.7262 | 0.81756 | -0.090431 | -0.99156 | -3.2304 | -4.3769 | -5.2219 | -6.145 | -7.0251 | 15.3042 | 14.4384 | 13.4659 | 12.4434 | 11.333 | 10.2806 | 9.2262 | 8.3176 | 7.4096 | 6.5084 | 4.2696 | 3.1231 | 2.2781 | 1.355 | 0.62656 | 5.6042 | 3.6409 | 2.3841 | 1.2849 | 0.054935 | 1.0805 | -0.13438 | -1.3647 | -2.512 | -3.6639 | -6.5626 | -8.1895 | -9.2961 | -10.2011 | -10.8072 | 15.3042 | 13.3409 | 12.0841 | 10.9849 | 9.7549 | 8.5805 | 7.3656 | 6.1353 | 4.988 | 3.8361 | 0.93744 | -0.68945 | -1.7961 | -2.7011 | -3.1976 | 383030 | 399104 | FREDERICK RD | KEARSLEY
| Blackley | 11.2349 | 10.5213 | 7.7393 | 3.0773 | 2.8689 | 2.6353 | 2.3969 | 2.1679 | 1.9598 | 1.7732 | 0.70127 | -0.96518 | -2.2274 | -3.3843 | -4.2034 | 15.8719 | 15.1583 | 12.3763 | 7.7143 | 7.5059 | 7.2723 | 7.0339 | 6.8049 | 6.5968 | 6.4102 | 5.3383 | 3.6718 | 2.4096 | 1.2527 | 0.29624 | 11.2349 | 11.0081 | 8.2585 | 3.6512 | 3.5364 | 3.4163 | 3.2552 | 3.0594 | 2.9037 | 2.7438 | 2.2686 | 1.8102 | 1.3754 | 0.9129 | 0.5666 | 15.8719 | 15.6451 | 12.8955 | 8.2882 | 8.1734 | 8.0533 | 7.8922 | 7.6964 | 7.5407 | 7.3808 | 6.9056 | 6.4472 | 6.0124 | 5.5499 | 5.2572 | 11.2349 | 10.3685 | 7.5288 | 2.8039 | 2.5313 | 2.2301 | 1.9162 | 1.6065 | 1.3267 | 1.0631 | -0.20505 | -1.9129 | -3.0828 | -3.9836 | -4.3136 | 15.8719 | 15.0055 | 12.1658 | 7.4409 | 7.1683 | 6.8671 | 6.5532 | 6.2435 | 5.9637 | 5.7001 | 4.432 | 2.7241 | 1.5542 | 0.6534 | 0.20999 | 11.2349 | 10.8503 | 8.0118 | 3.3224 | 3.0691 | 2.7623 | 2.3588 | 1.7114 | 1.092 | 0.50184 | -1.1358 | -2.5434 | -3.4235 | -3.7413 | -3.2385 | 15.8719 | 15.4873 | 12.6488 | 7.9594 | 7.7061 | 7.3993 | 6.9958 | 6.3484 | 5.729 | 5.1388 | 3.5012 | 2.0936 | 1.2135 | 0.8957 | 1.2776 | 11.2349 | 10.8498 | 8.0781 | 3.4831 | 3.3877 | 3.2565 | 3.0931 | 2.9082 | 2.7068 | 2.504 | 1.8128 | 1.0713 | 0.5599 | 0.06896 | -0.16788 | 15.8719 | 15.4868 | 12.7151 | 8.1201 | 8.0247 | 7.8935 | 7.7301 | 7.5452 | 7.3438 | 7.141 | 6.4498 | 5.7083 | 5.1969 | 4.706 | 4.4744 | 11.2349 | 10.511 | 7.6649 | 2.9102 | 2.6013 | 2.2733 | 1.856 | 1.1621 | 0.50519 | -0.11862 | -1.8318 | -3.2665 | -4.1958 | -4.5752 | -4.1862 | 15.8719 | 15.148 | 12.3019 | 7.5472 | 7.2383 | 6.9103 | 6.493 | 5.7991 | 5.1422 | 4.5184 | 2.8052 | 1.3705 | 0.44124 | 0.06181 | 0.35864 | 383882 | 403258 | RED BANK | WHITEGATE
| Blackpool | 11.6802 | 10.82 | 10.4063 | 9.9864 | 9.5431 | 9.0939 | 8.6762 | 8.5853 | 8.4831 | 8.393 | 7.4772 | 5.7089 | 4.2886 | 2.825 | 1.5493 | 19.4302 | 18.57 | 18.1563 | 17.7364 | 17.2931 | 16.8439 | 16.4262 | 16.3353 | 16.2331 | 16.143 | 15.2272 | 13.4589 | 12.0386 | 10.575 | 9.1563 | 11.6802 | 11.2348 | 11.0337 | 10.7678 | 10.4828 | 10.1893 | 9.8319 | 8.9376 | 8.8533 | 8.7683 | 8.5226 | 8.3015 | 8.0407 | 7.7568 | 7.5466 | 19.4302 | 18.9848 | 18.7837 | 18.5178 | 18.2328 | 17.9393 | 17.5819 | 16.6876 | 16.6033 | 16.5183 | 16.2726 | 16.0515 | 15.7907 | 15.5068 | 15.3078 | 11.6802 | 10.7783 | 10.3634 | 9.9657 | 9.5344 | 9.0963 | 8.6973 | 8.6234 | 8.5983 | 8.5573 | 7.8039 | 6.2204 | 5.0017 | 3.8243 | 2.9228 | 19.4302 | 18.5283 | 18.1134 | 17.7157 | 17.2844 | 16.8463 | 16.4473 | 16.3734 | 16.3483 | 16.3073 | 15.5539 | 13.9704 | 12.7517 | 11.5743 | 10.4682 | 11.6802 | 11.0146 | 10.6895 | 10.3469 | 9.971 | 9.5843 | 9.1136 | 8.5845 | 8.021 | 7.4418 | 5.8186 | 4.3154 | 3.1959 | 2.6772 | 3.557 | 19.4302 | 18.7646 | 18.4395 | 18.0969 | 17.721 | 17.3343 | 16.8636 | 16.3345 | 15.771 | 15.1918 | 13.5686 | 12.0654 | 10.9459 | 10.4272 | 11.0996 | 11.6802 | 10.898 | 10.5088 | 10.1192 | 9.747 | 9.3935 | 9.0406 | 8.9642 | 8.8507 | 8.7339 | 8.3361 | 7.9026 | 7.6433 | 7.4204 | 7.5367 | 19.4302 | 18.648 | 18.2588 | 17.8692 | 17.497 | 17.1435 | 16.7906 | 16.7142 | 16.6007 | 16.4839 | 16.0861 | 15.6526 | 15.3933 | 15.1704 | 15.2231 | 11.6802 | 10.7897 | 10.3655 | 9.9451 | 9.491 | 9.0344 | 8.4872 | 7.8666 | 7.2817 | 6.6811 | 4.9959 | 3.4453 | 2.2709 | 1.6728 | 2.4457 | 19.4302 | 18.5397 | 18.1155 | 17.6951 | 17.241 | 16.7844 | 16.2372 | 15.6166 | 15.0317 | 14.4311 | 12.7459 | 11.1953 | 10.0209 | 9.4228 | 10.0131 | 330835 | 435308 | BLACKPOOL | PENWORTHAM
| Bollington | 4.6617 | 4.0303 | 3.7965 | 3.6762 | 3.5058 | 3.3309 | 3.1723 | 3.0196 | 2.8216 | 2.6436 | 1.468 | -0.5737 | -2.2616 | -4.0479 | -5.5682 | 6.6617 | 6.0303 | 5.7965 | 5.6762 | 5.5058 | 5.3309 | 5.1723 | 5.0196 | 4.8216 | 4.6436 | 3.468 | 1.4263 | -0.26162 | -2.0479 | -3.6597 | 4.6617 | 4.4009 | 4.2533 | 4.1231 | 3.9516 | 3.7641 | 3.5274 | 3.228 | 2.9769 | 2.7246 | 1.974 | 1.2312 | 0.5262 | -0.26269 | -0.84005 | 6.6617 | 6.4009 | 6.2533 | 6.1231 | 5.9516 | 5.7641 | 5.5274 | 5.228 | 4.9769 | 4.7246 | 3.974 | 3.2312 | 2.5262 | 1.7373 | 1.2551 | 4.6617 | 3.9605 | 3.7298 | 3.6439 | 3.5109 | 3.3799 | 3.2817 | 3.1961 | 3.0717 | 2.956 | 1.9685 | 0.08959 | -1.4572 | -3.0776 | -4.4502 | 6.6617 | 5.9605 | 5.7298 | 5.6439 | 5.5109 | 5.3799 | 5.2817 | 5.1961 | 5.0717 | 4.956 | 3.9685 | 2.0896 | 0.5428 | -1.0776 | -2.5747 | 4.6617 | 4.3335 | 4.2027 | 4.1342 | 4.0039 | 3.8527 | 3.6115 | 3.0202 | 2.3845 | 1.7526 | -0.074107 | -1.855 | -3.2559 | -4.1708 | -3.6139 | 6.6617 | 6.3335 | 6.2027 | 6.1342 | 6.0039 | 5.8527 | 5.6115 | 5.0202 | 4.3845 | 3.7526 | 1.9259 | 0.14499 | -1.2559 | -2.1708 | -1.7418 | 4.6617 | 4.269 | 4.1144 | 4.0445 | 3.9563 | 3.847 | 3.7222 | 3.5903 | 3.3937 | 3.2025 | 2.5365 | 1.75 | 1.1498 | 0.53837 | 0.19715 | 6.6617 | 6.269 | 6.1144 | 6.0445 | 5.9563 | 5.847 | 5.7222 | 5.5903 | 5.3937 | 5.2025 | 4.5365 | 3.75 | 3.1498 | 2.5384 | 2.2151 | 4.6617 | 4.0141 | 3.7585 | 3.611 | 3.4105 | 3.2138 | 2.9172 | 2.2458 | 1.5516 | 0.862 | -1.1397 | -3.0724 | -4.6165 | -5.6906 | -5.3254 | 6.6617 | 6.0141 | 5.7585 | 5.611 | 5.4105 | 5.2138 | 4.9172 | 4.2458 | 3.5516 | 2.862 | 0.86028 | -1.0724 | -2.6165 | -3.6906 | -3.4118 | 393042 | 377873 | MACCLESFIELD | MACCLESFIELD
| Bolton By Bowland | 0.19792 | 0.13102 | 0.066259 | 0.015402 | -0.0463 | -0.10797 | -0.15981 | -0.2084 | -0.27066 | -0.35328 | -0.71326 | -1.2217 | -1.6434 | -2.0649 | -2.4212 | 4.6979 | 4.631 | 4.5663 | 4.5154 | 4.4537 | 4.392 | 4.3402 | 4.2916 | 4.2293 | 4.1467 | 3.7867 | 3.2783 | 2.8566 | 2.4351 | 2.0464 | 0.19792 | 0.13038 | 0.048248 | -0.032602 | -0.12241 | -0.21806 | -0.33071 | -0.45956 | -0.54178 | -0.62406 | -0.86558 | -1.1205 | -1.3507 | -1.5771 | -1.7336 | 4.6979 | 4.6304 | 4.5482 | 4.4674 | 4.3776 | 4.2819 | 4.1693 | 4.0404 | 3.9582 | 3.8759 | 3.6344 | 3.3795 | 3.1493 | 2.9229 | 2.7894 | 0.19792 | 0.13385 | 0.075069 | 0.036878 | -0.012389 | -0.059525 | -0.0919 | -0.11794 | -0.16781 | -0.23293 | -0.68646 | -1.2274 | -1.611 | -1.8973 | -2.0552 | 4.6979 | 4.6338 | 4.5751 | 4.5369 | 4.4876 | 4.4405 | 4.4081 | 4.3821 | 4.3322 | 4.2671 | 3.8135 | 3.2726 | 2.889 | 2.6027 | 2.4306 | 0.19792 | 0.1865 | 0.14948 | 0.1161 | 0.076493 | 0.033926 | -0.025787 | -0.16837 | -0.32783 | -0.49034 | -0.95034 | -1.3829 | -1.7137 | -1.8786 | -1.6626 | 4.6979 | 4.6865 | 4.6495 | 4.6161 | 4.5765 | 4.5339 | 4.4742 | 4.3316 | 4.1722 | 4.0097 | 3.5497 | 3.1171 | 2.7863 | 2.6214 | 2.786 | 0.19792 | 0.14495 | 0.089769 | 0.05044 | 0.014087 | -0.023175 | -0.062599 | -0.1033 | -0.16298 | -0.2209 | -0.48748 | -0.79731 | -1.0075 | -1.2587 | -1.3747 | 4.6979 | 4.645 | 4.5898 | 4.5504 | 4.5141 | 4.4768 | 4.4374 | 4.3967 | 4.337 | 4.2791 | 4.0125 | 3.7027 | 3.4925 | 3.2413 | 3.13 | 0.19792 | 0.15429 | 0.088464 | 0.024493 | -0.044477 | -0.11011 | -0.19601 | -0.37426 | -0.55481 | -0.73776 | -1.268 | -1.7615 | -2.1349 | -2.3437 | -2.1743 | 4.6979 | 4.6543 | 4.5885 | 4.5245 | 4.4555 | 4.3899 | 4.304 | 4.1257 | 3.9452 | 3.7622 | 3.232 | 2.7385 | 2.3651 | 2.1563 | 2.2847 | 378320 | 449559 | PADIHAM | PADIHAM | Firm Capacity marginally exceeded in FY28. There is potential to reinforce HV interconnection with Ribblesdale primary.
| Bolton Le Sands | 6.803 | 5.1083 | 4.7402 | 4.6403 | 4.4087 | 4.1247 | 3.819 | 3.4662 | 3.0432 | 2.6095 | 0.25112 | -3.0544 | -5.6215 | -8.0329 | -10.0822 | 10.303 | 8.6083 | 8.2402 | 8.1403 | 7.9087 | 7.6247 | 7.319 | 6.9662 | 6.5432 | 6.1095 | 3.7511 | 0.44559 | -2.1215 | -4.5329 | -6.6846 | 6.803 | 6.0744 | 5.827 | 5.6678 | 5.4611 | 5.2495 | 4.9667 | 4.5961 | 4.3126 | 4.0077 | 2.9383 | 1.579 | 0.015263 | -1.8355 | -3.2098 | 10.303 | 9.5744 | 9.327 | 9.1678 | 8.9611 | 8.7495 | 8.4667 | 8.0961 | 7.8126 | 7.5077 | 6.4383 | 5.079 | 3.5153 | 1.6645 | 0.49608 | 6.803 | 4.8677 | 4.4754 | 4.4128 | 4.2244 | 3.9972 | 3.7777 | 3.5244 | 3.2268 | 2.8995 | 0.59065 | -2.7867 | -5.5039 | -8.0184 | -9.6499 | 10.303 | 8.3677 | 7.9754 | 7.9128 | 7.7244 | 7.4972 | 7.2777 | 7.0244 | 6.7268 | 6.3995 | 4.0907 | 0.71333 | -2.0039 | -4.5184 | -6.1486 | 6.803 | 5.6358 | 5.3875 | 5.3036 | 5.1077 | 4.8626 | 4.4429 | 3.4735 | 2.4344 | 1.3695 | -1.8765 | -4.9213 | -7.1619 | -8.534 | -7.9909 | 10.303 | 9.1358 | 8.8875 | 8.8036 | 8.6077 | 8.3626 | 7.9429 | 6.9735 | 5.9344 | 4.8695 | 1.6235 | -1.4213 | -3.6619 | -5.034 | -4.575 | 6.803 | 5.5398 | 5.2612 | 5.1956 | 5.0806 | 4.9417 | 4.7276 | 4.3695 | 3.8978 | 3.3837 | 1.4971 | -0.80073 | -2.5751 | -4.4196 | -5.1513 | 10.303 | 9.0398 | 8.7612 | 8.6956 | 8.5806 | 8.4417 | 8.2276 | 7.8695 | 7.3978 | 6.8837 | 4.9971 | 2.6993 | 0.92487 | -0.91962 | -1.5988 | 6.803 | 4.8094 | 4.3716 | 4.2325 | 3.9912 | 3.7249 | 3.2852 | 2.2952 | 1.2751 | 0.22145 | -3.033 | -6.3802 | -8.9525 | -10.6358 | -10.269 | 10.303 | 8.3094 | 7.8716 | 7.7325 | 7.4912 | 7.2249 | 6.7852 | 5.7952 | 4.7751 | 3.7215 | 0.46702 | -2.8802 | -5.4525 | -7.1358 | -6.8706 | 347707 | 467237 | LANCASTER | HEYSHAM
| Botany Bay | 2.4475 | 2.0273 | 1.8556 | 1.7191 | 1.5059 | 1.2796 | 1.036 | 0.70586 | 0.31895 | -0.052899 | -2.3028 | -5.3076 | -7.5395 | -9.5043 | -10.8702 | 10.4475 | 10.0273 | 9.8556 | 9.7191 | 9.5059 | 9.2796 | 9.036 | 8.7059 | 8.3189 | 7.9471 | 5.6972 | 2.6924 | 0.46053 | -1.5043 | -2.8643 | 2.4475 | 2.2336 | 2.1135 | 1.9841 | 1.801 | 1.5908 | 1.3206 | 0.97569 | 0.70199 | 0.34208 | -0.85558 | -2.1448 | -3.6428 | -5.0515 | -5.8531 | 10.4475 | 10.2336 | 10.1135 | 9.9841 | 9.801 | 9.5908 | 9.3206 | 8.9757 | 8.702 | 8.3421 | 7.1444 | 5.8552 | 4.3572 | 2.9485 | 2.2576 | 2.4475 | 2.0023 | 1.8479 | 1.7493 | 1.5809 | 1.4089 | 1.2637 | 1.0686 | 0.77674 | 0.48405 | -2.4306 | -5.787 | -8.3464 | -10.6241 | -12.1989 | 10.4475 | 10.0023 | 9.8479 | 9.7493 | 9.5809 | 9.4089 | 9.2637 | 9.0686 | 8.7767 | 8.4841 | 5.5694 | 2.213 | -0.34643 | -2.6241 | -4.1613 | 2.4475 | 2.3094 | 2.2412 | 2.1765 | 2.0196 | 1.8322 | 1.5224 | 0.79356 | 0.003283 | -0.78172 | -3.3996 | -6.4698 | -8.7216 | -10.3863 | -10.613 | 10.4475 | 10.3094 | 10.2412 | 10.1765 | 10.0196 | 9.8322 | 9.5224 | 8.7936 | 8.0033 | 7.2183 | 4.6004 | 1.5302 | -0.72156 | -2.3863 | -2.6133 | 2.4475 | 2.1778 | 2.0694 | 1.9992 | 1.8972 | 1.7626 | 1.5952 | 1.3933 | 1.0413 | 0.67912 | -0.65286 | -3.0279 | -4.7842 | -6.2752 | -7.0437 | 10.4475 | 10.1778 | 10.0694 | 9.9992 | 9.8972 | 9.7626 | 9.5952 | 9.3933 | 9.0413 | 8.6791 | 7.3471 | 4.9721 | 3.2158 | 1.7248 | 1.042 | 2.4475 | 2.1238 | 1.9615 | 1.8182 | 1.5922 | 1.3633 | 1.0099 | 0.20649 | -0.63739 | -1.4945 | -4.0428 | -6.9282 | -9.1512 | -10.7483 | -11.0911 | 10.4475 | 10.1238 | 9.9615 | 9.8182 | 9.5922 | 9.3633 | 9.0099 | 8.2065 | 7.3626 | 6.5055 | 3.9572 | 1.0718 | -1.1512 | -2.7483 | -3.0558 | 359442 | 418850 | LEYLAND | PENWORTHAM
| Bow Lane | 6.2648 | 3.7405 | 2.3077 | 1.2662 | 0.096436 | -0.65704 | -1.143 | -1.6704 | -2.3122 | -2.9616 | -6.2084 | -10.9718 | -14.7352 | -18.6139 | -21.9998 | 10.9018 | 8.3775 | 6.9447 | 5.9032 | 4.7334 | 3.98 | 3.494 | 2.9666 | 2.3248 | 1.6754 | -1.5714 | -6.3348 | -10.0982 | -13.9769 | -17.4554 | 6.2648 | 5.4187 | 4.9207 | 4.5108 | 4.0178 | 3.6344 | 3.118 | 2.4199 | 1.8379 | 1.2305 | -0.72345 | -2.8751 | -5.0446 | -7.4476 | -9.0367 | 10.9018 | 10.0557 | 9.5577 | 9.1478 | 8.6548 | 8.2714 | 7.755 | 7.0569 | 6.4749 | 5.8675 | 3.9135 | 1.7619 | -0.40765 | -2.8106 | -4.1585 | 6.2648 | 3.3921 | 1.9293 | 0.94838 | -0.15095 | -0.8152 | -1.169 | -1.5448 | -2.0122 | -2.5082 | -5.4044 | -10.0295 | -13.7036 | -17.3969 | -20.4937 | 10.9018 | 8.0291 | 6.5663 | 5.5854 | 4.486 | 3.8218 | 3.468 | 3.0922 | 2.6248 | 2.1288 | -0.76736 | -5.3925 | -9.0666 | -12.7599 | -16.0037 | 6.2648 | 4.5598 | 3.3547 | 2.4255 | 1.3336 | 0.63143 | -0.0031313 | -1.3721 | -2.8614 | -4.3865 | -8.9042 | -13.215 | -16.4933 | -18.7208 | -18.1062 | 10.9018 | 9.1968 | 7.9917 | 7.0625 | 5.9706 | 5.2684 | 4.6339 | 3.2649 | 1.7756 | 0.25054 | -4.2672 | -8.578 | -11.8563 | -14.0838 | -13.6262 | 6.2648 | 4.8817 | 3.6998 | 2.7608 | 1.7639 | 1.1563 | 0.78005 | 0.3579 | -0.21451 | -0.81403 | -2.9069 | -5.177 | -6.9781 | -8.448 | -9.2692 | 10.9018 | 9.5187 | 8.3368 | 7.3978 | 6.4009 | 5.7933 | 5.4171 | 4.9949 | 4.4225 | 3.823 | 1.7301 | -0.53996 | -2.3411 | -3.811 | -4.5519 | 6.2648 | 3.3425 | 1.8212 | 0.75937 | -0.44922 | -1.2204 | -1.9327 | -3.4045 | -4.9429 | -6.5197 | -11.3116 | -15.993 | -19.6406 | -22.2218 | -21.9268 | 10.9018 | 7.9795 | 6.4582 | 5.3964 | 4.1878 | 3.4166 | 2.7043 | 1.2325 | -0.30589 | -1.8827 | -6.6746 | -11.356 | -15.0036 | -17.5848 | -17.378 | 354895 | 422392 | LEYLAND | PENWORTHAM
| Bowaters | 14.4847 | 14.5324 | 14.2927 | 14.2316 | 14.2963 | 14.3677 | 14.452 | 14.5328 | 14.3676 | 14.1999 | 13.265 | 12.9063 | 11.8586 | 12.183 | 12.8406 | 34.9847 | 35.0324 | 34.7927 | 34.7316 | 34.7963 | 34.8677 | 34.952 | 35.0328 | 34.8676 | 34.6999 | 33.765 | 33.4063 | 32.3586 | 32.683 | 33.1632 | 14.4847 | 14.5225 | 14.2807 | 14.2174 | 14.2793 | 14.3574 | 14.4391 | 14.5292 | 14.3133 | 14.0953 | 13.4536 | 12.8438 | 12.3221 | 11.8818 | 7.2761 | 34.9847 | 35.0225 | 34.7807 | 34.7174 | 34.7793 | 34.8574 | 34.9391 | 35.0292 | 34.8133 | 34.5953 | 33.9536 | 33.3438 | 32.8221 | 32.3818 | 27.7045 | 14.4847 | 14.5694 | 14.346 | 14.3303 | 14.3983 | 14.4877 | 14.5905 | 14.7053 | 14.6915 | 14.6956 | 3.4268 | 3.4149 | 3.6363 | 5.27 | 6.9836 | 34.9847 | 35.0694 | 34.846 | 34.8303 | 34.8983 | 34.9877 | 35.0905 | 35.2053 | 35.1915 | 35.1956 | 23.9268 | 23.9149 | 24.1363 | 25.77 | 27.0951 | 14.4847 | 14.584 | 13.8966 | 13.9177 | 7.4108 | 7.9458 | 8.4391 | 8.9121 | 8.425 | 8.5361 | 7.7956 | 8.0708 | 8.6197 | 9.8558 | 11.4278 | 34.9847 | 35.084 | 34.3966 | 34.4177 | 27.9108 | 28.4458 | 28.9391 | 29.4121 | 28.925 | 29.0361 | 28.2956 | 28.5708 | 29.1197 | 30.3558 | 31.5915 | 14.4847 | 14.5395 | 14.3148 | 14.2771 | 14.3705 | 14.4616 | 14.5613 | 14.6669 | 14.5313 | 14.3907 | 13.5247 | 13.2139 | 12.1921 | 12.5475 | 13.2927 | 34.9847 | 35.0395 | 34.8148 | 34.7771 | 34.8705 | 34.9616 | 35.0613 | 35.1669 | 35.0313 | 34.8907 | 34.0247 | 33.7139 | 32.6921 | 33.0475 | 33.6186 | 14.4847 | 14.5723 | 13.8655 | 13.8779 | 7.3576 | 7.8886 | 8.3809 | 8.848 | 8.3599 | 8.4704 | 7.6997 | 7.8967 | 8.3695 | 9.5553 | 11.1026 | 34.9847 | 35.0723 | 34.3655 | 34.3779 | 27.8576 | 28.3886 | 28.8809 | 29.348 | 28.8599 | 28.9704 | 28.1997 | 28.3967 | 28.8695 | 30.0553 | 31.271 | 319579 | 472480 | BARROW & SANDGATE | HARKER
| Bowdon | 8.4853 | 7.7746 | 7.5114 | 7.3859 | 7.1945 | 6.9995 | 6.8402 | 6.6991 | 6.4984 | 6.326 | 4.7166 | 1.6461 | -0.91732 | -3.662 | -5.8971 | 13.1223 | 12.4116 | 12.1484 | 12.0229 | 11.8315 | 11.6365 | 11.4772 | 11.3361 | 11.1354 | 10.963 | 9.3536 | 6.2831 | 3.7197 | 0.97497 | -1.4683 | 8.4853 | 8.1803 | 7.987 | 7.8115 | 7.5831 | 7.3429 | 7.0367 | 6.6591 | 6.3731 | 6.0848 | 5.2304 | 4.3887 | 3.6418 | 2.848 | 2.296 | 13.1223 | 12.8173 | 12.624 | 12.4485 | 12.2201 | 11.9799 | 11.6737 | 11.2961 | 11.0101 | 10.7218 | 9.8674 | 9.0257 | 8.2788 | 7.485 | 7.0182 | 8.4853 | 7.7011 | 7.4458 | 7.3683 | 7.2243 | 7.0824 | 6.9974 | 6.935 | 6.8378 | 6.7469 | 5.3954 | 2.5636 | 0.22124 | -2.2524 | -4.1736 | 13.1223 | 12.3381 | 12.0828 | 12.0053 | 11.8613 | 11.7194 | 11.6344 | 11.572 | 11.4748 | 11.3839 | 10.0324 | 7.2006 | 4.8582 | 2.3846 | 0.19666 | 8.4853 | 8.2045 | 8.0996 | 8.0936 | 7.9881 | 7.8519 | 7.5622 | 6.6496 | 5.6827 | 4.7189 | 1.9519 | -0.71504 | -2.8565 | -4.2121 | -3.0003 | 13.1223 | 12.8415 | 12.7366 | 12.7306 | 12.6251 | 12.4889 | 12.1992 | 11.2866 | 10.3197 | 9.3559 | 6.5889 | 3.922 | 1.7805 | 0.42495 | 1.3656 | 8.4853 | 8.0537 | 7.8955 | 7.8472 | 7.7816 | 7.6936 | 7.5907 | 7.4816 | 7.2843 | 7.0931 | 6.4372 | 5.6818 | 5.1677 | 4.5808 | 4.3275 | 13.1223 | 12.6907 | 12.5325 | 12.4842 | 12.4186 | 12.3306 | 12.2277 | 12.1186 | 11.9213 | 11.7301 | 11.0742 | 10.3188 | 9.8047 | 9.2178 | 8.9731 | 8.4853 | 7.8178 | 7.546 | 7.4265 | 7.2215 | 7.0208 | 6.6514 | 5.6247 | 4.5805 | 3.5398 | 0.54323 | -2.3196 | -4.6709 | -6.3185 | -5.4554 | 13.1223 | 12.4548 | 12.183 | 12.0635 | 11.8585 | 11.6578 | 11.2884 | 10.2617 | 9.2175 | 8.1768 | 5.1802 | 2.3174 | -0.033938 | -1.6815 | -1.012 | 376743 | 386810 | ALTRINCHAM | CARRINGTON
| Bradford | 8.5965 | 6.0723 | 5.2835 | 5.0333 | 4.7848 | 4.5332 | 4.3013 | 4.064 | 3.7064 | 3.3575 | 0.35692 | -3.3505 | -5.8428 | -7.6681 | -8.5954 | 13.2335 | 10.7093 | 9.9205 | 9.6703 | 9.4218 | 9.1702 | 8.9383 | 8.701 | 8.3434 | 7.9945 | 4.9939 | 1.2865 | -1.2058 | -3.0311 | -3.9522 | 8.5965 | 7.7571 | 7.3599 | 7.1743 | 7.0286 | 6.8818 | 6.7033 | 6.4582 | 6.1085 | 5.7589 | 4.7313 | 2.6032 | -0.51829 | -3.4756 | -5.173 | 13.2335 | 12.3941 | 11.9969 | 11.8113 | 11.6656 | 11.5188 | 11.3403 | 11.0952 | 10.7455 | 10.3959 | 9.3683 | 7.2402 | 4.1187 | 1.1614 | -0.3261 | 8.5965 | 5.6772 | 4.809 | 4.5577 | 4.3112 | 4.0639 | 3.8383 | 3.6115 | 3.3217 | 3.0464 | 1.3997 | -2.8188 | -5.8472 | -8.1506 | -9.2583 | 13.2335 | 10.3142 | 9.446 | 9.1947 | 8.9482 | 8.7009 | 8.4753 | 8.2485 | 7.9587 | 7.6834 | 6.0367 | 1.8182 | -1.2102 | -3.5136 | -4.6128 | 8.5965 | 6.5331 | 5.8652 | 5.6393 | 5.4121 | 5.1638 | 4.8141 | 4.1234 | 3.3465 | 2.5845 | 0.16361 | -3.457 | -5.8427 | -7.3546 | -7.4687 | 13.2335 | 11.1701 | 10.5022 | 10.2763 | 10.0491 | 9.8008 | 9.4511 | 8.7604 | 7.9835 | 7.2215 | 4.8006 | 1.18 | -1.2057 | -2.7176 | -2.8727 | 8.5965 | 7.0603 | 6.4906 | 6.2875 | 6.1344 | 5.971 | 5.793 | 5.5731 | 5.2005 | 4.8187 | 3.4795 | -0.14765 | -2.7253 | -4.684 | -5.4457 | 13.2335 | 11.6973 | 11.1276 | 10.9245 | 10.7714 | 10.608 | 10.43 | 10.2101 | 9.8375 | 9.4557 | 8.1165 | 4.4893 | 1.9117 | -0.047023 | -0.75081 | 8.5965 | 5.3319 | 4.3852 | 4.1135 | 3.8479 | 3.586 | 3.2299 | 2.5155 | 1.7302 | 0.96113 | -1.2282 | -3.5625 | -6.5121 | -8.5715 | -9.0428 | 13.2335 | 9.9689 | 9.0222 | 8.7505 | 8.4849 | 8.223 | 7.8669 | 7.1525 | 6.3672 | 5.5981 | 3.4088 | 1.0745 | -1.8751 | -3.9345 | -4.3997 | 387613 | 397710 | STUART ST | STALYBRIDGE
| Bradshawgate | 11.6563 | 10.5551 | 9.9551 | 9.5775 | 9.1844 | 8.7857 | 8.3927 | 7.9849 | 7.5478 | 7.1133 | 5.4821 | 3.4029 | 1.6036 | 0.22141 | -0.76553 | 22.2963 | 21.1951 | 20.5951 | 20.2175 | 19.8244 | 19.4257 | 19.0327 | 18.6249 | 18.1878 | 17.7533 | 16.1221 | 14.0429 | 12.2436 | 10.8614 | 9.8457 | 11.6563 | 11.2858 | 10.9745 | 10.7238 | 10.4612 | 10.1734 | 9.8443 | 9.4581 | 9.1796 | 8.8936 | 8.0411 | 7.1774 | 6.3801 | 5.6958 | 5.233 | 22.2963 | 21.9258 | 21.6145 | 21.3638 | 21.1012 | 20.8134 | 20.4843 | 20.0981 | 19.8196 | 19.5336 | 18.6811 | 17.8174 | 17.0201 | 16.3358 | 15.9413 | 11.6563 | 10.3888 | 9.7556 | 9.3769 | 8.9851 | 8.588 | 8.1963 | 7.7923 | 7.3882 | 6.9899 | 5.4604 | 3.4862 | 1.8018 | 0.59507 | -0.15146 | 22.2963 | 21.0288 | 20.3956 | 20.0169 | 19.6251 | 19.228 | 18.8363 | 18.4323 | 18.0282 | 17.6299 | 16.1004 | 14.1262 | 12.4418 | 11.2351 | 10.4168 | 11.6563 | 10.8204 | 10.3145 | 9.9865 | 9.6387 | 9.2658 | 8.8249 | 8.1783 | 7.4989 | 6.8236 | 4.8585 | 2.9446 | 1.3334 | 0.51178 | 0.7908 | 22.2963 | 21.4604 | 20.9545 | 20.6265 | 20.2787 | 19.9058 | 19.4649 | 18.8183 | 18.1389 | 17.4636 | 15.4985 | 13.5846 | 11.9734 | 11.1518 | 11.3521 | 11.6563 | 11.0933 | 10.6237 | 10.2856 | 9.9562 | 9.6039 | 9.2299 | 8.8376 | 8.4048 | 7.9645 | 6.6076 | 5.2097 | 4.032 | 3.3517 | 3.163 | 22.2963 | 21.7333 | 21.2637 | 20.9256 | 20.5962 | 20.2439 | 19.8699 | 19.4776 | 19.0448 | 18.6045 | 17.2476 | 15.8497 | 14.672 | 13.9917 | 13.8079 | 11.6563 | 10.2914 | 9.6314 | 9.2382 | 8.8326 | 8.4266 | 7.9572 | 7.2591 | 6.5593 | 5.8661 | 3.8557 | 1.9118 | 0.26555 | -0.59076 | -0.36841 | 22.2963 | 20.9314 | 20.2714 | 19.8782 | 19.4726 | 19.0666 | 18.5972 | 17.8991 | 17.1993 | 16.5061 | 14.4957 | 12.5518 | 10.9056 | 10.0492 | 10.2084 | 371891 | 408910 | BOLTON | KEARSLEY
| Bramhall | 6.6776 | 6.4246 | 6.336 | 6.2721 | 6.1895 | 6.1049 | 6.0216 | 5.9315 | 5.7824 | 5.6581 | 4.7067 | 2.976 | 1.0906 | -1.0918 | -2.9917 | 10.1776 | 9.9246 | 9.836 | 9.7721 | 9.6895 | 9.6049 | 9.5216 | 9.4315 | 9.2824 | 9.1581 | 8.2067 | 6.476 | 4.5906 | 2.4082 | 0.37449 | 6.6776 | 6.5799 | 6.5274 | 6.4412 | 6.3096 | 6.1463 | 5.9394 | 5.7061 | 5.4991 | 5.2905 | 4.6831 | 4.1351 | 3.6333 | 3.1368 | 2.8134 | 10.1776 | 10.0799 | 10.0274 | 9.9412 | 9.8096 | 9.6463 | 9.4394 | 9.2061 | 8.9991 | 8.7905 | 8.1831 | 7.6351 | 7.1333 | 6.6368 | 6.3604 | 6.6776 | 6.4139 | 6.3412 | 6.3141 | 6.2685 | 6.2258 | 6.123 | 6.0171 | 5.8367 | 5.665 | 4.7358 | 3.1752 | 1.444 | -0.56708 | -2.2788 | 10.1776 | 9.9139 | 9.8412 | 9.8141 | 9.7685 | 9.7258 | 9.623 | 9.5171 | 9.3367 | 9.165 | 8.2358 | 6.6752 | 4.944 | 2.9329 | 1.0518 | 6.6776 | 6.7087 | 6.7402 | 6.7658 | 6.7413 | 6.6775 | 6.4456 | 5.9076 | 5.2661 | 4.4934 | 2.3763 | 0.45832 | -1.1566 | -2.2589 | -1.4743 | 10.1776 | 10.2087 | 10.2402 | 10.2658 | 10.2413 | 10.1775 | 9.9456 | 9.4076 | 8.7661 | 7.9934 | 5.8763 | 3.9583 | 2.3434 | 1.2411 | 1.855 | 6.6776 | 6.5954 | 6.5931 | 6.6061 | 6.6078 | 6.5624 | 6.491 | 6.4286 | 6.3037 | 6.1889 | 5.7668 | 5.2502 | 4.8692 | 4.4766 | 4.3241 | 10.1776 | 10.0954 | 10.0931 | 10.1061 | 10.1078 | 10.0624 | 9.991 | 9.9286 | 9.8037 | 9.6889 | 9.2668 | 8.7502 | 8.3692 | 7.9766 | 7.8112 | 6.6776 | 6.5484 | 6.4666 | 6.3878 | 6.2745 | 6.1646 | 5.879 | 5.2518 | 4.5637 | 3.7839 | 1.4898 | -0.56371 | -2.309 | -3.5742 | -2.9779 | 10.1776 | 10.0484 | 9.9666 | 9.8878 | 9.7745 | 9.6646 | 9.379 | 8.7518 | 8.0637 | 7.2839 | 4.9898 | 2.9363 | 1.191 | -0.074173 | 0.39273 | 389440 | 386463 | HAZEL GROVE | BREDBURY
| Bridgewater | 6.5055 | 3.19 | 2.4235 | 2.3162 | 2.2368 | 2.1569 | 2.0952 | 2.035 | 1.8685 | 1.7122 | 1.0447 | 0.088922 | -0.66887 | -1.4594 | -2.138 | 13.5055 | 10.19 | 9.4235 | 9.3162 | 9.2368 | 9.1569 | 9.0952 | 9.035 | 8.8685 | 8.7122 | 8.0447 | 7.0889 | 6.3311 | 5.5406 | 4.8354 | 6.5055 | 5.4312 | 5.0955 | 4.9544 | 4.8574 | 4.7645 | 4.6637 | 4.5422 | 4.3093 | 4.0777 | 3.4384 | 2.8395 | 2.3529 | 1.8191 | 1.2965 | 13.5055 | 12.4312 | 12.0955 | 11.9544 | 11.8574 | 11.7645 | 11.6637 | 11.5422 | 11.3093 | 11.0777 | 10.4384 | 9.8395 | 9.3529 | 8.8191 | 8.3866 | 6.5055 | 2.6764 | 1.8103 | 1.726 | 1.6574 | 1.5867 | 1.5457 | 1.4998 | 1.4172 | 1.3135 | 0.81893 | 0.023156 | -0.56852 | -1.1294 | -1.5113 | 13.5055 | 9.6764 | 8.8103 | 8.726 | 8.6574 | 8.5867 | 8.5457 | 8.4998 | 8.4172 | 8.3135 | 7.8189 | 7.0232 | 6.4315 | 5.8706 | 5.4042 | 6.5055 | 3.8274 | 3.1991 | 3.125 | 3.0623 | 2.9974 | 2.916 | 2.6836 | 2.4069 | 2.1066 | 1.2972 | 0.54608 | 0.0093398 | -0.27022 | 0.091307 | 13.5055 | 10.8274 | 10.1991 | 10.125 | 10.0623 | 9.9974 | 9.916 | 9.6836 | 9.4069 | 9.1066 | 8.2972 | 7.5461 | 7.0093 | 6.7298 | 7.0028 | 6.5055 | 4.5308 | 4.0407 | 3.9438 | 3.8942 | 3.8438 | 3.7985 | 3.7431 | 3.5717 | 3.4058 | 2.9364 | 2.4926 | 2.2055 | 1.9366 | 1.794 | 13.5055 | 11.5308 | 11.0407 | 10.9438 | 10.8942 | 10.8438 | 10.7985 | 10.7431 | 10.5717 | 10.4058 | 9.9364 | 9.4926 | 9.2055 | 8.9366 | 8.7998 | 6.5055 | 2.2282 | 1.2627 | 1.1725 | 1.0944 | 1.0173 | 0.91633 | 0.66527 | 0.37849 | 0.06612 | -0.78775 | -1.5619 | -2.1257 | -2.4483 | -2.1483 | 13.5055 | 9.2282 | 8.2627 | 8.1725 | 8.0944 | 8.0173 | 7.9163 | 7.6653 | 7.3785 | 7.0661 | 6.2122 | 5.4381 | 4.8743 | 4.5517 | 4.7774 | 383543 | 397628 | BLOOM ST | SOUTH MANCHESTER
| Brinksway | 13.5731 | 8.5949 | 7.0049 | 5.8261 | 4.9201 | 4.0428 | 3.1265 | 2.2092 | 1.2775 | 0.36205 | -2.2665 | -5.0767 | -7.0115 | -8.573 | -9.445 | 18.2101 | 13.2319 | 11.6419 | 10.4631 | 9.5571 | 8.6428 | 7.7265 | 6.8092 | 5.8775 | 4.962 | 2.3335 | -0.47671 | -2.4115 | -3.973 | -4.8782 | 13.5731 | 11.4756 | 10.9442 | 10.2904 | 9.624 | 8.9859 | 8.2753 | 7.5292 | 6.8404 | 6.1679 | 5.6568 | 5.1437 | 4.2389 | 3.0195 | 1.9628 | 18.2101 | 16.1126 | 15.5812 | 14.9274 | 14.261 | 13.5859 | 12.8753 | 12.1292 | 11.4404 | 10.7679 | 10.2568 | 9.7437 | 8.8389 | 7.6195 | 6.702 | 13.5731 | 7.9405 | 6.176 | 4.9355 | 3.9629 | 3.0126 | 2.0172 | 1.0165 | 0.013689 | -0.92473 | -2.7131 | -5.6494 | -7.8455 | -9.755 | -10.8538 | 18.2101 | 12.5775 | 10.813 | 9.5725 | 8.5999 | 7.6126 | 6.6172 | 5.6165 | 4.6137 | 3.6753 | 1.8869 | -1.0494 | -3.2455 | -5.155 | -6.1844 | 13.5731 | 9.2801 | 7.8114 | 6.6034 | 5.6485 | 4.685 | 3.6024 | 2.2979 | 0.99223 | -0.21921 | -3.2336 | -5.9044 | -7.5963 | -8.8246 | -9.2224 | 18.2101 | 13.9171 | 12.4484 | 11.2404 | 10.2855 | 9.285 | 8.2024 | 6.8979 | 5.5922 | 4.3808 | 1.3664 | -1.3044 | -2.9963 | -4.2246 | -4.5937 | 13.5731 | 10.7256 | 9.5882 | 8.4477 | 7.6062 | 6.724 | 5.8591 | 4.9639 | 4.0114 | 3.0857 | 0.6989 | -1.6998 | -3.5892 | -5.1574 | -5.9625 | 18.2101 | 15.3626 | 14.2252 | 13.0847 | 12.2432 | 11.324 | 10.4591 | 9.5639 | 8.6114 | 7.6857 | 5.2989 | 2.9002 | 1.0108 | -0.55742 | -1.2747 | 13.5731 | 7.4662 | 5.5939 | 4.3378 | 3.347 | 2.3861 | 1.311 | -0.024384 | -1.3505 | -2.5807 | -4.7796 | -7.1251 | -9.2016 | -10.6606 | -11.045 | 18.2101 | 12.1032 | 10.2309 | 8.9748 | 7.984 | 6.9861 | 5.911 | 4.5756 | 3.2495 | 2.0193 | -0.1796 | -2.5251 | -4.6016 | -6.0606 | -6.4206 | 388434 | 389885 | ADSWOOD | BREDBURY
| Broadheath | 16.4929 | 13.9025 | 12.8984 | 12.3504 | 11.7153 | 11.0434 | 10.361 | 9.654 | 8.906 | 8.1747 | 4.8036 | -0.24724 | -4.0498 | -7.8134 | -10.872 | 21.3929 | 18.8025 | 17.7984 | 17.2504 | 16.6153 | 15.9434 | 15.261 | 14.554 | 13.806 | 13.0747 | 9.7036 | 4.6528 | 0.85015 | -2.9134 | -6.0381 | 16.4929 | 15.7062 | 15.1989 | 14.7483 | 14.1677 | 13.552 | 12.7831 | 11.793 | 11.0925 | 10.3688 | 8.1406 | 5.7863 | 3.5398 | 0.97673 | -1.0121 | 21.3929 | 20.6062 | 20.0989 | 19.6483 | 19.0677 | 18.452 | 17.6831 | 16.693 | 15.9925 | 15.2688 | 13.0406 | 10.6863 | 8.4398 | 5.8767 | 4.2311 | 16.4929 | 13.4104 | 12.1861 | 11.4705 | 10.6581 | 9.7948 | 8.9004 | 7.9676 | 7.0199 | 6.0501 | 2.0819 | -2.7465 | -6.0986 | -9.0937 | -11.0323 | 21.3929 | 18.3104 | 17.0861 | 16.3705 | 15.5581 | 14.6948 | 13.8004 | 12.8676 | 11.9199 | 10.9501 | 6.9819 | 2.1535 | -1.1986 | -4.1937 | -6.105 | 16.4929 | 14.5318 | 13.6167 | 13.0251 | 12.3051 | 11.482 | 10.4052 | 8.7695 | 7.0583 | 5.3854 | 0.54637 | -3.6981 | -6.4574 | -8.2803 | -8.5072 | 21.3929 | 19.4318 | 18.5167 | 17.9251 | 17.2051 | 16.382 | 15.3052 | 13.6695 | 11.9583 | 10.2854 | 5.4464 | 1.2019 | -1.5574 | -3.3803 | -3.6019 | 16.4929 | 15.2143 | 14.5376 | 14.1048 | 13.6499 | 13.1257 | 12.5419 | 11.917 | 11.1951 | 10.4605 | 8.1069 | 5.5965 | 3.7807 | 1.8459 | 0.14154 | 21.3929 | 20.1143 | 19.4376 | 19.0048 | 18.5499 | 18.0257 | 17.4419 | 16.817 | 16.0951 | 15.3605 | 13.0069 | 10.4965 | 8.6807 | 6.7459 | 5.3112 | 16.4929 | 13.3726 | 12.1138 | 11.3782 | 10.5328 | 9.6517 | 8.5725 | 6.8912 | 5.1739 | 3.4424 | -1.6915 | -6.1909 | -9.1108 | -10.9754 | -11.2028 | 21.3929 | 18.2726 | 17.0138 | 16.2782 | 15.4328 | 14.5517 | 13.4725 | 11.7912 | 10.0739 | 8.3424 | 3.2085 | -1.2909 | -4.2108 | -6.0754 | -6.2521 | 376412 | 389026 | ALTRINCHAM | CARRINGTON
| Broadway | 11.9506 | 11.2976 | 11.0605 | 10.9322 | 10.7566 | 10.5756 | 10.4105 | 10.2497 | 10.0231 | 9.818 | 8.2361 | 5.4112 | 3.0328 | 0.4403 | -1.8311 | 16.0876 | 15.4346 | 15.1975 | 15.0692 | 14.8936 | 14.7126 | 14.5475 | 14.3867 | 14.1601 | 13.955 | 12.3731 | 9.5482 | 7.1698 | 4.5773 | 2.1537 | 11.9506 | 11.5957 | 11.3989 | 11.2456 | 11.0621 | 10.8838 | 10.6633 | 10.4022 | 10.1564 | 9.9086 | 9.164 | 8.4306 | 7.7005 | 6.9045 | 6.3014 | 16.0876 | 15.7327 | 15.5359 | 15.3826 | 15.1991 | 15.0208 | 14.8003 | 14.5392 | 14.2934 | 14.0456 | 13.301 | 12.5676 | 11.8375 | 11.0415 | 10.5246 | 11.9506 | 11.2293 | 10.9992 | 10.9106 | 10.7761 | 10.6438 | 10.5475 | 10.464 | 10.3402 | 10.2185 | 8.8667 | 6.2194 | 4.0246 | 1.643 | -0.36554 | 16.0876 | 15.3663 | 15.1362 | 15.0476 | 14.9131 | 14.7808 | 14.6845 | 14.601 | 14.4772 | 14.3555 | 13.0037 | 10.3564 | 8.1616 | 5.78 | 3.5716 | 11.9506 | 11.6057 | 11.4665 | 11.3774 | 11.2203 | 11.0397 | 10.7155 | 9.8639 | 8.9485 | 8.0259 | 5.3557 | 2.8442 | 0.84572 | -0.44526 | 0.4453 | 16.0876 | 15.7427 | 15.6035 | 15.5144 | 15.3573 | 15.1767 | 14.8525 | 14.0009 | 13.0855 | 12.1629 | 9.4927 | 6.9812 | 4.9827 | 3.6917 | 4.3803 | 11.9506 | 11.4121 | 11.2292 | 11.162 | 11.0867 | 10.9953 | 10.8968 | 10.7874 | 10.5894 | 10.3929 | 9.6778 | 8.8652 | 8.2256 | 7.6068 | 7.3707 | 16.0876 | 15.5491 | 15.3662 | 15.299 | 15.2237 | 15.1323 | 15.0338 | 14.9244 | 14.7264 | 14.5299 | 13.8148 | 13.0022 | 12.3626 | 11.7438 | 11.4895 | 11.9506 | 11.2897 | 11.0326 | 10.8638 | 10.6351 | 10.4089 | 10.0318 | 9.1056 | 8.14 | 7.1674 | 4.3225 | 1.6284 | -0.58391 | -2.0774 | -1.3956 | 16.0876 | 15.4267 | 15.1696 | 15.0008 | 14.7721 | 14.5459 | 14.1688 | 13.2426 | 12.277 | 11.3044 | 8.4595 | 5.7654 | 3.5531 | 2.0596 | 2.585 | 344792 | 464471 | LANCASTER | HEYSHAM
| Buckshaw | 12.8926 | 10.5072 | 9.8566 | 9.6025 | 9.312 | 9.0043 | 8.6759 | 8.3185 | 7.8523 | 7.3664 | 5.5237 | 3.4115 | 1.9212 | 0.58854 | -0.44514 | 17.3926 | 15.0072 | 14.3566 | 14.1025 | 13.812 | 13.5043 | 13.1759 | 12.8185 | 12.3523 | 11.8664 | 10.0237 | 7.9115 | 6.4212 | 5.0885 | 4.0637 | 12.8926 | 11.8255 | 11.4689 | 11.2878 | 11.0931 | 10.8888 | 10.6313 | 10.2955 | 9.9365 | 9.5564 | 8.3347 | 6.9877 | 5.6698 | 4.2251 | 3.1598 | 17.3926 | 16.3255 | 15.9689 | 15.7878 | 15.5931 | 15.3888 | 15.1313 | 14.7955 | 14.4365 | 14.0564 | 12.8347 | 11.4877 | 10.1698 | 8.7251 | 7.8243 | 12.8926 | 10.1172 | 9.3718 | 9.0961 | 8.78 | 8.4501 | 8.1147 | 7.755 | 7.3227 | 6.8415 | 4.9337 | 2.7724 | 1.3186 | 0.17269 | -0.49488 | 17.3926 | 14.6172 | 13.8718 | 13.5961 | 13.28 | 12.9501 | 12.6147 | 12.255 | 11.8227 | 11.3415 | 9.4337 | 7.2724 | 5.8186 | 4.6727 | 4.0141 | 12.8926 | 10.9807 | 10.4103 | 10.1589 | 9.8501 | 9.5058 | 9.0804 | 8.4336 | 7.7195 | 6.9724 | 4.7791 | 2.9026 | 1.7499 | 1.0722 | 0.99118 | 17.3926 | 15.4807 | 14.9103 | 14.6589 | 14.3501 | 14.0058 | 13.5804 | 12.9336 | 12.2195 | 11.4724 | 9.2791 | 7.4026 | 6.2499 | 5.5722 | 5.4931 | 12.8926 | 10.9092 | 10.3512 | 10.141 | 9.9239 | 9.6784 | 9.3999 | 9.0961 | 8.6729 | 8.2241 | 6.7394 | 5.256 | 4.2453 | 3.3851 | 2.7705 | 17.3926 | 15.4092 | 14.8512 | 14.641 | 14.4239 | 14.1784 | 13.8999 | 13.5961 | 13.1729 | 12.7241 | 11.2394 | 9.756 | 8.7453 | 7.8851 | 7.3612 | 12.8926 | 9.8608 | 9.0532 | 8.7493 | 8.3972 | 8.033 | 7.5884 | 6.9156 | 6.199 | 5.4475 | 3.1554 | 1.0929 | -0.2444 | -1.0713 | -1.2668 | 17.3926 | 14.3608 | 13.5532 | 13.2493 | 12.8972 | 12.533 | 12.0884 | 11.4156 | 10.699 | 9.9475 | 7.6554 | 5.5929 | 4.2556 | 3.4287 | 3.2589 | 356748 | 421312 | LEYLAND | PENWORTHAM
| Burnley | 10.5885 | 10.2118 | 10.0678 | 9.996 | 9.8684 | 9.7358 | 9.6321 | 9.5352 | 9.377 | 9.2365 | 7.774 | 4.9355 | 2.5158 | -0.092789 | -2.2036 | 10.5885 | 10.2118 | 10.0678 | 9.996 | 9.8684 | 9.7358 | 9.6321 | 9.5352 | 9.377 | 9.2365 | 7.774 | 4.9355 | 2.5158 | -0.092789 | -2.4027 | 10.5885 | 10.4409 | 10.3315 | 10.2459 | 10.1391 | 10.0106 | 9.8373 | 9.6094 | 9.3963 | 9.1828 | 8.541 | 7.8634 | 7.1832 | 6.4618 | 5.9732 | 10.5885 | 10.4409 | 10.3315 | 10.2459 | 10.1391 | 10.0106 | 9.8373 | 9.6094 | 9.3963 | 9.1828 | 8.541 | 7.8634 | 7.1832 | 6.4618 | 6.048 | 10.5885 | 10.1792 | 10.0458 | 10.0082 | 9.9147 | 9.8215 | 9.7736 | 9.7371 | 9.6619 | 9.587 | 8.3222 | 5.6702 | 3.4023 | 0.97467 | -0.89884 | 10.5885 | 10.1792 | 10.0458 | 10.0082 | 9.9147 | 9.8215 | 9.7736 | 9.7371 | 9.6619 | 9.587 | 8.3222 | 5.6702 | 3.4023 | 0.97467 | -1.1413 | 10.5885 | 10.4821 | 10.4248 | 10.3979 | 10.2945 | 10.1711 | 9.891 | 9.0149 | 8.1004 | 7.1904 | 4.57 | 2.0728 | 0.015893 | -1.2871 | -0.168 | 10.5885 | 10.4821 | 10.4248 | 10.3979 | 10.2945 | 10.1711 | 9.891 | 9.0149 | 8.1004 | 7.1904 | 4.57 | 2.0728 | 0.015893 | -1.2871 | -0.41259 | 10.5885 | 10.406 | 10.325 | 10.3082 | 10.2883 | 10.2416 | 10.1746 | 10.0963 | 9.939 | 9.7853 | 9.2172 | 8.4848 | 7.8895 | 7.3629 | 7.1662 | 10.5885 | 10.406 | 10.325 | 10.3082 | 10.2883 | 10.2416 | 10.1746 | 10.0963 | 9.939 | 9.7853 | 9.2172 | 8.4848 | 7.8895 | 7.3629 | 7.1522 | 10.5885 | 10.285 | 10.1387 | 10.0412 | 9.8735 | 9.7072 | 9.3752 | 8.4259 | 7.4581 | 6.4943 | 3.7017 | 1.0389 | -1.1987 | -2.7678 | -1.9433 | 10.5885 | 10.285 | 10.1387 | 10.0412 | 9.8735 | 9.7072 | 9.3752 | 8.4259 | 7.4581 | 6.4943 | 3.7017 | 1.0389 | -1.1987 | -2.7678 | -2.123 | 385569 | 434469 | BURNLEY | ROCHDALE
| Burnley Centre | 9.6035 | 9.2193 | 8.7469 | 8.3434 | 7.9097 | 7.4662 | 7.0436 | 6.8616 | 6.6696 | 6.4947 | 5.3041 | 3.2112 | 1.2453 | -1.0055 | -2.8841 | 9.6035 | 9.2193 | 8.7469 | 8.3434 | 7.9097 | 7.4662 | 7.0436 | 6.8616 | 6.6696 | 6.4947 | 5.3041 | 3.2112 | 1.2453 | -1.0055 | -3.0264 | 9.6035 | 9.3935 | 9.0727 | 8.7714 | 8.4612 | 8.1251 | 7.7336 | 7.338 | 7.1213 | 6.9098 | 6.2863 | 5.6584 | 5.1175 | 4.5453 | 4.1257 | 9.6035 | 9.3935 | 9.0727 | 8.7714 | 8.4612 | 8.1251 | 7.7336 | 7.338 | 7.1213 | 6.9098 | 6.2863 | 5.6584 | 5.1175 | 4.5453 | 4.1866 | 9.6035 | 9.1782 | 8.6988 | 8.2935 | 7.8591 | 7.4152 | 6.9901 | 6.8074 | 6.6458 | 6.5047 | 5.4217 | 3.4598 | 1.7811 | -0.26777 | -1.8923 | 9.6035 | 9.1782 | 8.6988 | 8.2935 | 7.8591 | 7.4152 | 6.9901 | 6.8074 | 6.6458 | 6.5047 | 5.4217 | 3.4598 | 1.7811 | -0.26777 | -2.0794 | 9.6035 | 9.4228 | 9.0294 | 8.6825 | 8.2995 | 7.8963 | 7.3748 | 6.6858 | 5.9747 | 5.287 | 3.244 | 1.0137 | -0.77844 | -1.9199 | -1.0854 | 9.6035 | 9.4228 | 9.0294 | 8.6825 | 8.2995 | 7.8963 | 7.3748 | 6.6858 | 5.9747 | 5.287 | 3.244 | 1.0137 | -0.77844 | -1.9199 | -1.2769 | 9.6035 | 9.4306 | 9.0111 | 8.644 | 8.2892 | 7.9208 | 7.5366 | 7.3649 | 7.1565 | 6.9502 | 6.2865 | 5.5809 | 5.106 | 4.6625 | 4.5322 | 9.6035 | 9.4306 | 9.0111 | 8.644 | 8.2892 | 7.9208 | 7.5366 | 7.3649 | 7.1565 | 6.9502 | 6.2865 | 5.5809 | 5.106 | 4.6625 | 4.5201 | 9.6035 | 9.2627 | 8.7914 | 8.3793 | 7.9336 | 7.4845 | 6.9187 | 6.1634 | 5.4299 | 4.7211 | 2.529 | 0.19734 | -1.7204 | -3.0574 | -2.4641 | 9.6035 | 9.2627 | 8.7914 | 8.3793 | 7.9336 | 7.4845 | 6.9187 | 6.1634 | 5.4299 | 4.7211 | 2.529 | 0.19734 | -1.7204 | -3.0574 | -2.6012 | 384308 | 432288 | BURNLEY | ROCHDALE
| Burnley North | 5.3338 | 4.2446 | 3.9286 | 3.7744 | 3.5737 | 3.3623 | 3.134 | 2.6814 | 1.8193 | 0.94533 | -1.991 | -5.0139 | -7.2118 | -9.0708 | -10.1724 | 11.3338 | 10.2446 | 9.9286 | 9.7744 | 9.5737 | 9.3623 | 9.134 | 8.6814 | 7.8193 | 6.9453 | 4.009 | 0.98606 | -1.2118 | -3.0708 | -4.1813 | 5.3338 | 4.8159 | 4.6312 | 4.5078 | 4.3548 | 4.1795 | 3.961 | 3.6724 | 3.3879 | 3.0766 | 1.2764 | -1.1774 | -3.2869 | -5.1969 | -6.2557 | 11.3338 | 10.8159 | 10.6312 | 10.5078 | 10.3548 | 10.1795 | 9.961 | 9.6724 | 9.3879 | 9.0766 | 7.2764 | 4.8226 | 2.7131 | 0.80307 | -0.12332 | 5.3338 | 4.1094 | 3.7871 | 3.665 | 3.4996 | 3.3304 | 3.1913 | 3.0374 | 2.577 | 1.8189 | -1.202 | -4.7696 | -7.4815 | -9.849 | -11.2557 | 11.3338 | 10.1094 | 9.7871 | 9.665 | 9.4996 | 9.3304 | 9.1913 | 9.0374 | 8.577 | 7.8189 | 4.798 | 1.2304 | -1.4815 | -3.849 | -5.2364 | 5.3338 | 4.5685 | 4.3553 | 4.2692 | 4.1201 | 3.9418 | 3.6389 | 2.8523 | 1.7482 | 0.63175 | -2.6531 | -5.6827 | -7.9541 | -9.6044 | -9.7606 | 11.3338 | 10.5685 | 10.3553 | 10.2692 | 10.1201 | 9.9418 | 9.6389 | 8.8523 | 7.7482 | 6.6317 | 3.3469 | 0.31729 | -1.9541 | -3.6044 | -3.7832 | 5.3338 | 4.439 | 4.1886 | 4.0905 | 3.9801 | 3.8409 | 3.6847 | 3.4977 | 3.1954 | 2.5197 | 0.05836 | -2.3689 | -4.1262 | -5.725 | -6.5282 | 11.3338 | 10.439 | 10.1886 | 10.0905 | 9.9801 | 9.8409 | 9.6847 | 9.4977 | 9.1954 | 8.5197 | 6.0584 | 3.6311 | 1.8738 | 0.27503 | -0.43998 | 5.3338 | 4.0687 | 3.721 | 3.5748 | 3.3747 | 3.1712 | 2.8582 | 2.1085 | 1.298 | 0.48435 | -2.7271 | -5.9958 | -8.4685 | -10.329 | -10.6262 | 11.3338 | 10.0687 | 9.721 | 9.5748 | 9.3747 | 9.1712 | 8.8582 | 8.1085 | 7.298 | 6.4843 | 3.2729 | 0.0042241 | -2.4685 | -4.329 | -4.5973 | 384418 | 434168 | BURNLEY | ROCHDALE
| Burrow Beck | 6.4337 | 3.2488 | 0.96629 | -0.4414 | -1.9177 | -3.4401 | -4.9977 | -6.6227 | -8.4104 | -8.9959 | -12.7433 | -16.8267 | -19.5758 | -21.7224 | -23.5026 | 10.4337 | 7.2488 | 4.9663 | 3.5586 | 2.0823 | 0.55986 | -0.99768 | -2.6227 | -4.4104 | -4.9959 | -8.7433 | -12.8267 | -15.5758 | -17.7224 | -19.5726 | 6.4337 | 4.9932 | 4.6117 | 4.1695 | 3.678 | 3.1424 | 2.5263 | 1.8275 | 1.1776 | 0.70714 | -0.83917 | -2.9873 | -5.7758 | -8.7969 | -10.7775 | 10.4337 | 8.9932 | 8.6117 | 8.1695 | 7.678 | 7.1424 | 6.5263 | 5.8275 | 5.1776 | 4.7071 | 3.1608 | 1.0127 | -1.7758 | -4.7969 | -6.525 | 6.4337 | 2.8116 | 0.48124 | -0.86335 | -2.2717 | -3.7084 | -5.1411 | -6.6169 | -8.2009 | -8.6179 | -12.226 | -16.5904 | -19.655 | -21.8614 | -23.4775 | 10.4337 | 6.8116 | 4.4812 | 3.1367 | 1.7283 | 0.29159 | -1.1411 | -2.6169 | -4.2009 | -4.6179 | -8.226 | -12.5904 | -15.655 | -17.8614 | -19.5922 | 6.4337 | 4.0293 | 1.9657 | 0.67076 | -0.71431 | -2.1741 | -3.7763 | -5.8145 | -7.9978 | -9.1531 | -13.2638 | -17.1102 | -19.825 | -21.5729 | -21.1675 | 10.4337 | 8.0293 | 5.9657 | 4.6708 | 3.2857 | 1.8259 | 0.22366 | -1.8145 | -3.9978 | -5.1531 | -9.2638 | -13.1102 | -15.825 | -17.5729 | -17.2981 | 6.4337 | 4.0347 | 1.9392 | 0.61771 | -0.72513 | -2.1363 | -3.6183 | -5.1614 | -6.8683 | -7.3904 | -10.1008 | -13.4262 | -15.6216 | -17.0374 | -17.4443 | 10.4337 | 8.0347 | 5.9392 | 4.6177 | 3.2749 | 1.8637 | 0.38169 | -1.1614 | -2.8683 | -3.3904 | -6.1008 | -9.4262 | -11.6216 | -13.0374 | -13.4406 | 6.4337 | 2.5461 | 0.12928 | -1.2849 | -2.771 | -4.2826 | -5.9345 | -8.0437 | -10.2451 | -11.2895 | -15.2002 | -18.9061 | -21.8679 | -23.9814 | -23.7588 | 10.4337 | 6.5461 | 4.1293 | 2.7151 | 1.229 | -0.28264 | -1.9345 | -4.0437 | -6.2451 | -7.2895 | -11.2002 | -14.9061 | -17.8679 | -19.9814 | -19.851 | 347903 | 458401 | LANCASTER | HEYSHAM | Firm Capacity marginally exceeded in FY27. There will potentiallty be a new connections driven/MSA primary in the Lancaster area to offload this primary.
| Burscough Bridge | 6.2791 | 5.7966 | 5.5976 | 5.4919 | 5.339 | 5.1548 | 4.9676 | 4.7463 | 4.4723 | 4.2035 | 2.6803 | 0.38268 | -1.303 | -2.7641 | -3.8898 | 9.7791 | 9.2966 | 9.0976 | 8.9919 | 8.839 | 8.6548 | 8.4676 | 8.2463 | 7.9723 | 7.7035 | 6.1803 | 3.8827 | 2.197 | 0.73586 | -0.45508 | 6.2791 | 6.0654 | 5.8889 | 5.7406 | 5.5676 | 5.3602 | 5.0974 | 4.77 | 4.566 | 4.3575 | 3.6674 | 2.4088 | 1.2209 | -0.073754 | -0.83017 | 9.7791 | 9.5654 | 9.3889 | 9.2406 | 9.0676 | 8.8602 | 8.5974 | 8.27 | 8.066 | 7.8575 | 7.1674 | 5.9088 | 4.7209 | 3.4262 | 2.7655 | 6.2791 | 5.7262 | 5.5162 | 5.4121 | 5.262 | 5.086 | 4.9101 | 4.7075 | 4.4845 | 4.2688 | 3.1615 | 1.0958 | -0.89307 | -2.5235 | -3.6164 | 9.7791 | 9.2262 | 9.0162 | 8.9121 | 8.762 | 8.586 | 8.4101 | 8.2075 | 7.9845 | 7.7688 | 6.6615 | 4.5958 | 2.6069 | 0.97654 | -0.10047 | 6.2791 | 6.0401 | 5.9319 | 5.863 | 5.7432 | 5.5832 | 5.3302 | 4.8088 | 4.2458 | 3.687 | 1.9659 | 0.02339 | -1.4287 | -2.2723 | -2.1303 | 9.7791 | 9.5401 | 9.4319 | 9.363 | 9.2432 | 9.0832 | 8.8302 | 8.3088 | 7.7458 | 7.187 | 5.4659 | 3.5234 | 2.0713 | 1.2277 | 1.3583 | 6.2791 | 5.9961 | 5.8574 | 5.7967 | 5.729 | 5.6231 | 5.4671 | 5.2561 | 4.9692 | 4.6682 | 3.5531 | 1.8427 | 0.66169 | -0.24726 | -0.47256 | 9.7791 | 9.4961 | 9.3574 | 9.2967 | 9.229 | 9.1231 | 8.9671 | 8.7561 | 8.4692 | 8.1682 | 7.0531 | 5.3427 | 4.1617 | 3.2527 | 3.0139 | 6.2791 | 5.7837 | 5.5748 | 5.4583 | 5.2905 | 5.1105 | 4.8482 | 4.2943 | 3.7221 | 3.1563 | 1.1622 | -1.0887 | -2.7594 | -3.7752 | -3.4918 | 9.7791 | 9.2837 | 9.0748 | 8.9583 | 8.7905 | 8.6105 | 8.3482 | 7.7943 | 7.2221 | 6.6563 | 4.6622 | 2.4113 | 0.74059 | -0.27524 | -0.067233 | 344595 | 412486 | WRIGHTINGTON | PENWORTHAM
| Bury Town Centre | 10.28 | 8.6148 | 7.9453 | 7.6045 | 7.2154 | 6.8097 | 6.4094 | 6.0081 | 5.5753 | 5.1652 | 3.2408 | 0.36771 | -2.1053 | -4.8173 | -7.1449 | 14.417 | 12.7518 | 12.0823 | 11.7415 | 11.3524 | 10.9467 | 10.5464 | 10.1451 | 9.7123 | 9.3022 | 7.3778 | 4.5047 | 2.0317 | -0.68033 | -3.0863 | 10.28 | 9.8462 | 9.5812 | 9.3918 | 9.1854 | 8.9493 | 8.6567 | 8.3035 | 8.0126 | 7.721 | 6.8443 | 5.9685 | 5.1758 | 4.319 | 3.6418 | 14.417 | 13.9832 | 13.7182 | 13.5288 | 13.3224 | 13.0863 | 12.7937 | 12.4405 | 12.1496 | 11.858 | 10.9813 | 10.1055 | 9.3128 | 8.456 | 7.8872 | 10.28 | 8.3612 | 7.6408 | 7.2991 | 6.9105 | 6.5059 | 6.1056 | 5.7062 | 5.3114 | 4.943 | 3.1481 | 0.42147 | -1.8939 | -4.3807 | -6.4143 | 14.417 | 12.4982 | 11.7778 | 11.4361 | 11.0475 | 10.6429 | 10.2426 | 9.8432 | 9.4484 | 9.08 | 7.2851 | 4.5585 | 2.2431 | -0.24369 | -2.411 | 10.28 | 9.0888 | 8.5663 | 8.2966 | 7.9617 | 7.5764 | 7.0597 | 6.1534 | 5.2176 | 4.3019 | 1.6287 | -0.9949 | -3.3066 | -5.1044 | -4.9605 | 14.417 | 13.2258 | 12.7033 | 12.4336 | 12.0987 | 11.7134 | 11.1967 | 10.2904 | 9.3546 | 8.4389 | 5.7657 | 3.1421 | 0.83045 | -0.96744 | -0.96859 | 10.28 | 9.6075 | 9.1786 | 8.9134 | 8.6506 | 8.3446 | 7.997 | 7.627 | 7.1955 | 6.7653 | 5.3886 | 3.9194 | 2.7295 | 1.413 | 0.61534 | 14.417 | 13.7445 | 13.3156 | 13.0504 | 12.7876 | 12.4816 | 12.134 | 11.764 | 11.3325 | 10.9023 | 9.5256 | 8.0564 | 6.8665 | 5.55 | 4.7695 | 10.28 | 8.2784 | 7.5249 | 7.1659 | 6.7524 | 6.3302 | 5.7833 | 4.8082 | 3.8293 | 2.8746 | 0.11146 | -2.5592 | -4.8372 | -6.8185 | -6.8202 | 14.417 | 12.4154 | 11.6619 | 11.3029 | 10.8894 | 10.4672 | 9.9203 | 8.9452 | 7.9663 | 7.0116 | 4.2485 | 1.5778 | -0.70021 | -2.6815 | -2.7822 | 380863 | 410807 | BURY | KEARSLEY
| Campbell St | 5.5849 | 4.8227 | 4.6322 | 4.5817 | 4.4327 | 9.5586 | 9.1852 | 8.7138 | 8.1698 | 7.4546 | 3.4121 | -0.97481 | -4.2275 | -6.9865 | -8.7548 | 9.0849 | 8.3227 | 8.1322 | 8.0817 | 7.9327 | 14.1586 | 13.7852 | 13.3138 | 12.7698 | 12.0546 | 8.0121 | 3.6252 | 0.37248 | -2.3865 | -4.1896 | 5.5849 | 5.3116 | 5.201 | 5.1318 | 5.0257 | 10.2943 | 10.1081 | 9.7995 | 9.4835 | 9.0699 | 7.4977 | 4.6803 | 1.8519 | -0.81836 | -2.3534 | 9.0849 | 8.8116 | 8.701 | 8.6318 | 8.5257 | 14.8943 | 14.7081 | 14.3995 | 14.0835 | 13.6699 | 12.0977 | 9.2803 | 6.4519 | 3.7816 | 2.4376 | 5.5849 | 4.7211 | 4.5243 | 4.4957 | 4.3762 | 9.6403 | 9.5094 | 9.1701 | 8.7744 | 8.3374 | 4.3484 | -0.62708 | -4.48 | -7.8348 | -9.9495 | 9.0849 | 8.2211 | 8.0243 | 7.9957 | 7.8762 | 14.2403 | 14.1094 | 13.7701 | 13.3744 | 12.9374 | 8.9484 | 3.9729 | 0.11998 | -3.2348 | -5.3497 | 5.5849 | 5.21 | 5.1223 | 5.1033 | 4.969 | 10.1591 | 9.6832 | 8.6183 | 7.4325 | 6.1092 | 1.6778 | -2.6778 | -5.8474 | -8.0249 | -8.0884 | 9.0849 | 8.71 | 8.6223 | 8.6033 | 8.469 | 14.7591 | 14.2832 | 13.2183 | 12.0325 | 10.7092 | 6.2778 | 1.9222 | -1.2474 | -3.4249 | -3.5438 | 5.5849 | 5.1587 | 5.0659 | 5.084 | 5.0758 | 10.4388 | 10.3066 | 10.0061 | 9.5675 | 9.0866 | 6.5096 | 2.9423 | 0.2972 | -1.8736 | -2.8608 | 9.0849 | 8.6587 | 8.5659 | 8.584 | 8.5758 | 15.0388 | 14.9066 | 14.6061 | 14.1675 | 13.6866 | 11.1096 | 7.5423 | 4.8972 | 2.7264 | 1.8197 | 5.5849 | 4.8431 | 4.6355 | 4.5578 | 4.3727 | 9.5762 | 8.8641 | 7.5474 | 6.1869 | 4.7974 | 0.16325 | -4.4372 | -7.7071 | -10.1831 | -10.6022 | 9.0849 | 8.3431 | 8.1355 | 8.0578 | 7.8727 | 14.1762 | 13.4641 | 12.1474 | 10.7869 | 9.3974 | 4.7632 | 0.16282 | -3.1071 | -5.5831 | -5.9868 | 372937 | 406428 | KEARSLEY LOCAL | KEARSLEY
| Cannon St | 13.1314 | 8.7527 | 7.4965 | 7.2294 | 7.0483 | 6.8863 | 6.7609 | 6.642 | 6.3487 | 6.074 | 4.9161 | 3.2791 | 1.973 | 0.62098 | -0.50892 | 34.1314 | 29.7527 | 28.4965 | 28.2294 | 28.0483 | 27.8863 | 27.7609 | 27.642 | 27.3487 | 27.074 | 25.9161 | 24.2791 | 22.973 | 21.621 | 20.4126 | 13.1314 | 11.8315 | 11.1588 | 10.8292 | 10.5873 | 10.3344 | 10.0619 | 9.757 | 9.3836 | 9.0167 | 8.0106 | 7.1097 | 6.409 | 5.6932 | 5.0546 | 34.1314 | 32.8315 | 32.1588 | 31.8292 | 31.5873 | 31.3344 | 31.0619 | 30.757 | 30.3836 | 30.0167 | 29.0106 | 28.1097 | 27.409 | 26.6932 | 26.1374 | 13.1314 | 8.0434 | 6.645 | 6.3707 | 6.1861 | 6.0208 | 5.8897 | 5.7657 | 5.5554 | 5.3787 | 4.532 | 3.2524 | 2.3353 | 1.5366 | 1.1345 | 34.1314 | 29.0434 | 27.645 | 27.3707 | 27.1861 | 27.0208 | 26.8897 | 26.7657 | 26.5554 | 26.3787 | 25.532 | 24.2524 | 23.3353 | 22.5366 | 21.9201 | 13.1314 | 9.4886 | 8.4176 | 8.177 | 8.0281 | 7.8908 | 7.6974 | 7.2596 | 6.687 | 6.1446 | 4.6866 | 3.4192 | 2.5322 | 2.1866 | 3.0427 | 34.1314 | 30.4886 | 29.4176 | 29.177 | 29.0281 | 28.8908 | 28.6974 | 28.2596 | 27.687 | 27.1446 | 25.6866 | 24.4192 | 23.5322 | 23.1866 | 23.8242 | 13.1314 | 10.8013 | 9.9734 | 9.7331 | 9.6076 | 9.4942 | 9.383 | 9.2565 | 8.9471 | 8.646 | 7.8011 | 7.0412 | 6.5739 | 6.1933 | 6.2808 | 34.1314 | 31.8013 | 30.9734 | 30.7331 | 30.6076 | 30.4942 | 30.383 | 30.2565 | 29.9471 | 29.646 | 28.8011 | 28.0412 | 27.5739 | 27.1933 | 27.2081 | 13.1314 | 7.3668 | 5.825 | 5.5321 | 5.3325 | 5.1561 | 4.9239 | 4.4329 | 3.848 | 3.2949 | 1.8166 | 0.54554 | -0.34513 | -0.69248 | 0.14713 | 34.1314 | 28.3668 | 26.825 | 26.5321 | 26.3325 | 26.1561 | 25.9239 | 25.4329 | 24.848 | 24.2949 | 22.8166 | 21.5455 | 20.6549 | 20.3075 | 20.9339 | 384064 | 398635 | RED BANK | WHITEGATE
| Capontree | 15.4073 | 14.8743 | 14.6864 | 14.5755 | 14.3739 | 14.1423 | 13.9179 | 13.6802 | 13.4039 | 13.1287 | 11.7204 | 9.6744 | 8.0969 | 6.6888 | 5.4425 | 17.7443 | 17.2113 | 17.0234 | 16.9125 | 16.7109 | 16.4793 | 16.2549 | 16.0172 | 15.7409 | 15.4657 | 14.0574 | 12.0114 | 10.4339 | 9.0258 | 7.677 | 15.4073 | 15.1948 | 15.0399 | 14.8907 | 14.711 | 14.5364 | 14.3102 | 14.0183 | 13.8067 | 13.5828 | 12.8498 | 12.0444 | 11.2182 | 10.2321 | 9.4895 | 17.7443 | 17.5318 | 17.3769 | 17.2277 | 17.048 | 16.8734 | 16.6472 | 16.3553 | 16.1437 | 15.9198 | 15.1868 | 14.3814 | 13.5552 | 12.5691 | 11.9369 | 15.4073 | 14.8134 | 14.627 | 14.543 | 14.3712 | 14.1778 | 14.0101 | 13.8398 | 13.652 | 13.4516 | 12.2025 | 10.2096 | 8.6653 | 7.3476 | 6.2552 | 17.7443 | 17.1504 | 16.964 | 16.88 | 16.7082 | 16.5148 | 16.3471 | 16.1768 | 15.989 | 15.7886 | 14.5395 | 12.5466 | 11.0023 | 9.6846 | 8.4617 | 15.4073 | 15.1051 | 14.9828 | 14.8713 | 14.6975 | 14.4931 | 14.1994 | 13.5808 | 12.9109 | 12.2212 | 10.1976 | 8.3551 | 7.0491 | 6.3893 | 6.981 | 17.7443 | 17.4421 | 17.3198 | 17.2083 | 17.0345 | 16.8301 | 16.5364 | 15.9178 | 15.2479 | 14.5582 | 12.5346 | 10.6921 | 9.3861 | 8.7263 | 9.1813 | 15.4073 | 15.131 | 14.9961 | 14.9066 | 14.7948 | 14.6786 | 14.5347 | 14.3339 | 14.0622 | 13.7697 | 12.6843 | 11.4769 | 10.6731 | 10.0046 | 9.7727 | 17.7443 | 17.468 | 17.3331 | 17.2436 | 17.1318 | 17.0156 | 16.8717 | 16.6709 | 16.3992 | 16.1067 | 15.0213 | 13.8139 | 13.0101 | 12.3416 | 12.0718 | 15.4073 | 14.8454 | 14.6324 | 14.4631 | 14.238 | 14.002 | 13.676 | 13.0154 | 12.3348 | 11.633 | 9.5058 | 7.4896 | 6.0064 | 5.1825 | 5.6347 | 17.7443 | 17.1824 | 16.9694 | 16.8001 | 16.575 | 16.339 | 16.013 | 15.3524 | 14.6718 | 13.97 | 11.8428 | 9.8266 | 8.3434 | 7.5195 | 7.8651 | 352906 | 559671 | CARLISLE | HARKER
| Carleton | 2.6301 | 2.4649 | 2.3922 | 2.3461 | 2.2831 | 2.2164 | 2.0327 | 1.7835 | 1.5663 | 1.3595 | 0.69775 | 0.0088815 | -0.48423 | -0.84927 | -1.0812 | 5.1301 | 4.9649 | 4.8922 | 4.8461 | 4.7831 | 4.7164 | 4.5327 | 4.2835 | 4.0663 | 3.8595 | 3.1977 | 2.5089 | 2.0158 | 1.6507 | 1.4143 | 2.6301 | 2.5893 | 2.5398 | 2.4931 | 2.4435 | 2.3952 | 2.2136 | 2.0097 | 1.9031 | 1.7941 | 1.4708 | 1.0669 | 0.69861 | 0.34324 | 0.11571 | 5.1301 | 5.0893 | 5.0398 | 4.9931 | 4.9435 | 4.8952 | 4.7136 | 4.5097 | 4.4031 | 4.2941 | 3.9708 | 3.5669 | 3.1986 | 2.8432 | 2.6481 | 2.6301 | 2.4419 | 2.3651 | 2.3186 | 2.2554 | 2.1537 | 1.9172 | 1.6338 | 1.4013 | 1.1774 | 0.43955 | -0.34367 | -0.90978 | -1.3325 | -1.5913 | 5.1301 | 4.9419 | 4.8651 | 4.8186 | 4.7554 | 4.6537 | 4.4172 | 4.1338 | 3.9013 | 3.6774 | 2.9396 | 2.1563 | 1.5902 | 1.1675 | 0.90712 | 2.6301 | 2.512 | 2.4557 | 2.4007 | 2.343 | 2.2748 | 2.1007 | 1.807 | 1.5498 | 1.2975 | 0.54449 | -0.1919 | -0.69585 | -1.0258 | -1.0396 | 5.1301 | 5.012 | 4.9557 | 4.9007 | 4.843 | 4.7748 | 4.6007 | 4.307 | 4.0498 | 3.7975 | 3.0445 | 2.3081 | 1.8041 | 1.4742 | 1.4482 | 2.6301 | 2.5832 | 2.5362 | 2.499 | 2.4618 | 2.4261 | 2.3429 | 2.1381 | 1.9569 | 1.7728 | 1.1572 | 0.50061 | 0.031216 | -0.38165 | -0.58193 | 5.1301 | 5.0832 | 5.0362 | 4.999 | 4.9618 | 4.9261 | 4.8429 | 4.6381 | 4.4569 | 4.2728 | 3.6572 | 3.0006 | 2.5312 | 2.1184 | 1.9256 | 2.6301 | 2.4313 | 2.3443 | 2.2672 | 2.1903 | 2.1148 | 1.9885 | 1.6996 | 1.4417 | 1.1885 | 0.43992 | -0.24872 | -0.72319 | -1.0251 | -1.0447 | 5.1301 | 4.9313 | 4.8443 | 4.7672 | 4.6903 | 4.6148 | 4.4885 | 4.1996 | 3.9417 | 3.6885 | 2.9399 | 2.2513 | 1.7768 | 1.4749 | 1.4495 | 308796 | 498305 | EGREMONT | HARKER
| Carlisle North | 9.6115 | 3.765 | 2.5834 | 2.4159 | 2.2672 | 2.0767 | 1.8284 | 1.4436 | 0.84272 | 0.18345 | -2.0527 | -4.1361 | -5.439 | -6.2804 | -6.6354 | 30.1115 | 24.265 | 23.0834 | 22.9159 | 22.7672 | 22.5767 | 22.3284 | 21.9436 | 21.3427 | 20.6834 | 18.4473 | 16.3639 | 15.061 | 14.2196 | 13.7838 | 9.6115 | 7.4754 | 6.9723 | 6.8558 | 6.7871 | 6.6913 | 6.5483 | 6.3646 | 6.0254 | 5.6501 | 4.3135 | 2.7253 | 1.1327 | -0.6727 | -2.0128 | 30.1115 | 27.9754 | 27.4723 | 27.3558 | 27.2871 | 27.1913 | 27.0483 | 26.8646 | 26.5254 | 26.1501 | 24.8135 | 23.2253 | 21.6327 | 19.8273 | 18.6404 | 9.6115 | 2.8066 | 1.4618 | 1.3003 | 1.1682 | 1.0071 | 0.81313 | 0.53664 | 0.092988 | -0.40711 | -2.3794 | -4.4829 | -5.8205 | -6.535 | -6.6553 | 30.1115 | 23.3066 | 21.9618 | 21.8003 | 21.6682 | 21.5071 | 21.3131 | 21.0366 | 20.593 | 20.0929 | 18.1206 | 16.0171 | 14.6795 | 13.965 | 13.6984 | 9.6115 | 4.7673 | 3.79 | 3.6493 | 3.5299 | 3.3475 | 3.0662 | 2.5363 | 1.8334 | 1.0768 | -1.2123 | -3.0483 | -4.3052 | -4.772 | -4.1821 | 30.1115 | 25.2673 | 24.29 | 24.1493 | 24.0299 | 23.8475 | 23.5662 | 23.0363 | 22.3334 | 21.5768 | 19.2877 | 17.4517 | 16.1948 | 15.728 | 16.1642 | 9.6115 | 5.4368 | 4.5701 | 4.4486 | 4.3714 | 4.246 | 4.0628 | 3.7743 | 3.2854 | 2.7358 | 0.82767 | -0.97369 | -2.091 | -2.6743 | -2.6358 | 30.1115 | 25.9368 | 25.0701 | 24.9486 | 24.8714 | 24.746 | 24.5628 | 24.2743 | 23.7854 | 23.2358 | 21.3277 | 19.5263 | 18.409 | 17.8257 | 17.8105 | 9.6115 | 1.8699 | -0.26662 | -1.0688 | -1.8352 | -2.6274 | -3.4966 | -4.5583 | -5.8041 | -7.1103 | -10.6298 | -12.7196 | -14.0285 | -14.4901 | -13.861 | 30.1115 | 22.3699 | 20.2334 | 19.4312 | 18.6648 | 17.8726 | 17.0034 | 15.9417 | 14.6959 | 13.3897 | 9.8702 | 7.7804 | 6.4715 | 6.0099 | 6.4785 | 338547 | 560280 | - | HARKER
| Carr St | 11.0093 | 10.9267 | 10.8666 | 10.8127 | 10.6436 | 10.4427 | 10.2343 | 10.0253 | 9.691 | 9.3247 | 7.2021 | 3.8609 | 1.1708 | -1.5435 | -3.9561 | 15.1463 | 15.0637 | 15.0036 | 14.9497 | 14.7806 | 14.5797 | 14.3713 | 14.1623 | 13.828 | 13.4617 | 11.3391 | 7.9979 | 5.3078 | 2.5935 | -0.011725 | 11.0093 | 10.9106 | 10.8559 | 10.7816 | 10.6405 | 10.4692 | 10.2264 | 9.9133 | 9.6725 | 9.422 | 8.5125 | 7.4188 | 6.3565 | 5.2587 | 4.5589 | 15.1463 | 15.0476 | 14.9929 | 14.9186 | 14.7775 | 14.6062 | 14.3634 | 14.0503 | 13.8095 | 13.559 | 12.6495 | 11.5558 | 10.4935 | 9.3957 | 8.7968 | 11.0093 | 10.9457 | 10.9109 | 10.8962 | 10.7736 | 10.6295 | 10.5056 | 10.3707 | 10.0778 | 9.7882 | 7.8446 | 4.5699 | 1.9212 | -0.70697 | -2.8019 | 15.1463 | 15.0827 | 15.0479 | 15.0332 | 14.9106 | 14.7665 | 14.6426 | 14.5077 | 14.2148 | 13.9252 | 11.9816 | 8.7069 | 6.0582 | 3.43 | 1.1464 | 11.0093 | 11.2981 | 11.3533 | 11.3571 | 11.2181 | 11.0293 | 10.6476 | 9.6158 | 8.5292 | 7.4444 | 4.2643 | 1.2313 | -1.1831 | -2.6907 | -1.6585 | 15.1463 | 15.4351 | 15.4903 | 15.4941 | 15.3551 | 15.1663 | 14.7846 | 13.7528 | 12.6662 | 11.5814 | 8.4013 | 5.3683 | 2.9539 | 1.4463 | 2.2519 | 11.0093 | 10.9519 | 10.9374 | 10.9651 | 10.9442 | 10.8748 | 10.7562 | 10.6093 | 10.3941 | 10.0572 | 8.8411 | 7.5046 | 6.5997 | 5.8418 | 5.5121 | 15.1463 | 15.0889 | 15.0744 | 15.1021 | 15.0812 | 15.0118 | 14.8932 | 14.7463 | 14.5311 | 14.1942 | 12.9781 | 11.6416 | 10.7367 | 9.9788 | 9.6467 | 11.0093 | 11.2351 | 11.2054 | 11.1156 | 10.8942 | 10.6553 | 10.2116 | 9.0968 | 7.9554 | 6.8141 | 3.4181 | 0.15413 | -2.4996 | -4.2818 | -3.5372 | 15.1463 | 15.3721 | 15.3424 | 15.2526 | 15.0312 | 14.7923 | 14.3486 | 13.2338 | 12.0924 | 10.9511 | 7.5551 | 4.2911 | 1.6374 | -0.14484 | 0.43605 | 376984 | 401329 | KEARSLEY LOCAL | KEARSLEY
| Castleton | 9.7504 | 8.8215 | 8.5326 | 8.4068 | 8.1993 | 7.9662 | 7.7415 | 7.5267 | 7.234 | 6.9503 | 5.1551 | 2.1674 | -0.29248 | -2.8069 | -5.0204 | 14.3874 | 13.4585 | 13.1696 | 13.0438 | 12.8363 | 12.6032 | 12.3785 | 12.1637 | 11.871 | 11.5873 | 9.7921 | 6.8044 | 4.3445 | 1.8301 | -0.50192 | 9.7504 | 9.4621 | 9.2993 | 9.1754 | 9.034 | 8.8783 | 8.6676 | 8.3795 | 8.0785 | 7.7691 | 6.7905 | 5.7229 | 4.6693 | 3.4843 | 2.613 | 14.3874 | 14.0991 | 13.9363 | 13.8124 | 13.671 | 13.5153 | 13.3046 | 13.0165 | 12.7155 | 12.4061 | 11.4275 | 10.3599 | 9.3063 | 8.1213 | 7.3904 | 9.7504 | 8.7077 | 8.411 | 7.9304 | 7.3965 | 6.8433 | 6.2895 | 6.1422 | 5.9561 | 5.7562 | 4.182 | 1.3397 | -0.98849 | -3.3017 | -5.2401 | 14.3874 | 13.3447 | 13.048 | 12.5674 | 12.0335 | 11.4803 | 10.9265 | 10.7792 | 10.5931 | 10.3932 | 8.819 | 5.9767 | 3.6485 | 1.3353 | -0.77393 | 9.7504 | 9.2101 | 9.032 | 8.5694 | 8.0308 | 7.4531 | 6.702 | 5.8202 | 4.8797 | 3.9243 | 1.142 | -1.5177 | -3.6122 | -4.8957 | -4.1301 | 14.3874 | 13.8471 | 13.669 | 13.2064 | 12.6678 | 12.0901 | 11.339 | 10.4572 | 9.5167 | 8.5613 | 5.779 | 3.1193 | 1.0248 | -0.25867 | 0.33037 | 9.7504 | 9.3418 | 9.1851 | 9.1235 | 9.0519 | 8.9495 | 8.8159 | 8.6526 | 8.3746 | 8.0874 | 7.069 | 5.9363 | 5.1554 | 4.4521 | 4.0888 | 14.3874 | 13.9788 | 13.8221 | 13.7605 | 13.6889 | 13.5865 | 13.4529 | 13.2896 | 13.0116 | 12.7244 | 11.706 | 10.5733 | 9.7924 | 9.0891 | 8.7411 | 9.7504 | 8.7685 | 8.4503 | 7.9222 | 7.3256 | 6.7131 | 5.9203 | 4.9834 | 4.0108 | 3.0213 | 0.089909 | -2.7499 | -5.0404 | -6.5549 | -6.0367 | 14.3874 | 13.4055 | 13.0873 | 12.5592 | 11.9626 | 11.3501 | 10.5573 | 9.6204 | 8.6478 | 7.6583 | 4.7269 | 1.8871 | -0.4034 | -1.9179 | -1.5216 | 388461 | 411290 | CASTLETON | ROCHDALE
| Catterall Waterworks | -3.3362 | -3.4963 | -3.6238 | -3.6806 | -3.7152 | 1.5511 | 1.5229 | 1.4909 | 1.3805 | 1.2737 | 0.86298 | 0.38308 | 0.07864 | -0.18214 | -0.33658 | -0.83623 | -0.99633 | -1.1238 | -1.1806 | -1.2152 | 1.5511 | 1.5229 | 1.4909 | 1.3805 | 1.2737 | 0.86298 | 0.38308 | 0.07864 | -0.18214 | -0.37143 | -3.3362 | -3.3616 | -3.4521 | -3.4927 | -3.5042 | 1.7852 | 1.7702 | 1.7411 | 1.6049 | 1.4541 | 0.98187 | 0.5025 | 0.076337 | -0.35107 | -0.61362 | -0.83623 | -0.86161 | -0.95213 | -0.99274 | -1.0042 | 1.7852 | 1.7702 | 1.7411 | 1.6049 | 1.4541 | 0.98187 | 0.5025 | 0.076337 | -0.35107 | -0.57945 | -3.3362 | -3.5211 | -3.6528 | -3.7111 | -3.745 | 1.5232 | 1.4975 | 1.47 | 1.3973 | 1.3326 | 1.0539 | 0.69111 | 0.48494 | 0.39922 | 0.48176 | -0.83623 | -1.0211 | -1.1528 | -1.2111 | -1.245 | 1.5232 | 1.4975 | 1.47 | 1.3973 | 1.3326 | 1.0539 | 0.69111 | 0.48494 | 0.39922 | 0.40127 | -3.3362 | -3.4518 | -3.562 | -3.6111 | -3.6365 | 1.6332 | 1.5874 | 1.4877 | 1.338 | 1.1957 | 0.79899 | 0.46217 | 0.28807 | 0.3119 | 0.6689 | -0.83623 | -0.95177 | -1.062 | -1.1111 | -1.1365 | 1.6332 | 1.5874 | 1.4877 | 1.338 | 1.1957 | 0.79899 | 0.46217 | 0.28807 | 0.3119 | 0.58592 | -3.3362 | -3.3732 | -3.4731 | -3.5178 | -3.5316 | 1.7516 | 1.7328 | 1.709 | 1.6023 | 1.4961 | 1.1677 | 0.78269 | 0.54571 | 0.42529 | 0.49411 | -0.83623 | -0.87318 | -0.97307 | -1.0178 | -1.0316 | 1.7516 | 1.7328 | 1.709 | 1.6023 | 1.4961 | 1.1677 | 0.78269 | 0.54571 | 0.42529 | 0.46542 | -3.3362 | -3.53 | -3.665 | -3.7284 | -3.7656 | 1.5006 | 1.454 | 1.3481 | 1.1963 | 1.0524 | 0.64448 | 0.28956 | 0.096315 | 0.10839 | 0.45432 | -0.83623 | -1.03 | -1.165 | -1.2284 | -1.2656 | 1.5006 | 1.454 | 1.3481 | 1.1963 | 1.0524 | 0.64448 | 0.28956 | 0.096315 | 0.10839 | 0.37449 | 349381 | 442178 | RIBBLE | PENWORTHAM | Firm Capacity exceeded due to cancellation of a Flex contract. Reinforcement project initiated.
| Cecil St | 10.8049 | 8.2785 | 7.234 | 6.3845 | 5.4424 | 4.4783 | 3.5345 | 2.6198 | 1.7236 | 1.5918 | 0.048182 | -3.0174 | -5.566 | -8.287 | -10.6037 | 15.9949 | 13.4685 | 12.424 | 11.5745 | 10.6324 | 9.6683 | 8.7245 | 7.8098 | 6.9136 | 6.7818 | 5.2382 | 2.1726 | -0.37596 | -3.097 | -5.5998 | 10.8049 | 9.8455 | 9.4229 | 8.9804 | 8.4784 | 7.9662 | 7.2081 | 6.3283 | 5.9229 | 5.7472 | 5.1895 | 4.5814 | 4.0238 | 3.2845 | 2.7089 | 15.9949 | 15.0355 | 14.6129 | 14.1704 | 13.6684 | 13.1562 | 12.3981 | 11.5183 | 11.1129 | 10.9372 | 10.3795 | 9.7714 | 9.2138 | 8.4745 | 7.9923 | 10.8049 | 8.0297 | 6.9535 | 6.1281 | 5.2084 | 4.2695 | 3.3661 | 2.4894 | 1.6524 | 1.5673 | 0.17819 | -2.746 | -5.1569 | -7.7181 | -9.8955 | 15.9949 | 13.2197 | 12.1435 | 11.3181 | 10.3984 | 9.4595 | 8.5561 | 7.6794 | 6.8424 | 6.7573 | 5.3682 | 2.444 | 0.033066 | -2.5281 | -4.9127 | 10.8049 | 8.8187 | 7.922 | 7.148 | 6.2643 | 5.3511 | 4.2662 | 2.5506 | 0.82039 | -0.15475 | -2.9712 | -5.7122 | -7.8959 | -9.2703 | -8.2571 | 15.9949 | 14.0087 | 13.112 | 12.338 | 11.4543 | 10.5411 | 9.4562 | 7.7406 | 6.0104 | 5.0352 | 2.2188 | -0.52216 | -2.7059 | -4.0803 | -3.2951 | 10.8049 | 8.9653 | 8.0594 | 7.2566 | 6.421 | 5.5867 | 4.7347 | 3.8535 | 2.945 | 2.7786 | 2.1404 | 1.3484 | 0.79114 | 0.21893 | -0.082141 | 15.9949 | 14.1553 | 13.2494 | 12.4466 | 11.611 | 10.7767 | 9.9247 | 9.0435 | 8.135 | 7.9686 | 7.3304 | 6.5384 | 5.9811 | 5.4089 | 5.1238 | 10.8049 | 7.9713 | 6.8603 | 5.9994 | 5.0312 | 4.0491 | 2.8821 | 1.0658 | -0.71077 | -1.7341 | -4.7047 | -7.5816 | -9.9277 | -11.5488 | -10.8568 | 15.9949 | 13.1613 | 12.0503 | 11.1894 | 10.2212 | 9.2391 | 8.0721 | 6.2558 | 4.4792 | 3.4559 | 0.48531 | -2.3916 | -4.7377 | -6.3588 | -5.8117 | 331301 | 437023 | BLACKPOOL | PENWORTHAM
| Central Manchester | 16.0542 | 11.0248 | 9.545 | 8.9654 | 8.4281 | 26.8922 | 26.7261 | 26.5494 | 26.2985 | 26.0629 | 25.3119 | 24.4678 | 23.8298 | 23.1733 | 22.5915 | 25.0542 | 20.0248 | 18.545 | 17.9654 | 17.4281 | 35.8922 | 35.7261 | 35.5494 | 35.2985 | 35.0629 | 34.3119 | 33.4678 | 32.8298 | 32.1733 | 31.6161 | 16.0542 | 14.515 | 14.0039 | 13.7371 | 13.5006 | 32.2413 | 31.9609 | 31.6432 | 31.3523 | 31.0579 | 30.2539 | 29.5182 | 28.9319 | 28.3058 | 27.676 | 25.0542 | 23.515 | 23.0039 | 22.7371 | 22.5006 | 41.2413 | 40.9609 | 40.6432 | 40.3523 | 40.0579 | 39.2539 | 38.5182 | 37.9319 | 37.3058 | 36.7836 | 16.0542 | 10.2741 | 8.6374 | 8.048 | 7.5018 | 25.9564 | 25.7943 | 25.6223 | 25.4171 | 25.2248 | 24.6074 | 23.9162 | 23.4452 | 23.0252 | 22.7544 | 25.0542 | 19.2741 | 17.6374 | 17.048 | 16.5018 | 34.9564 | 34.7943 | 34.6223 | 34.4171 | 34.2248 | 33.6074 | 32.9162 | 32.4452 | 32.0252 | 31.7192 | 16.0542 | 11.8208 | 10.5257 | 9.9738 | 9.4625 | 27.9444 | 27.7852 | 27.5542 | 27.2622 | 26.9803 | 26.2239 | 25.554 | 25.1079 | 24.8357 | 24.9355 | 25.0542 | 20.8208 | 19.5257 | 18.9738 | 18.4625 | 36.9444 | 36.7852 | 36.5542 | 36.2622 | 35.9803 | 35.2239 | 34.554 | 34.1079 | 33.8357 | 33.8947 | 16.0542 | 12.8988 | 11.81 | 11.2478 | 10.735 | 29.2138 | 29.0494 | 28.8734 | 28.6214 | 28.3802 | 27.7129 | 27.0997 | 26.6825 | 26.2787 | 26.0124 | 25.0542 | 21.8988 | 20.81 | 20.2478 | 19.735 | 38.2138 | 38.0494 | 37.8734 | 37.6214 | 37.3802 | 36.7129 | 36.0997 | 35.6825 | 35.2787 | 35.0427 | 16.0542 | 9.5711 | 7.7894 | 7.1986 | 6.6503 | 25.1053 | 24.9201 | 24.6514 | 24.3495 | 24.058 | 23.2825 | 22.606 | 22.152 | 21.8695 | 21.9388 | 25.0542 | 18.5711 | 16.7894 | 16.1986 | 15.6503 | 34.1053 | 33.9201 | 33.6514 | 33.3495 | 33.058 | 32.2825 | 31.606 | 31.152 | 30.8695 | 30.9063 | 384852 | 397718 | STUART ST | STALYBRIDGE
| Chadderton | 25.0981 | 22.6978 | 22.0165 | 21.771 | 21.4911 | 21.1871 | 20.87 | 20.5229 | 20.0939 | 19.6622 | 17.4147 | 13.5869 | 10.9247 | 8.7853 | 7.4626 | 32.0981 | 29.6978 | 29.0165 | 28.771 | 28.4911 | 28.1871 | 27.87 | 27.5229 | 27.0939 | 26.6622 | 24.4147 | 20.5869 | 17.9247 | 15.7853 | 14.5211 | 25.0981 | 24.5449 | 24.307 | 24.1517 | 23.9961 | 23.8193 | 23.601 | 23.3316 | 23.0193 | 22.6925 | 21.6621 | 20.2945 | 18.2101 | 15.9572 | 14.4437 | 32.0981 | 31.5449 | 31.307 | 31.1517 | 30.9961 | 30.8193 | 30.601 | 30.3316 | 30.0193 | 29.6925 | 28.6621 | 27.2945 | 25.2101 | 22.9572 | 21.657 | 25.0981 | 22.2661 | 21.4365 | 21.1062 | 20.7085 | 20.2821 | 19.8363 | 19.3576 | 18.8348 | 18.304 | 16.2206 | 12.1252 | 8.8995 | 6.309 | 4.825 | 32.0981 | 29.2661 | 28.4365 | 28.1062 | 27.7085 | 27.2821 | 26.8363 | 26.3576 | 25.8348 | 25.304 | 23.2206 | 19.1252 | 15.8995 | 13.309 | 11.9575 | 25.0981 | 23.1713 | 22.5578 | 22.269 | 21.8977 | 21.469 | 20.9142 | 20.0508 | 19.1511 | 18.2648 | 15.6225 | 11.9773 | 9.359 | 7.4841 | 6.7493 | 32.0981 | 30.1713 | 29.5578 | 29.269 | 28.8977 | 28.469 | 27.9142 | 27.0508 | 26.1511 | 25.2648 | 22.6225 | 18.9773 | 16.359 | 14.4841 | 13.8398 | 25.0981 | 24.1268 | 23.7679 | 23.5849 | 23.4053 | 23.1793 | 22.9064 | 22.5989 | 22.1946 | 21.7739 | 20.0971 | 16.629 | 14.1115 | 12.0364 | 10.8356 | 32.0981 | 31.1268 | 30.7679 | 30.5849 | 30.4053 | 30.1793 | 29.9064 | 29.5989 | 29.1946 | 28.7739 | 27.0971 | 23.629 | 21.1115 | 19.0364 | 17.9938 | 25.0981 | 22.0569 | 21.1688 | 20.8166 | 20.393 | 19.9494 | 19.3914 | 18.4982 | 17.5839 | 16.6853 | 14.1524 | 10.8332 | 8.4361 | 6.7026 | 5.7478 | 32.0981 | 29.0569 | 28.1688 | 27.8166 | 27.393 | 26.9494 | 26.3914 | 25.4982 | 24.5839 | 23.6853 | 21.1524 | 17.8332 | 15.4361 | 13.7026 | 12.878 | 389161 | 403872 | CHADDERTON | WHITEGATE
| Chamberhall | 4.8248 | 4.3764 | 3.9664 | 3.6172 | 3.0586 | 2.4719 | 2.0069 | 1.5191 | 0.97931 | 0.46185 | -2.2709 | -6.5949 | -10.3834 | -14.6291 | -18.3208 | 10.1448 | 9.6964 | 9.2864 | 8.9372 | 8.3786 | 7.7919 | 7.3269 | 6.8391 | 6.2993 | 5.7819 | 3.0491 | -1.2749 | -5.0634 | -9.3091 | -13.2155 | 4.8248 | 4.603 | 4.3471 | 4.1026 | 3.8096 | 3.4738 | 3.1009 | 2.6579 | 2.3007 | 1.9368 | 0.80874 | -0.41492 | -1.74 | -3.2241 | -4.2221 | 10.1448 | 9.923 | 9.6671 | 9.4226 | 9.1296 | 8.7938 | 8.4209 | 7.9779 | 7.6207 | 7.2568 | 6.1287 | 4.9051 | 3.58 | 2.0959 | 1.243 | 4.8248 | 4.3319 | 3.9146 | 3.5669 | 2.9528 | 2.2533 | 1.6756 | 1.2028 | 0.71853 | 0.25971 | -2.3208 | -6.5256 | -9.7079 | -13.1196 | -16.4648 | 10.1448 | 9.6519 | 9.2346 | 8.8869 | 8.2728 | 7.5733 | 6.9956 | 6.5228 | 6.0385 | 5.5797 | 2.9992 | -1.2056 | -4.3879 | -7.7996 | -11.4203 | 4.8248 | 4.7414 | 4.474 | 4.2179 | 3.6642 | 2.9666 | 2.1543 | 0.78129 | -0.65933 | -2.085 | -6.252 | -10.5107 | -13.9756 | -16.2616 | -15.047 | 10.1448 | 10.0614 | 9.794 | 9.5379 | 8.9842 | 8.2866 | 7.4743 | 6.1013 | 4.6607 | 3.235 | -0.93197 | -5.1907 | -8.6556 | -10.9416 | -10.0101 | 4.8248 | 4.5883 | 4.2847 | 4.0531 | 3.6829 | 3.24 | 2.8439 | 2.4042 | 1.8815 | 1.3504 | -0.41092 | -2.2963 | -3.3905 | -4.3998 | -4.8009 | 10.1448 | 9.9083 | 9.6047 | 9.3731 | 9.0029 | 8.56 | 8.1639 | 7.7242 | 7.2015 | 6.6704 | 4.9091 | 3.0237 | 1.9295 | 0.92024 | 0.51754 | 4.8248 | 4.539 | 4.137 | 3.7567 | 3.099 | 2.3666 | 1.5351 | 0.085029 | -1.3845 | -2.8484 | -7.4472 | -12.3489 | -16.1393 | -18.8105 | -18.0188 | 10.1448 | 9.859 | 9.457 | 9.0767 | 8.419 | 7.6866 | 6.8551 | 5.405 | 3.9355 | 2.4716 | -2.1272 | -7.0289 | -10.8193 | -13.4905 | -12.8879 | 380280 | 411215 | BURY | KEARSLEY
| Chapel Wharf | 12.4756 | 7.138 | 5.3654 | 4.0422 | 2.7291 | 1.5448 | 0.66522 | -0.21042 | -1.1303 | -1.4352 | -2.4179 | -3.5278 | -4.4503 | -5.518 | -6.665 | 17.1126 | 11.775 | 10.0024 | 8.6792 | 7.3661 | 6.1818 | 5.3022 | 4.4266 | 3.5067 | 3.2018 | 2.2191 | 1.1092 | 0.18669 | -0.88101 | -1.8803 | 12.4756 | 10.6975 | 9.9507 | 9.5241 | 9.1091 | 8.6965 | 8.3688 | 8.0169 | 7.6606 | 7.3067 | 6.2772 | 5.2521 | 4.3596 | 3.3094 | 2.1236 | 17.1126 | 15.3345 | 14.5877 | 14.1611 | 13.7461 | 13.3335 | 13.0058 | 12.6539 | 12.2976 | 11.9437 | 10.9142 | 9.8891 | 8.9966 | 7.9464 | 6.9854 | 12.4756 | 6.3015 | 4.3596 | 3.0365 | 1.7249 | 0.54264 | -0.33651 | -1.2091 | -2.1066 | -2.3867 | -3.2931 | -4.3121 | -5.139 | -6.0745 | -7.05 | 17.1126 | 10.9385 | 8.9966 | 7.6735 | 6.3619 | 5.1796 | 4.3005 | 3.4279 | 2.5304 | 2.2503 | 1.3439 | 0.32494 | -0.50203 | -1.4375 | -2.2983 | 12.4756 | 8.0625 | 6.4875 | 5.1835 | 3.8867 | 2.7214 | 1.8418 | 0.90709 | -0.063948 | -0.42109 | -1.4368 | -2.4114 | -3.1885 | -3.9531 | -4.5602 | 17.1126 | 12.6995 | 11.1245 | 9.8205 | 8.5237 | 7.3584 | 6.4788 | 5.5441 | 4.5731 | 4.2159 | 3.2002 | 2.2256 | 1.4485 | 0.68387 | 0.18268 | 12.4756 | 9.2814 | 7.9462 | 6.6275 | 5.326 | 4.1552 | 3.2864 | 2.415 | 1.4905 | 1.1782 | 0.26913 | -0.62821 | -1.3517 | -2.1949 | -3.0997 | 17.1126 | 13.9184 | 12.5832 | 11.2645 | 9.963 | 8.7922 | 7.9234 | 7.052 | 6.1275 | 5.8152 | 4.9061 | 4.0088 | 3.2853 | 2.4421 | 1.6996 | 12.4756 | 5.545 | 3.4468 | 2.1275 | 0.81532 | -0.3643 | -1.2575 | -2.2111 | -3.1881 | -3.5507 | -4.5811 | -5.579 | -6.3837 | -7.1922 | -7.8707 | 17.1126 | 10.182 | 8.0838 | 6.7645 | 5.4523 | 4.2727 | 3.3795 | 2.4259 | 1.4489 | 1.0863 | 0.055902 | -0.94199 | -1.7467 | -2.5552 | -3.1114 | 383499 | 398634 | FREDERICK RD | KEARSLEY
| Chassen Rd | 3.4665 | 3.1537 | 2.8541 | 2.5819 | 2.2472 | 1.9071 | 1.5961 | 1.3131 | 0.97829 | 0.66456 | -1.3066 | -4.448 | -6.8599 | -9.1436 | -10.7046 | 14.3665 | 14.0537 | 13.7541 | 13.4819 | 13.1472 | 12.8071 | 12.4961 | 12.2131 | 11.8783 | 11.5646 | 9.5934 | 6.452 | 4.0401 | 1.7564 | -0.028598 | 3.4665 | 3.2858 | 3.0872 | 2.8945 | 2.6628 | 2.4186 | 2.116 | 1.7516 | 1.4406 | 1.1171 | 0.1537 | -0.78187 | -1.6903 | -2.6797 | -3.4263 | 14.3665 | 14.1858 | 13.9872 | 13.7945 | 13.5628 | 13.3186 | 13.016 | 12.6516 | 12.3406 | 12.0171 | 11.0537 | 10.1181 | 9.2097 | 8.2203 | 7.5957 | 3.4665 | 3.0644 | 2.6798 | 2.3343 | 1.7372 | 1.1322 | 0.56534 | 0.01952 | -0.55587 | -1.1465 | -3.874 | -7.3402 | -9.8169 | -11.9881 | -12.2903 | 14.3665 | 13.9644 | 13.5798 | 13.2343 | 12.6372 | 12.0322 | 11.4653 | 10.9195 | 10.3441 | 9.7535 | 7.026 | 3.5598 | 1.0831 | -1.0881 | -1.6585 | 3.4665 | 3.3422 | 3.0495 | 2.7319 | 2.1362 | 1.5008 | 0.71781 | -0.58863 | -1.8954 | -3.1724 | -6.7302 | -9.6902 | -11.644 | -12.7301 | -11.4531 | 14.3665 | 14.2422 | 13.9495 | 13.6319 | 13.0362 | 12.4008 | 11.6178 | 10.3114 | 9.0046 | 7.7276 | 4.1698 | 1.2098 | -0.74405 | -1.8301 | -0.82451 | 3.4665 | 3.2215 | 2.9828 | 2.7981 | 2.6065 | 2.3848 | 2.1513 | 1.9153 | 1.5924 | 1.2663 | 0.17738 | -0.96686 | -1.8176 | -2.7888 | -3.3682 | 14.3665 | 14.1215 | 13.8828 | 13.6981 | 13.5065 | 13.2848 | 13.0513 | 12.8153 | 12.4924 | 12.1663 | 11.0774 | 9.9331 | 9.0824 | 8.1112 | 7.5871 | 3.4665 | 3.222 | 2.8209 | 2.393 | 1.6981 | 0.99705 | 0.13572 | -1.2843 | -2.6732 | -4.0316 | -7.8319 | -10.9987 | -13.144 | -14.4493 | -13.4222 | 14.3665 | 14.122 | 13.7209 | 13.293 | 12.5981 | 11.897 | 11.0357 | 9.6157 | 8.2268 | 6.8684 | 3.0681 | -0.098718 | -2.244 | -3.5493 | -2.7399 | 375542 | 394453 | BARTON | CARRINGTON
| Chatsworth St | 8.202 | 7.797 | 7.428 | 7.132 | 6.7455 | 6.3501 | 5.9915 | 5.6575 | 5.3814 | 5.1262 | 3.27 | -0.014378 | -2.5707 | -5.0534 | -7.0946 | 15.602 | 15.197 | 14.828 | 14.532 | 14.1455 | 13.7501 | 13.3915 | 13.0575 | 12.7814 | 12.5262 | 10.67 | 7.3856 | 4.8293 | 2.3466 | 0.061737 | 8.202 | 8.0151 | 7.7696 | 7.5351 | 7.269 | 6.9991 | 6.6633 | 6.2699 | 6.0565 | 5.8396 | 5.1898 | 4.542 | 4.0685 | 3.6402 | 3.3713 | 15.602 | 15.4151 | 15.1696 | 14.9351 | 14.669 | 14.3991 | 14.0633 | 13.6699 | 13.4565 | 13.2396 | 12.5898 | 11.942 | 11.4685 | 11.0402 | 10.7968 | 8.202 | 7.7661 | 7.4064 | 7.1417 | 6.785 | 6.4237 | 6.1043 | 5.7348 | 5.4574 | 5.2017 | 3.6196 | 0.63978 | -1.7692 | -4.0609 | -5.8665 | 15.602 | 15.1661 | 14.8064 | 14.5417 | 14.185 | 13.8237 | 13.5043 | 13.1348 | 12.8574 | 12.6017 | 11.0196 | 8.0398 | 5.6308 | 3.3391 | 1.2484 | 8.202 | 8.1089 | 7.8399 | 7.603 | 7.2741 | 6.9306 | 6.4171 | 5.256 | 4.1549 | 3.0635 | -0.048021 | -3.0068 | -5.1929 | -6.3473 | -5.0095 | 15.602 | 15.5089 | 15.2399 | 15.003 | 14.6741 | 14.3306 | 13.8171 | 12.656 | 11.5549 | 10.4635 | 7.352 | 4.3932 | 2.2071 | 1.0527 | 2.0968 | 8.202 | 8.047 | 7.7409 | 7.491 | 7.2317 | 6.9755 | 6.6811 | 6.3065 | 5.9408 | 5.5627 | 4.295 | 2.9441 | 2.1433 | 1.5734 | 1.7086 | 15.602 | 15.447 | 15.1409 | 14.891 | 14.6317 | 14.3755 | 14.0811 | 13.7065 | 13.3408 | 12.9627 | 11.695 | 10.3441 | 9.5433 | 8.9734 | 9.0155 | 8.202 | 7.9104 | 7.5457 | 7.2296 | 6.8255 | 6.4254 | 5.845 | 4.5979 | 3.4526 | 2.3147 | -0.95426 | -4.0632 | -6.419 | -7.8119 | -6.7526 | 15.602 | 15.3104 | 14.9457 | 14.6296 | 14.2255 | 13.8254 | 13.245 | 11.9979 | 10.8526 | 9.7147 | 6.4457 | 3.3368 | 0.98098 | -0.4119 | 0.41547 | 319188 | 470003 | BARROW & SANDGATE | HARKER
| Cheadle Heath | 7.7097 | 7.1139 | 6.9809 | 6.9616 | 6.8737 | 6.7694 | 6.6695 | 6.5697 | 6.418 | 6.2146 | 4.7967 | 2.5537 | 0.6955 | -1.4474 | -3.2486 | 11.2097 | 10.6139 | 10.4809 | 10.4616 | 10.3737 | 10.2694 | 10.1695 | 10.0697 | 9.918 | 9.7146 | 8.2967 | 6.0537 | 4.1955 | 2.0526 | 0.10401 | 7.7097 | 7.5933 | 7.5299 | 7.4699 | 7.3706 | 7.2437 | 7.0731 | 6.8724 | 6.7007 | 6.5206 | 5.957 | 5.1992 | 4.4925 | 3.8006 | 3.3755 | 11.2097 | 11.0933 | 11.0299 | 10.9699 | 10.8706 | 10.7437 | 10.5731 | 10.3724 | 10.2007 | 10.0206 | 9.457 | 8.6992 | 7.9925 | 7.3006 | 6.931 | 7.7097 | 7.0349 | 6.898 | 6.9056 | 6.8469 | 6.7778 | 6.7442 | 6.7159 | 6.6481 | 6.4724 | 5.2025 | 3.0406 | 1.2619 | -0.53933 | -2.137 | 11.2097 | 10.5349 | 10.398 | 10.4056 | 10.3469 | 10.2778 | 10.2442 | 10.2159 | 10.1481 | 9.9724 | 8.7025 | 6.5406 | 4.7619 | 2.9607 | 1.1801 | 7.7097 | 7.452 | 7.416 | 7.4417 | 7.378 | 7.2836 | 7.0657 | 6.3731 | 5.6321 | 4.888 | 2.7211 | 0.66265 | -1.0311 | -2.0895 | -1.2646 | 11.2097 | 10.952 | 10.916 | 10.9417 | 10.878 | 10.7836 | 10.5657 | 9.8731 | 9.1321 | 8.388 | 6.2211 | 4.1626 | 2.4689 | 1.4105 | 2.0503 | 7.7097 | 7.5782 | 7.5702 | 7.6094 | 7.6264 | 7.6087 | 7.5536 | 7.478 | 7.3372 | 7.1862 | 6.3721 | 5.4896 | 4.874 | 4.3739 | 4.2351 | 11.2097 | 11.0782 | 11.0702 | 11.1094 | 11.1264 | 11.1087 | 11.0536 | 10.978 | 10.8372 | 10.6862 | 9.8721 | 8.9896 | 8.374 | 7.8739 | 7.7153 | 7.7097 | 7.1351 | 6.9818 | 6.9383 | 6.8131 | 6.6804 | 6.4152 | 5.6579 | 4.8728 | 4.0838 | 1.7572 | -0.46429 | -2.3415 | -3.614 | -3.0037 | 11.2097 | 10.6351 | 10.4818 | 10.4383 | 10.3131 | 10.1804 | 9.9152 | 9.1579 | 8.3728 | 7.5838 | 5.2572 | 3.0357 | 1.1585 | -0.11404 | 0.35846 | 387062 | 389054 | ADSWOOD | BREDBURY
| Cheadle Hulme | 8.9703 | 8.393 | 8.1122 | 7.9121 | 7.6525 | 7.3865 | 7.1207 | 6.8501 | 6.3319 | 5.9482 | 4.1131 | 1.3747 | -0.72728 | -2.7818 | -4.1982 | 13.6073 | 13.03 | 12.7492 | 12.5491 | 12.2895 | 12.0235 | 11.7577 | 11.4871 | 10.9689 | 10.5852 | 8.7501 | 6.0117 | 3.9097 | 1.8552 | 0.30247 | 8.9703 | 8.7284 | 8.5817 | 8.4364 | 8.2192 | 7.9681 | 7.6477 | 7.2669 | 6.9446 | 6.6108 | 5.5416 | 4.5135 | 3.5642 | 2.5883 | 1.9117 | 13.6073 | 13.3654 | 13.2187 | 13.0734 | 12.8562 | 12.6051 | 12.2847 | 11.9039 | 11.5816 | 11.2478 | 10.1786 | 9.1505 | 8.2012 | 7.2253 | 6.657 | 8.9703 | 8.268 | 7.9095 | 7.6518 | 7.3307 | 7.0014 | 6.6155 | 6.0184 | 5.3272 | 4.7541 | 2.55 | -0.13978 | -2.0172 | -3.5911 | -4.2544 | 13.6073 | 12.905 | 12.5465 | 12.2888 | 11.9677 | 11.6384 | 11.2525 | 10.6554 | 9.9642 | 9.3911 | 7.187 | 4.4972 | 2.6198 | 1.0459 | 0.26465 | 8.9703 | 8.7441 | 8.5297 | 8.332 | 8.0322 | 7.6801 | 7.1186 | 5.9366 | 4.7381 | 3.6865 | 0.97157 | -1.1784 | -2.5617 | -3.2765 | -2.7574 | 13.6073 | 13.3811 | 13.1667 | 12.969 | 12.6692 | 12.3171 | 11.7556 | 10.5736 | 9.3751 | 8.3235 | 5.6086 | 3.4586 | 2.0753 | 1.3605 | 1.7504 | 8.9703 | 8.6028 | 8.4263 | 8.3244 | 8.1873 | 7.9926 | 7.7592 | 7.5272 | 7.0705 | 6.7048 | 5.5658 | 4.3291 | 3.4067 | 2.4352 | 1.7505 | 13.6073 | 13.2398 | 13.0633 | 12.9614 | 12.8243 | 12.6296 | 12.3962 | 12.1642 | 11.7075 | 11.3418 | 10.2028 | 8.9661 | 8.0437 | 7.0722 | 6.4708 | 8.9703 | 8.4673 | 8.0933 | 7.7607 | 7.3427 | 6.9204 | 6.2735 | 4.964 | 3.6647 | 2.515 | -0.47483 | -2.8645 | -4.3968 | -5.1861 | -4.7714 | 13.6073 | 13.1043 | 12.7303 | 12.3977 | 11.9797 | 11.5574 | 10.9105 | 9.601 | 8.3017 | 7.152 | 4.1622 | 1.7725 | 0.24019 | -0.54909 | -0.21965 | 387386 | 386308 | ADSWOOD | BREDBURY
| Cheetham Hill | 2.4727 | 1.9157 | 1.4363 | 0.99909 | 0.50987 | -0.00034204 | -0.50742 | -0.99261 | -1.497 | -1.9729 | -3.7872 | -6.3898 | -8.2924 | -10.0275 | -11.1412 | 5.1823 | 4.6253 | 4.1458 | 3.7086 | 3.2194 | 2.7092 | 2.2021 | 1.7169 | 1.2125 | 0.73665 | -1.0777 | -3.6802 | -5.5828 | -7.3179 | -8.6869 | 2.4727 | 2.1947 | 1.9229 | 1.6598 | 1.3614 | 1.0699 | 0.71287 | 0.29015 | -0.025918 | -0.34659 | -1.0995 | -1.7442 | -2.3149 | -2.9204 | -3.3365 | 5.1823 | 4.9043 | 4.6324 | 4.3694 | 4.0709 | 3.7794 | 3.4224 | 2.9997 | 2.6836 | 2.3629 | 1.61 | 0.9653 | 0.3946 | -0.21087 | -0.56397 | 2.4727 | 1.8498 | 1.3116 | 0.82575 | 0.28135 | -0.28623 | -0.95709 | -1.6683 | -2.3305 | -2.9757 | -5.1693 | -7.6703 | -9.2341 | -10.3306 | -10.4055 | 5.1823 | 4.5594 | 4.0211 | 3.5353 | 2.9909 | 2.4233 | 1.7525 | 1.0413 | 0.37902 | -0.26619 | -2.4598 | -4.9607 | -6.5245 | -7.6211 | -7.9672 | 2.4727 | 2.2259 | 1.7893 | 1.3533 | 0.83275 | 0.2745 | -0.56706 | -1.891 | -3.1747 | -4.4064 | -7.2838 | -9.3202 | -10.4125 | -10.5565 | -9.2666 | 5.1823 | 4.9354 | 4.4988 | 4.0629 | 3.5423 | 2.984 | 2.1425 | 0.8185 | -0.46516 | -1.6968 | -4.5742 | -6.6107 | -7.703 | -7.847 | -6.8352 | 2.4727 | 1.973 | 1.5342 | 1.1531 | 0.75747 | 0.34815 | -0.078764 | -0.52921 | -1.0436 | -1.5564 | -2.5942 | -3.5117 | -4.1174 | -4.6916 | -4.9461 | 5.1823 | 4.6826 | 4.2438 | 3.8626 | 3.467 | 3.0577 | 2.6308 | 2.1803 | 1.666 | 1.1532 | 0.1153 | -0.80216 | -1.4078 | -1.982 | -2.2348 | 2.4727 | 2.1197 | 1.5947 | 1.0708 | 0.46861 | -0.14957 | -0.95099 | -2.3454 | -3.6658 | -4.9322 | -7.9027 | -10.0731 | -11.3019 | -11.5823 | -10.4288 | 5.1823 | 4.8293 | 4.3042 | 3.7804 | 3.1782 | 2.56 | 1.7586 | 0.36418 | -0.9563 | -2.2227 | -5.1932 | -7.3635 | -8.5923 | -8.8728 | -7.9626 | 383606 | 402218 | AGECROFT | KEARSLEY
| Chester Rd T11 & T12 | 5.5138 | 2.9919 | 2.0656 | 1.7525 | 1.4495 | 1.1407 | 0.83482 | 0.52037 | 0.11921 | -0.28254 | -1.5052 | -3.0448 | -4.3503 | -5.7202 | -6.8901 | 10.5138 | 7.9919 | 7.0656 | 6.7525 | 6.4495 | 6.1407 | 5.8348 | 5.5204 | 5.1192 | 4.7175 | 3.4948 | 1.9552 | 0.64968 | -0.72019 | -1.9094 | 5.5138 | 4.9907 | 4.6911 | 4.5037 | 4.3435 | 4.1851 | 4.0103 | 3.8066 | 3.5203 | 3.2277 | 2.4325 | 1.4713 | 0.52494 | -0.53621 | -1.3554 | 10.5138 | 9.9907 | 9.6911 | 9.5037 | 9.3435 | 9.1851 | 9.0103 | 8.8066 | 8.5203 | 8.2277 | 7.4325 | 6.4713 | 5.5249 | 4.4638 | 3.7708 | 5.5138 | 2.5983 | 1.2929 | 0.67827 | 0.076965 | -0.52791 | -1.1282 | -1.7325 | -2.3853 | -3.0334 | -5.0208 | -7.3244 | -9.1655 | -10.1926 | -10.9383 | 10.5138 | 7.5983 | 6.2929 | 5.6783 | 5.077 | 4.4721 | 3.8718 | 3.2675 | 2.6147 | 1.9666 | -0.02084 | -2.3244 | -4.1655 | -5.1926 | -6.0246 | 5.5138 | 3.4448 | 2.3301 | 1.7387 | 1.1537 | 0.54964 | -0.12078 | -1.0143 | -1.9783 | -2.9381 | -5.4567 | -7.7098 | -9.4524 | -10.0653 | -9.7311 | 10.5138 | 8.4448 | 7.3301 | 6.7387 | 6.1537 | 5.5496 | 4.8792 | 3.9857 | 3.0217 | 2.0619 | -0.45672 | -2.7098 | -4.4524 | -5.0653 | -4.8224 | 5.5138 | 4.6393 | 4.0625 | 3.7787 | 3.5254 | 3.263 | 2.9881 | 2.6962 | 2.3053 | 1.905 | 0.95538 | 0.15063 | -0.48091 | -1.0716 | -1.3682 | 10.5138 | 9.6393 | 9.0625 | 8.7787 | 8.5254 | 8.263 | 7.9881 | 7.6962 | 7.3053 | 6.905 | 5.9554 | 5.1506 | 4.5191 | 3.9284 | 3.657 | 5.5138 | 2.2604 | 0.88124 | 0.25917 | -0.3505 | -0.96068 | -1.631 | -2.5115 | -3.4526 | -4.4114 | -6.9522 | -9.2628 | -11.0759 | -11.7616 | -11.5068 | 10.5138 | 7.2604 | 5.8812 | 5.2592 | 4.6495 | 4.0393 | 3.369 | 2.4885 | 1.5474 | 0.58857 | -1.9522 | -4.2628 | -6.0759 | -6.7616 | -6.5792 | 381030 | 396165 | STRETFORD | SOUTH MANCHESTER
| Chester Rd T13 | 9.9184 | 8.393 | 7.3801 | 6.4856 | 5.438 | 4.3885 | 3.4919 | 2.8938 | 2.2849 | 1.6795 | 0.25849 | -0.30603 | -0.73941 | -1.1879 | -1.5916 | 14.6684 | 13.143 | 12.1301 | 11.2356 | 10.188 | 9.1385 | 8.2419 | 7.6438 | 7.0349 | 6.4295 | 5.0085 | 4.444 | 4.0106 | 3.5621 | 3.1848 | 9.9184 | 9.533 | 9.3322 | 9.1401 | 8.8965 | 8.6486 | 8.4378 | 8.3052 | 8.1885 | 8.0692 | 7.716 | 7.3627 | 7.0386 | 6.668 | 6.339 | 14.6684 | 14.283 | 14.0822 | 13.8901 | 13.6465 | 13.3986 | 13.1878 | 13.0552 | 12.9385 | 12.8192 | 12.466 | 12.1127 | 11.7886 | 11.418 | 11.1467 | 9.9184 | 8.1655 | 7.0962 | 6.186 | 5.1218 | 4.0541 | 3.1372 | 2.5169 | 1.8942 | 1.2743 | -0.19086 | -0.75557 | -1.1601 | -1.5514 | -1.8917 | 14.6684 | 12.9155 | 11.8462 | 10.936 | 9.8718 | 8.8041 | 7.8872 | 7.2669 | 6.6442 | 6.0243 | 4.5591 | 3.9944 | 3.5899 | 3.1986 | 2.8947 | 9.9184 | 8.6299 | 7.669 | 6.7782 | 5.7305 | 4.6715 | 3.7444 | 3.0685 | 2.3869 | 1.7108 | 0.18731 | -0.32507 | -0.67668 | -0.97466 | -1.1683 | 14.6684 | 13.3799 | 12.419 | 11.5282 | 10.4805 | 9.4215 | 8.4944 | 7.8185 | 7.1369 | 6.4608 | 4.9373 | 4.4249 | 4.0733 | 3.7753 | 3.6138 | 9.9184 | 9.1747 | 8.329 | 7.4495 | 6.4232 | 5.3896 | 4.5018 | 3.9113 | 3.3031 | 2.6944 | 1.3426 | 0.94712 | 0.65002 | 0.3252 | 0.040758 | 14.6684 | 13.9247 | 13.079 | 12.1995 | 11.1732 | 10.1396 | 9.2518 | 8.6613 | 8.0531 | 7.4444 | 6.0926 | 5.6971 | 5.4 | 5.0752 | 4.838 | 9.9184 | 7.9789 | 6.8698 | 5.9577 | 4.8911 | 3.8227 | 2.8878 | 2.1951 | 1.5034 | 0.81833 | -0.72438 | -1.2431 | -1.6017 | -1.896 | -2.1141 | 14.6684 | 12.7289 | 11.6198 | 10.7077 | 9.6411 | 8.5727 | 7.6378 | 6.9451 | 6.2534 | 5.5683 | 4.0256 | 3.5069 | 3.1483 | 2.854 | 2.6749 | 381040 | 396175 | STRETFORD | SOUTH MANCHESTER
| Chorley South | 3.4631 | 2.2556 | 1.6222 | 1.1375 | 0.47008 | 5.3 | 4.8211 | 4.364 | 3.8426 | 3.3576 | 0.72312 | -3.591 | -7.0208 | -10.633 | -13.8745 | 6.9631 | 5.7556 | 5.1222 | 4.6375 | 3.9701 | 9.8 | 9.3211 | 8.864 | 8.3426 | 7.8576 | 5.2231 | 0.90904 | -2.5208 | -6.133 | -9.4629 | 3.4631 | 2.9294 | 2.6052 | 2.3135 | 1.9612 | 7.052 | 6.494 | 5.7535 | 5.2205 | 4.6871 | 2.9044 | 1.0461 | -0.70096 | -2.6569 | -3.9628 | 6.9631 | 6.4294 | 6.1052 | 5.8135 | 5.4612 | 11.552 | 10.994 | 10.2535 | 9.7205 | 9.1871 | 7.4044 | 5.5461 | 3.799 | 1.8431 | 0.76623 | 3.4631 | 2.133 | 1.5054 | 1.0745 | 0.46402 | 5.3606 | 4.9745 | 4.6198 | 4.2211 | 3.8372 | 1.5085 | -2.5414 | -5.7397 | -9.0751 | -12.0007 | 6.9631 | 5.633 | 5.0054 | 4.5745 | 3.964 | 9.8606 | 9.4745 | 9.1198 | 8.7211 | 8.3372 | 6.0085 | 1.9586 | -1.2397 | -4.5751 | -7.6482 | 3.4631 | 2.733 | 2.2701 | 1.8942 | 1.3085 | 6.1873 | 5.548 | 4.2394 | 2.8771 | 1.5289 | -2.3589 | -6.2201 | -9.1632 | -11.183 | -10.527 | 6.9631 | 6.233 | 5.7701 | 5.3942 | 4.8085 | 10.6873 | 10.048 | 8.7394 | 7.3771 | 6.0289 | 2.1411 | -1.7201 | -4.6632 | -6.683 | -6.1857 | 3.4631 | 2.6764 | 2.1651 | 1.7744 | 1.2748 | 6.2482 | 5.8643 | 5.4587 | 4.9168 | 4.3821 | 2.6555 | 0.70543 | -0.59118 | -1.82 | -2.628 | 6.9631 | 6.1764 | 5.6651 | 5.2744 | 4.7748 | 10.7482 | 10.3643 | 9.9587 | 9.4168 | 8.8821 | 7.1555 | 5.2054 | 3.9088 | 2.68 | 1.9572 | 3.4631 | 2.1993 | 1.5406 | 1.0316 | 0.3259 | 5.1276 | 4.3973 | 2.9552 | 1.4951 | 0.050448 | -4.1276 | -8.2371 | -11.4275 | -13.7564 | -13.4621 | 6.9631 | 5.6993 | 5.0406 | 4.5316 | 3.8259 | 9.6276 | 8.8973 | 7.4552 | 5.9951 | 4.5504 | 0.3724 | -3.7371 | -6.9275 | -9.2564 | -9.0397 | 358658 | 417041 | WRIGHTINGTON | PENWORTHAM
| Chorlton | 4.9261 | 4.5211 | 4.2652 | 4.0437 | 3.7764 | 2.5068 | 2.2585 | 2.0237 | 1.7813 | 1.5597 | 0.38026 | -1.3612 | -2.6071 | -3.6642 | -4.2379 | 10.9261 | 10.5211 | 10.2652 | 10.0437 | 9.7764 | 8.5068 | 8.2585 | 8.0237 | 7.7813 | 7.5597 | 6.3803 | 4.6388 | 3.3929 | 2.3358 | 1.6013 | 4.9261 | 4.8103 | 4.689 | 4.5463 | 4.3575 | 3.1685 | 2.943 | 2.6871 | 2.4815 | 2.2691 | 1.6577 | 1.1169 | 0.67235 | 0.27125 | 0.05071 | 10.9261 | 10.8103 | 10.689 | 10.5463 | 10.3575 | 9.1685 | 8.943 | 8.6871 | 8.4815 | 8.2691 | 7.6577 | 7.1169 | 6.6723 | 6.2712 | 6.0799 | 4.9261 | 4.427 | 4.1073 | 3.8322 | 3.5068 | 2.1764 | 1.871 | 1.5713 | 1.2719 | 0.97626 | -0.3898 | -2.0838 | -3.1413 | -3.8478 | -3.8559 | 10.9261 | 10.427 | 10.1073 | 9.8322 | 9.5068 | 8.1764 | 7.871 | 7.5713 | 7.2719 | 6.9763 | 5.6102 | 3.9162 | 2.8587 | 2.1522 | 1.9723 | 4.9261 | 4.6783 | 4.4591 | 4.252 | 3.9705 | 2.6424 | 2.2363 | 1.5544 | 0.88779 | 0.24693 | -1.5172 | -2.9362 | -3.7225 | -3.8918 | -3.0938 | 10.9261 | 10.6783 | 10.4591 | 10.252 | 9.9705 | 8.6424 | 8.2363 | 7.5544 | 6.8878 | 6.2469 | 4.4828 | 3.0638 | 2.2775 | 2.1082 | 2.7294 | 4.9261 | 4.7509 | 4.587 | 4.4406 | 4.2755 | 3.0876 | 2.8878 | 2.687 | 2.4562 | 2.2264 | 1.4972 | 0.78066 | 0.30612 | -0.10012 | -0.24213 | 10.9261 | 10.7509 | 10.587 | 10.4406 | 10.2755 | 9.0876 | 8.8878 | 8.687 | 8.4562 | 8.2264 | 7.4972 | 6.7807 | 6.3061 | 5.8999 | 5.7575 | 4.9261 | 4.4925 | 4.1652 | 3.8659 | 3.5065 | 2.1431 | 1.6989 | 0.94273 | 0.21429 | -0.48577 | -2.4082 | -3.9324 | -4.8218 | -5.1145 | -4.4892 | 10.9261 | 10.4925 | 10.1652 | 9.8659 | 9.5065 | 8.1431 | 7.6989 | 6.9427 | 6.2143 | 5.5142 | 3.5918 | 2.0676 | 1.1782 | 0.88549 | 1.375 | 381411 | 393754 | WEST DIDSBURY | SOUTH MANCHESTER
| Church | 1.2129 | 1.0493 | 1.0128 | 1.0016 | 0.93873 | 0.86094 | 0.78402 | 0.70488 | 0.60365 | 0.4999 | -0.62385 | -2.4198 | -3.9206 | -5.4889 | -6.7483 | 8.0129 | 7.8493 | 7.8128 | 7.8016 | 7.7387 | 7.6609 | 7.584 | 7.5049 | 7.4036 | 7.2999 | 6.1762 | 4.3802 | 2.8794 | 1.3111 | -0.055188 | 1.2129 | 1.1081 | 1.0602 | 1.0221 | 0.96393 | 0.89536 | 0.79347 | 0.6547 | 0.55119 | 0.44155 | 0.071473 | -0.50854 | -1.081 | -1.6974 | -2.0961 | 8.0129 | 7.9081 | 7.8602 | 7.8221 | 7.7639 | 7.6954 | 7.5935 | 7.4547 | 7.3512 | 7.2415 | 6.8715 | 6.2915 | 5.719 | 5.1026 | 4.7622 | 1.2129 | 1.0384 | 1.0083 | 1.0128 | 0.96699 | 0.90989 | 0.86509 | 0.81917 | 0.75892 | 0.69366 | -0.31697 | -2.1192 | -3.6527 | -5.2045 | -6.3124 | 8.0129 | 7.8384 | 7.8083 | 7.8128 | 7.767 | 7.7099 | 7.6651 | 7.6192 | 7.5589 | 7.4937 | 6.483 | 4.6808 | 3.1473 | 1.5955 | 0.38276 | 1.2129 | 1.2255 | 1.2374 | 1.2568 | 1.2137 | 1.154 | 0.98248 | 0.42908 | -0.14077 | -0.70971 | -2.3651 | -4.0415 | -5.3972 | -6.2978 | -5.7379 | 8.0129 | 8.0255 | 8.0374 | 8.0568 | 8.0137 | 7.954 | 7.7825 | 7.2291 | 6.6592 | 6.0903 | 4.4349 | 2.7585 | 1.4028 | 0.5022 | 0.93711 | 1.2129 | 1.0808 | 1.061 | 1.074 | 1.0698 | 1.0511 | 1.0084 | 0.94284 | 0.83908 | 0.72621 | 0.18709 | -0.53115 | -1.0417 | -1.472 | -1.6771 | 8.0129 | 7.8808 | 7.861 | 7.874 | 7.8698 | 7.8511 | 7.8084 | 7.7428 | 7.6391 | 7.5262 | 6.9871 | 6.2688 | 5.7583 | 5.328 | 5.1479 | 1.2129 | 1.1487 | 1.1248 | 1.1159 | 1.0473 | 0.97034 | 0.77633 | 0.19632 | -0.3866 | -0.97176 | -2.7054 | -4.5026 | -6.0123 | -7.1118 | -6.7619 | 8.0129 | 7.9487 | 7.9248 | 7.9159 | 7.8473 | 7.7703 | 7.5763 | 6.9963 | 6.4134 | 5.8282 | 4.0946 | 2.2974 | 0.78765 | -0.3118 | -0.041774 | 374687 | 428919 | HUNCOAT | PADIHAM
| Circle Sq | 17.0264 | 15.6596 | 15.3078 | 15.2692 | 15.2586 | 15.2526 | 15.2525 | 15.2556 | 15.2089 | 15.1661 | 15.0281 | 14.8728 | 14.7691 | 14.6868 | 14.6572 | 21.6664 | 20.2996 | 19.9478 | 19.9092 | 19.8986 | 19.8926 | 19.8925 | 19.8956 | 19.8489 | 19.8061 | 19.6681 | 19.5128 | 19.4091 | 19.3268 | 19.276 | 17.0264 | 16.6081 | 16.4431 | 16.3953 | 16.3754 | 16.3572 | 16.3387 | 16.3154 | 16.2415 | 16.1705 | 15.9798 | 15.8144 | 15.6837 | 15.5496 | 15.4373 | 21.6664 | 21.2481 | 21.0831 | 21.0353 | 21.0154 | 20.9972 | 20.9787 | 20.9554 | 20.8815 | 20.8105 | 20.6198 | 20.4544 | 20.3237 | 20.1896 | 20.0936 | 17.0264 | 15.4323 | 15.0343 | 14.9941 | 14.9827 | 14.9762 | 14.9751 | 14.9774 | 14.9524 | 14.9349 | 14.8764 | 14.8076 | 14.7953 | 14.8406 | 14.9768 | 21.6664 | 20.0723 | 19.6743 | 19.6341 | 19.6227 | 19.6162 | 19.6151 | 19.6174 | 19.5924 | 19.5749 | 19.5164 | 19.4476 | 19.4353 | 19.4806 | 19.563 | 17.0264 | 15.8902 | 15.5879 | 15.5504 | 15.5424 | 15.54 | 15.5361 | 15.5148 | 15.4601 | 15.4126 | 15.3046 | 15.2382 | 15.2299 | 15.3143 | 15.5531 | 21.6664 | 20.5302 | 20.2279 | 20.1904 | 20.1824 | 20.18 | 20.1761 | 20.1548 | 20.1001 | 20.0526 | 19.9446 | 19.8782 | 19.8699 | 19.9543 | 20.1389 | 17.0264 | 16.215 | 15.9761 | 15.9381 | 15.9308 | 15.929 | 15.9315 | 15.9345 | 15.886 | 15.8407 | 15.7278 | 15.644 | 15.6084 | 15.6043 | 15.6744 | 21.6664 | 20.855 | 20.6161 | 20.5781 | 20.5708 | 20.569 | 20.5715 | 20.5745 | 20.526 | 20.4807 | 20.3678 | 20.284 | 20.2484 | 20.2443 | 20.293 | 17.0264 | 15.2104 | 14.7669 | 14.7253 | 14.7129 | 14.7056 | 14.6967 | 14.6699 | 14.6152 | 14.5677 | 14.4597 | 14.3926 | 14.3833 | 14.4658 | 14.7014 | 21.6664 | 19.8504 | 19.4069 | 19.3653 | 19.3529 | 19.3456 | 19.3367 | 19.3099 | 19.2552 | 19.2077 | 19.0997 | 19.0326 | 19.0233 | 19.1058 | 19.2879 | 384363 | 397283 | LONGSIGHT | BREDBURY
| Clarendon Rd | 9.2274 | 6.6264 | 6.0053 | 5.8233 | 5.5875 | 5.3372 | 5.0846 | 4.8165 | 4.5145 | 4.2286 | 2.6436 | 0.070149 | -2.4044 | -5.3724 | -8.0021 | 13.8644 | 11.2634 | 10.6423 | 10.4603 | 10.2245 | 9.9742 | 9.7216 | 9.4535 | 9.1515 | 8.8656 | 7.2806 | 4.7071 | 2.2326 | -0.73538 | -3.4568 | 9.2274 | 8.3889 | 8.1594 | 8.0752 | 7.9701 | 7.842 | 7.6602 | 7.4193 | 7.1981 | 6.9745 | 6.3163 | 5.6084 | 4.8611 | 4.0652 | 3.5351 | 13.8644 | 13.0259 | 12.7964 | 12.7122 | 12.6071 | 12.479 | 12.2972 | 12.0563 | 11.8351 | 11.6115 | 10.9533 | 10.2454 | 9.4981 | 8.7022 | 8.252 | 9.2274 | 6.1607 | 5.409 | 5.1647 | 4.868 | 4.5573 | 4.2421 | 3.9144 | 3.5841 | 3.2731 | 1.6103 | -1.0287 | -3.2794 | -5.6913 | -7.9667 | 13.8644 | 10.7977 | 10.046 | 9.8017 | 9.505 | 9.1943 | 8.8791 | 8.5514 | 8.2211 | 7.9101 | 6.2473 | 3.6083 | 1.3576 | -1.0543 | -3.446 | 9.2274 | 7.2188 | 6.693 | 6.4997 | 6.2358 | 5.9283 | 5.4697 | 4.5795 | 3.6714 | 2.7783 | 0.1877 | -2.6135 | -5.0187 | -6.7356 | -6.1517 | 13.8644 | 11.8558 | 11.33 | 11.1367 | 10.8728 | 10.5653 | 10.1067 | 9.2165 | 8.3084 | 7.4153 | 4.8247 | 2.0235 | -0.38165 | -2.0986 | -1.6399 | 9.2274 | 7.5746 | 7.1527 | 7.0355 | 6.908 | 6.7396 | 6.5238 | 6.2773 | 5.9727 | 5.6661 | 4.6654 | 3.5669 | 2.7229 | 1.8338 | 1.2331 | 13.8644 | 12.2116 | 11.7897 | 11.6725 | 11.545 | 11.3766 | 11.1608 | 10.9143 | 10.6097 | 10.3031 | 9.3024 | 8.2039 | 7.3599 | 6.4708 | 5.9351 | 9.2274 | 5.9698 | 5.1702 | 4.9017 | 4.573 | 4.2393 | 3.7635 | 2.8202 | 1.8742 | 0.947 | -1.9071 | -5.0169 | -7.6771 | -9.657 | -9.3316 | 13.8644 | 10.6068 | 9.8072 | 9.5387 | 9.21 | 8.8763 | 8.4005 | 7.4572 | 6.5112 | 5.584 | 2.7299 | -0.37993 | -3.0401 | -5.02 | -4.7751 | 369051 | 429883 | BLACKBURN | PENWORTHAM
| Claughton | 0.93548 | 0.8765 | 0.83532 | 0.81681 | 0.80296 | 0.78752 | 0.76912 | 0.74644 | 0.62578 | 0.59434 | 0.46643 | -0.099945 | -0.57073 | -1.0357 | -1.4612 | 4.4355 | 4.3765 | 4.3353 | 4.3168 | 4.303 | 4.2875 | 4.2691 | 4.2464 | 4.1258 | 4.0943 | 3.9664 | 3.4001 | 2.9293 | 2.4643 | 2.0075 | 0.93548 | 0.89341 | 0.84311 | 0.80653 | 0.77204 | 0.7307 | 0.65688 | 0.45798 | 0.33521 | 0.29911 | 0.18751 | 0.076528 | -0.020598 | -0.11972 | -0.18498 | 4.4355 | 4.3934 | 4.3431 | 4.3065 | 4.272 | 4.2307 | 4.1569 | 3.958 | 3.8352 | 3.7991 | 3.6875 | 3.5765 | 3.4794 | 3.3803 | 3.324 | 0.93548 | 0.86833 | 0.82571 | 0.80685 | 0.79316 | 0.77818 | 0.76028 | 0.66093 | 0.63892 | 0.62144 | 0.51901 | -0.019072 | -0.45968 | -0.87773 | -1.2381 | 4.4355 | 4.3683 | 4.3257 | 4.3069 | 4.2932 | 4.2782 | 4.2603 | 4.1609 | 4.1389 | 4.1214 | 4.019 | 3.4809 | 3.0403 | 2.6223 | 2.2184 | 0.93548 | 0.92135 | 0.89725 | 0.79751 | 0.8018 | 0.80119 | 0.79229 | 0.7451 | 0.5533 | 0.36383 | -0.18462 | -0.70053 | -1.0864 | -1.3096 | -1.1047 | 4.4355 | 4.4214 | 4.3973 | 4.2975 | 4.3018 | 4.3012 | 4.2923 | 4.2451 | 4.0533 | 3.8638 | 3.3154 | 2.7995 | 2.4136 | 2.1904 | 2.3487 | 0.93548 | 0.88669 | 0.85143 | 0.83956 | 0.83399 | 0.82312 | 0.80537 | 0.78405 | 0.66474 | 0.63318 | 0.53251 | 0.28908 | 0.084507 | -0.11287 | -0.18352 | 4.4355 | 4.3867 | 4.3514 | 4.3396 | 4.334 | 4.3231 | 4.3054 | 4.2841 | 4.1647 | 4.1332 | 4.0325 | 3.7891 | 3.5845 | 3.3871 | 3.3064 | 0.93548 | 0.88874 | 0.84862 | 0.73544 | 0.7272 | 0.71837 | 0.70213 | 0.66508 | 0.498 | 0.30885 | -0.24799 | -0.77864 | -1.1853 | -1.4385 | -1.2711 | 4.4355 | 4.3887 | 4.3486 | 4.2354 | 4.2272 | 4.2184 | 4.2021 | 4.1651 | 3.998 | 3.8088 | 3.252 | 2.7214 | 2.3147 | 2.0615 | 2.191 | 355872 | 466268 | LANCASTER | HEYSHAM
| Cleveleys | 5.491 | 4.6624 | 4.4724 | 4.4171 | 4.301 | 4.1763 | 4.0595 | 3.947 | 3.814 | 3.7117 | 2.3243 | -0.50326 | -2.9445 | -5.7201 | -8.1752 | 8.991 | 8.1624 | 7.9724 | 7.9171 | 7.801 | 7.6763 | 7.5595 | 7.447 | 7.314 | 7.2117 | 5.8243 | 2.9967 | 0.55546 | -2.2201 | -4.84 | 5.491 | 5.2774 | 5.1478 | 5.0145 | 4.8192 | 4.6027 | 4.3235 | 3.9905 | 3.7925 | 3.5929 | 2.9977 | 2.4376 | 1.8451 | 1.1858 | 0.66695 | 8.991 | 8.7774 | 8.6478 | 8.5145 | 8.3192 | 8.1027 | 7.8235 | 7.4905 | 7.2925 | 7.0929 | 6.4977 | 5.9376 | 5.3451 | 4.6858 | 4.2491 | 5.491 | 4.5593 | 4.3726 | 4.3566 | 4.2831 | 4.2079 | 4.1621 | 4.1241 | 4.072 | 4.039 | 2.8719 | 0.23928 | -2.0294 | -4.6047 | -6.8396 | 8.991 | 8.0593 | 7.8726 | 7.8566 | 7.7831 | 7.7079 | 7.6621 | 7.6241 | 7.572 | 7.539 | 6.3719 | 3.7393 | 1.4706 | -1.1047 | -3.5437 | 5.491 | 5.1033 | 5.0438 | 5.0305 | 4.9318 | 4.8045 | 4.5203 | 3.6776 | 2.7921 | 1.913 | -0.65452 | -3.1627 | -5.2207 | -6.5789 | -5.6472 | 8.991 | 8.6033 | 8.5438 | 8.5305 | 8.4318 | 8.3045 | 8.0203 | 7.1776 | 6.2921 | 5.413 | 2.8455 | 0.33726 | -1.7207 | -3.0789 | -2.3528 | 5.491 | 5.2561 | 5.2107 | 5.2249 | 5.2104 | 5.1633 | 5.0966 | 5.0266 | 4.9154 | 4.8146 | 4.3543 | 3.7062 | 3.2423 | 2.7585 | 2.5192 | 8.991 | 8.7561 | 8.7107 | 8.7249 | 8.7104 | 8.6633 | 8.5966 | 8.5266 | 8.4154 | 8.3146 | 7.8543 | 7.2062 | 6.7423 | 6.2585 | 5.9848 | 5.491 | 4.6658 | 4.4483 | 4.3288 | 4.1321 | 3.936 | 3.5678 | 2.6128 | 1.6521 | 0.69867 | -2.084 | -4.7536 | -6.9624 | -8.5031 | -7.7821 | 8.991 | 8.1658 | 7.9483 | 7.8288 | 7.6321 | 7.436 | 7.0678 | 6.1128 | 5.1521 | 4.1987 | 1.416 | -1.2536 | -3.4624 | -5.0031 | -4.4412 | 332286 | 443104 | BISPHAM | PENWORTHAM
| Clifton Junction | 8.7816 | 7.4553 | 7.0773 | 6.977 | 6.8545 | 6.7189 | 6.5785 | 6.4318 | 6.1986 | 5.9686 | 4.8404 | 3.2091 | 1.9433 | 0.73611 | -0.36771 | 12.2816 | 10.9553 | 10.5773 | 10.477 | 10.3545 | 10.2189 | 10.0785 | 9.9318 | 9.6986 | 9.4686 | 8.3404 | 6.7091 | 5.4433 | 4.2361 | 3.0841 | 8.7816 | 8.3422 | 8.1589 | 8.0825 | 8.0157 | 7.942 | 7.8012 | 7.6074 | 7.3964 | 7.1707 | 6.442 | 5.6581 | 4.9011 | 4.0794 | 3.4972 | 12.2816 | 11.8422 | 11.6589 | 11.5825 | 11.5157 | 11.442 | 11.3012 | 11.1074 | 10.8964 | 10.6707 | 9.942 | 9.1581 | 8.4011 | 7.5794 | 7.0851 | 8.7816 | 7.2463 | 6.8264 | 6.7262 | 6.6061 | 6.4748 | 6.3402 | 6.2071 | 6.0477 | 5.8959 | 5.0992 | 3.6061 | 2.4188 | 1.3453 | 0.43518 | 12.2816 | 10.7463 | 10.3264 | 10.2262 | 10.1061 | 9.9748 | 9.8402 | 9.7071 | 9.5477 | 9.3959 | 8.5992 | 7.1061 | 5.9188 | 4.8453 | 3.8498 | 8.7816 | 7.7708 | 7.467 | 7.3785 | 7.2605 | 7.1192 | 6.9152 | 6.5364 | 6.1175 | 5.6066 | 4.0747 | 2.6411 | 1.5905 | 1.0186 | 1.3777 | 12.2816 | 11.2708 | 10.967 | 10.8785 | 10.7605 | 10.6192 | 10.4152 | 10.0364 | 9.6175 | 9.1066 | 7.5747 | 6.1411 | 5.0905 | 4.5186 | 4.7898 | 8.7816 | 7.9768 | 7.7177 | 7.6501 | 7.5917 | 7.5194 | 7.4291 | 7.319 | 7.1404 | 6.9578 | 6.2343 | 5.3557 | 4.7595 | 4.2891 | 4.0696 | 12.2816 | 11.4768 | 11.2177 | 11.1501 | 11.0917 | 11.0194 | 10.9291 | 10.819 | 10.6404 | 10.4578 | 9.7343 | 8.8557 | 8.2595 | 7.7891 | 7.579 | 8.7816 | 7.1328 | 6.6794 | 6.5648 | 6.4259 | 6.2798 | 6.0771 | 5.6713 | 5.1523 | 4.6135 | 2.9856 | 1.4219 | 0.24268 | -0.44794 | -0.1939 | 12.2816 | 10.6328 | 10.1794 | 10.0648 | 9.9259 | 9.7798 | 9.5771 | 9.1713 | 8.6523 | 8.1135 | 6.4856 | 4.9219 | 3.7427 | 3.0521 | 3.2404 | 379289 | 403073 | KEARSLEY LOCAL | KEARSLEY
| Clover Hill | 10.8506 | 10.7492 | 10.651 | 10.5648 | 10.4114 | 10.2547 | 10.1367 | 10.0337 | 9.8249 | 9.6249 | 8.0033 | 5.0451 | 2.4994 | -0.41968 | -2.6788 | 18.9506 | 18.8492 | 18.751 | 18.6648 | 18.5114 | 18.3547 | 18.2367 | 18.1337 | 17.9249 | 17.7249 | 16.1033 | 13.1451 | 10.5994 | 7.6803 | 5.1573 | 10.8506 | 10.7662 | 10.6731 | 10.5888 | 10.4878 | 10.3765 | 10.2263 | 10.0269 | 9.8281 | 9.5789 | 8.8487 | 8.1789 | 7.5871 | 7.0149 | 6.6948 | 18.9506 | 18.8662 | 18.7731 | 18.6888 | 18.5878 | 18.4765 | 18.3263 | 18.1269 | 17.9281 | 17.6789 | 16.9487 | 16.2789 | 15.6871 | 15.1149 | 14.8404 | 10.8506 | 10.7453 | 10.653 | 10.5764 | 10.4368 | 10.2974 | 10.1986 | 10.122 | 10.0292 | 9.9277 | 8.4506 | 5.5909 | 3.0576 | 0.35919 | -1.6582 | 18.9506 | 18.8453 | 18.753 | 18.6764 | 18.5368 | 18.3974 | 18.2986 | 18.222 | 18.1292 | 18.0277 | 16.5506 | 13.6909 | 11.1576 | 8.4592 | 6.1452 | 10.8506 | 10.9037 | 10.8649 | 10.8081 | 10.675 | 10.5241 | 10.1742 | 9.1232 | 8.0519 | 7.0107 | 4.0405 | 1.2602 | -1.0494 | -2.5091 | -1.1247 | 18.9506 | 19.0037 | 18.9649 | 18.9081 | 18.775 | 18.6241 | 18.2742 | 17.2232 | 16.1519 | 15.1107 | 12.1405 | 9.3602 | 7.0506 | 5.5909 | 6.6754 | 10.8506 | 10.7731 | 10.7026 | 10.665 | 10.624 | 10.5707 | 10.5007 | 10.4091 | 10.2581 | 10.0409 | 9.2901 | 8.4735 | 7.9161 | 7.4549 | 7.3849 | 18.9506 | 18.8731 | 18.8026 | 18.765 | 18.724 | 18.6707 | 18.6007 | 18.5091 | 18.3581 | 18.1409 | 17.3901 | 16.5735 | 16.0161 | 15.5549 | 15.4518 | 10.8506 | 10.8497 | 10.7571 | 10.6421 | 10.4557 | 10.2714 | 9.8885 | 8.7786 | 7.6657 | 6.5835 | 3.4875 | 0.56576 | -1.9812 | -3.7788 | -2.7541 | 18.9506 | 18.9497 | 18.8571 | 18.7421 | 18.5557 | 18.3714 | 17.9885 | 16.8786 | 15.7657 | 14.6835 | 11.5875 | 8.6658 | 6.1188 | 4.3212 | 5.1283 | 386638 | 437064 | NELSON | PADIHAM
| Cog Lane | 7.9828 | 7.0189 | 6.1985 | 5.5538 | 5.3789 | 5.1683 | 4.9794 | 4.8 | 4.5406 | 4.301 | 1.936 | -2.5159 | -6.3329 | -10.3956 | -13.8378 | 18.4077 | 17.4438 | 16.6234 | 15.9787 | 15.8038 | 15.5932 | 15.4043 | 15.2249 | 14.9655 | 14.7259 | 12.3609 | 7.909 | 4.0919 | 0.029295 | -3.6879 | 7.9828 | 7.6896 | 7.3317 | 7.0272 | 6.8911 | 6.7293 | 6.4869 | 6.1388 | 5.8398 | 5.5375 | 4.5695 | 3.496 | 2.4224 | 1.2155 | 0.3586 | 18.4077 | 18.1145 | 17.7566 | 17.4521 | 17.316 | 17.1542 | 16.9118 | 16.5637 | 16.2647 | 15.9624 | 14.9944 | 13.9209 | 12.8473 | 11.6404 | 10.9112 | 7.9828 | 6.9012 | 6.0807 | 5.4808 | 5.3493 | 5.1898 | 5.0828 | 4.9864 | 4.8535 | 4.7154 | 2.6295 | -1.6387 | -5.3072 | -9.135 | -12.259 | 18.4077 | 17.3261 | 16.5056 | 15.9057 | 15.7742 | 15.6147 | 15.5077 | 15.4113 | 15.2784 | 15.1403 | 13.0544 | 8.7862 | 5.1177 | 1.2899 | -2.1672 | 7.9828 | 7.5996 | 6.9207 | 6.3347 | 6.1859 | 5.9962 | 5.5576 | 4.1873 | 2.7564 | 1.3215 | -2.8487 | -6.8367 | -10.1433 | -12.2001 | -10.6695 | 18.4077 | 18.0245 | 17.3456 | 16.7596 | 16.6108 | 16.4211 | 15.9825 | 14.6122 | 13.1813 | 11.7464 | 7.5762 | 3.5882 | 0.28163 | -1.7752 | -0.58343 | 7.9828 | 7.5965 | 6.9048 | 6.3336 | 6.3409 | 6.3104 | 6.2347 | 6.1074 | 5.8503 | 5.5888 | 4.5708 | 3.3792 | 2.5694 | 1.8382 | 1.5624 | 18.4077 | 18.0214 | 17.3297 | 16.7585 | 16.7658 | 16.7353 | 16.6596 | 16.5323 | 16.2752 | 16.0137 | 14.9957 | 13.8041 | 12.9943 | 12.2631 | 11.9581 | 7.9828 | 7.1164 | 6.2894 | 5.6219 | 5.398 | 5.1548 | 4.6468 | 3.1959 | 1.722 | 0.23936 | -4.1374 | -8.3907 | -11.9791 | -14.3979 | -13.2652 | 18.4077 | 17.5413 | 16.7143 | 16.0468 | 15.8229 | 15.5797 | 15.0717 | 13.6208 | 12.1469 | 10.6643 | 6.2875 | 2.0342 | -1.5542 | -3.973 | -3.0913 | 382462 | 432232 | HUNCOAT | PADIHAM
| Coniston | -0.53647 | -0.61324 | -0.66156 | -0.71274 | -0.78002 | 1.3492 | 1.2816 | 1.2071 | 1.1437 | 1.0874 | 0.7801 | 0.13536 | -0.40561 | -0.95746 | -1.4639 | 1.6635 | 1.5868 | 1.5384 | 1.4873 | 1.42 | 1.3492 | 1.2816 | 1.2071 | 1.1437 | 1.0874 | 0.7801 | 0.13536 | -0.40561 | -0.95746 | -1.4958 | -0.53647 | -0.61472 | -0.69755 | -0.79115 | -0.90539 | 1.165 | 1.0105 | 0.81893 | 0.76349 | 0.69676 | 0.50242 | 0.32768 | 0.17811 | 0.01868 | -0.10218 | 1.6635 | 1.5853 | 1.5025 | 1.4089 | 1.2946 | 1.165 | 1.0105 | 0.81893 | 0.76349 | 0.69676 | 0.50242 | 0.32768 | 0.17811 | 0.01868 | -0.084131 | -0.53647 | -0.61427 | -0.65916 | -0.70316 | -0.76302 | 1.3725 | 1.3112 | 1.2473 | 1.1996 | 1.1554 | 0.91852 | 0.32339 | -0.17646 | -0.67574 | -1.1183 | 1.6635 | 1.5857 | 1.5408 | 1.4968 | 1.437 | 1.3725 | 1.3112 | 1.2473 | 1.1996 | 1.1554 | 0.91852 | 0.32339 | -0.17646 | -0.67574 | -1.1604 | -0.53647 | -0.5525 | -0.5755 | -0.61038 | -0.66312 | 1.4807 | 1.3952 | 1.194 | 0.98585 | 0.77946 | 0.18384 | -0.38936 | -0.83979 | -1.1105 | -0.93347 | 1.6635 | 1.6475 | 1.6245 | 1.5896 | 1.5369 | 1.4807 | 1.3952 | 1.194 | 0.98585 | 0.77946 | 0.18384 | -0.38936 | -0.83979 | -1.1105 | -0.97672 | -0.53647 | -0.59884 | -0.63936 | -0.67616 | -0.72096 | 1.4276 | 1.369 | 1.3013 | 1.2405 | 1.1815 | 0.98022 | 0.75255 | 0.57352 | 0.38228 | 0.28274 | 1.6635 | 1.6012 | 1.5606 | 1.5238 | 1.479 | 1.4276 | 1.369 | 1.3013 | 1.2405 | 1.1815 | 0.98022 | 0.75255 | 0.57352 | 0.38228 | 0.27634 | -0.53647 | -0.58376 | -0.63879 | -0.70019 | -0.77302 | 1.3535 | 1.244 | 1.0124 | 0.78946 | 0.56835 | -0.069978 | -0.67785 | -1.1609 | -1.4716 | -1.3409 | 1.6635 | 1.6162 | 1.5612 | 1.4998 | 1.427 | 1.3535 | 1.244 | 1.0124 | 0.78946 | 0.56835 | -0.069978 | -0.67785 | -1.1609 | -1.4716 | -1.3736 | 329874 | 497641 | ULVERSTON | HARKER | Firm Capacity marginally exceeded. Storm Arwen Reinforcement project in RIIO-ED2 will increase firm capacity
| Copse Rd | 7.539 | 7.0033 | 6.7096 | 6.4941 | 6.1822 | 5.8578 | 5.5827 | 5.3554 | 5.076 | 4.8266 | 2.6146 | -1.5437 | -5.025 | -8.7605 | -12.0852 | 9.176 | 8.6403 | 8.3466 | 8.1311 | 7.8192 | 7.4948 | 7.2197 | 6.9924 | 6.713 | 6.4636 | 4.2516 | 0.09327 | -3.388 | -7.1235 | -10.6768 | 7.539 | 7.1875 | 6.9193 | 6.6924 | 6.4332 | 6.1781 | 5.8482 | 5.4043 | 5.057 | 4.7095 | 3.6654 | 2.6163 | 1.6115 | 0.50397 | -0.30649 | 9.176 | 8.8245 | 8.5563 | 8.3294 | 8.0702 | 7.8151 | 7.4852 | 7.0413 | 6.694 | 6.3465 | 5.3024 | 4.2533 | 3.2485 | 2.141 | 1.4573 | 7.539 | 6.972 | 6.6929 | 6.5229 | 6.2528 | 5.9761 | 5.7448 | 5.5699 | 5.3783 | 5.2174 | 3.2845 | -0.56794 | -3.7851 | -7.2089 | -10.1486 | 9.176 | 8.609 | 8.3299 | 8.1599 | 7.8898 | 7.6131 | 7.3818 | 7.2069 | 7.0153 | 6.8544 | 4.9215 | 1.0691 | -2.1481 | -5.5719 | -8.8081 | 7.539 | 7.3278 | 7.144 | 6.9807 | 6.6974 | 6.3866 | 5.8575 | 4.5425 | 3.162 | 1.8127 | -2.0643 | -5.7285 | -8.7063 | -10.542 | -9.2057 | 9.176 | 8.9648 | 8.781 | 8.6177 | 8.3344 | 8.0236 | 7.4945 | 6.1795 | 4.799 | 3.4497 | -0.42729 | -4.0915 | -7.0693 | -8.905 | -7.8706 | 7.539 | 7.0987 | 6.8523 | 6.7121 | 6.5651 | 6.4185 | 6.2751 | 6.1061 | 5.8188 | 5.5315 | 4.5095 | 3.3309 | 2.55 | 1.8161 | 1.5388 | 9.176 | 8.7357 | 8.4893 | 8.3491 | 8.2021 | 8.0555 | 7.9121 | 7.7431 | 7.4558 | 7.1685 | 6.1465 | 4.9679 | 4.187 | 3.4531 | 3.1449 | 7.539 | 7.0952 | 6.7968 | 6.5375 | 6.1642 | 5.7865 | 5.196 | 3.7891 | 2.359 | 0.95287 | -3.1389 | -7.0595 | -10.2725 | -12.3961 | -11.3964 | 9.176 | 8.7322 | 8.4338 | 8.1745 | 7.8012 | 7.4235 | 6.833 | 5.4261 | 3.996 | 2.5899 | -1.5019 | -5.4225 | -8.6355 | -10.7591 | -9.9867 | 333013 | 446934 | THORNTON | STANAH
| Cox Green | 5.4466 | 5.1266 | 5.0182 | 4.9767 | 4.8713 | 4.7669 | 4.6895 | 4.6164 | 4.4791 | 4.3639 | 3.0639 | 0.48655 | -1.727 | -4.1367 | -6.0885 | 9.7466 | 9.4266 | 9.3182 | 9.2767 | 9.1713 | 9.0669 | 8.9895 | 8.9164 | 8.7791 | 8.6639 | 7.3639 | 4.7866 | 2.573 | 0.16331 | -1.9762 | 5.4466 | 5.3359 | 5.2672 | 5.1983 | 5.0794 | 4.935 | 4.7395 | 4.4983 | 4.2744 | 4.0463 | 3.3745 | 2.7391 | 2.1549 | 1.5529 | 1.1603 | 9.7466 | 9.6359 | 9.5672 | 9.4983 | 9.3794 | 9.235 | 9.0395 | 8.7983 | 8.5744 | 8.3463 | 7.6745 | 7.0391 | 6.4549 | 5.8529 | 5.5203 | 5.4466 | 5.1038 | 5.0141 | 5.0178 | 4.9617 | 4.9149 | 4.9168 | 4.9307 | 4.8858 | 4.849 | 3.793 | 1.4333 | -0.59358 | -2.7959 | -4.5293 | 9.7466 | 9.4038 | 9.3141 | 9.3178 | 9.2617 | 9.2149 | 9.2168 | 9.2307 | 9.1858 | 9.149 | 8.093 | 5.7333 | 3.7064 | 1.5041 | -0.45797 | 5.4466 | 5.4578 | 5.4681 | 5.5034 | 5.4536 | 5.3829 | 5.1759 | 4.43 | 3.6327 | 2.8395 | 0.54597 | -1.6827 | -3.5283 | -4.7242 | -3.6635 | 9.7466 | 9.7578 | 9.7681 | 9.8034 | 9.7536 | 9.6829 | 9.4759 | 8.73 | 7.9327 | 7.1395 | 4.846 | 2.6173 | 0.77168 | -0.42424 | 0.40561 | 5.4466 | 5.314 | 5.2856 | 5.3121 | 5.3172 | 5.2897 | 5.2369 | 5.1801 | 5.0467 | 4.9193 | 4.442 | 3.8421 | 3.2504 | 2.681 | 2.4554 | 9.7466 | 9.614 | 9.5856 | 9.6121 | 9.6172 | 9.5897 | 9.5369 | 9.4801 | 9.3467 | 9.2193 | 8.742 | 8.1421 | 7.5504 | 6.981 | 6.7484 | 5.4466 | 5.259 | 5.1551 | 5.0929 | 4.9557 | 4.8282 | 4.5501 | 3.7021 | 2.8221 | 1.9473 | -0.58625 | -3.0144 | -5.0538 | -6.4966 | -5.7148 | 9.7466 | 9.559 | 9.4551 | 9.3929 | 9.2557 | 9.1282 | 8.8501 | 8.0021 | 7.1221 | 6.2473 | 3.7137 | 1.2856 | -0.75383 | -2.1966 | -1.5846 | 371893 | 413641 | BOLTON | KEARSLEY
| Craggs Row & Bushell St | 6.0947 | 3.5068 | 2.8759 | 2.7063 | 2.4879 | 2.2662 | 2.0789 | 1.9186 | 1.6832 | 1.4818 | -0.12174 | -3.0777 | -5.5011 | -8.0452 | -10.1583 | 10.2347 | 7.6468 | 7.0159 | 6.8463 | 6.6279 | 6.4062 | 6.2189 | 6.0586 | 5.8232 | 5.6218 | 4.0183 | 1.0623 | -1.3611 | -3.9052 | -6.2301 | 6.0947 | 5.2858 | 4.9337 | 4.7113 | 4.469 | 4.2239 | 3.9124 | 3.5259 | 3.2128 | 2.9047 | 2.0303 | 1.2114 | 0.5326 | -0.14847 | -0.59691 | 10.2347 | 9.4258 | 9.0737 | 8.8513 | 8.609 | 8.3639 | 8.0524 | 7.6659 | 7.3528 | 7.0447 | 6.1703 | 5.3514 | 4.6726 | 3.9915 | 3.6007 | 6.0947 | 3.1237 | 2.4432 | 2.3146 | 2.13 | 1.945 | 1.8133 | 1.7088 | 1.5868 | 1.467 | 0.12526 | -2.5767 | -4.7504 | -6.9699 | -8.6859 | 10.2347 | 7.2637 | 6.5832 | 6.4546 | 6.27 | 6.085 | 5.9533 | 5.8488 | 5.7268 | 5.607 | 4.2653 | 1.5633 | -0.61041 | -2.8299 | -4.8288 | 6.0947 | 4.1874 | 3.7392 | 3.6665 | 3.517 | 3.3437 | 3.021 | 2.1072 | 1.1411 | 0.17752 | -2.5263 | -5.0831 | -7.0718 | -8.1961 | -6.9095 | 10.2347 | 8.3274 | 7.8792 | 7.8065 | 7.657 | 7.4837 | 7.161 | 6.2472 | 5.2811 | 4.3175 | 1.6137 | -0.94309 | -2.9318 | -4.0561 | -3.0588 | 6.0947 | 4.7176 | 4.3301 | 4.2267 | 4.1342 | 4.0361 | 3.9232 | 3.7827 | 3.524 | 3.2707 | 2.441 | 1.5655 | 1.0104 | 0.52378 | 0.56222 | 10.2347 | 8.8576 | 8.4701 | 8.3667 | 8.2742 | 8.1761 | 8.0632 | 7.9227 | 7.664 | 7.4107 | 6.581 | 5.7055 | 5.1504 | 4.6638 | 4.6339 | 6.0947 | 2.9074 | 2.1618 | 1.9918 | 1.7519 | 1.5152 | 1.1173 | 0.10102 | -0.9277 | -1.9538 | -4.8427 | -7.5455 | -9.6919 | -11.0362 | -10.0237 | 10.2347 | 7.0474 | 6.3018 | 6.1318 | 5.8919 | 5.6552 | 5.2573 | 4.241 | 3.2123 | 2.1862 | -0.70269 | -3.4055 | -5.5519 | -6.8962 | -6.1103 | 353740 | 430080 | RIBBLE | PENWORTHAM
| Crown Lane | 6.742 | 5.4672 | 4.2851 | 3.2593 | 2.0826 | 0.83542 | -0.44985 | -1.8249 | -3.3744 | -4.9838 | -11.1809 | -17.1544 | -21.1637 | -24.589 | -26.7659 | 11.379 | 10.1042 | 8.9221 | 7.8963 | 6.7196 | 5.4724 | 4.1871 | 2.8121 | 1.2626 | -0.34677 | -6.5439 | -12.5174 | -16.5267 | -19.952 | -22.3666 | 6.742 | 6.3609 | 6.043 | 5.7336 | 5.3487 | 4.9127 | 4.3621 | 3.6652 | 3.0377 | 2.3451 | -0.026051 | -2.7361 | -5.4472 | -9.1027 | -11.4557 | 11.379 | 10.9979 | 10.68 | 10.3706 | 9.9857 | 9.5497 | 8.9991 | 8.3022 | 7.6747 | 6.9821 | 4.6109 | 1.9009 | -0.81023 | -4.4657 | -6.4951 | 6.742 | 5.2203 | 3.8992 | 2.7825 | 1.5167 | 0.19329 | -1.1349 | -2.5352 | -4.0674 | -5.717 | -12.2177 | -18.2907 | -22.0892 | -25.0751 | -26.2201 | 11.379 | 9.8573 | 8.5362 | 7.4195 | 6.1537 | 4.8303 | 3.5021 | 2.1018 | 0.56963 | -1.08 | -7.5807 | -13.6537 | -17.4522 | -20.4381 | -21.6886 | 6.742 | 5.8092 | 4.6563 | 3.5728 | 2.3037 | 0.91538 | -0.74976 | -3.207 | -5.7627 | -8.3602 | -15.9143 | -21.0718 | -23.91 | -25.0667 | -24.2332 | 11.379 | 10.4462 | 9.2933 | 8.2098 | 6.9407 | 5.5524 | 3.8872 | 1.43 | -1.1257 | -3.7232 | -11.2773 | -16.4348 | -19.273 | -20.4297 | -19.7219 | 6.742 | 6.1623 | 5.1883 | 4.2925 | 3.3443 | 2.3027 | 1.1642 | -0.086664 | -1.5347 | -3.0709 | -8.12 | -11.8729 | -14.4174 | -16.5194 | -17.4702 | 11.379 | 10.7993 | 9.8253 | 8.9295 | 7.9813 | 6.9397 | 5.8012 | 4.5503 | 3.1023 | 1.5661 | -3.483 | -7.2359 | -9.7804 | -11.8824 | -12.7328 | 6.742 | 5.266 | 3.8967 | 2.68 | 1.3032 | -0.12914 | -1.8282 | -4.3439 | -6.8986 | -9.5044 | -17.3345 | -23.0458 | -26.4464 | -28.1031 | -27.3409 | 11.379 | 9.903 | 8.5337 | 7.317 | 5.9402 | 4.5079 | 2.8088 | 0.29313 | -2.2616 | -4.8674 | -12.6975 | -18.4088 | -21.8094 | -23.4661 | -22.8928 | 362706 | 410859 | WESTHOUGHTON | KEARSLEY
| Culcheth | 3.3091 | 3.0596 | 2.9358 | 2.8772 | 2.7851 | 2.6871 | 2.5981 | 2.5027 | 2.3643 | 2.2355 | 1.5556 | 0.48195 | -0.38471 | -1.2341 | -2.1607 | 9.3091 | 9.0596 | 8.9358 | 8.8772 | 8.7851 | 8.6871 | 8.5981 | 8.5027 | 8.3643 | 8.2355 | 7.5556 | 6.482 | 5.6153 | 4.7659 | 3.8036 | 3.3091 | 3.2628 | 3.1903 | 3.144 | 3.0995 | 3.0559 | 2.9893 | 2.8947 | 2.7557 | 2.6154 | 2.1859 | 1.7444 | 1.2688 | 0.67231 | 0.2348 | 9.3091 | 9.2628 | 9.1903 | 9.144 | 9.0995 | 9.0559 | 8.9893 | 8.8947 | 8.7557 | 8.6154 | 8.1859 | 7.7444 | 7.2688 | 6.6723 | 6.3067 | 3.3091 | 3.022 | 2.8905 | 2.831 | 2.2559 | 1.6757 | 1.1039 | 0.52796 | -0.066808 | -0.34777 | -0.94752 | -1.9439 | -2.7302 | -3.46 | -4.0596 | 9.3091 | 9.022 | 8.8905 | 8.831 | 8.2559 | 7.6757 | 7.1039 | 6.528 | 5.9332 | 5.6522 | 5.0525 | 4.0561 | 3.2698 | 2.54 | 1.8712 | 3.3091 | 3.2118 | 3.1345 | 3.0942 | 2.5399 | 1.9668 | 1.3381 | 0.53107 | -0.29544 | -0.80954 | -1.7772 | -2.7159 | -3.4207 | -3.823 | -3.4883 | 9.3091 | 9.2118 | 9.1345 | 9.0942 | 8.5399 | 7.9668 | 7.3381 | 6.5311 | 5.7046 | 5.1905 | 4.2228 | 3.2841 | 2.5793 | 2.177 | 2.4332 | 3.3091 | 3.2475 | 3.1767 | 3.1463 | 3.117 | 3.0745 | 3.0017 | 2.8842 | 2.7034 | 2.5182 | 1.9018 | 1.2298 | 0.73596 | 0.29393 | 0.19504 | 9.3091 | 9.2475 | 9.1767 | 9.1463 | 9.117 | 9.0745 | 9.0017 | 8.8842 | 8.7034 | 8.5182 | 7.9018 | 7.2298 | 6.736 | 6.2939 | 6.1821 | 3.3091 | 3.0816 | 2.9517 | 2.8764 | 2.2928 | 1.7109 | 1.0787 | 0.25089 | -0.59171 | -1.1199 | -2.124 | -3.0904 | -3.8291 | -4.2704 | -3.9955 | 9.3091 | 9.0816 | 8.9517 | 8.8764 | 8.2928 | 7.7109 | 7.0787 | 6.2509 | 5.4083 | 4.8801 | 3.876 | 2.9096 | 2.1709 | 1.7296 | 1.9415 | 365430 | 395366 | GOLBORNE | BOLD
| Cutacre | 18.0791 | 12.6394 | 11.4849 | 11.4669 | 11.4666 | 6.4654 | 6.4639 | 6.4562 | 6.3903 | 6.3201 | 6.0447 | 5.7318 | 5.5126 | 5.3369 | 5.2454 | 22.0791 | 16.6394 | 15.4849 | 15.4669 | 15.4666 | 10.4654 | 10.4639 | 10.4562 | 10.3903 | 10.3201 | 10.0447 | 9.7318 | 9.5126 | 9.3369 | 9.2181 | 18.0791 | 16.4768 | 16.1047 | 16.0925 | 16.1041 | 11.1174 | 11.1319 | 11.1469 | 11.0888 | 11.0283 | 10.8337 | 10.6215 | 10.4214 | 10.2122 | 10.0732 | 22.0791 | 20.4768 | 20.1047 | 20.0925 | 20.1041 | 15.1174 | 15.1319 | 15.1469 | 15.0888 | 15.0283 | 14.8337 | 14.6215 | 14.4214 | 14.2122 | 14.0875 | 18.0791 | 11.7318 | 10.3932 | 10.3747 | 10.3759 | 5.3777 | 5.3809 | 5.3802 | 5.3428 | 5.3039 | 5.1065 | 4.8497 | 4.6894 | 4.6168 | 4.6764 | 22.0791 | 15.7318 | 14.3932 | 14.3747 | 14.3759 | 9.3777 | 9.3809 | 9.3802 | 9.3428 | 9.3039 | 9.1065 | 8.8497 | 8.6894 | 8.6168 | 8.6203 | 18.0791 | 13.5467 | 12.5781 | 12.5589 | 12.5588 | 7.5566 | 7.5392 | 7.4774 | 7.3761 | 7.2737 | 6.982 | 6.7518 | 6.6223 | 6.6309 | 6.8727 | 22.0791 | 17.5467 | 16.5781 | 16.5589 | 16.5588 | 11.5566 | 11.5392 | 11.4774 | 11.3761 | 11.2737 | 10.982 | 10.7518 | 10.6223 | 10.6309 | 10.8159 | 18.0791 | 14.8718 | 14.173 | 14.16 | 14.1702 | 9.1793 | 9.1846 | 9.1833 | 9.1251 | 9.0618 | 8.8507 | 8.6565 | 8.5432 | 8.4975 | 8.5784 | 22.0791 | 18.8718 | 18.173 | 18.16 | 18.1702 | 13.1793 | 13.1846 | 13.1833 | 13.1251 | 13.0618 | 12.8507 | 12.6565 | 12.5432 | 12.4975 | 12.5523 | 18.0791 | 10.8257 | 9.302 | 9.2803 | 9.2789 | 4.2787 | 4.2659 | 3.6073 | 2.9115 | 2.2146 | 0.11769 | -1.341 | -1.496 | -1.5022 | -1.264 | 22.0791 | 14.8257 | 13.302 | 13.2803 | 13.2789 | 8.2787 | 8.2659 | 7.6073 | 6.9115 | 6.2146 | 4.1177 | 2.659 | 2.504 | 2.4978 | 2.6799 | 369848 | 404515 | KEARSLEY LOCAL | KEARSLEY
| Deansgate | 8.693 | 6.2169 | 5.5518 | 5.4485 | 5.3931 | 5.3472 | 5.3156 | 5.2873 | 5.1832 | 5.0886 | 4.7046 | 4.1802 | 3.781 | 3.4026 | 3.155 | 16.023 | 13.5469 | 12.8818 | 12.7785 | 12.7231 | 12.6772 | 12.6456 | 12.6173 | 12.5132 | 12.4186 | 12.0346 | 11.5102 | 11.111 | 10.7326 | 10.4293 | 8.693 | 7.9379 | 7.5813 | 7.4166 | 7.2899 | 7.1493 | 6.9901 | 6.8063 | 6.6572 | 6.5126 | 6.1216 | 5.7854 | 5.5281 | 5.2761 | 5.0769 | 16.023 | 15.2679 | 14.9113 | 14.7466 | 14.6199 | 14.4793 | 14.3201 | 14.1363 | 13.9872 | 13.8426 | 13.4516 | 13.1154 | 12.8581 | 12.6061 | 12.4288 | 8.693 | 5.8091 | 5.0618 | 4.9559 | 4.8991 | 4.8521 | 4.8186 | 4.7885 | 4.7296 | 4.6863 | 4.4645 | 4.1208 | 3.9153 | 3.8101 | 3.9192 | 16.023 | 13.1391 | 12.3918 | 12.2859 | 12.2291 | 12.1821 | 12.1486 | 12.1185 | 12.0596 | 12.0163 | 11.7945 | 11.4508 | 11.2453 | 11.1401 | 11.1254 | 8.693 | 6.6405 | 6.0849 | 6.0049 | 5.9762 | 5.9542 | 5.9157 | 5.7972 | 5.6136 | 5.4449 | 5.0123 | 4.6684 | 4.4702 | 4.5156 | 5.0483 | 16.023 | 13.9705 | 13.4149 | 13.3349 | 13.3062 | 13.2842 | 13.2457 | 13.1272 | 12.9436 | 12.7749 | 12.3423 | 11.9984 | 11.8002 | 11.8456 | 12.2527 | 8.693 | 7.3175 | 6.881 | 6.7881 | 6.7527 | 6.7228 | 6.6946 | 6.6632 | 6.5539 | 6.4505 | 6.1722 | 5.9432 | 5.8267 | 5.7759 | 5.9397 | 16.023 | 14.6475 | 14.211 | 14.1181 | 14.0827 | 14.0528 | 14.0246 | 13.9932 | 13.8839 | 13.7805 | 13.5022 | 13.2732 | 13.1567 | 13.1059 | 13.2155 | 8.693 | 5.4087 | 4.578 | 4.465 | 4.4028 | 4.3514 | 4.2824 | 4.1265 | 3.9394 | 3.7679 | 3.3309 | 2.9901 | 2.7938 | 2.8413 | 3.3695 | 16.023 | 12.7387 | 11.908 | 11.795 | 11.7328 | 11.6814 | 11.6124 | 11.4565 | 11.2694 | 11.0979 | 10.6609 | 10.3201 | 10.1238 | 10.1713 | 10.5758 | 383463 | 398149 | BLOOM ST | SOUTH MANCHESTER
| Denton East | 9.0417 | 8.685 | 8.4814 | 8.2756 | 7.9483 | 7.6066 | 7.2973 | 7.0415 | 6.7748 | 6.534 | 4.8253 | 1.9959 | -0.19962 | -2.161 | -3.6038 | 9.0417 | 8.685 | 8.4814 | 8.2756 | 7.9483 | 7.6066 | 7.2973 | 7.0415 | 6.7748 | 6.534 | 4.8253 | 1.9959 | -0.19962 | -2.161 | -3.821 | 9.0417 | 8.8506 | 8.7177 | 8.5857 | 8.4012 | 8.1921 | 7.9202 | 7.593 | 7.3735 | 7.1256 | 6.386 | 5.6774 | 4.9801 | 4.2372 | 3.6698 | 9.0417 | 8.8506 | 8.7177 | 8.5857 | 8.4012 | 8.1921 | 7.9202 | 7.593 | 7.3735 | 7.1256 | 6.386 | 5.6774 | 4.9801 | 4.2372 | 3.7605 | 9.0417 | 8.5739 | 8.2792 | 7.991 | 7.5783 | 7.1501 | 6.7637 | 6.4194 | 6.0715 | 5.7184 | 3.5798 | 0.84071 | -1.0143 | -2.394 | -2.8894 | 9.0417 | 8.5739 | 8.2792 | 7.991 | 7.5783 | 7.1501 | 6.7637 | 6.4194 | 6.0715 | 5.7184 | 3.5798 | 0.84071 | -1.0143 | -2.394 | -3.0686 | 9.0417 | 8.9263 | 8.7154 | 8.4539 | 8.0427 | 7.5888 | 7.0125 | 5.9725 | 4.942 | 3.949 | 1.2138 | -0.97468 | -2.256 | -2.5835 | -1.7431 | 9.0417 | 8.9263 | 8.7154 | 8.4539 | 8.0427 | 7.5888 | 7.0125 | 5.9725 | 4.942 | 3.949 | 1.2138 | -0.97468 | -2.256 | -2.5835 | -1.9303 | 9.0417 | 8.778 | 8.639 | 8.5333 | 8.4025 | 8.2367 | 8.0429 | 7.8385 | 7.5748 | 7.3094 | 6.3779 | 5.205 | 4.3639 | 3.5535 | 3.0666 | 9.0417 | 8.778 | 8.639 | 8.5333 | 8.4025 | 8.2367 | 8.0429 | 7.8385 | 7.5748 | 7.3094 | 6.3779 | 5.205 | 4.3639 | 3.5535 | 3.1079 | 9.0417 | 8.7754 | 8.4501 | 8.0839 | 7.5771 | 7.0589 | 6.4054 | 5.2569 | 4.1472 | 3.076 | 0.11471 | -2.2486 | -3.6911 | -4.1076 | -3.4318 | 9.0417 | 8.7754 | 8.4501 | 8.0839 | 7.5771 | 7.0589 | 6.4054 | 5.2569 | 4.1472 | 3.076 | 0.11471 | -2.2486 | -3.6911 | -4.1076 | -3.5737 | 392394 | 395626 | DROYLSDEN | STALYBRIDGE
| Denton West | 10.3035 | 7.7216 | 7.1463 | 6.7275 | 6.0967 | 5.7599 | 5.4323 | 5.0999 | 4.7034 | 4.4788 | 2.7571 | -0.30765 | -2.8323 | -5.4729 | -7.7997 | 14.9405 | 12.3586 | 11.7833 | 11.3645 | 10.7337 | 10.3969 | 10.0693 | 9.7369 | 9.3404 | 9.1158 | 7.3941 | 4.3294 | 1.8047 | -0.83591 | -3.3757 | 10.3035 | 9.8251 | 9.6641 | 9.5731 | 9.4064 | 9.2145 | 8.9587 | 8.633 | 8.333 | 8.0283 | 7.1104 | 6.2007 | 5.3697 | 4.5171 | 3.979 | 14.9405 | 14.4621 | 14.3011 | 14.2101 | 14.0434 | 13.8515 | 13.5957 | 13.27 | 12.97 | 12.6653 | 11.7474 | 10.8377 | 10.0067 | 9.1541 | 8.6966 | 10.3035 | 7.3239 | 6.6923 | 6.312 | 5.7378 | 5.4499 | 5.1925 | 4.9327 | 4.6299 | 4.4822 | 2.9722 | 0.06986 | -2.3137 | -4.7753 | -6.8667 | 14.9405 | 11.9609 | 11.3293 | 10.949 | 10.3748 | 10.0869 | 9.8295 | 9.5697 | 9.2669 | 9.1192 | 7.6092 | 4.7069 | 2.3233 | -0.13831 | -2.4826 | 10.3035 | 8.4645 | 8.0702 | 7.7471 | 7.2034 | 6.9005 | 6.4225 | 5.3394 | 4.2156 | 3.2498 | 0.41736 | -2.3999 | -4.6665 | -6.1271 | -4.9441 | 14.9405 | 13.1015 | 12.7072 | 12.3841 | 11.8404 | 11.5375 | 11.0595 | 9.9764 | 8.8526 | 7.8868 | 5.0544 | 2.2371 | -0.029517 | -1.4901 | -0.56366 | 10.3035 | 9.4885 | 9.3105 | 8.9747 | 8.4692 | 8.229 | 7.9517 | 7.65 | 7.2558 | 7.0079 | 6.1012 | 5.0794 | 4.3919 | 3.8078 | 3.6303 | 14.9405 | 14.1255 | 13.9475 | 13.6117 | 13.1062 | 12.866 | 12.5887 | 12.287 | 11.8928 | 11.6449 | 10.7382 | 9.7164 | 9.0289 | 8.4448 | 8.2353 | 10.3035 | 7.1683 | 6.424 | 5.9946 | 5.3583 | 5.0056 | 4.4696 | 3.2947 | 2.0991 | 1.0623 | -1.9714 | -4.922 | -7.4082 | -9.1657 | -8.3268 | 14.9405 | 11.8053 | 11.061 | 10.6316 | 9.9953 | 9.6426 | 9.1066 | 7.9317 | 6.7361 | 5.6993 | 2.6656 | -0.28498 | -2.7712 | -4.5287 | -3.8694 | 390380 | 395565 | DROYLSDEN | STALYBRIDGE
| Dickinson St T11 & T12 | 6.194 | 5.7287 | 5.1079 | 4.583 | 4.1263 | 3.6807 | 3.6135 | 3.5457 | 3.3358 | 3.1377 | 2.4607 | 1.6472 | 1.0373 | 0.43894 | -0.0093675 | 10.694 | 10.2287 | 9.6079 | 9.083 | 8.6263 | 8.1807 | 8.1135 | 8.0457 | 7.8358 | 7.6377 | 6.9607 | 6.1472 | 5.5373 | 4.9389 | 4.4576 | 6.194 | 6.0832 | 5.8137 | 5.6344 | 5.5231 | 5.4085 | 5.291 | 5.1574 | 4.8808 | 4.6095 | 3.8673 | 3.2019 | 2.6807 | 2.1356 | 1.6235 | 10.694 | 10.5832 | 10.3137 | 10.1344 | 10.0231 | 9.9085 | 9.791 | 9.6574 | 9.3808 | 9.1095 | 8.3673 | 7.7019 | 7.1807 | 6.6356 | 6.2026 | 6.194 | 5.7235 | 5.1015 | 4.5718 | 4.1131 | 3.666 | 3.5952 | 3.5248 | 3.375 | 3.2464 | 2.7883 | 2.2191 | 1.8622 | 1.6245 | 1.6468 | 10.694 | 10.2235 | 9.6015 | 9.0718 | 8.6131 | 8.166 | 8.0952 | 8.0248 | 7.875 | 7.7464 | 7.2883 | 6.7191 | 6.3622 | 6.1245 | 6.0233 | 6.194 | 5.7647 | 5.1683 | 4.6597 | 4.2201 | 3.7847 | 3.6906 | 3.5047 | 3.2245 | 2.9635 | 2.2908 | 1.7361 | 1.4007 | 1.3477 | 1.8584 | 10.694 | 10.2647 | 9.6683 | 9.1597 | 8.7201 | 8.2847 | 8.1906 | 8.0047 | 7.7245 | 7.4635 | 6.7908 | 6.2361 | 5.9007 | 5.8477 | 6.2308 | 6.194 | 5.7362 | 5.126 | 4.6179 | 4.1884 | 3.7613 | 3.6966 | 3.6269 | 3.4129 | 3.2058 | 2.6465 | 2.159 | 1.8599 | 1.6218 | 1.621 | 10.694 | 10.2362 | 9.626 | 9.1179 | 8.6884 | 8.2613 | 8.1966 | 8.1269 | 7.9129 | 7.7058 | 7.1465 | 6.659 | 6.3599 | 6.1218 | 6.0928 | 6.194 | 5.7468 | 5.1272 | 4.5924 | 4.1292 | 3.6797 | 3.5734 | 3.3655 | 3.0763 | 2.8078 | 2.1214 | 1.563 | 1.2281 | 1.1691 | 1.6598 | 10.694 | 10.2468 | 9.6272 | 9.0924 | 8.6292 | 8.1797 | 8.0734 | 7.8655 | 7.5763 | 7.3078 | 6.6214 | 6.063 | 5.7281 | 5.6691 | 6.0378 | 384109 | 397722 | BLOOM ST | SOUTH MANCHESTER
| Dickinson St T13 | 10.3474 | 10.2919 | 10.2296 | 10.1719 | 10.1174 | 10.0552 | 9.9941 | 9.9244 | 9.8542 | 9.7855 | 9.5375 | 9.2181 | 8.9569 | 8.6553 | 8.3347 | 13.8474 | 13.7919 | 13.7296 | 13.6719 | 13.6174 | 13.5552 | 13.4941 | 13.4244 | 13.3542 | 13.2855 | 13.0375 | 12.7181 | 12.4569 | 12.1553 | 11.861 | 10.3474 | 10.2753 | 10.1904 | 10.1045 | 10.0169 | 9.9068 | 9.786 | 9.6459 | 9.5674 | 9.4866 | 9.2629 | 9.0428 | 8.8651 | 8.6615 | 8.4292 | 13.8474 | 13.7753 | 13.6904 | 13.6045 | 13.5169 | 13.4068 | 13.286 | 13.1459 | 13.0674 | 12.9866 | 12.7629 | 12.5428 | 12.3651 | 12.1615 | 11.9708 | 10.3474 | 10.2908 | 10.2282 | 10.1709 | 10.1169 | 10.0584 | 10.0025 | 9.9362 | 9.8762 | 9.8141 | 9.5904 | 9.2903 | 9.0506 | 8.7802 | 8.5015 | 13.8474 | 13.7908 | 13.7282 | 13.6709 | 13.6169 | 13.5584 | 13.5025 | 13.4362 | 13.3762 | 13.3141 | 13.0904 | 12.7903 | 12.5506 | 12.2802 | 12.0208 | 10.3474 | 10.3097 | 10.256 | 10.2053 | 10.1585 | 10.1116 | 10.0586 | 9.9685 | 9.8684 | 9.7636 | 9.4688 | 9.1778 | 8.9494 | 8.7479 | 8.6351 | 13.8474 | 13.8097 | 13.756 | 13.7053 | 13.6585 | 13.6116 | 13.5586 | 13.4685 | 13.3684 | 13.2636 | 12.9688 | 12.6778 | 12.4494 | 12.2479 | 12.1527 | 10.3474 | 10.2926 | 10.2303 | 10.1731 | 10.1223 | 10.068 | 10.0096 | 9.9387 | 9.8653 | 9.7926 | 9.5829 | 9.3741 | 9.2193 | 9.0409 | 8.8687 | 13.8474 | 13.7926 | 13.7303 | 13.6731 | 13.6223 | 13.568 | 13.5096 | 13.4387 | 13.3653 | 13.2926 | 13.0829 | 12.8741 | 12.7193 | 12.5409 | 12.3967 | 10.3474 | 10.3033 | 10.2424 | 10.1841 | 10.1291 | 10.0705 | 10.0013 | 9.8893 | 9.7838 | 9.6744 | 9.3679 | 9.073 | 8.8407 | 8.6322 | 8.5072 | 13.8474 | 13.8033 | 13.7424 | 13.6841 | 13.6291 | 13.5705 | 13.5013 | 13.3893 | 13.2838 | 13.1744 | 12.8679 | 12.573 | 12.3407 | 12.1322 | 12.0276 | 384109 | 397722 | STUART ST | STALYBRIDGE
| Didsbury | 8.0509 | 7.7602 | 7.6089 | 7.4698 | 7.2281 | 6.9745 | 6.7442 | 6.543 | 6.3124 | 6.1267 | 4.543 | 1.5833 | -0.81373 | -3.3541 | -5.6566 | 12.6879 | 12.3972 | 12.2459 | 12.1068 | 11.8651 | 11.6115 | 11.3812 | 11.18 | 10.9494 | 10.7637 | 9.18 | 6.2203 | 3.8233 | 1.2829 | -1.255 | 8.0509 | 7.8603 | 7.7082 | 7.546 | 7.3188 | 7.0644 | 6.7377 | 6.353 | 6.0572 | 5.7604 | 4.9027 | 4.125 | 3.4597 | 2.8197 | 2.4413 | 12.6879 | 12.4973 | 12.3452 | 12.183 | 11.9558 | 11.7014 | 11.3747 | 10.99 | 10.6942 | 10.3974 | 9.5397 | 8.762 | 8.0967 | 7.4567 | 7.1278 | 8.0509 | 7.7565 | 7.6301 | 7.5312 | 7.3366 | 7.1366 | 6.9838 | 6.8627 | 6.7274 | 6.6195 | 5.2808 | 2.534 | 0.3263 | -1.9098 | -3.8831 | 12.6879 | 12.3935 | 12.2671 | 12.1682 | 11.9736 | 11.7736 | 11.6208 | 11.4997 | 11.3644 | 11.2565 | 9.9178 | 7.171 | 4.9633 | 2.7272 | 0.46796 | 8.0509 | 8.1572 | 8.1518 | 8.1352 | 7.9913 | 7.7751 | 7.4209 | 6.5282 | 5.5835 | 4.6143 | 1.8285 | -0.85027 | -2.9461 | -4.1286 | -2.828 | 12.6879 | 12.7942 | 12.7888 | 12.7722 | 12.6283 | 12.4121 | 12.0579 | 11.1652 | 10.2205 | 9.2513 | 6.4655 | 3.7867 | 1.6909 | 0.5084 | 1.5203 | 8.0509 | 7.8599 | 7.7797 | 7.7569 | 7.6871 | 7.5744 | 7.4468 | 7.3173 | 7.1144 | 6.9234 | 6.243 | 5.4487 | 4.9322 | 4.473 | 4.3593 | 12.6879 | 12.4969 | 12.4167 | 12.3939 | 12.3241 | 12.2114 | 12.0838 | 11.9543 | 11.7514 | 11.5604 | 10.88 | 10.0857 | 9.5692 | 9.11 | 8.9623 | 8.0509 | 7.9906 | 7.8583 | 7.6876 | 7.4071 | 7.1233 | 6.6885 | 5.6696 | 4.6297 | 3.6027 | 0.58954 | -2.2924 | -4.5893 | -6.0282 | -5.032 | 12.6879 | 12.6276 | 12.4953 | 12.3246 | 12.0441 | 11.7603 | 11.3255 | 10.3066 | 9.2667 | 8.2397 | 5.2265 | 2.3446 | 0.047722 | -1.3912 | -0.61631 | 384792 | 391153 | WEST DIDSBURY | SOUTH MANCHESTER
| Dodgson Rd | 15.7753 | 15.6108 | 15.6267 | 15.5649 | 15.4122 | 15.2323 | 15.0501 | 14.8785 | 14.6732 | 14.2368 | 11.78 | 8.9747 | 6.8561 | 5.0166 | 3.7772 | 19.9123 | 19.7478 | 19.7637 | 19.7019 | 19.5492 | 19.3693 | 19.1871 | 19.0155 | 18.8102 | 18.3738 | 15.917 | 13.1117 | 10.9931 | 9.1536 | 7.8243 | 15.7753 | 15.607 | 15.5962 | 15.5111 | 15.3933 | 15.2597 | 15.0756 | 14.8364 | 14.6726 | 14.5016 | 13.8908 | 12.3162 | 10.6629 | 9.1016 | 8.1853 | 19.9123 | 19.744 | 19.7332 | 19.6481 | 19.5303 | 19.3967 | 19.2126 | 18.9734 | 18.8096 | 18.6386 | 18.0278 | 16.4532 | 14.7999 | 13.2386 | 12.4347 | 15.7753 | 15.6289 | 15.6616 | 15.6249 | 15.4995 | 15.3527 | 15.2204 | 15.0994 | 14.9775 | 14.8531 | 12.6335 | 9.5836 | 7.0927 | 4.9267 | 3.5371 | 19.9123 | 19.7659 | 19.7986 | 19.7619 | 19.6365 | 19.4897 | 19.3574 | 19.2364 | 19.1145 | 18.9901 | 16.7705 | 13.7206 | 11.2297 | 9.0637 | 7.6362 | 15.7753 | 15.8255 | 15.9039 | 15.8766 | 15.7435 | 15.5783 | 15.2795 | 14.5268 | 13.7349 | 12.9238 | 10.1102 | 7.4946 | 5.5328 | 4.3353 | 4.5629 | 19.9123 | 19.9625 | 20.0409 | 20.0136 | 19.8805 | 19.7153 | 19.4165 | 18.6638 | 17.8719 | 17.0608 | 14.2472 | 11.6316 | 9.6698 | 8.4723 | 8.6305 | 15.7753 | 15.6347 | 15.6754 | 15.6663 | 15.6322 | 15.5794 | 15.4929 | 15.3703 | 15.1985 | 15.0153 | 13.5708 | 11.6698 | 10.2168 | 8.999 | 8.493 | 19.9123 | 19.7717 | 19.8124 | 19.8033 | 19.7692 | 19.7164 | 19.6299 | 19.5073 | 19.3355 | 19.1523 | 17.7078 | 15.8068 | 14.3538 | 13.136 | 12.6617 | 15.7753 | 15.8033 | 15.8465 | 15.7809 | 15.6149 | 15.432 | 15.111 | 14.33 | 13.5462 | 12.7577 | 10.2185 | 7.3274 | 5.0262 | 3.4433 | 3.5647 | 19.9123 | 19.9403 | 19.9835 | 19.9179 | 19.7519 | 19.569 | 19.248 | 18.467 | 17.6832 | 16.8947 | 14.3555 | 11.4644 | 9.1632 | 7.5803 | 7.6488 | 355190 | 430397 | PRESTON EAST | PENWORTHAM
| Douglas St | 8.8796 | 8.1428 | 7.9104 | 7.7968 | 7.6876 | 7.5695 | 7.4443 | 7.2994 | 7.0961 | 6.9003 | 6.0445 | 4.8445 | 3.6984 | 2.5036 | 1.5802 | 15.5396 | 14.8028 | 14.5704 | 14.4568 | 14.3476 | 14.2295 | 14.1043 | 13.9594 | 13.7561 | 13.5603 | 12.7045 | 11.5045 | 10.3584 | 9.1636 | 8.1464 | 8.8796 | 8.5923 | 8.4134 | 8.2599 | 8.1073 | 7.9272 | 7.7074 | 7.4486 | 7.2572 | 7.0653 | 6.4922 | 5.9334 | 5.4458 | 4.9634 | 4.6632 | 15.5396 | 15.2523 | 15.0734 | 14.9199 | 14.7673 | 14.5872 | 14.3674 | 14.1086 | 13.9172 | 13.7253 | 13.1522 | 12.5934 | 12.1058 | 11.6234 | 11.3566 | 8.8796 | 8.0349 | 7.7843 | 7.6704 | 7.5634 | 7.4499 | 7.3304 | 7.1956 | 7.0417 | 6.899 | 6.1842 | 5.1071 | 4.0691 | 3.0719 | 2.4271 | 15.5396 | 14.6949 | 14.4443 | 14.3304 | 14.2234 | 14.1099 | 13.9904 | 13.8556 | 13.7017 | 13.559 | 12.8442 | 11.7671 | 10.7291 | 9.7319 | 8.9416 | 8.8796 | 8.3739 | 8.2253 | 8.1665 | 8.1046 | 8.0122 | 7.845 | 7.4985 | 7.0959 | 6.702 | 5.3543 | 4.0189 | 3.0402 | 2.5253 | 3.161 | 15.5396 | 15.0339 | 14.8853 | 14.8265 | 14.7646 | 14.6722 | 14.505 | 14.1585 | 13.7559 | 13.362 | 12.0143 | 10.6789 | 9.7002 | 9.1853 | 9.6694 | 8.8796 | 8.4773 | 8.327 | 8.2552 | 8.2041 | 8.1263 | 8.0182 | 7.8922 | 7.7045 | 7.5152 | 6.9099 | 6.3131 | 5.925 | 5.66 | 5.7296 | 15.5396 | 15.1373 | 14.987 | 14.9152 | 14.8641 | 14.7863 | 14.6782 | 14.5522 | 14.3645 | 14.1752 | 13.5699 | 12.9731 | 12.585 | 12.32 | 12.3438 | 8.8796 | 8.014 | 7.7539 | 7.6319 | 7.5136 | 7.3924 | 7.2106 | 6.8334 | 6.435 | 6.0373 | 4.7162 | 3.328 | 2.287 | 1.7111 | 2.2688 | 15.5396 | 14.674 | 14.4139 | 14.2919 | 14.1736 | 14.0524 | 13.8706 | 13.4934 | 13.095 | 12.6973 | 11.3762 | 9.988 | 8.947 | 8.3711 | 8.7973 | 352220 | 429932 | RIBBLE | PENWORTHAM
| Droylsden East | 8.3949 | 8.0419 | 7.83 | 7.6349 | 7.3226 | 6.9887 | 6.6591 | 6.3478 | 5.9424 | 5.5202 | 3.1978 | -0.33445 | -3.0387 | -5.6432 | -7.5748 | 13.0349 | 12.6819 | 12.47 | 12.2749 | 11.9626 | 11.6287 | 11.2991 | 10.9878 | 10.5824 | 10.1602 | 7.8378 | 4.3055 | 1.6013 | -1.0032 | -3.0854 | 8.3949 | 8.1915 | 8.0617 | 7.9277 | 7.729 | 7.51 | 7.2067 | 6.8025 | 6.4892 | 6.166 | 5.1032 | 3.8773 | 2.6657 | 1.3322 | 0.34743 | 13.0349 | 12.8315 | 12.7017 | 12.5677 | 12.369 | 12.15 | 11.8467 | 11.4425 | 11.1292 | 10.806 | 9.7432 | 8.5173 | 7.3057 | 5.9722 | 5.156 | 8.3949 | 7.9399 | 7.6366 | 7.3572 | 6.9562 | 6.5308 | 6.1231 | 5.6576 | 5.1048 | 4.5476 | 1.8694 | -1.62 | -4.0076 | -5.984 | -6.956 | 13.0349 | 12.5799 | 12.2766 | 11.9972 | 11.5962 | 11.1708 | 10.7631 | 10.2976 | 9.7448 | 9.1876 | 6.5094 | 3.02 | 0.63236 | -1.344 | -2.4252 | 8.3949 | 8.3677 | 8.1683 | 7.9013 | 7.4831 | 7.0213 | 6.3827 | 5.158 | 3.9419 | 2.7563 | -0.69078 | -3.6424 | -5.4695 | -6.3103 | -5.6228 | 13.0349 | 13.0077 | 12.8083 | 12.5413 | 12.1231 | 11.6613 | 11.0227 | 9.798 | 8.5819 | 7.3963 | 3.9492 | 0.99757 | -0.8295 | -1.6703 | -1.1373 | 8.3949 | 8.1239 | 7.9669 | 7.8528 | 7.6912 | 7.4887 | 7.2475 | 6.985 | 6.6464 | 6.2239 | 4.7523 | 3.1407 | 1.9906 | 0.8383 | -0.027142 | 13.0349 | 12.7639 | 12.6069 | 12.4928 | 12.3312 | 12.1287 | 11.8875 | 11.625 | 11.2864 | 10.8639 | 9.3923 | 7.7807 | 6.6306 | 5.4783 | 4.7172 | 8.3949 | 8.2364 | 7.9325 | 7.5626 | 7.0495 | 6.5206 | 5.796 | 4.4363 | 3.0866 | 1.7754 | -1.94 | -5.0886 | -7.097 | -8.1372 | -7.6986 | 13.0349 | 12.8764 | 12.5725 | 12.2026 | 11.6895 | 11.1606 | 10.436 | 9.0763 | 7.7266 | 6.4154 | 2.7 | -0.44857 | -2.457 | -3.4972 | -3.1562 | 390532 | 398053 | DROYLSDEN | STALYBRIDGE
| Dukinfield | 12.3114 | 11.7308 | 11.4694 | 11.3577 | 11.1644 | 10.9733 | 10.8032 | 10.6428 | 10.389 | 10.1421 | 8.9361 | 7.0931 | 5.5779 | 4.2008 | 3.0416 | 16.9484 | 16.3678 | 16.1064 | 15.9947 | 15.8014 | 15.6103 | 15.4402 | 15.2798 | 15.026 | 14.7791 | 13.5731 | 11.7301 | 10.2149 | 8.8378 | 7.6002 | 12.3114 | 12.1435 | 12.016 | 11.9743 | 11.8907 | 11.8196 | 11.7318 | 11.5954 | 11.3288 | 11.0608 | 10.25 | 9.3417 | 8.4328 | 7.5875 | 7.077 | 16.9484 | 16.7805 | 16.653 | 16.6113 | 16.5277 | 16.4566 | 16.3688 | 16.2324 | 15.9658 | 15.6978 | 14.887 | 13.9787 | 13.0698 | 12.2245 | 11.7953 | 12.3114 | 11.6371 | 11.3567 | 11.2429 | 11.0497 | 10.8598 | 10.6914 | 10.5344 | 10.3259 | 10.1298 | 9.0703 | 7.3712 | 6.0083 | 4.8571 | 4.0416 | 16.9484 | 16.2741 | 15.9937 | 15.8799 | 15.6867 | 15.4968 | 15.3284 | 15.1714 | 14.9629 | 14.7668 | 13.7073 | 12.0082 | 10.6453 | 9.4941 | 8.5477 | 12.3114 | 11.8462 | 11.6195 | 11.5107 | 11.3194 | 11.1193 | 10.8443 | 10.2982 | 9.6926 | 9.1026 | 7.4028 | 5.7697 | 4.4921 | 3.831 | 4.4135 | 16.9484 | 16.4832 | 16.2565 | 16.1477 | 15.9564 | 15.7563 | 15.4813 | 14.9352 | 14.3296 | 13.7396 | 12.0398 | 10.4067 | 9.1291 | 8.468 | 8.9159 | 12.3114 | 11.97 | 11.7674 | 11.6842 | 11.5581 | 11.4316 | 11.3065 | 11.17 | 10.9137 | 10.6535 | 9.8321 | 8.9612 | 8.3278 | 7.9358 | 7.8755 | 16.9484 | 16.607 | 16.4044 | 16.3212 | 16.1951 | 16.0686 | 15.9435 | 15.807 | 15.5507 | 15.2905 | 14.4691 | 13.5982 | 12.9648 | 12.5728 | 12.4938 | 12.3114 | 11.5607 | 11.2597 | 11.1292 | 10.92 | 10.7155 | 10.4395 | 9.8824 | 9.2688 | 8.6713 | 6.9425 | 5.2721 | 3.9443 | 3.1716 | 3.6522 | 16.9484 | 16.1977 | 15.8967 | 15.7662 | 15.557 | 15.3525 | 15.0765 | 14.5194 | 13.9058 | 13.3083 | 11.5795 | 9.9091 | 8.5813 | 7.8086 | 8.1787 | 394372 | 396438 | HYDE | STALYBRIDGE
| Dumers Lane | 10.1562 | 8.4838 | 7.7375 | 7.3718 | 6.7389 | 6.0871 | 5.5798 | 5.0499 | 4.4956 | 3.936 | 1.7051 | -1.1419 | -2.8142 | -4.5077 | -5.9358 | 16.6562 | 14.9838 | 14.2375 | 13.8718 | 13.2389 | 12.5871 | 12.0798 | 11.5499 | 10.9956 | 10.436 | 8.2051 | 5.3581 | 3.6858 | 1.9923 | 0.51686 | 10.1562 | 9.7185 | 9.5101 | 9.3938 | 9.2708 | 9.1315 | 8.9517 | 8.7212 | 8.4386 | 8.143 | 7.1761 | 6.1093 | 5.0655 | 3.9455 | 3.1844 | 16.6562 | 16.2185 | 16.0101 | 15.8938 | 15.7708 | 15.6315 | 15.4517 | 15.2212 | 14.9386 | 14.643 | 13.6761 | 12.6093 | 11.5655 | 10.4455 | 9.7965 | 10.1562 | 8.2704 | 7.4959 | 7.1671 | 6.5707 | 5.9631 | 5.5195 | 5.0634 | 4.6221 | 4.1507 | 2.125 | -0.60956 | -2.1845 | -3.7046 | -4.8727 | 16.6562 | 14.7704 | 13.9959 | 13.6671 | 13.0707 | 12.4631 | 12.0195 | 11.5634 | 11.1221 | 10.6507 | 8.625 | 5.8904 | 4.3155 | 2.7954 | 1.5306 | 10.1562 | 8.8806 | 8.2501 | 7.9436 | 7.3502 | 6.7217 | 6.1477 | 5.2536 | 4.3688 | 3.4539 | 0.7361 | -1.8602 | -3.2672 | -4.1735 | -3.7813 | 16.6562 | 15.3806 | 14.7501 | 14.4436 | 13.8502 | 13.2217 | 12.6477 | 11.7536 | 10.8688 | 9.9539 | 7.2361 | 4.6398 | 3.2328 | 2.3265 | 2.6165 | 10.1562 | 9.2487 | 8.6854 | 8.37 | 7.8175 | 7.2312 | 6.7668 | 6.2773 | 5.7546 | 5.2155 | 3.4566 | 1.644 | 0.90016 | 0.28779 | 0.015563 | 16.6562 | 15.7487 | 15.1854 | 14.87 | 14.3175 | 13.7312 | 13.2668 | 12.7773 | 12.2546 | 11.7155 | 9.9566 | 8.144 | 7.4002 | 6.7878 | 6.5287 | 10.1562 | 8.1403 | 7.3167 | 6.956 | 6.318 | 5.6695 | 5.0754 | 4.1491 | 3.2489 | 2.3167 | -0.51491 | -3.2825 | -4.862 | -5.9328 | -5.6851 | 16.6562 | 14.6403 | 13.8167 | 13.456 | 12.818 | 12.1695 | 11.5754 | 10.6491 | 9.7489 | 8.8167 | 5.9851 | 3.2175 | 1.638 | 0.56724 | 0.74313 | 380057 | 408141 | BURY | KEARSLEY
| Dumplington | 17.1342 | 9.146 | 6.0166 | 4.1981 | 1.8571 | 1.3299 | 0.8171 | 0.30451 | -0.36221 | -1.0258 | -3.1381 | -5.3946 | -7.4502 | -9.9172 | -12.6405 | 18.5342 | 10.546 | 7.4166 | 5.5981 | 3.2571 | 2.7299 | 2.2171 | 1.7045 | 1.0378 | 0.37424 | -1.7381 | -3.9946 | -6.0502 | -8.5172 | -10.825 | 17.1342 | 15.0007 | 13.9683 | 13.4222 | 12.7515 | 12.637 | 12.4915 | 12.3291 | 12.1123 | 11.8943 | 11.2641 | 10.6652 | 10.1392 | 9.5996 | 9.1952 | 18.5342 | 16.4007 | 15.3683 | 14.8222 | 14.1515 | 14.037 | 13.8915 | 13.7291 | 13.5123 | 13.2943 | 12.6641 | 12.0652 | 11.5392 | 10.9996 | 10.6493 | 17.1342 | 7.9614 | 4.5913 | 2.7686 | 0.4282 | -0.096287 | -0.60543 | -1.1116 | -1.7027 | -2.2788 | -4.1339 | -6.1337 | -7.9168 | -9.9821 | -12.1649 | 18.5342 | 9.3614 | 5.9913 | 4.1686 | 1.8282 | 1.3037 | 0.79457 | 0.28836 | -0.30273 | -0.87882 | -2.7339 | -4.7337 | -6.5168 | -8.5821 | -10.454 | 17.1342 | 10.3469 | 7.4863 | 5.6904 | 3.3747 | 2.8614 | 2.3233 | 1.6934 | 0.95762 | 0.23575 | -1.852 | -3.8286 | -5.5826 | -7.466 | -9.152 | 18.5342 | 11.7469 | 8.8863 | 7.0904 | 4.7747 | 4.2614 | 3.7233 | 3.0934 | 2.3576 | 1.6357 | -0.45201 | -2.4286 | -4.1826 | -6.066 | -7.4435 | 17.1342 | 12.5174 | 10.0868 | 8.2928 | 5.9873 | 5.4831 | 4.9758 | 4.4693 | 3.8098 | 3.1485 | 1.1746 | -0.75539 | -2.5024 | -4.6016 | -6.8333 | 18.5342 | 13.9174 | 11.4868 | 9.6928 | 7.3873 | 6.8831 | 6.3758 | 5.8693 | 5.2098 | 4.5485 | 2.5746 | 0.64461 | -1.1024 | -3.2016 | -5.0186 | 17.1342 | 6.7806 | 3.1678 | 1.3358 | -1.0121 | -1.543 | -2.0956 | -2.7511 | -3.493 | -4.2199 | -6.3289 | -8.3297 | -10.1071 | -11.9985 | -13.6901 | 18.5342 | 8.1806 | 4.5678 | 2.7358 | 0.38787 | -0.14296 | -0.69558 | -1.3511 | -2.093 | -2.8199 | -4.9289 | -6.9297 | -8.7071 | -10.5985 | -11.9791 | 376770 | 397157 | BARTON | CARRINGTON
| Eastlands | 11.2436 | 7.0651 | 5.4847 | 4.4946 | 3.5142 | 21.6616 | 20.6807 | 19.6944 | 18.6387 | 17.5875 | 14.3107 | 10.8751 | 7.735 | 3.7864 | 1.8138 | 15.8806 | 11.7021 | 10.1217 | 9.1316 | 8.1512 | 34.6616 | 33.6807 | 32.6944 | 31.6387 | 30.5875 | 27.3107 | 23.8751 | 20.735 | 16.7864 | 14.8844 | 11.2436 | 9.1206 | 7.9807 | 7.0128 | 6.0631 | 24.2435 | 23.2685 | 22.2484 | 21.1786 | 20.0997 | 16.9217 | 13.7731 | 10.7561 | 6.9018 | 4.9689 | 15.8806 | 13.7576 | 12.6177 | 11.6498 | 10.7001 | 37.2435 | 36.2685 | 35.2484 | 34.1786 | 33.0997 | 29.9217 | 26.7731 | 23.7561 | 19.9018 | 18.133 | 11.2436 | 6.5794 | 4.2745 | 2.6589 | 1.0425 | 18.5494 | 16.937 | 15.3064 | 13.6429 | 11.9596 | 6.7744 | 1.4636 | -2.8681 | -6.717 | -8.4967 | 15.8806 | 11.2164 | 8.9115 | 7.2959 | 5.6795 | 31.5494 | 29.937 | 28.3064 | 26.6429 | 24.9596 | 19.7744 | 14.4636 | 10.1319 | 6.283 | 4.583 | 11.2436 | 7.6151 | 5.5334 | 3.9416 | 2.3402 | 19.855 | 18.221 | 16.4797 | 14.707 | 12.9192 | 7.6292 | 2.4323 | -1.784 | -5.4129 | -6.8927 | 15.8806 | 12.2521 | 10.1704 | 8.5786 | 6.9772 | 32.855 | 31.221 | 29.4797 | 27.707 | 25.9192 | 20.6292 | 15.4323 | 11.216 | 7.5871 | 6.1801 | 11.2436 | 8.3658 | 7.06 | 6.0915 | 5.1485 | 23.3297 | 22.3733 | 21.3996 | 20.3411 | 19.2804 | 16.1183 | 12.9805 | 10.0981 | 6.4264 | 4.7382 | 15.8806 | 13.0028 | 11.697 | 10.7285 | 9.7855 | 36.3297 | 35.3733 | 34.3996 | 33.3411 | 32.2804 | 29.1183 | 25.9805 | 23.0981 | 19.4264 | 17.8518 | 11.2436 | 6.2117 | 3.8212 | 2.1986 | 0.56899 | 18.0655 | 16.4032 | 14.631 | 12.837 | 11.0258 | 5.6549 | 0.41126 | -3.8509 | -7.5386 | -9.1074 | 15.8806 | 10.8487 | 8.4582 | 6.8356 | 5.206 | 31.0655 | 29.4032 | 27.631 | 25.837 | 24.0258 | 18.6549 | 13.4113 | 9.1491 | 5.4614 | 3.9862 | 386458 | 398693 | STUART ST | STALYBRIDGE
| Easton | 0.11896 | 0.038279 | 0.0068038 | -0.011485 | -0.044186 | -0.080608 | -0.113 | -0.13996 | -0.16501 | -0.18351 | -0.30348 | -0.51409 | -0.6806 | -0.80375 | -0.94072 | 0.41896 | 0.33828 | 0.3068 | 0.28851 | 0.25581 | 0.21939 | 0.187 | 0.16004 | 0.13499 | 0.11649 | -0.0034793 | -0.21409 | -0.3806 | -0.50375 | -0.65812 | 0.11896 | 0.066055 | 0.025625 | -0.013841 | -0.059258 | -0.099515 | -0.14808 | -0.20481 | -0.23573 | -0.26682 | -0.35534 | -0.43175 | -0.51749 | -0.64803 | -0.78283 | 0.41896 | 0.36605 | 0.32562 | 0.28616 | 0.24074 | 0.20048 | 0.15192 | 0.09519 | 0.06427 | 0.033184 | -0.055338 | -0.13175 | -0.21749 | -0.34803 | -0.45911 | 0.11896 | 0.030204 | -0.00028838 | -0.0132 | -0.040346 | -0.070092 | -0.093109 | -0.10955 | -0.12075 | -0.12811 | -0.21324 | -0.39158 | -0.53021 | -0.62217 | -0.72533 | 0.41896 | 0.3302 | 0.29971 | 0.2868 | 0.25965 | 0.22991 | 0.20689 | 0.19045 | 0.17925 | 0.17189 | 0.086756 | -0.091582 | -0.23021 | -0.32217 | -0.44888 | 0.11896 | 0.075459 | 0.054097 | 0.02739 | -0.0016566 | -0.032769 | -0.067485 | -0.12441 | -0.18806 | -0.25246 | -0.43462 | -0.6056 | -0.71162 | -0.72117 | -0.61385 | 0.41896 | 0.37546 | 0.3541 | 0.32739 | 0.29834 | 0.26723 | 0.23251 | 0.17559 | 0.11194 | 0.047542 | -0.13462 | -0.3056 | -0.41162 | -0.42117 | -0.33752 | 0.11896 | 0.050786 | 0.02086 | 0.0016695 | -0.020108 | -0.035722 | -0.049092 | -0.062257 | -0.081717 | -0.10022 | -0.19056 | -0.32592 | -0.41146 | -0.50349 | -0.56577 | 0.41896 | 0.35079 | 0.32086 | 0.30167 | 0.27989 | 0.26428 | 0.25091 | 0.23774 | 0.21828 | 0.19978 | 0.10944 | -0.025923 | -0.11146 | -0.20349 | -0.27725 | 0.11896 | 0.033941 | -0.0048557 | -0.045362 | -0.088078 | -0.13047 | -0.17836 | -0.25225 | -0.32588 | -0.40009 | -0.61033 | -0.80252 | -0.92542 | -0.95137 | -0.86127 | 0.41896 | 0.33394 | 0.29514 | 0.25464 | 0.21192 | 0.16953 | 0.12164 | 0.047755 | -0.025882 | -0.10009 | -0.31033 | -0.50252 | -0.62542 | -0.65137 | -0.58113 | 343201 | 571738 | - | HARKER | Firm Capacity marginally exceeded in FY27. HV transfers from Easton are available.
| Egremont | 3.6454 | 2.9222 | 2.5815 | 2.3563 | 2.0179 | 1.6808 | 1.4228 | 1.2459 | 1.0152 | 0.82026 | -0.86553 | -4.0004 | -6.5939 | -9.1261 | -11.1332 | 6.1454 | 5.4222 | 5.0815 | 4.8563 | 4.5179 | 4.1808 | 3.9228 | 3.7459 | 3.5152 | 3.3203 | 1.6345 | -1.5004 | -4.0939 | -6.6261 | -8.9103 | 3.6454 | 3.4579 | 3.2776 | 3.0998 | 2.8811 | 2.6552 | 2.3647 | 1.9984 | 1.7157 | 1.4336 | 0.59805 | -0.1996 | -1.0419 | -1.875 | -2.352 | 6.1454 | 5.9579 | 5.7776 | 5.5998 | 5.3811 | 5.1552 | 4.8647 | 4.4984 | 4.2157 | 3.9336 | 3.098 | 2.3004 | 1.4581 | 0.62502 | 0.20861 | 3.6454 | 2.8517 | 2.5266 | 2.353 | 2.0693 | 1.7965 | 1.624 | 1.5436 | 1.4286 | 1.325 | -0.10728 | -3.1288 | -5.9348 | -8.4421 | -10.202 | 6.1454 | 5.3517 | 5.0266 | 4.853 | 4.5693 | 4.2965 | 4.124 | 4.0436 | 3.9286 | 3.825 | 2.3927 | -0.62877 | -3.4348 | -5.9421 | -7.7717 | 3.6454 | 3.2547 | 3.0353 | 2.8664 | 2.6014 | 2.3198 | 1.898 | 0.88335 | -0.17034 | -1.2036 | -4.1225 | -6.8515 | -8.9788 | -10.1012 | -8.56 | 6.1454 | 5.7547 | 5.5353 | 5.3664 | 5.1014 | 4.8198 | 4.398 | 3.3834 | 2.3297 | 1.2964 | -1.6225 | -4.3515 | -6.4788 | -7.6012 | -6.3963 | 3.6454 | 3.4532 | 3.2405 | 3.0837 | 2.9199 | 2.7521 | 2.56 | 2.3533 | 2.0438 | 1.7322 | 0.64807 | -0.68622 | -1.7969 | -3.21 | -3.8305 | 6.1454 | 5.9532 | 5.7405 | 5.5837 | 5.4199 | 5.2521 | 5.06 | 4.8533 | 4.5438 | 4.2322 | 3.1481 | 1.8138 | 0.70308 | -0.71004 | -1.2973 | 3.6454 | 2.8922 | 2.5256 | 2.2482 | 1.8853 | 1.541 | 1.0487 | -0.073289 | -1.2018 | -2.3117 | -5.4773 | -8.4402 | -10.8041 | -12.2271 | -11.0134 | 6.1454 | 5.3922 | 5.0256 | 4.7482 | 4.3853 | 4.041 | 3.5487 | 2.4267 | 1.2982 | 0.1883 | -2.9773 | -5.9402 | -8.3041 | -9.7271 | -8.7795 | 301070 | 513074 | EGREMONT | HARKER
| Embleton | 5.1373 | 4.3205 | 4.0406 | 3.8938 | 3.6936 | 3.4781 | 3.2759 | 3.0618 | 2.8233 | 2.607 | 1.5509 | -0.18625 | -1.7905 | -3.3304 | -4.7095 | 16.1373 | 15.3205 | 15.0406 | 14.8938 | 14.6936 | 14.4781 | 14.2759 | 14.0618 | 13.8233 | 13.607 | 12.5509 | 10.8138 | 9.2095 | 7.6696 | 6.1769 | 5.1373 | 4.6701 | 4.4022 | 4.1637 | 3.8684 | 3.5274 | 3.1088 | 2.597 | 2.3333 | 2.0706 | 1.2669 | 0.48593 | -0.20316 | -0.91141 | -1.3501 | 16.1373 | 15.6701 | 15.4022 | 15.1637 | 14.8684 | 14.5274 | 14.1088 | 13.597 | 13.3333 | 13.0706 | 12.2669 | 11.4859 | 10.7968 | 10.0886 | 9.7109 | 5.1373 | 4.2234 | 3.9408 | 3.8285 | 3.6636 | 3.4901 | 3.349 | 3.2024 | 3.0551 | 2.9119 | 2.0562 | 0.48925 | -0.97528 | -2.3333 | -3.4901 | 16.1373 | 15.2234 | 14.9408 | 14.8285 | 14.6636 | 14.4901 | 14.349 | 14.2024 | 14.0551 | 13.9119 | 13.0562 | 11.4892 | 10.0247 | 8.6667 | 7.3565 | 5.1373 | 4.6768 | 4.5345 | 4.4846 | 4.3817 | 4.2446 | 4.0593 | 3.5474 | 2.9157 | 2.2881 | 0.46407 | -1.2839 | -2.5657 | -3.2315 | -2.5172 | 16.1373 | 15.6768 | 15.5345 | 15.4846 | 15.3817 | 15.2446 | 15.0593 | 14.5474 | 13.9157 | 13.2881 | 11.4641 | 9.7161 | 8.4343 | 7.7685 | 8.3224 | 5.1373 | 4.4661 | 4.2426 | 4.1466 | 4.0353 | 3.892 | 3.7185 | 3.5052 | 3.2472 | 2.992 | 2.0999 | 1.1267 | 0.47883 | -0.047517 | -0.13019 | 16.1373 | 15.4661 | 15.2426 | 15.1466 | 15.0353 | 14.892 | 14.7185 | 14.5052 | 14.2472 | 13.992 | 13.0999 | 12.1267 | 11.4788 | 10.9525 | 10.833 | 5.1373 | 4.2614 | 3.9513 | 3.7874 | 3.5779 | 3.3651 | 3.0965 | 2.5793 | 1.9809 | 1.3064 | -0.6775 | -2.5791 | -4.0081 | -4.8359 | -4.2904 | 16.1373 | 15.2614 | 14.9513 | 14.7874 | 14.5779 | 14.3651 | 14.0965 | 13.5793 | 12.9809 | 12.3064 | 10.3225 | 8.4209 | 6.9919 | 6.1641 | 6.5861 | 315767 | 529389 | STAINBURN & SIDDICK | HARKER
| Exchange St | 7.924 | 5.4864 | 5.0273 | 4.7951 | 4.4633 | 4.0935 | 3.7075 | 3.2874 | 2.5836 | 1.8044 | -1.3468 | -4.6723 | -7.1357 | -9.3658 | -10.9921 | 11.424 | 8.9864 | 8.5273 | 8.2951 | 7.9633 | 7.5935 | 7.2075 | 6.7874 | 6.0836 | 5.3044 | 2.1532 | -1.1723 | -3.6357 | -5.8658 | -7.612 | 7.924 | 7.0591 | 6.9725 | 6.8568 | 6.6925 | 6.5015 | 6.2419 | 5.9018 | 5.6606 | 5.3974 | 4.4607 | 2.902 | 1.2962 | -0.4351 | -1.5434 | 11.424 | 10.5591 | 10.4725 | 10.3568 | 10.1925 | 10.0015 | 9.7419 | 9.4018 | 9.1606 | 8.8974 | 7.9607 | 6.402 | 4.7962 | 3.0649 | 2.097 | 7.924 | 5.1267 | 4.5706 | 4.3148 | 3.9646 | 3.5875 | 3.2192 | 2.7819 | 2.1245 | 1.4047 | -1.7561 | -5.3167 | -7.9481 | -10.2081 | -11.6974 | 11.424 | 8.6267 | 8.0706 | 7.8148 | 7.4646 | 7.0875 | 6.7192 | 6.2819 | 5.6245 | 4.9047 | 1.7439 | -1.8167 | -4.4481 | -6.7081 | -8.3443 | 7.924 | 6.0519 | 5.6853 | 5.4608 | 5.1193 | 4.7295 | 4.148 | 2.9485 | 1.6777 | 0.29761 | -3.8293 | -7.0402 | -9.2719 | -10.6103 | -9.9918 | 11.424 | 9.5519 | 9.1853 | 8.9608 | 8.6193 | 8.2295 | 7.648 | 6.4485 | 5.1777 | 3.7976 | -0.3293 | -3.5402 | -5.7719 | -7.1103 | -6.648 | 7.924 | 6.3357 | 6.0502 | 5.8736 | 5.6593 | 5.405 | 5.0974 | 4.7335 | 4.1313 | 3.443 | 1.0539 | -0.89024 | -2.1801 | -3.057 | -3.3023 | 11.424 | 9.8357 | 9.5502 | 9.3736 | 9.1593 | 8.905 | 8.5974 | 8.2335 | 7.6313 | 6.943 | 4.5539 | 2.6098 | 1.3199 | 0.44304 | 0.19546 | 7.924 | 4.9757 | 4.3679 | 4.0759 | 3.6759 | 3.2524 | 2.6355 | 1.3924 | 0.12481 | -1.1716 | -5.0676 | -8.4497 | -11.0197 | -12.6444 | -12.2364 | 11.424 | 8.4757 | 7.8679 | 7.5759 | 7.1759 | 6.7524 | 6.1355 | 4.8924 | 3.6248 | 2.3284 | -1.5676 | -4.9497 | -7.5197 | -9.1444 | -8.8464 | 369100 | 423028 | LOWER DARWEN | ROCHDALE
| Failsworth | 10.3623 | 9.2313 | 8.923 | 8.8227 | 8.6205 | 8.393 | 8.1767 | 7.9762 | 7.7444 | 7.5405 | 5.8248 | 2.6358 | -0.099761 | -3.0593 | -5.7555 | 14.9993 | 13.8683 | 13.56 | 13.4597 | 13.2575 | 13.03 | 12.8137 | 12.6132 | 12.3814 | 12.1775 | 10.4618 | 7.2728 | 4.5372 | 1.5777 | -1.2329 | 10.3623 | 10.0501 | 9.8829 | 9.7537 | 9.5821 | 9.3849 | 9.122 | 8.774 | 8.4977 | 8.2162 | 7.3549 | 6.4453 | 5.5549 | 4.5444 | 3.7626 | 14.9993 | 14.6871 | 14.5199 | 14.3907 | 14.2191 | 14.0219 | 13.759 | 13.411 | 13.1347 | 12.8532 | 11.9919 | 11.0823 | 10.1919 | 9.1814 | 8.5301 | 10.3623 | 9.0789 | 8.7511 | 8.6774 | 8.5015 | 8.3049 | 8.1503 | 8.0112 | 7.8605 | 7.718 | 6.1907 | 3.1535 | 0.55932 | -2.2167 | -4.6882 | 14.9993 | 13.7159 | 13.3881 | 13.3144 | 13.1385 | 12.9419 | 12.7873 | 12.6482 | 12.4975 | 12.355 | 10.8277 | 7.7905 | 5.1963 | 2.4203 | -0.20615 | 10.3623 | 9.7132 | 9.5331 | 9.4853 | 9.3112 | 9.0997 | 8.7322 | 7.762 | 6.7572 | 5.7561 | 2.8353 | -0.040604 | -2.4187 | -4.0227 | -3.3308 | 14.9993 | 14.3502 | 14.1701 | 14.1223 | 13.9482 | 13.7367 | 13.3692 | 12.399 | 11.3942 | 10.3931 | 7.4723 | 4.5964 | 2.2183 | 0.61428 | 1.1447 | 10.3623 | 9.9369 | 9.8003 | 9.7665 | 9.7025 | 9.6037 | 9.4694 | 9.3065 | 9.0723 | 8.8453 | 8.0122 | 7.016 | 6.2946 | 5.5534 | 5.0935 | 14.9993 | 14.5739 | 14.4373 | 14.4035 | 14.3395 | 14.2407 | 14.1064 | 13.9435 | 13.7093 | 13.4823 | 12.6492 | 11.653 | 10.9316 | 10.1904 | 9.7605 | 10.3623 | 9.167 | 8.8173 | 8.6917 | 8.4459 | 8.1848 | 7.7549 | 6.704 | 5.6463 | 4.5909 | 1.4939 | -1.5328 | -4.0739 | -5.8957 | -5.4636 | 14.9993 | 13.804 | 13.4543 | 13.3287 | 13.0829 | 12.8218 | 12.3919 | 11.341 | 10.2833 | 9.2279 | 6.1309 | 3.1042 | 0.56311 | -1.2587 | -0.92959 | 389631 | 401496 | CHADDERTON | WHITEGATE
| Fallowfield | 7.4209 | 5.8116 | 5.0944 | 4.601 | 4.0154 | 3.4097 | 2.8193 | 2.2501 | 1.6874 | 1.3596 | -0.26463 | -2.5064 | -3.9796 | -5.1632 | -5.7537 | 12.0579 | 10.4486 | 9.7314 | 9.238 | 8.6524 | 8.0467 | 7.4563 | 6.8871 | 6.3244 | 5.9966 | 4.3724 | 2.1306 | 0.6574 | -0.52624 | -1.3076 | 7.4209 | 6.9485 | 6.5716 | 6.1951 | 5.746 | 5.2812 | 4.7284 | 4.0813 | 3.6001 | 3.0444 | 1.7608 | 0.74633 | -0.11124 | -0.86339 | -1.3127 | 12.0579 | 11.5855 | 11.2086 | 10.8321 | 10.383 | 9.9182 | 9.3654 | 8.7183 | 8.2371 | 7.6814 | 6.3978 | 5.3833 | 4.5258 | 3.7736 | 3.3909 | 7.4209 | 5.3987 | 4.3991 | 3.6506 | 2.7914 | 1.8923 | 1.3868 | 0.88192 | 0.33815 | -0.21824 | -2.5005 | -4.9138 | -6.2417 | -7.0331 | -6.8343 | 12.0579 | 10.0357 | 9.0361 | 8.2876 | 7.4284 | 6.5293 | 6.0238 | 5.5189 | 4.9752 | 4.4188 | 2.1365 | -0.27684 | -1.6047 | -2.3961 | -2.3858 | 7.4209 | 6.1479 | 5.3422 | 4.6658 | 3.8535 | 2.9772 | 2.3741 | 1.4283 | 0.50955 | -0.41325 | -3.0189 | -5.0015 | -5.9071 | -6.0177 | -5.1667 | 12.0579 | 10.7849 | 9.9792 | 9.3028 | 8.4905 | 7.6142 | 7.0111 | 6.0653 | 5.1465 | 4.2237 | 1.6181 | -0.36445 | -1.2701 | -1.3807 | -0.72585 | 7.4209 | 6.6895 | 6.1904 | 5.7774 | 5.3271 | 4.8482 | 4.3404 | 3.8052 | 3.2312 | 2.882 | 1.7217 | 0.61146 | -0.04314 | -0.61851 | -0.89045 | 12.0579 | 11.3265 | 10.8274 | 10.4144 | 9.9641 | 9.4852 | 8.9774 | 8.4422 | 7.8682 | 7.519 | 6.3587 | 5.2485 | 4.5939 | 4.0185 | 3.7616 | 7.4209 | 5.4789 | 4.455 | 3.6703 | 2.7598 | 1.8202 | 1.1394 | 0.08812 | -0.88217 | -1.8463 | -4.6498 | -6.7598 | -7.7931 | -8.0617 | -7.4466 | 12.0579 | 10.1159 | 9.092 | 8.3073 | 7.3968 | 6.4572 | 5.7764 | 4.7251 | 3.7548 | 2.7907 | -0.012775 | -2.1228 | -3.1561 | -3.4247 | -2.9506 | 385608 | 393881 | WEST DIDSBURY | SOUTH MANCHESTER
| Farnworth | 10.0881 | 9.3771 | 9.1401 | 8.936 | 8.5964 | 8.2247 | 7.8583 | 7.5117 | 7.1019 | 6.6855 | 4.4954 | 1.3162 | -1.078 | -3.2126 | -4.7427 | 14.0881 | 13.3771 | 13.1401 | 12.936 | 12.5964 | 12.2247 | 11.8583 | 11.5117 | 11.1019 | 10.6855 | 8.4954 | 5.3162 | 2.922 | 0.78743 | -0.91415 | 10.0881 | 9.7703 | 9.6536 | 9.5102 | 9.3049 | 9.0711 | 8.7618 | 8.3675 | 8.0915 | 7.7931 | 6.7802 | 5.5903 | 4.4498 | 3.2501 | 2.4115 | 14.0881 | 13.7703 | 13.6536 | 13.5102 | 13.3049 | 13.0711 | 12.7618 | 12.3675 | 12.0915 | 11.7931 | 10.7802 | 9.5903 | 8.4498 | 7.2501 | 6.5397 | 10.0881 | 9.2252 | 8.8893 | 8.6034 | 8.1798 | 7.7239 | 7.2875 | 6.858 | 6.4262 | 5.9194 | 3.4498 | 0.29661 | -1.9369 | -3.7122 | -4.4996 | 14.0881 | 13.2252 | 12.8893 | 12.6034 | 12.1798 | 11.7239 | 11.2875 | 10.858 | 10.4262 | 9.9194 | 7.4498 | 4.2966 | 2.0631 | 0.28783 | -0.61083 | 10.0881 | 9.7064 | 9.4925 | 9.2428 | 8.8281 | 8.3589 | 7.7417 | 6.6257 | 5.4777 | 4.3472 | 1.1732 | -1.4469 | -3.027 | -3.5911 | -3.0955 | 14.0881 | 13.7064 | 13.4925 | 13.2428 | 12.8281 | 12.3589 | 11.7417 | 10.6257 | 9.4777 | 8.3472 | 5.1732 | 2.5531 | 0.97297 | 0.40886 | 0.77901 | 10.0881 | 9.6321 | 9.4839 | 9.3688 | 9.2076 | 9.0045 | 8.7535 | 8.4586 | 8.1043 | 7.6793 | 6.202 | 4.6729 | 3.4278 | 2.2599 | 1.5971 | 14.0881 | 13.6321 | 13.4839 | 13.3688 | 13.2076 | 13.0045 | 12.7535 | 12.4586 | 12.1043 | 11.6793 | 10.202 | 8.6729 | 7.4278 | 6.2599 | 5.6687 | 10.0881 | 9.4277 | 9.0876 | 8.7466 | 8.2494 | 7.7271 | 7.045 | 5.8435 | 4.6622 | 3.4761 | 0.079028 | -2.7757 | -4.5863 | -5.3922 | -5.0985 | 14.0881 | 13.4277 | 13.0876 | 12.7466 | 12.2494 | 11.7271 | 11.045 | 9.8435 | 8.6622 | 7.4761 | 4.079 | 1.2243 | -0.5863 | -1.3922 | -1.1697 | 373726 | 405532 | KEARSLEY LOCAL | KEARSLEY
| Feniscowles | 3.0003 | 2.6566 | 2.5404 | 2.48 | 2.4069 | 2.3345 | 2.2675 | 2.202 | 2.1194 | 2.0402 | 1.572 | 0.78843 | 0.17582 | -0.45939 | -0.99566 | 15.3003 | 14.9566 | 14.8404 | 14.78 | 14.7069 | 14.6345 | 14.5675 | 14.502 | 14.4194 | 14.3402 | 13.872 | 13.0884 | 12.4758 | 11.8406 | 11.2674 | 3.0003 | 2.9485 | 2.9104 | 2.8779 | 2.8361 | 2.7885 | 2.7256 | 2.6408 | 2.5593 | 2.4763 | 2.2327 | 1.9919 | 1.7717 | 1.5422 | 1.3921 | 15.3003 | 15.2485 | 15.2104 | 15.1779 | 15.1361 | 15.0885 | 15.0256 | 14.9408 | 14.8593 | 14.7763 | 14.5327 | 14.2919 | 14.0717 | 13.8422 | 13.7167 | 3.0003 | 2.6132 | 2.4951 | 2.4459 | 2.3843 | 2.3256 | 2.2771 | 2.2324 | 2.1745 | 2.1155 | 1.7069 | 0.97422 | 0.40569 | -0.17731 | -0.65511 | 15.3003 | 14.9132 | 14.7951 | 14.7459 | 14.6843 | 14.6256 | 14.5771 | 14.5324 | 14.4745 | 14.4155 | 14.0069 | 13.2742 | 12.7057 | 12.1227 | 11.5968 | 3.0003 | 2.7645 | 2.6801 | 2.6324 | 2.5655 | 2.4939 | 2.3886 | 2.1557 | 1.91 | 1.6626 | 0.94464 | 0.24385 | -0.2761 | -0.59498 | -0.37315 | 15.3003 | 15.0645 | 14.9801 | 14.9324 | 14.8655 | 14.7939 | 14.6886 | 14.4557 | 14.21 | 13.9626 | 13.2446 | 12.5439 | 12.0239 | 11.705 | 11.8782 | 3.0003 | 2.9069 | 2.8437 | 2.8003 | 2.7544 | 2.7014 | 2.6449 | 2.5887 | 2.51 | 2.4316 | 2.1723 | 1.8749 | 1.7092 | 1.5859 | 1.5237 | 15.3003 | 15.2069 | 15.1437 | 15.1003 | 15.0544 | 15.0014 | 14.9449 | 14.8887 | 14.81 | 14.7316 | 14.4723 | 14.1749 | 14.0092 | 13.8859 | 13.8201 | 3.0003 | 2.6037 | 2.4738 | 2.4034 | 2.3165 | 2.232 | 2.1112 | 1.8558 | 1.5927 | 1.3283 | 0.55807 | -0.18997 | -0.75593 | -1.1305 | -0.96995 | 15.3003 | 14.9037 | 14.7738 | 14.7034 | 14.6165 | 14.532 | 14.4112 | 14.1558 | 13.8927 | 13.6283 | 12.8581 | 12.11 | 11.5441 | 11.1695 | 11.2948 | 364660 | 425120 | LOWER DARWEN | ROCHDALE
| Ferodo | 5.9536 | 5.7119 | 5.4879 | 5.3393 | 5.1773 | 5.0108 | 4.7019 | 4.5547 | 4.3258 | 4.1041 | 3.0498 | 1.4519 | 0.15405 | -1.1566 | -2.3099 | 16.9136 | 16.6719 | 16.4479 | 16.2993 | 16.1373 | 15.9708 | 15.6619 | 15.5147 | 15.2858 | 15.0641 | 14.0098 | 12.4119 | 11.114 | 9.8034 | 8.5962 | 5.9536 | 5.837 | 5.6706 | 5.5621 | 5.4794 | 5.408 | 5.3096 | 5.1508 | 4.915 | 4.6784 | 3.8331 | 3.0921 | 2.3869 | 1.3462 | 0.59958 | 16.9136 | 16.797 | 16.6306 | 16.5221 | 16.4394 | 16.368 | 16.2696 | 16.1108 | 15.875 | 15.6384 | 14.7931 | 14.0521 | 13.3469 | 12.3062 | 11.682 | 5.9536 | 5.684 | 5.4547 | 5.3049 | 4.9778 | 4.8222 | 4.6801 | 4.5404 | 4.3571 | 4.1855 | 0.20866 | -1.359 | -2.6004 | -3.7254 | -4.6133 | 16.9136 | 16.644 | 16.4147 | 16.2649 | 15.9378 | 15.7822 | 15.6401 | 15.5004 | 15.3171 | 15.1455 | 11.1687 | 9.601 | 8.3596 | 7.2346 | 6.2405 | 5.9536 | 5.8157 | 5.4416 | 5.3091 | 5.1709 | 1.3958 | 1.3408 | 1.0392 | 0.61754 | 0.20394 | -1.3348 | -2.9724 | -4.1253 | -4.7637 | -4.2943 | 16.9136 | 16.7757 | 16.4016 | 16.2691 | 16.1309 | 12.3558 | 12.3008 | 11.9992 | 11.5775 | 11.1639 | 9.6252 | 7.9876 | 6.8347 | 6.1963 | 6.5517 | 5.9536 | 5.7898 | 5.589 | 5.4601 | 5.3539 | 5.2469 | 4.9738 | 4.8334 | 4.5835 | 4.3296 | 3.483 | 2.5535 | 1.9328 | 1.4034 | 1.1972 | 16.9136 | 16.7498 | 16.549 | 16.4201 | 16.3139 | 16.2069 | 15.9338 | 15.7934 | 15.5435 | 15.2896 | 14.443 | 13.5135 | 12.8928 | 12.3634 | 12.1566 | 5.9536 | 5.7214 | 5.3071 | 5.1466 | 4.9848 | 1.201 | 1.1559 | 0.8585 | 0.43362 | 0.017139 | -1.5217 | -3.1846 | -4.4073 | -5.1305 | -4.7576 | 16.9136 | 16.6814 | 16.2671 | 16.1066 | 15.9448 | 12.161 | 12.1159 | 11.8185 | 11.3936 | 10.9771 | 9.4383 | 7.7754 | 6.5527 | 5.8295 | 6.1108 | 405720 | 381338 | NEW MILLS | STALYBRIDGE
| Flat Lane | 0.43736 | -0.24674 | -0.4118 | -0.47014 | -0.56813 | -0.66997 | -0.75077 | -0.82634 | -0.91276 | -0.98702 | -1.4975 | -2.4009 | -3.1459 | -3.8884 | -4.5532 | 5.9374 | 5.2533 | 5.0882 | 5.0299 | 4.9319 | 4.83 | 4.7492 | 4.6737 | 4.5872 | 4.513 | 4.0025 | 3.0991 | 2.3541 | 1.6116 | 0.89752 | 0.43736 | 0.22765 | 0.12667 | 0.037132 | -0.071666 | -0.18799 | -0.33179 | -0.51164 | -0.6172 | -0.73697 | -1.0855 | -1.3966 | -1.6545 | -1.9106 | -2.1425 | 5.9374 | 5.7276 | 5.6267 | 5.5371 | 5.4283 | 5.312 | 5.1682 | 4.9884 | 4.8828 | 4.763 | 4.4145 | 4.1034 | 3.8455 | 3.5894 | 3.394 | 0.43736 | -0.34333 | -0.51826 | -0.56253 | -0.64358 | -0.72547 | -0.78029 | -0.82686 | -0.87835 | -0.92375 | -1.3432 | -2.1603 | -2.8287 | -3.4823 | -4.0478 | 5.9374 | 5.1567 | 4.9817 | 4.9375 | 4.8564 | 4.7745 | 4.7197 | 4.6731 | 4.6216 | 4.5762 | 4.1568 | 3.3397 | 2.6713 | 2.0177 | 1.3855 | 0.43736 | -0.048426 | -0.15763 | -0.1952 | -0.26735 | -0.34456 | -0.45167 | -0.72082 | -1.0071 | -1.2907 | -2.1008 | -2.88 | -3.4845 | -3.83 | -3.533 | 5.9374 | 5.4516 | 5.3424 | 5.3048 | 5.2326 | 5.1554 | 5.0483 | 4.7792 | 4.4929 | 4.2093 | 3.3992 | 2.62 | 2.0155 | 1.67 | 1.8985 | 0.43736 | 0.12236 | 0.029432 | -0.012531 | -0.061654 | -0.11435 | -0.17394 | -0.24301 | -0.33525 | -0.42423 | -0.73129 | -1.0909 | -1.3312 | -1.5647 | -1.6699 | 5.9374 | 5.6224 | 5.5294 | 5.4875 | 5.4383 | 5.3856 | 5.3261 | 5.257 | 5.1648 | 5.0758 | 4.7687 | 4.4091 | 4.1688 | 3.9353 | 3.8223 | 0.43736 | -0.38481 | -0.58104 | -0.65735 | -0.7664 | -0.87193 | -1.0124 | -1.3264 | -1.6408 | -1.9522 | -2.8432 | -3.688 | -4.3527 | -4.7701 | -4.5534 | 5.9374 | 5.1152 | 4.919 | 4.8427 | 4.7336 | 4.6281 | 4.4876 | 4.1736 | 3.8592 | 3.5478 | 2.6568 | 1.812 | 1.1473 | 0.72994 | 0.896 | 383248 | 456995 | NELSON | PADIHAM | Firm Capacity marginally exceeded in FY25. Review in RIIO-ED2. Potential requirement for 2nd transformer in future.
| Frederick Rd | 6.4974 | 4.2717 | 3.2827 | 2.6661 | 1.8074 | 0.92317 | -0.090395 | -1.1091 | -2.1935 | -2.7903 | -5.0589 | -7.9052 | -10.017 | -11.9861 | -13.7103 | 13.4974 | 11.2717 | 10.2827 | 9.6661 | 8.8074 | 7.9232 | 6.9096 | 5.8909 | 4.8065 | 4.2097 | 1.9411 | -0.90517 | -3.017 | -4.9861 | -6.6756 | 6.4974 | 5.9089 | 5.5447 | 5.2521 | 4.9259 | 4.5975 | 4.1916 | 3.651 | 3.1339 | 2.6038 | 0.97764 | -0.73032 | -2.323 | -4.0787 | -5.3827 | 13.4974 | 12.9089 | 12.5447 | 12.2521 | 11.9259 | 11.5975 | 11.1916 | 10.651 | 10.1339 | 9.6038 | 7.9776 | 6.2697 | 4.677 | 2.9213 | 1.8383 | 6.4974 | 3.918 | 2.8019 | 2.1326 | 1.213 | 0.26112 | -0.79729 | -1.8738 | -2.9833 | -3.6371 | -6.1512 | -9.199 | -11.2695 | -13.07 | -14.399 | 13.4974 | 10.918 | 9.8019 | 9.1326 | 8.213 | 7.2611 | 6.2027 | 5.1262 | 4.0167 | 3.3629 | 0.84875 | -2.199 | -4.2695 | -6.07 | -7.3293 | 6.4974 | 4.7784 | 3.8694 | 3.2446 | 2.3357 | 1.3811 | 0.21475 | -1.2702 | -2.7866 | -3.8239 | -6.8145 | -9.4931 | -11.1834 | -12.2918 | -12.6846 | 13.4974 | 11.7784 | 10.8694 | 10.2446 | 9.3357 | 8.3811 | 7.2148 | 5.7298 | 4.2134 | 3.1761 | 0.18553 | -2.4931 | -4.1834 | -5.2918 | -5.6257 | 6.4974 | 5.5798 | 4.8907 | 4.3482 | 3.608 | 2.8418 | 1.9235 | 0.97501 | -0.087303 | -0.68262 | -2.591 | -4.536 | -5.8744 | -7.1316 | -8.1436 | 13.4974 | 12.5798 | 11.8907 | 11.3482 | 10.608 | 9.8418 | 8.9235 | 7.975 | 6.9127 | 6.3174 | 4.409 | 2.464 | 1.1256 | -0.13157 | -0.98194 | 6.4974 | 3.7951 | 2.6224 | 1.9307 | 0.9705 | -0.023607 | -1.2409 | -2.7879 | -4.3399 | -5.4158 | -8.5742 | -11.4301 | -13.296 | -14.585 | -15.1787 | 13.4974 | 10.7951 | 9.6224 | 8.9307 | 7.9705 | 6.9764 | 5.7591 | 4.2121 | 2.6601 | 1.5842 | -1.5742 | -4.4301 | -6.296 | -7.585 | -8.0756 | 381697 | 399348 | FREDERICK RD | KEARSLEY
| Fusehill | 4.7239 | 4.3934 | 4.2307 | 4.1593 | 4.0353 | 3.8966 | 3.7886 | 3.7133 | 3.5792 | 3.4679 | 2.3195 | 0.083482 | -1.7277 | -3.5289 | -4.9884 | 11.2239 | 10.8934 | 10.7307 | 10.6593 | 10.5353 | 10.3966 | 10.2886 | 10.2133 | 10.0792 | 9.9679 | 8.8195 | 6.5835 | 4.7723 | 2.9711 | 1.2963 | 4.7239 | 4.5434 | 4.3754 | 4.2602 | 4.144 | 4.0279 | 3.8573 | 3.6166 | 3.4149 | 3.2162 | 2.6486 | 2.0955 | 1.6291 | 1.1826 | 0.97346 | 11.2239 | 11.0434 | 10.8754 | 10.7602 | 10.644 | 10.5279 | 10.3573 | 10.1166 | 9.9149 | 9.7162 | 9.1486 | 8.5955 | 8.1291 | 7.6826 | 7.4922 | 4.7239 | 4.3727 | 4.2181 | 4.1795 | 4.0804 | 3.9687 | 3.905 | 3.8716 | 3.8363 | 3.7942 | 2.8 | 0.73136 | -0.90991 | -2.4763 | -3.6364 | 11.2239 | 10.8727 | 10.7181 | 10.6795 | 10.5804 | 10.4687 | 10.405 | 10.3716 | 10.3363 | 10.2942 | 9.3 | 7.2314 | 5.5901 | 4.0237 | 2.596 | 4.7239 | 4.6972 | 4.6249 | 4.6176 | 4.5382 | 4.4367 | 4.2265 | 3.551 | 2.8415 | 2.1226 | 0.080715 | -1.8572 | -3.3307 | -4.0274 | -2.7817 | 11.2239 | 11.1972 | 11.1249 | 11.1176 | 11.0382 | 10.9367 | 10.7265 | 10.051 | 9.3415 | 8.6226 | 6.5807 | 4.6428 | 3.1693 | 2.4726 | 3.4451 | 4.7239 | 4.5104 | 4.3842 | 4.3569 | 4.3432 | 4.3263 | 4.3008 | 4.2526 | 4.1015 | 3.9535 | 3.4441 | 2.8759 | 2.5586 | 2.3448 | 2.5276 | 11.2239 | 11.0104 | 10.8842 | 10.8569 | 10.8432 | 10.8263 | 10.8008 | 10.7526 | 10.6015 | 10.4535 | 9.9441 | 9.3759 | 9.0586 | 8.8448 | 8.9439 | 4.7239 | 4.5296 | 4.3797 | 4.3097 | 4.1708 | 4.0255 | 3.7613 | 3.0185 | 2.2726 | 1.5155 | -0.64129 | -2.6701 | -4.2558 | -5.112 | -4.0634 | 11.2239 | 11.0296 | 10.8797 | 10.8097 | 10.6708 | 10.5255 | 10.2613 | 9.5185 | 8.7726 | 8.0155 | 5.8587 | 3.8299 | 2.2442 | 1.388 | 2.2094 | 341042 | 555452 | CARLISLE | HARKER
| Gale | 13.5997 | 13.5074 | 13.3898 | 13.2867 | 13.1253 | 12.9593 | 12.8226 | 12.7063 | 12.5496 | 12.4119 | 11.0706 | 8.4696 | 6.2407 | 3.815 | 1.7129 | 18.2367 | 18.1444 | 18.0268 | 17.9237 | 17.7623 | 17.5963 | 17.4596 | 17.3433 | 17.1866 | 17.0489 | 15.7076 | 13.1066 | 10.8777 | 8.452 | 6.2099 | 13.5997 | 13.501 | 13.3815 | 13.2758 | 13.1544 | 13.0291 | 12.863 | 12.6379 | 12.439 | 12.2305 | 11.6102 | 10.9837 | 10.3583 | 9.6388 | 9.088 | 18.2367 | 18.138 | 18.0185 | 17.9128 | 17.7914 | 17.6661 | 17.5 | 17.2749 | 17.076 | 16.8675 | 16.2472 | 15.6207 | 14.9953 | 14.2758 | 13.82 | 13.5997 | 13.5215 | 13.4191 | 13.3434 | 13.2075 | 13.0704 | 12.9756 | 12.9029 | 12.8134 | 12.7271 | 11.5482 | 9.0975 | 7.0091 | 4.757 | 2.8595 | 18.2367 | 18.1585 | 18.0561 | 17.9804 | 17.8445 | 17.7074 | 17.6126 | 17.5399 | 17.4504 | 17.3641 | 16.1852 | 13.7345 | 11.6461 | 9.394 | 7.3179 | 13.5997 | 13.6877 | 13.6328 | 13.5624 | 13.416 | 13.2532 | 12.9573 | 12.1417 | 11.2994 | 10.462 | 8.0551 | 5.7284 | 3.8142 | 2.561 | 3.3853 | 18.2367 | 18.3247 | 18.2698 | 18.1994 | 18.053 | 17.8902 | 17.5943 | 16.7787 | 15.9364 | 15.099 | 12.6921 | 10.3654 | 8.4512 | 7.198 | 7.8405 | 13.5997 | 13.5247 | 13.4326 | 13.3767 | 13.3167 | 13.2444 | 13.1647 | 13.0755 | 12.9151 | 12.757 | 12.1926 | 11.5157 | 11.0393 | 10.5637 | 10.311 | 18.2367 | 18.1617 | 18.0696 | 18.0137 | 17.9537 | 17.8814 | 17.8017 | 17.7125 | 17.5521 | 17.394 | 16.8296 | 16.1527 | 15.6763 | 15.2007 | 14.9479 | 13.5997 | 13.651 | 13.5456 | 13.4182 | 13.2193 | 13.0204 | 12.68 | 11.8029 | 10.9161 | 10.0337 | 7.4887 | 5.039 | 2.9881 | 1.5387 | 2.1274 | 18.2367 | 18.288 | 18.1826 | 18.0552 | 17.8563 | 17.6574 | 17.317 | 16.4399 | 15.5531 | 14.6707 | 12.1257 | 9.676 | 7.6251 | 6.1757 | 6.6353 | 389570 | 414943 | BELFIELD | ROCHDALE
| Garstang | 2.5219 | 2.0154 | 1.6973 | 1.4288 | 1.0606 | 0.683 | 0.3425 | -0.0033667 | -0.38489 | -0.74271 | -2.4108 | -4.874 | -7.111 | -9.3273 | -11.5387 | 2.5219 | 2.0154 | 1.6973 | 1.4288 | 1.0606 | 0.683 | 0.3425 | -0.0033667 | -0.38489 | -0.74271 | -2.4108 | -4.874 | -7.111 | -9.3273 | -11.535 | 2.5219 | 2.2556 | 1.9967 | 1.7211 | 1.3796 | 1.0118 | 0.5521 | -0.057694 | -0.48917 | -0.92398 | -2.246 | -3.5841 | -4.7982 | -6.1524 | -7.1159 | 2.5219 | 2.2556 | 1.9967 | 1.7211 | 1.3796 | 1.0118 | 0.5521 | -0.057694 | -0.48917 | -0.92398 | -2.246 | -3.5841 | -4.7982 | -6.1524 | -6.9549 | 2.5219 | 1.9914 | 1.6903 | 1.4647 | 1.1429 | 0.82032 | 0.55669 | 0.29688 | 0.017615 | -0.25459 | -1.6705 | -3.9803 | -6.063 | -8.085 | -10.072 | 2.5219 | 1.9914 | 1.6903 | 1.4647 | 1.1429 | 0.82032 | 0.55669 | 0.29688 | 0.017615 | -0.25459 | -1.6705 | -3.9803 | -6.063 | -8.085 | -10.1073 | 2.5219 | 2.3283 | 2.1423 | 1.9698 | 1.6986 | 1.3996 | 1.0424 | 0.35935 | -0.37452 | -1.1114 | -3.3648 | -5.9598 | -7.8494 | -9.0951 | -8.9531 | 2.5219 | 2.3283 | 2.1423 | 1.9698 | 1.6986 | 1.3996 | 1.0424 | 0.35935 | -0.37452 | -1.1114 | -3.3648 | -5.9598 | -7.8494 | -9.0951 | -9.0012 | 2.5219 | 2.283 | 2.0451 | 1.839 | 1.5994 | 1.3334 | 1.0404 | 0.69024 | 0.2602 | -0.17082 | -1.6001 | -3.1735 | -4.2535 | -5.2663 | -5.934 | 2.5219 | 2.283 | 2.0451 | 1.839 | 1.5994 | 1.3334 | 1.0404 | 0.69024 | 0.2602 | -0.17082 | -1.6001 | -3.1735 | -4.2535 | -5.2663 | -5.86 | 2.5219 | 2.1127 | 1.7983 | 1.5078 | 1.1272 | 0.75112 | 0.30564 | -0.49896 | -1.3059 | -2.1141 | -4.5741 | -7.3569 | -9.4168 | -10.8424 | -10.9048 | 2.5219 | 2.1127 | 1.7983 | 1.5078 | 1.1272 | 0.75112 | 0.30564 | -0.49896 | -1.3059 | -2.1141 | -4.5741 | -7.3569 | -9.4168 | -10.8424 | -10.9079 | 348319 | 445221 | THORNTON | STANAH
| Gatley | 1.5604 | 1.5397 | 1.5197 | 1.505 | 1.4324 | 1.3473 | 1.2704 | 1.2212 | 1.1409 | 1.0779 | 0.35425 | -1.0759 | -2.3101 | -3.5538 | -4.7533 | 12.0604 | 12.0397 | 12.0197 | 12.005 | 11.9324 | 11.8473 | 11.7704 | 11.7212 | 11.6409 | 11.5779 | 10.8543 | 9.4241 | 8.1899 | 6.9462 | 5.6602 | 1.5604 | 1.5266 | 1.4863 | 1.4555 | 1.4061 | 1.3443 | 1.2536 | 1.1415 | 1.0225 | 0.9025 | 0.54092 | 0.18662 | -0.16223 | -0.53953 | -0.79814 | 12.0604 | 12.0266 | 11.9863 | 11.9555 | 11.9061 | 11.8443 | 11.7536 | 11.6415 | 11.5225 | 11.4025 | 11.0409 | 10.6866 | 10.3378 | 9.9605 | 9.7401 | 1.5604 | 1.5532 | 1.5476 | 1.558 | 1.5102 | 1.4533 | 1.4179 | 1.4118 | 1.3908 | 1.3748 | 0.79196 | -0.51798 | -1.6449 | -2.7546 | -3.7961 | 12.0604 | 12.0532 | 12.0476 | 12.058 | 12.0102 | 11.9533 | 11.9179 | 11.9118 | 11.8908 | 11.8748 | 11.292 | 9.982 | 8.8551 | 7.7454 | 6.5875 | 1.5604 | 1.7276 | 1.768 | 1.7894 | 1.735 | 1.6572 | 1.5137 | 1.1116 | 0.67529 | 0.23558 | -1.0431 | -2.2814 | -3.3046 | -3.8463 | -3.3015 | 12.0604 | 12.2276 | 12.268 | 12.2894 | 12.235 | 12.1572 | 12.0137 | 11.6116 | 11.1753 | 10.7356 | 9.4569 | 8.2186 | 7.1954 | 6.6537 | 7.0801 | 1.5604 | 1.5509 | 1.555 | 1.592 | 1.6211 | 1.6305 | 1.6225 | 1.6101 | 1.5413 | 1.476 | 1.2028 | 0.82534 | 0.52967 | 0.24232 | 0.14175 | 12.0604 | 12.0509 | 12.055 | 12.092 | 12.1211 | 12.1305 | 12.1225 | 12.1101 | 12.0413 | 11.976 | 11.7028 | 11.3253 | 11.0297 | 10.7423 | 10.6285 | 1.5604 | 1.6955 | 1.6915 | 1.6635 | 1.5653 | 1.4598 | 1.2811 | 0.83107 | 0.35897 | -0.11645 | -1.5051 | -2.8335 | -3.9434 | -4.5844 | -4.1515 | 12.0604 | 12.1955 | 12.1915 | 12.1635 | 12.0653 | 11.9598 | 11.7811 | 11.3311 | 10.859 | 10.3835 | 8.9949 | 7.6665 | 6.5566 | 5.9156 | 6.2547 | 384242 | 388388 | MOSS NOOK | SOUTH MANCHESTER
| Gidlow | 8.9073 | 6.9494 | 6.4098 | 6.2159 | 5.8966 | 5.5661 | 5.2714 | 5.0081 | 4.7105 | 4.4505 | 2.2968 | -1.7315 | -5.1472 | -8.798 | -12.0528 | 13.5443 | 11.5864 | 11.0468 | 10.8529 | 10.5336 | 10.2031 | 9.9084 | 9.6451 | 9.3475 | 9.0875 | 6.9338 | 2.9055 | -0.51021 | -4.161 | -7.6001 | 8.9073 | 8.2244 | 7.9586 | 7.768 | 7.4984 | 7.193 | 6.7987 | 6.2996 | 5.9141 | 5.526 | 4.3709 | 3.2256 | 2.1634 | 1.0333 | 0.23805 | 13.5443 | 12.8614 | 12.5956 | 12.405 | 12.1354 | 11.83 | 11.4357 | 10.9366 | 10.5511 | 10.163 | 9.0079 | 7.8626 | 6.8004 | 5.6703 | 5.0026 | 8.9073 | 6.6813 | 6.1148 | 5.9717 | 5.5889 | 5.2046 | 4.8835 | 4.6001 | 4.2841 | 4.0023 | 2.1316 | -1.6444 | -4.8384 | -8.2346 | -11.2119 | 13.5443 | 11.3183 | 10.7518 | 10.6087 | 10.2259 | 9.8416 | 9.5205 | 9.2371 | 8.9211 | 8.6393 | 6.7686 | 2.9926 | -0.20144 | -3.5976 | -6.8081 | 8.9073 | 7.6388 | 7.3159 | 7.2332 | 6.8715 | 6.4639 | 5.8647 | 4.5262 | 3.1336 | 1.7665 | -1.8788 | -5.4725 | -8.419 | -10.3653 | -9.3231 | 13.5443 | 12.2758 | 11.9529 | 11.8702 | 11.5085 | 11.1009 | 10.5017 | 9.1632 | 7.7706 | 6.4035 | 2.7582 | -0.83552 | -3.782 | -5.7283 | -4.9254 | 8.9073 | 7.7934 | 7.4824 | 7.402 | 7.2817 | 7.1165 | 6.9173 | 6.7088 | 6.4205 | 6.1416 | 5.1549 | 3.9646 | 3.1302 | 2.3008 | 1.8395 | 13.5443 | 12.4304 | 12.1194 | 12.039 | 11.9187 | 11.7535 | 11.5543 | 11.3458 | 11.0575 | 10.7786 | 9.7919 | 8.6016 | 7.7672 | 6.9378 | 6.4929 | 8.9073 | 6.6729 | 6.0464 | 5.8216 | 5.3315 | 4.8415 | 4.1428 | 2.6609 | 1.1599 | -0.31412 | -4.2682 | -8.1019 | -11.2863 | -13.5368 | -12.8584 | 13.5443 | 11.3099 | 10.6834 | 10.4586 | 9.9685 | 9.4785 | 8.7798 | 7.2979 | 5.7969 | 4.3229 | 0.36884 | -3.4649 | -6.6493 | -8.8998 | -8.3792 | 357620 | 406662 | WIGAN | KIRKBY
| Gillsrow | 1.1153 | 0.96103 | 0.88593 | 0.83569 | 0.71448 | 0.57891 | 0.46346 | 0.36984 | 0.28754 | 0.23156 | -0.32596 | -1.4189 | -2.3315 | -3.1393 | -4.0139 | 3.3153 | 3.161 | 3.0859 | 3.0357 | 2.9145 | 2.7789 | 2.6635 | 2.5698 | 2.4875 | 2.4316 | 1.874 | 0.78107 | -0.13153 | -0.93927 | -1.8865 | 1.1153 | 0.9862 | 0.85505 | 0.71923 | 0.5634 | 0.43883 | 0.23208 | -0.046066 | -0.15002 | -0.25301 | -0.55016 | -0.80917 | -1.075 | -1.4453 | -2.0073 | 3.3153 | 3.1862 | 3.0551 | 2.9192 | 2.7634 | 2.6388 | 2.4321 | 2.1539 | 2.05 | 1.947 | 1.6498 | 1.3908 | 1.125 | 0.7547 | 0.29294 | 1.1153 | 0.95535 | 0.88612 | 0.85178 | 0.74564 | 0.62761 | 0.53819 | 0.47195 | 0.43229 | 0.40945 | -0.041291 | -1.0312 | -1.847 | -2.5352 | -3.2684 | 3.3153 | 3.1553 | 3.0861 | 3.0518 | 2.9456 | 2.8276 | 2.7382 | 2.6719 | 2.6323 | 2.6095 | 2.1587 | 1.1688 | 0.35297 | -0.33518 | -1.1648 | 1.1153 | 1.0831 | 1.0322 | 0.93001 | 0.80627 | 0.67958 | 0.51658 | 0.18594 | -0.16496 | -0.51535 | -1.5154 | -2.4621 | -3.1292 | -3.3644 | -2.9302 | 3.3153 | 3.2831 | 3.2322 | 3.13 | 3.0063 | 2.8796 | 2.7166 | 2.3859 | 2.035 | 1.6847 | 0.68461 | -0.26207 | -0.92918 | -1.1644 | -0.82842 | 1.1153 | 1.0065 | 0.93103 | 0.87052 | 0.79539 | 0.75297 | 0.71836 | 0.66867 | 0.59193 | 0.51794 | 0.13919 | -0.43481 | -0.81923 | -1.2632 | -1.5606 | 3.3153 | 3.2065 | 3.131 | 3.0705 | 2.9954 | 2.953 | 2.9184 | 2.8687 | 2.7919 | 2.7179 | 2.3392 | 1.7652 | 1.3808 | 0.93684 | 0.59945 | 1.1153 | 1.0132 | 0.91973 | 0.77703 | 0.61294 | 0.45174 | 0.24759 | -0.1332 | -0.50974 | -0.88585 | -1.9627 | -2.9686 | -3.6889 | -3.9856 | -3.621 | 3.3153 | 3.2132 | 3.1197 | 2.977 | 2.8129 | 2.6517 | 2.4476 | 2.0668 | 1.6903 | 1.3141 | 0.23733 | -0.76864 | -1.4889 | -1.7856 | -1.5037 | 337117 | 526444 | PENRITH & SHAP | HUTTON
| Glaxo | 8.8347 | 8.6814 | 8.3675 | 8.0485 | 7.6697 | 7.2937 | 7.146 | 6.9998 | 6.8232 | 6.6491 | 4.9139 | 3.2233 | 3.1633 | -0.3269 | -0.31389 | 20.7847 | 20.6314 | 20.3175 | 19.9985 | 19.6197 | 19.2437 | 19.096 | 18.9498 | 18.7732 | 18.5991 | 16.8639 | 15.1733 | 15.1133 | 11.6231 | 11.6133 | 8.8347 | 8.7766 | 8.7801 | 8.7614 | 8.758 | 8.7549 | 8.7514 | 8.7477 | 8.7094 | 8.6727 | 8.571 | 7.6711 | 7.6009 | 3.3002 | 2.3298 | 20.7847 | 20.7266 | 20.7301 | 20.7114 | 20.708 | 20.7049 | 20.7014 | 20.6977 | 20.6594 | 20.6227 | 20.521 | 19.6211 | 19.5509 | 15.2502 | 14.2819 | 8.8347 | 8.6634 | 8.3463 | 8.0266 | 7.6478 | 7.272 | 7.1245 | 6.9788 | 6.6855 | 6.5288 | 0.4697 | -0.86431 | -0.8582 | -0.82321 | -0.71286 | 20.7847 | 20.6134 | 20.2963 | 19.9766 | 19.5978 | 19.222 | 19.0745 | 18.9288 | 18.6355 | 18.4788 | 12.4197 | 11.0857 | 11.0918 | 11.1268 | 11.1952 | 8.8347 | 8.705 | 8.399 | 8.0836 | 7.7086 | 6.4903 | 4.8212 | 1.1619 | 0.75883 | -0.18276 | -1.1183 | -1.0931 | -1.0805 | -1.015 | -0.84247 | 20.7847 | 20.655 | 20.349 | 20.0336 | 19.6586 | 18.4403 | 16.7712 | 13.1119 | 12.7088 | 11.7672 | 10.8317 | 10.8569 | 10.8695 | 10.935 | 11.0651 | 8.8347 | 8.7707 | 8.4745 | 8.1595 | 7.7865 | 7.4141 | 7.2674 | 7.1224 | 6.9467 | 6.7727 | 5.0595 | 3.4218 | 3.4106 | -0.024318 | 0.053821 | 20.7847 | 20.7207 | 20.4245 | 20.1095 | 19.7365 | 19.3641 | 19.2174 | 19.0724 | 18.8967 | 18.7227 | 17.0095 | 15.3718 | 15.3606 | 11.9257 | 11.9832 | 8.8347 | 8.6492 | 8.3292 | 8.0081 | 7.628 | 6.4071 | 4.7359 | 1.0725 | 0.6676 | -0.27555 | -1.2155 | -1.1935 | -1.1843 | -1.1213 | -0.95236 | 20.7847 | 20.5992 | 20.2792 | 19.9581 | 19.578 | 18.3571 | 16.6859 | 13.0225 | 12.6176 | 11.6745 | 10.7345 | 10.7565 | 10.7657 | 10.8287 | 10.9563 | 330458 | 477825 | ULVERSTON | HARKER
| Glossop | 9.4171 | 9.1445 | 8.9488 | 8.7947 | 8.5509 | 8.2983 | 8.0694 | 7.8571 | 7.5937 | 7.3515 | 5.526 | 2.2142 | -0.55752 | -3.5407 | -6.11 | 14.0541 | 13.7815 | 13.5858 | 13.4317 | 13.1879 | 12.9353 | 12.7064 | 12.4941 | 12.2307 | 11.9885 | 10.163 | 6.8512 | 4.0795 | 1.0963 | -1.6257 | 9.4171 | 9.206 | 9.014 | 8.8385 | 8.6275 | 8.4106 | 8.1213 | 7.7286 | 7.4101 | 7.0896 | 6.1319 | 5.1311 | 4.1781 | 3.1226 | 2.3661 | 14.0541 | 13.843 | 13.651 | 13.4755 | 13.2645 | 13.0476 | 12.7583 | 12.3656 | 12.0471 | 11.7266 | 10.7689 | 9.7681 | 8.8151 | 7.7596 | 7.1299 | 9.4171 | 9.1444 | 8.9642 | 8.8442 | 8.6327 | 8.4171 | 8.2459 | 8.0915 | 7.9159 | 7.743 | 6.1254 | 2.978 | 0.35762 | -2.4272 | -4.7522 | 14.0541 | 13.7814 | 13.6012 | 13.4812 | 13.2697 | 13.0541 | 12.8829 | 12.7285 | 12.5529 | 12.38 | 10.7624 | 7.615 | 4.9946 | 2.2098 | -0.31394 | 9.4171 | 9.4664 | 9.3759 | 9.295 | 9.1009 | 8.8866 | 8.5046 | 7.483 | 6.4214 | 5.3611 | 2.3078 | -0.65905 | -3.0508 | -4.6558 | -3.7485 | 14.0541 | 14.1034 | 14.0129 | 13.932 | 13.7379 | 13.5236 | 13.1416 | 12.12 | 11.0584 | 9.9981 | 6.9448 | 3.978 | 1.5862 | -0.018801 | 0.68342 | 9.4171 | 9.2142 | 9.0582 | 8.9587 | 8.8369 | 8.6994 | 8.5405 | 8.366 | 8.1019 | 7.8408 | 6.9623 | 5.9593 | 5.216 | 4.5203 | 4.1168 | 14.0541 | 13.8512 | 13.6952 | 13.5957 | 13.4739 | 13.3364 | 13.1775 | 13.003 | 12.7389 | 12.4778 | 11.5993 | 10.5963 | 9.853 | 9.1573 | 8.7852 | 9.4171 | 9.3617 | 9.191 | 9.0325 | 8.7665 | 8.5011 | 8.0553 | 6.952 | 5.8407 | 4.7288 | 1.499 | -1.6348 | -4.2138 | -6.0773 | -5.4754 | 14.0541 | 13.9987 | 13.828 | 13.6695 | 13.4035 | 13.1381 | 12.6923 | 11.589 | 10.4777 | 9.3658 | 6.136 | 3.0022 | 0.4232 | -1.4403 | -0.97512 | 402300 | 394074 | HYDE | STALYBRIDGE
| Golborne T11 & T12 | 11.317 | 10.9813 | 10.4399 | 9.8654 | 9.1772 | 8.4671 | 7.7704 | 7.0256 | 6.0026 | 4.9712 | 0.60991 | -5.2055 | -9.6685 | -14.0866 | -17.7012 | 16.817 | 16.4813 | 15.9399 | 15.3654 | 14.6772 | 13.9671 | 13.2704 | 12.5256 | 11.5026 | 10.4712 | 6.1099 | 0.29449 | -4.1685 | -8.5866 | -12.2955 | 11.317 | 11.0592 | 10.7374 | 10.3811 | 9.9237 | 9.3839 | 8.7104 | 7.8386 | 6.9854 | 6.1012 | 3.3399 | 0.48341 | -2.2992 | -5.2043 | -7.0095 | 16.817 | 16.5592 | 16.2374 | 15.8811 | 15.4237 | 14.8839 | 14.2104 | 13.3386 | 12.4854 | 11.6012 | 8.8399 | 5.9834 | 3.2008 | 0.29574 | -1.2316 | 11.317 | 11.0233 | 10.5344 | 10.0499 | 9.4646 | 8.8819 | 8.3562 | 7.6949 | 6.8737 | 6.0186 | 0.62922 | -5.9426 | -10.8711 | -15.2262 | -18.4838 | 16.817 | 16.5233 | 16.0344 | 15.5499 | 14.9646 | 14.3819 | 13.8562 | 13.1949 | 12.3737 | 11.5186 | 6.1292 | -0.44255 | -5.3711 | -9.7262 | -12.9136 | 11.317 | 11.3128 | 10.9986 | 10.6284 | 10.0926 | 9.4391 | 8.5597 | 6.9229 | 5.1219 | 3.2735 | -2.3257 | -7.6708 | -11.6889 | -15.0301 | -15.5295 | 16.817 | 16.8128 | 16.4986 | 16.1284 | 15.5926 | 14.9391 | 14.0597 | 12.4229 | 10.6219 | 8.7735 | 3.1743 | -2.1708 | -6.1889 | -9.5301 | -10.0127 | 11.317 | 11.06 | 10.6505 | 10.2811 | 9.8808 | 9.3585 | 8.7722 | 8.1632 | 7.3309 | 6.3894 | 3.2536 | -0.18718 | -3.3806 | -5.9976 | -7.4622 | 16.817 | 16.56 | 16.1505 | 15.7811 | 15.3808 | 14.8585 | 14.2722 | 13.6632 | 12.8309 | 11.8894 | 8.7536 | 5.3128 | 2.1194 | -0.49757 | -1.7817 | 11.317 | 11.1699 | 10.6458 | 10.0409 | 9.3094 | 8.5712 | 7.615 | 5.8199 | 3.9009 | 1.9498 | -4.0202 | -9.7841 | -14.4038 | -17.604 | -17.3901 | 16.817 | 16.6699 | 16.1458 | 15.5409 | 14.8094 | 14.0712 | 13.115 | 11.3199 | 9.4009 | 7.4498 | 1.4798 | -4.2841 | -8.9038 | -12.104 | -11.9741 | 360621 | 397766 | GOLBORNE | BOLD
| Gowhole | 6.2848 | 5.7364 | 5.5037 | 5.3922 | 5.1681 | 4.9313 | 4.7387 | 4.5587 | 4.2736 | 4.0243 | 1.7782 | -2.4448 | -6.0003 | -9.6666 | -12.6305 | 10.9218 | 10.3734 | 10.1407 | 10.0292 | 9.8051 | 9.5683 | 9.3757 | 9.1957 | 8.9106 | 8.6613 | 6.4152 | 2.1922 | -1.3633 | -5.0296 | -8.2943 | 6.2848 | 6.0117 | 5.7796 | 5.5704 | 5.3002 | 4.987 | 4.5849 | 4.1032 | 3.7095 | 3.3122 | 2.1247 | 0.90357 | -0.27729 | -1.5155 | -2.3541 | 10.9218 | 10.6487 | 10.4166 | 10.2074 | 9.9372 | 9.624 | 9.2219 | 8.7402 | 8.3465 | 7.9492 | 6.7617 | 5.5406 | 4.3597 | 3.1215 | 2.4083 | 6.2848 | 5.7035 | 5.4966 | 5.4543 | 5.3016 | 5.1484 | 5.0735 | 4.8788 | 4.6136 | 4.3834 | 2.6311 | -0.88564 | -4.073 | -7.3999 | -9.9498 | 10.9218 | 10.3405 | 10.1336 | 10.0913 | 9.9386 | 9.7854 | 9.7105 | 9.5158 | 9.2506 | 9.0204 | 7.2681 | 3.7514 | 0.56398 | -2.7629 | -5.6946 | 6.2848 | 6.2608 | 6.2094 | 6.2118 | 6.0806 | 5.9137 | 5.5355 | 4.3155 | 3.0126 | 1.7095 | -2.0383 | -5.6065 | -8.5234 | -10.2774 | -8.5298 | 10.9218 | 10.8978 | 10.8464 | 10.8488 | 10.7176 | 10.5507 | 10.1725 | 8.9525 | 7.6496 | 6.3465 | 2.5987 | -0.96945 | -3.8864 | -5.6404 | -4.2819 | 6.2848 | 5.9955 | 5.869 | 5.8531 | 5.8173 | 5.7377 | 5.6055 | 5.4332 | 5.1243 | 4.8203 | 3.7287 | 2.2568 | 1.1452 | 0.15654 | -0.18161 | 10.9218 | 10.6325 | 10.506 | 10.4901 | 10.4543 | 10.3747 | 10.2425 | 10.0702 | 9.7613 | 9.4573 | 8.3657 | 6.8938 | 5.7822 | 4.7935 | 4.429 | 6.2848 | 5.9544 | 5.73 | 5.5855 | 5.3197 | 5.0588 | 4.566 | 3.1889 | 1.7771 | 0.3647 | -3.7274 | -7.65 | -10.9195 | -13.0857 | -11.7972 | 10.9218 | 10.5914 | 10.367 | 10.2225 | 9.9567 | 9.6958 | 9.203 | 7.8259 | 6.4141 | 5.0017 | 0.90959 | -3.013 | -6.2825 | -8.4487 | -7.4482 | 401104 | 383846 | NEW MILLS | STALYBRIDGE
| Grane Rd & Prinny Hill | 10.2903 | 10.0367 | 9.5661 | 9.4378 | 9.2485 | 8.9962 | 8.6707 | 8.2426 | 7.7058 | 7.1147 | 4.8348 | 2.3359 | 0.54436 | -1.0151 | -2.1211 | 15.3903 | 15.1367 | 14.6661 | 14.5378 | 14.3485 | 14.0962 | 13.7707 | 13.3426 | 12.8058 | 12.2147 | 9.9348 | 7.4359 | 5.6444 | 4.0849 | 2.9285 | 10.2903 | 10.0396 | 9.7362 | 9.6371 | 9.5145 | 9.3583 | 9.1561 | 8.905 | 8.6391 | 8.3373 | 7.2029 | 5.7979 | 4.3401 | 2.7666 | 1.7299 | 15.3903 | 15.1396 | 14.8362 | 14.7371 | 14.6145 | 14.4583 | 14.2561 | 14.005 | 13.7391 | 13.4373 | 12.3029 | 10.8979 | 9.4401 | 7.8666 | 6.9643 | 10.2903 | 10.0369 | 9.57 | 9.451 | 9.2807 | 9.0608 | 8.7857 | 8.4308 | 8 | 7.5118 | 5.3458 | 2.7047 | 0.75443 | -0.83643 | -1.8188 | 15.3903 | 15.1369 | 14.67 | 14.551 | 14.3807 | 14.1608 | 13.8857 | 13.5308 | 13.1 | 12.6118 | 10.4458 | 7.8047 | 5.8544 | 4.2636 | 3.2055 | 10.2903 | 10.1579 | 9.74 | 9.6493 | 9.4877 | 9.2411 | 8.8348 | 8.0936 | 7.2527 | 6.3574 | 3.6216 | 1.2596 | -0.37166 | -1.3627 | -1.081 | 15.3903 | 15.2579 | 14.84 | 14.7493 | 14.5877 | 14.3411 | 13.9348 | 13.1936 | 12.3527 | 11.4574 | 8.7216 | 6.3596 | 4.7283 | 3.7373 | 3.9356 | 10.2903 | 10.0515 | 9.6121 | 9.5369 | 9.4305 | 9.2529 | 8.9918 | 8.6538 | 8.2208 | 7.73 | 5.9712 | 4.2475 | 3.0924 | 2.3168 | 2.0561 | 15.3903 | 15.1515 | 14.7121 | 14.6369 | 14.5305 | 14.3529 | 14.0918 | 13.7538 | 13.3208 | 12.83 | 11.0712 | 9.3475 | 8.1924 | 7.4168 | 7.1669 | 10.2903 | 10.1299 | 9.6721 | 9.541 | 9.3546 | 9.1228 | 8.7556 | 8.051 | 7.2707 | 6.4334 | 3.692 | 1.0845 | -0.82409 | -2.0173 | -1.854 | 15.3903 | 15.2299 | 14.7721 | 14.641 | 14.4546 | 14.2228 | 13.8556 | 13.151 | 12.3707 | 11.5334 | 8.792 | 6.1845 | 4.2759 | 3.0827 | 3.1884 | 378312 | 422726 | ROSSENDALE | PADIHAM
| Grange | 5.6206 | 4.9302 | 4.7741 | 4.71 | 4.549 | 4.3807 | 4.2427 | 4.1186 | 4.0024 | 3.9081 | 2.9539 | 1.0832 | -0.50814 | -2.1676 | -3.7074 | 11.6206 | 10.9302 | 10.7741 | 10.71 | 10.549 | 10.3807 | 10.2427 | 10.1186 | 10.0024 | 9.9081 | 8.9539 | 7.0832 | 5.4919 | 3.8324 | 2.1989 | 5.6206 | 5.3884 | 5.2702 | 5.1427 | 4.9706 | 4.796 | 4.5687 | 4.2743 | 4.119 | 3.9652 | 3.5064 | 3.0382 | 2.5905 | 2.0342 | 1.5757 | 11.6206 | 11.3884 | 11.2702 | 11.1427 | 10.9706 | 10.796 | 10.5687 | 10.2743 | 10.119 | 9.9652 | 9.5064 | 9.0382 | 8.5905 | 8.0342 | 7.6511 | 5.6206 | 4.8442 | 4.6842 | 4.6405 | 4.5022 | 4.3607 | 4.2632 | 4.1799 | 4.1064 | 4.0504 | 3.2216 | 1.4606 | -0.032242 | -1.5756 | -2.9844 | 11.6206 | 10.8442 | 10.6842 | 10.6405 | 10.5022 | 10.3607 | 10.2632 | 10.1799 | 10.1064 | 10.0504 | 9.2216 | 7.4606 | 5.9678 | 4.4244 | 2.9004 | 5.6206 | 5.2369 | 5.162 | 5.1191 | 4.9936 | 4.8637 | 4.6491 | 4.0596 | 3.4572 | 2.8668 | 1.165 | -0.50494 | -1.8484 | -2.6907 | -2.1621 | 11.6206 | 11.2369 | 11.162 | 11.1191 | 10.9936 | 10.8637 | 10.6491 | 10.0596 | 9.4572 | 8.8668 | 7.165 | 5.4951 | 4.1516 | 3.3093 | 3.7171 | 5.6206 | 5.3412 | 5.2654 | 5.2236 | 5.1494 | 5.0777 | 4.9857 | 4.8531 | 4.6943 | 4.5378 | 3.9575 | 3.2379 | 2.7204 | 2.1742 | 1.9186 | 11.6206 | 11.3412 | 11.2654 | 11.2236 | 11.1494 | 11.0777 | 10.9857 | 10.8531 | 10.6943 | 10.5378 | 9.9575 | 9.2379 | 8.7204 | 8.1742 | 7.9111 | 5.6206 | 4.907 | 4.73 | 4.6286 | 4.4468 | 4.271 | 3.9989 | 3.3396 | 2.6978 | 2.0669 | 0.23936 | -1.5334 | -2.9819 | -3.9659 | -3.6027 | 11.6206 | 10.907 | 10.73 | 10.6286 | 10.4468 | 10.271 | 9.9989 | 9.3396 | 8.6978 | 8.0669 | 6.2394 | 4.4666 | 3.0181 | 2.0341 | 2.3131 | 340240 | 478314 | ULVERSTON | HARKER
| Great Harwood | 11.6603 | 10.6388 | 10.2612 | 10.0448 | 9.7927 | 9.5414 | 9.3217 | 9.1086 | 8.8521 | 8.5977 | 7.1605 | 4.9978 | 3.3629 | 1.8667 | 0.98304 | 19.7803 | 18.7588 | 18.3812 | 18.1648 | 17.9127 | 17.6614 | 17.4417 | 17.2286 | 16.9721 | 16.7177 | 15.2805 | 13.1178 | 11.4829 | 9.9867 | 8.9332 | 11.6603 | 11.423 | 11.2264 | 11.0337 | 10.6887 | 10.268 | 9.7658 | 9.1769 | 8.9698 | 8.7454 | 8.0228 | 7.3146 | 6.7207 | 6.2018 | 5.9369 | 19.7803 | 19.543 | 19.3464 | 19.1537 | 18.8087 | 18.388 | 17.8858 | 17.2969 | 17.0898 | 16.8654 | 16.1428 | 15.4346 | 14.8407 | 14.3218 | 14.0864 | 11.6603 | 10.442 | 9.9751 | 9.6979 | 9.3781 | 9.0561 | 8.7671 | 8.4819 | 8.1747 | 7.8435 | 6.2015 | 4.1149 | 2.7399 | 1.7407 | 1.5917 | 19.7803 | 18.562 | 18.0951 | 17.8179 | 17.4981 | 17.1761 | 16.8871 | 16.6019 | 16.2947 | 15.9635 | 14.3215 | 12.2349 | 10.8599 | 9.8607 | 9.5287 | 11.6603 | 10.8087 | 10.4347 | 10.1822 | 9.8766 | 9.5491 | 9.1155 | 8.3001 | 7.4872 | 6.6907 | 4.4945 | 2.7547 | 1.7283 | 1.4264 | 2.2865 | 19.7803 | 18.9287 | 18.5547 | 18.3022 | 17.9966 | 17.6691 | 17.2355 | 16.4201 | 15.6072 | 14.8107 | 12.6145 | 10.8747 | 9.8483 | 9.5464 | 10.2199 | 11.6603 | 11.2738 | 11.032 | 10.8627 | 10.7003 | 10.5238 | 10.3383 | 10.1437 | 9.8926 | 9.6311 | 8.7878 | 7.9539 | 7.3855 | 6.836 | 6.5346 | 19.7803 | 19.3938 | 19.152 | 18.9827 | 18.8203 | 18.6438 | 18.4583 | 18.2637 | 18.0126 | 17.7511 | 16.9078 | 16.0739 | 15.5055 | 14.956 | 14.6834 | 11.6603 | 10.3294 | 9.8267 | 9.5143 | 9.1546 | 8.7915 | 8.3197 | 7.4454 | 6.595 | 5.7601 | 3.4304 | 1.5461 | 0.37351 | -0.10297 | 0.56059 | 19.7803 | 18.4494 | 17.9467 | 17.6343 | 17.2746 | 16.9115 | 16.4397 | 15.5654 | 14.715 | 13.8801 | 11.5504 | 9.6661 | 8.4935 | 8.017 | 8.5361 | 373765 | 431955 | HUNCOAT | PADIHAM
| Green Lane (Altrincham) | 6.6791 | 5.8553 | 5.5838 | 5.4708 | 5.284 | 5.092 | 4.9257 | 4.7854 | 4.5638 | 4.3815 | 2.5597 | -0.98403 | -4.0315 | -7.3558 | -10.2988 | 11.3161 | 10.4923 | 10.2208 | 10.1078 | 9.921 | 9.729 | 9.5627 | 9.4224 | 9.2008 | 9.0185 | 7.1967 | 3.653 | 0.60555 | -2.7188 | -5.8583 | 6.6791 | 6.4277 | 6.2748 | 6.134 | 5.9294 | 5.6971 | 5.3992 | 5.0473 | 4.7185 | 4.3853 | 3.4042 | 2.4758 | 1.594 | 0.65649 | -0.015885 | 11.3161 | 11.0647 | 10.9118 | 10.771 | 10.5664 | 10.3341 | 10.0362 | 9.6843 | 9.3555 | 9.0223 | 8.0412 | 7.1128 | 6.231 | 5.2935 | 4.7261 | 6.6791 | 5.7662 | 5.5097 | 5.4609 | 5.3419 | 5.2272 | 4.739 | 4.2864 | 3.7673 | 3.2647 | 0.92231 | -2.315 | -5.0893 | -8.0945 | -10.684 | 11.3161 | 10.4032 | 10.1467 | 10.0979 | 9.9789 | 9.8642 | 9.376 | 8.9234 | 8.4043 | 7.9017 | 5.5593 | 2.322 | -0.45234 | -3.4575 | -6.3099 | 6.6791 | 6.3704 | 6.2811 | 6.2746 | 6.1524 | 5.9863 | 5.2156 | 3.7749 | 2.2536 | 0.73493 | -3.2846 | -6.3692 | -8.9207 | -10.5691 | -9.3653 | 11.3161 | 11.0074 | 10.9181 | 10.9116 | 10.7894 | 10.6233 | 9.8526 | 8.4119 | 6.8906 | 5.3719 | 1.3524 | -1.7322 | -4.2837 | -5.9321 | -4.9944 | 6.6791 | 6.3246 | 6.2158 | 6.2158 | 6.1966 | 6.1279 | 6.0363 | 5.95 | 5.75 | 5.5601 | 4.8459 | 3.7585 | 2.9111 | 2.1114 | 1.7387 | 11.3161 | 10.9616 | 10.8528 | 10.8528 | 10.8336 | 10.7649 | 10.6733 | 10.587 | 10.387 | 10.1971 | 9.4829 | 8.3955 | 7.5481 | 6.7484 | 6.3738 | 6.6791 | 5.909 | 5.6169 | 5.4691 | 5.2242 | 4.9835 | 4.1201 | 2.5415 | 0.91154 | -0.71334 | -5.0374 | -8.3626 | -11.1414 | -13.0656 | -12.1765 | 11.3161 | 10.546 | 10.2539 | 10.1061 | 9.8612 | 9.6205 | 8.7571 | 7.1785 | 5.5485 | 3.9237 | -0.40035 | -3.7256 | -6.5044 | -8.4286 | -7.7367 | 378744 | 387772 | ALTRINCHAM | CARRINGTON
| Green Lane (Hazel Grove) | 6.6404 | 5.758 | 5.2809 | 5.0832 | 4.7937 | 4.4981 | 4.2311 | 3.9883 | 3.6627 | 3.3495 | 1.0493 | -3.0847 | -6.5843 | -10.3986 | -13.7884 | 11.2774 | 10.395 | 9.9179 | 9.7202 | 9.4307 | 9.1351 | 8.8681 | 8.6253 | 8.2997 | 7.9865 | 5.6863 | 1.5523 | -1.9473 | -5.7616 | -9.3295 | 6.6404 | 6.4186 | 6.2094 | 6.0115 | 5.7582 | 5.4811 | 5.1203 | 4.6575 | 4.2513 | 3.8387 | 2.5302 | 1.2324 | -0.020397 | -1.4008 | -2.3917 | 11.2774 | 11.0556 | 10.8464 | 10.6485 | 10.3952 | 10.1181 | 9.7573 | 9.2945 | 8.8883 | 8.4757 | 7.1672 | 5.8694 | 4.6166 | 3.2362 | 2.4072 | 6.6404 | 5.6928 | 5.231 | 5.0924 | 4.8631 | 4.6368 | 4.4659 | 4.3285 | 4.1402 | 3.9568 | 1.9824 | -1.856 | -5.1167 | -8.6069 | -11.6196 | 11.2774 | 10.3298 | 9.868 | 9.7294 | 9.5001 | 9.2738 | 9.1029 | 8.9655 | 8.7772 | 8.5938 | 6.6194 | 2.781 | -0.47971 | -3.9699 | -7.2304 | 6.6404 | 6.2013 | 5.8878 | 5.7878 | 5.5603 | 5.2926 | 4.8232 | 3.6056 | 2.311 | 1.0123 | -2.7671 | -6.4514 | -9.452 | -11.4508 | -10.3421 | 11.2774 | 10.8383 | 10.5248 | 10.4248 | 10.1973 | 9.9296 | 9.4602 | 8.2426 | 6.948 | 5.6493 | 1.8699 | -1.8144 | -4.815 | -6.8138 | -5.9582 | 6.6404 | 6.2643 | 5.946 | 5.8546 | 5.7448 | 5.5965 | 5.4234 | 5.2476 | 4.9504 | 4.6451 | 3.5658 | 2.1962 | 1.1309 | 0.14265 | -0.42974 | 11.2774 | 10.9013 | 10.583 | 10.4916 | 10.3818 | 10.2335 | 10.0604 | 9.8846 | 9.5874 | 9.2821 | 8.2028 | 6.8332 | 5.7679 | 4.7796 | 4.2424 | 6.6404 | 5.8306 | 5.3389 | 5.1039 | 4.7552 | 4.4095 | 3.8476 | 2.4963 | 1.1047 | -0.28937 | -4.3551 | -8.2847 | -11.5289 | -13.8298 | -13.0686 | 11.2774 | 10.4676 | 9.9759 | 9.7409 | 9.3922 | 9.0465 | 8.4846 | 7.1333 | 5.7417 | 4.3476 | 0.2819 | -3.6477 | -6.8919 | -9.1928 | -8.6078 | 391570 | 387132 | HAZEL GROVE | BREDBURY
| Green St T11 | 3.418 | 2.8619 | 2.5994 | 2.4655 | 2.3329 | 2.1991 | 2.0751 | 1.9518 | 1.7796 | 1.6196 | 0.84166 | -0.33349 | -1.2593 | -2.1683 | -3.017 | 8.168 | 7.6119 | 7.3494 | 7.2155 | 7.0829 | 6.9491 | 6.8251 | 6.7018 | 6.5296 | 6.3696 | 5.5917 | 4.4165 | 3.4907 | 2.5817 | 1.6697 | 3.418 | 3.2715 | 3.1082 | 2.9896 | 2.8805 | 2.7629 | 2.6197 | 2.4004 | 2.2569 | 2.0704 | 1.526 | 1.0032 | 0.55009 | 0.087239 | -0.23978 | 8.168 | 8.0215 | 7.8582 | 7.7396 | 7.6305 | 7.5129 | 7.3697 | 7.1504 | 7.0069 | 6.8204 | 6.276 | 5.7532 | 5.3001 | 4.8372 | 4.5579 | 3.418 | 2.78 | 2.5015 | 2.3657 | 2.233 | 2.0995 | 1.9749 | 1.8525 | 1.7132 | 1.5905 | 0.92946 | -0.12099 | -0.914 | -1.6338 | -2.1644 | 8.168 | 7.53 | 7.2515 | 7.1157 | 6.983 | 6.8495 | 6.7249 | 6.6025 | 6.4632 | 6.3405 | 5.6795 | 4.629 | 3.836 | 3.1162 | 2.4781 | 3.418 | 3.0237 | 2.8261 | 2.7333 | 2.6355 | 2.5159 | 2.3418 | 1.9963 | 1.6145 | 1.2467 | 0.19385 | -0.81069 | -1.5488 | -2.0305 | -1.5583 | 8.168 | 7.7737 | 7.5761 | 7.4833 | 7.3855 | 7.2659 | 7.0918 | 6.7463 | 6.3645 | 5.9967 | 4.9439 | 3.9393 | 3.2012 | 2.7195 | 3.08 | 3.418 | 3.2186 | 3.0495 | 2.9552 | 2.884 | 2.7983 | 2.7006 | 2.5958 | 2.427 | 2.2594 | 1.731 | 1.1755 | 0.80587 | 0.50141 | 0.45067 | 8.168 | 7.9686 | 7.7995 | 7.7052 | 7.634 | 7.5483 | 7.4506 | 7.3458 | 7.177 | 7.0094 | 6.481 | 5.9255 | 5.5559 | 5.2514 | 5.1835 | 3.418 | 2.759 | 2.4703 | 2.3272 | 2.185 | 2.0447 | 1.8543 | 1.471 | 1.0658 | 0.67704 | -0.42393 | -1.453 | -2.3116 | -2.8662 | -2.4901 | 8.168 | 7.509 | 7.2203 | 7.0772 | 6.935 | 6.7947 | 6.6043 | 6.221 | 5.8158 | 5.427 | 4.3261 | 3.297 | 2.4384 | 1.8838 | 2.171 | 358235 | 404898 | WIGAN | KIRKBY
| Green St T12 & T13 | 4.8368 | 3.5283 | 3.146 | 2.6387 | 1.9931 | 1.3145 | 0.65814 | 0.037615 | -0.61047 | -1.2419 | -3.4717 | -7.5487 | -11.097 | -14.7454 | -18.0172 | 10.3768 | 9.0683 | 8.686 | 8.1787 | 7.5331 | 6.8545 | 6.1981 | 5.5776 | 4.9295 | 4.2981 | 2.0683 | -2.0087 | -5.557 | -9.2054 | -12.6877 | 4.8368 | 4.5088 | 4.2702 | 4.0619 | 3.8104 | 3.5233 | 3.1501 | 2.6798 | 2.3745 | 2.063 | 1.0816 | -0.063058 | -1.1558 | -2.323 | -3.1622 | 10.3768 | 10.0488 | 9.8102 | 9.6019 | 9.3504 | 9.0633 | 8.6901 | 8.2198 | 7.9145 | 7.603 | 6.6216 | 5.4769 | 4.3842 | 3.217 | 2.4984 | 4.8368 | 3.3442 | 2.9374 | 2.4503 | 1.6537 | 0.83342 | -0.016666 | -0.81376 | -1.4671 | -2.0129 | -4.0157 | -7.8793 | -11.1445 | -14.4995 | -17.463 | 10.3768 | 8.8842 | 8.4774 | 7.9903 | 7.1937 | 6.3734 | 5.5233 | 4.7262 | 4.0729 | 3.5271 | 1.5243 | -2.3393 | -5.6045 | -8.9595 | -12.1876 | 4.8368 | 4.053 | 3.8205 | 3.3729 | 2.592 | 1.7693 | 0.65359 | -1.2397 | -3.0474 | -4.7473 | -8.6091 | -12.2435 | -15.2167 | -17.0463 | -15.8548 | 10.3768 | 9.593 | 9.3605 | 8.9129 | 8.132 | 7.3093 | 6.1936 | 4.3003 | 2.4926 | 0.79268 | -3.0691 | -6.7035 | -9.6767 | -11.5063 | -10.5882 | 4.8368 | 4.4661 | 4.3044 | 3.8824 | 3.4398 | 2.969 | 2.4541 | 1.8861 | 1.2252 | 0.54637 | -0.60123 | -1.8663 | -2.7647 | -3.6402 | -3.9082 | 10.3768 | 10.0061 | 9.8444 | 9.4224 | 8.9798 | 8.509 | 7.9941 | 7.4261 | 6.7652 | 6.0864 | 4.9388 | 3.6737 | 2.7753 | 1.8998 | 1.6042 | 4.8368 | 3.4257 | 2.9952 | 2.4536 | 1.5842 | 0.69687 | -0.48251 | -2.471 | -4.3229 | -6.0664 | -10.0929 | -13.9479 | -17.2502 | -19.4473 | -18.5944 | 10.3768 | 8.9657 | 8.5352 | 7.9936 | 7.1242 | 6.2369 | 5.0575 | 3.069 | 1.2171 | -0.52643 | -4.5529 | -8.4079 | -11.7102 | -13.9073 | -13.2527 | 358225 | 404888 | WIGAN | KIRKBY
| Greenfield | 13.6845 | 13.5167 | 13.3529 | 13.1992 | 12.9816 | 12.7623 | 12.5739 | 12.3944 | 12.1623 | 11.9512 | 10.2393 | 7.5618 | 5.3812 | 2.9473 | 0.8725 | 18.1845 | 18.0167 | 17.8529 | 17.6992 | 17.4816 | 17.2623 | 17.0739 | 16.8944 | 16.6623 | 16.4512 | 14.7393 | 12.0618 | 9.8812 | 7.4473 | 5.2509 | 13.6845 | 13.5279 | 13.3734 | 13.2091 | 12.9972 | 12.761 | 12.468 | 12.1041 | 11.8055 | 11.5025 | 10.5904 | 9.6099 | 8.671 | 7.7236 | 7.1088 | 18.1845 | 18.0279 | 17.8734 | 17.7091 | 17.4972 | 17.261 | 16.968 | 16.6041 | 16.3055 | 16.0025 | 15.0904 | 14.1099 | 13.171 | 12.2236 | 11.7049 | 13.6845 | 13.5319 | 13.3939 | 13.2835 | 13.0527 | 12.8287 | 12.6548 | 12.5 | 12.2986 | 12.1197 | 10.5684 | 8.0445 | 5.9874 | 3.9121 | 2.2756 | 18.1845 | 18.0319 | 17.8939 | 17.7835 | 17.5527 | 17.3287 | 17.1548 | 17 | 16.7986 | 16.6197 | 15.0684 | 12.5445 | 10.4874 | 8.4121 | 6.6077 | 13.6845 | 13.7537 | 13.6976 | 13.6311 | 13.4203 | 13.1864 | 12.8307 | 11.9812 | 11.0779 | 10.2402 | 7.813 | 5.4237 | 3.4915 | 2.2025 | 2.9418 | 18.1845 | 18.2537 | 18.1976 | 18.1311 | 17.9203 | 17.6864 | 17.3307 | 16.4812 | 15.5779 | 14.7402 | 12.313 | 9.9237 | 7.9915 | 6.7025 | 7.2705 | 13.6845 | 13.5537 | 13.4371 | 13.3523 | 13.2502 | 13.1194 | 12.972 | 12.8174 | 12.589 | 12.3639 | 11.4393 | 10.249 | 9.4146 | 8.6651 | 8.2602 | 18.1845 | 18.0537 | 17.9371 | 17.8523 | 17.7502 | 17.6194 | 17.472 | 17.3174 | 17.089 | 16.8639 | 15.9393 | 14.749 | 13.9146 | 13.1651 | 12.7976 | 13.6845 | 13.6762 | 13.5296 | 13.3641 | 13.0631 | 12.7673 | 12.3379 | 11.3832 | 10.4023 | 9.4882 | 6.7958 | 4.1885 | 2.0548 | 0.51907 | 0.98215 | 18.1845 | 18.1762 | 18.0296 | 17.8641 | 17.5631 | 17.2673 | 16.8379 | 15.8832 | 14.9023 | 13.9882 | 11.2958 | 8.6885 | 6.5548 | 5.0191 | 5.3715 | 399322 | 404583 | HARTSHEAD-HEYROD | STALYBRIDGE
| Greenhill | 16.1756 | 14.5616 | 13.5805 | 12.5922 | 11.647 | 10.674 | 9.7053 | 8.7147 | 7.8313 | 7.1728 | 3.6808 | -1.9952 | -6.0246 | -9.317 | -11.2425 | 30.1756 | 28.5616 | 27.5805 | 26.5922 | 25.647 | 24.674 | 23.7053 | 22.7147 | 21.8313 | 21.1728 | 17.6808 | 12.0048 | 7.9754 | 4.683 | 2.6922 | 16.1756 | 15.6189 | 15.1348 | 14.7703 | 14.4028 | 13.9899 | 13.4901 | 12.8775 | 12.3487 | 11.8047 | 10.1548 | 8.4732 | 6.5406 | 2.9323 | 0.66163 | 30.1756 | 29.6189 | 29.1348 | 28.7703 | 28.4028 | 27.9899 | 27.4901 | 26.8775 | 26.3487 | 25.8047 | 24.1548 | 22.4732 | 20.5406 | 16.9323 | 14.9837 | 16.1756 | 14.2242 | 13.0638 | 11.9185 | 10.8063 | 9.6531 | 8.4858 | 7.2836 | 6.2594 | 5.4502 | 2.1635 | -2.9056 | -7.3171 | -10.8137 | -12.4198 | 30.1756 | 28.2242 | 27.0638 | 25.9185 | 24.8063 | 23.6531 | 22.4858 | 21.2836 | 20.2594 | 19.4502 | 16.1635 | 11.0944 | 6.6829 | 3.1863 | 1.5811 | 16.1756 | 14.977 | 14.0402 | 12.9997 | 11.9694 | 10.8571 | 9.5384 | 7.665 | 5.9708 | 4.5373 | 0.56391 | -4.4392 | -7.812 | -9.9494 | -10.0631 | 30.1756 | 28.977 | 28.0402 | 26.9997 | 25.9694 | 24.8571 | 23.5384 | 21.665 | 19.9708 | 18.5373 | 14.5639 | 9.5608 | 6.188 | 4.0506 | 3.8837 | 16.1756 | 15.3335 | 14.559 | 13.669 | 12.8908 | 12.0495 | 11.1437 | 10.1881 | 9.3007 | 8.6106 | 6.5047 | 2.6887 | -0.67223 | -3.4794 | -4.9835 | 30.1756 | 29.3335 | 28.559 | 27.669 | 26.8908 | 26.0495 | 25.1437 | 24.1881 | 23.3007 | 22.6106 | 20.5047 | 16.6887 | 13.3278 | 10.5206 | 9.1898 | 16.1756 | 14.2905 | 13.1199 | 11.9528 | 10.8091 | 9.6381 | 8.2729 | 6.3007 | 4.5558 | 3.076 | -1.0254 | -5.6213 | -9.6388 | -12.3437 | -12.8862 | 30.1756 | 28.2905 | 27.1199 | 25.9528 | 24.8091 | 23.6381 | 22.2729 | 20.3007 | 18.5558 | 17.076 | 12.9746 | 8.3787 | 4.3612 | 1.6563 | 1.1426 | 393262 | 404755 | GREENHILL | WHITEGATE
| Griffin | 7.6613 | 7.0589 | 6.8108 | 6.5787 | 6.2287 | 5.8586 | 5.5105 | 5.1652 | 4.7328 | 4.3153 | 1.8617 | -1.8811 | -4.6904 | -7.213 | -8.6775 | 12.3013 | 11.6989 | 11.4508 | 11.2187 | 10.8687 | 10.4986 | 10.1505 | 9.8052 | 9.3728 | 8.9553 | 6.5017 | 2.7589 | -0.050449 | -2.573 | -4.3616 | 7.6613 | 7.3683 | 7.2155 | 7.0141 | 6.744 | 6.4443 | 6.0537 | 5.5731 | 5.2545 | 4.916 | 3.8428 | 2.6762 | 1.6171 | 0.54192 | -0.18064 | 12.3013 | 12.0083 | 11.8555 | 11.6541 | 11.384 | 11.0843 | 10.6937 | 10.2131 | 9.8945 | 9.556 | 8.4828 | 7.3162 | 6.2571 | 5.1819 | 4.5618 | 7.6613 | 6.9073 | 6.5386 | 6.1991 | 5.7325 | 5.2416 | 4.786 | 4.3241 | 3.8286 | 3.2822 | 0.38876 | -3.323 | -5.7848 | -7.596 | -7.9984 | 12.3013 | 11.5473 | 11.1786 | 10.8391 | 10.3725 | 9.8816 | 9.426 | 8.9641 | 8.4686 | 7.9222 | 5.0288 | 1.317 | -1.1448 | -2.956 | -3.6137 | 7.6613 | 7.4062 | 7.1787 | 6.902 | 6.4723 | 5.9894 | 5.3022 | 3.909 | 2.5188 | 1.1644 | -2.5504 | -5.4994 | -7.1786 | -7.568 | -6.3923 | 12.3013 | 12.0462 | 11.8187 | 11.542 | 11.1123 | 10.6294 | 9.9422 | 8.549 | 7.1588 | 5.8044 | 2.0896 | -0.85938 | -2.5386 | -2.928 | -2.0211 | 7.6613 | 7.2967 | 7.1365 | 6.9911 | 6.8086 | 6.5891 | 6.3176 | 5.9978 | 5.5868 | 5.1254 | 3.5829 | 1.8883 | 0.6291 | -0.45911 | -0.89977 | 12.3013 | 11.9367 | 11.7765 | 11.6311 | 11.4486 | 11.2291 | 10.9576 | 10.6378 | 10.2268 | 9.7654 | 8.2229 | 6.5283 | 5.2691 | 4.1809 | 3.7579 | 7.6613 | 7.1752 | 6.8072 | 6.402 | 5.8545 | 5.2908 | 4.4977 | 2.9652 | 1.4843 | 0.037603 | -3.9822 | -7.2151 | -9.1756 | -9.8544 | -8.9228 | 12.3013 | 11.8152 | 11.4472 | 11.042 | 10.4945 | 9.9308 | 9.1377 | 7.6052 | 6.1243 | 4.6776 | 0.65782 | -2.5751 | -4.5356 | -5.2144 | -4.4726 | 367171 | 427130 | LOWER DARWEN | ROCHDALE
| Hadfield | 13.1026 | 12.9598 | 12.6353 | 12.3297 | 11.983 | 11.6066 | 11.2267 | 10.8052 | 10.3739 | 9.9635 | 8.1698 | 5.6793 | 3.6972 | 1.0773 | -1.3134 | 17.7396 | 17.5968 | 17.2723 | 16.9667 | 16.62 | 16.2436 | 15.8637 | 15.4422 | 15.0109 | 14.6005 | 12.8068 | 10.3163 | 8.3342 | 5.7143 | 3.0932 | 13.1026 | 13.0596 | 12.8727 | 12.7402 | 12.6357 | 12.519 | 12.3833 | 12.2255 | 11.9134 | 11.5756 | 10.5945 | 9.693 | 8.8098 | 7.7612 | 7.1457 | 17.7396 | 17.6966 | 17.5097 | 17.3772 | 17.2727 | 17.156 | 17.0203 | 16.8625 | 16.5504 | 16.2126 | 15.2315 | 14.33 | 13.4468 | 12.3982 | 11.8665 | 13.1026 | 12.9373 | 12.5864 | 12.2433 | 11.8508 | 11.4203 | 10.9772 | 10.4772 | 10.0505 | 9.6508 | 7.8782 | 5.3932 | 3.462 | 1.7917 | -0.061325 | 17.7396 | 17.5743 | 17.2234 | 16.8803 | 16.4878 | 16.0573 | 15.6142 | 15.1142 | 14.6875 | 14.2878 | 12.5152 | 10.0302 | 8.099 | 6.4287 | 4.3078 | 13.1026 | 13.0229 | 12.7615 | 12.5128 | 12.2073 | 11.7977 | 11.2435 | 10.3182 | 9.4328 | 8.5702 | 5.8564 | 2.9598 | 0.61163 | -0.76145 | 0.41751 | 17.7396 | 17.6599 | 17.3985 | 17.1498 | 16.8443 | 16.4347 | 15.8805 | 14.9552 | 14.0698 | 13.2072 | 10.4934 | 7.5968 | 5.2486 | 3.8756 | 4.7799 | 13.1026 | 12.9973 | 12.7336 | 12.5341 | 12.356 | 12.1026 | 11.7861 | 11.4358 | 11.048 | 10.6595 | 9.4353 | 8.2 | 7.3337 | 6.6573 | 6.4757 | 17.7396 | 17.6343 | 17.3706 | 17.1711 | 16.993 | 16.7396 | 16.4231 | 16.0728 | 15.685 | 15.2965 | 14.0723 | 12.837 | 11.9707 | 11.2943 | 11.0978 | 13.1026 | 12.9647 | 12.6344 | 12.3053 | 11.9365 | 11.5406 | 11.0268 | 10.0913 | 9.1877 | 8.3122 | 5.1738 | 2.1742 | -0.31324 | -1.8654 | -0.89134 | 17.7396 | 17.6017 | 17.2714 | 16.9423 | 16.5735 | 16.1776 | 15.6638 | 14.7283 | 13.8247 | 12.9492 | 9.8108 | 6.8112 | 4.3238 | 2.7716 | 3.5261 | 401790 | 395876 | HYDE | STALYBRIDGE
| Hall Cross | 4.0676 | 2.5156 | 1.9092 | 1.4193 | 0.79034 | 0.16354 | -0.4289 | -0.85734 | -1.3195 | -1.7456 | -3.9654 | -7.5117 | -10.3503 | -13.3393 | -16.0463 | 8.7046 | 7.1526 | 6.5462 | 6.0563 | 5.4273 | 4.8005 | 4.2081 | 3.7797 | 3.3175 | 2.8914 | 0.67159 | -2.8747 | -5.7133 | -8.7023 | -11.4854 | 4.0676 | 3.3706 | 2.9516 | 2.6318 | 2.2783 | 1.9138 | 1.456 | 0.84366 | 0.28229 | -0.28445 | -1.951 | -3.7078 | -5.2867 | -6.9755 | -8.1145 | 8.7046 | 8.0076 | 7.5886 | 7.2688 | 6.9153 | 6.5508 | 6.093 | 5.4807 | 4.9193 | 4.3526 | 2.686 | 0.92916 | -0.64968 | -2.3385 | -3.2914 | 4.0676 | 2.3394 | 1.7314 | 1.305 | 0.73733 | 0.18069 | -0.31295 | -0.63356 | -0.93558 | -1.2378 | -3.0809 | -6.2887 | -8.8157 | -11.4117 | -13.6479 | 8.7046 | 6.9764 | 6.3684 | 5.942 | 5.3743 | 4.8177 | 4.3241 | 4.0034 | 3.7014 | 3.3992 | 1.5561 | -1.6517 | -4.1787 | -6.7747 | -9.1758 | 4.0676 | 3.0802 | 2.659 | 2.2843 | 1.7442 | 1.1777 | 0.48214 | -0.60184 | -1.6821 | -2.7696 | -5.8873 | -8.9538 | -11.2748 | -12.7813 | -12.0644 | 8.7046 | 7.7172 | 7.296 | 6.9213 | 6.3812 | 5.8147 | 5.1191 | 4.0352 | 2.9549 | 1.8674 | -1.2503 | -4.3168 | -6.6378 | -8.1443 | -7.6032 | 4.0676 | 3.0044 | 2.5309 | 2.1269 | 1.6445 | 1.1364 | 0.60864 | 0.19953 | -0.29625 | -0.78442 | -2.3614 | -4.1951 | -5.4541 | -6.5965 | -7.1502 | 8.7046 | 7.6414 | 7.1679 | 6.7639 | 6.2815 | 5.7734 | 5.2456 | 4.8365 | 4.3408 | 3.8526 | 2.2756 | 0.44195 | -0.81708 | -1.9595 | -2.4829 | 4.0676 | 2.3629 | 1.7141 | 1.207 | 0.54722 | -0.09864 | -0.88853 | -2.1058 | -3.2783 | -4.4563 | -7.8453 | -11.1361 | -13.6656 | -15.4089 | -14.9572 | 8.7046 | 6.9999 | 6.3511 | 5.844 | 5.1842 | 4.5384 | 3.7485 | 2.5312 | 1.3587 | 0.18067 | -3.2083 | -6.4991 | -9.0286 | -10.7719 | -10.4372 | 342288 | 430650 | PEEL | PENWORTHAM
| Handforth | 10.7698 | 8.8983 | 8.1158 | 7.2273 | 6.3785 | 5.5142 | 4.6581 | 3.8181 | 2.9379 | 2.0874 | -1.0273 | -4.3904 | -6.3537 | -8.3797 | -10.3123 | 15.4068 | 13.5353 | 12.7528 | 11.8643 | 11.0155 | 10.1512 | 9.2951 | 8.4551 | 7.5749 | 6.7244 | 3.6097 | 0.24662 | -1.7167 | -3.7427 | -5.7183 | 10.7698 | 10.1888 | 9.9246 | 9.7406 | 9.5079 | 9.2635 | 8.954 | 8.549 | 8.1955 | 7.8403 | 6.7729 | 5.5611 | 4.415 | 3.1825 | 2.3404 | 15.4068 | 14.8258 | 14.5616 | 14.3776 | 14.1449 | 13.9005 | 13.591 | 13.186 | 12.8325 | 12.4773 | 11.4099 | 10.1981 | 9.052 | 7.8195 | 7.1156 | 10.7698 | 8.6358 | 7.8203 | 6.9723 | 6.1661 | 5.351 | 4.5663 | 3.8021 | 3.0128 | 2.2382 | -0.65365 | -3.8435 | -5.6545 | -7.4875 | -9.191 | 15.4068 | 13.2728 | 12.4573 | 11.6093 | 10.8031 | 9.988 | 9.2033 | 8.4391 | 7.6498 | 6.8752 | 3.9834 | 0.79345 | -1.0175 | -2.8505 | -4.6407 | 10.7698 | 9.4722 | 8.8615 | 8.0557 | 7.2613 | 6.4262 | 5.5044 | 4.238 | 2.92 | 1.6029 | -2.1691 | -5.2427 | -6.8942 | -7.953 | -7.5806 | 15.4068 | 14.1092 | 13.4985 | 12.6927 | 11.8983 | 11.0632 | 10.1414 | 8.875 | 7.557 | 6.2399 | 2.4679 | -0.60575 | -2.2572 | -3.316 | -3.0377 | 10.7698 | 9.8045 | 9.2474 | 8.4381 | 7.7176 | 6.9626 | 6.193 | 5.4149 | 4.553 | 3.6982 | 1.139 | -0.87294 | -1.6307 | -2.4319 | -2.9313 | 15.4068 | 14.4415 | 13.8844 | 13.0751 | 12.3546 | 11.5996 | 10.83 | 10.0519 | 9.19 | 8.3352 | 5.776 | 3.7641 | 3.0063 | 2.2051 | 1.7519 | 10.7698 | 8.5579 | 7.6866 | 6.7834 | 5.9034 | 5.0163 | 4.0308 | 2.674 | 1.2925 | -0.087356 | -4.0551 | -7.29 | -9.0934 | -10.3183 | -10.1335 | 15.4068 | 13.1949 | 12.3236 | 11.4204 | 10.5404 | 9.6533 | 8.6678 | 7.311 | 5.9295 | 4.5496 | 0.58186 | -2.653 | -4.4564 | -5.6813 | -5.5491 | 385958 | 383397 | MOSS NOOK | SOUTH MANCHESTER
| Hanging Bridge | 2.2211 | 1.5036 | 1.3111 | 1.2224 | 1.0889 | 0.945 | 0.76323 | 0.56364 | 0.32395 | 0.083803 | -1.6406 | -3.7515 | -5.2185 | -6.384 | -7.1658 | 6.2211 | 5.5036 | 5.3111 | 5.2224 | 5.0889 | 4.945 | 4.7632 | 4.5636 | 4.3239 | 4.0838 | 2.3594 | 0.24846 | -1.2185 | -2.384 | -3.1605 | 2.2211 | 2.087 | 2.0199 | 1.9596 | 1.8367 | 1.7013 | 1.5174 | 1.2532 | 1.0475 | 0.83415 | 0.13548 | -0.82305 | -2.0181 | -3.3654 | -4.1683 | 6.2211 | 6.087 | 6.0199 | 5.9596 | 5.8367 | 5.7013 | 5.5174 | 5.2532 | 5.0475 | 4.8342 | 4.1355 | 3.177 | 1.9819 | 0.63463 | -0.058536 | 2.2211 | 1.3963 | 1.1856 | 1.0979 | 0.96749 | 0.82927 | 0.70188 | 0.56644 | 0.415 | 0.26618 | -1.5369 | -3.9036 | -5.6214 | -6.9852 | -7.8544 | 6.2211 | 5.3963 | 5.1856 | 5.0979 | 4.9675 | 4.8293 | 4.7019 | 4.5664 | 4.415 | 4.2662 | 2.4631 | 0.096385 | -1.6214 | -2.9852 | -3.8387 | 2.2211 | 1.6985 | 1.5516 | 1.4691 | 1.3484 | 1.2117 | 1.0145 | 0.60853 | 0.15458 | -0.37353 | -2.1384 | -4.2612 | -5.7078 | -6.6812 | -6.7907 | 6.2211 | 5.6985 | 5.5516 | 5.4691 | 5.3484 | 5.2117 | 5.0145 | 4.6085 | 4.1546 | 3.6265 | 1.8616 | -0.26117 | -1.7078 | -2.6812 | -2.797 | 2.2211 | 2.015 | 1.9178 | 1.8478 | 1.7714 | 1.6892 | 1.5898 | 1.4175 | 1.1744 | 0.91786 | -0.3323 | -2.217 | -3.5417 | -4.5711 | -5.0329 | 6.2211 | 6.015 | 5.9178 | 5.8478 | 5.7714 | 5.6892 | 5.5898 | 5.4175 | 5.1744 | 4.9179 | 3.6677 | 1.783 | 0.45834 | -0.57109 | -0.98875 | 2.2211 | 1.3622 | 1.138 | 1.0315 | 0.89121 | 0.74923 | 0.5524 | 0.085357 | -0.43778 | -0.97502 | -2.6142 | -4.418 | -5.9886 | -7.0996 | -7.306 | 6.2211 | 5.3622 | 5.138 | 5.0315 | 4.8912 | 4.7492 | 4.5524 | 4.0854 | 3.5622 | 3.025 | 1.3858 | -0.41797 | -1.9886 | -3.0996 | -3.2932 | 346186 | 417486 | WRIGHTINGTON | PENWORTHAM
| Hareholme | 8.8232 | 8.6184 | 8.4153 | 8.1196 | 7.7976 | 7.466 | 7.181 | 6.8437 | 6.4045 | 6.0023 | 3.5082 | -0.68522 | -4.1949 | -8.0828 | -11.3541 | 13.4602 | 13.2554 | 13.0523 | 12.7566 | 12.4346 | 12.103 | 11.818 | 11.4807 | 11.0415 | 10.6393 | 8.1452 | 3.9518 | 0.44211 | -3.4458 | -6.9546 | 8.8232 | 8.5862 | 8.3547 | 8.1029 | 7.7755 | 7.4 | 6.9348 | 6.3686 | 5.9702 | 5.5332 | 4.035 | 2.6322 | 1.3998 | 0.17952 | -0.59254 | 13.4602 | 13.2232 | 12.9917 | 12.7399 | 12.4125 | 12.037 | 11.5718 | 11.0056 | 10.6072 | 10.1702 | 8.672 | 7.2692 | 6.0368 | 4.8165 | 4.158 | 8.8232 | 8.6457 | 8.4779 | 8.2403 | 7.982 | 7.7255 | 7.5432 | 7.3332 | 7.0248 | 6.7318 | 4.4274 | 0.51289 | -2.6872 | -6.023 | -8.9938 | 13.4602 | 13.2827 | 13.1149 | 12.8773 | 12.619 | 12.3625 | 12.1802 | 11.9702 | 11.6618 | 11.3688 | 9.0644 | 5.1499 | 1.9498 | -1.386 | -4.6571 | 8.8232 | 8.9758 | 8.9313 | 8.7582 | 8.5289 | 8.2592 | 7.772 | 6.4386 | 5.0406 | 3.6551 | -0.32748 | -4.1505 | -7.2823 | -9.2984 | -7.9267 | 13.4602 | 13.6128 | 13.5683 | 13.3952 | 13.1659 | 12.8962 | 12.409 | 11.0756 | 9.6776 | 8.2921 | 4.3095 | 0.48645 | -2.6453 | -4.6614 | -3.6 | 8.8232 | 8.6561 | 8.5186 | 8.3322 | 8.2079 | 8.0364 | 7.829 | 7.598 | 7.1953 | 6.7836 | 5.4108 | 3.8497 | 2.7136 | 1.7194 | 1.3127 | 13.4602 | 13.2931 | 13.1556 | 12.9692 | 12.8449 | 12.6734 | 12.466 | 12.235 | 11.8323 | 11.4206 | 10.0478 | 8.4867 | 7.3506 | 6.3564 | 5.9557 | 8.8232 | 8.8777 | 8.7012 | 8.379 | 8.0125 | 7.6465 | 7.0464 | 5.5538 | 4.047 | 2.5541 | -1.7532 | -5.917 | -9.3609 | -11.7533 | -10.8291 | 13.4602 | 13.5147 | 13.3382 | 13.016 | 12.6495 | 12.2835 | 11.6834 | 10.1908 | 8.684 | 7.1911 | 2.8838 | -1.28 | -4.7239 | -7.1163 | -6.4052 | 382535 | 422283 | ROSSENDALE | PADIHAM
| Harpurhey | 11.2638 | 10.3295 | 9.3226 | 8.5248 | 7.2884 | 6.2425 | 5.8786 | 5.5575 | 5.2168 | 5.0571 | 3.6304 | 0.91573 | -1.3527 | -3.6236 | -5.7536 | 15.9038 | 14.9695 | 13.9626 | 13.1648 | 11.9284 | 10.8825 | 10.5186 | 10.1975 | 9.8568 | 9.6971 | 8.2704 | 5.5557 | 3.2873 | 1.0164 | -1.265 | 11.2638 | 10.9009 | 10.5256 | 10.2165 | 9.8579 | 9.4997 | 9.2902 | 9.0015 | 8.7463 | 8.4895 | 7.7333 | 6.9896 | 6.2904 | 5.5291 | 5.0583 | 15.9038 | 15.5409 | 15.1656 | 14.8565 | 14.4979 | 14.1397 | 13.9302 | 13.6415 | 13.3863 | 13.1295 | 12.3733 | 11.6296 | 10.9304 | 10.1691 | 9.7714 | 11.2638 | 10.3033 | 9.309 | 8.5497 | 7.3574 | 6.3577 | 6.0611 | 5.8096 | 5.5437 | 5.4485 | 4.2224 | 1.6736 | -0.45042 | -2.5535 | -4.5452 | 15.9038 | 14.9433 | 13.949 | 13.1897 | 11.9974 | 10.9977 | 10.7011 | 10.4496 | 10.1837 | 10.0885 | 8.8624 | 6.3136 | 4.1896 | 2.0865 | -0.088899 | 11.2638 | 10.7048 | 9.8074 | 9.064 | 7.8619 | 6.8291 | 6.3344 | 5.351 | 4.3312 | 3.4747 | 1.0128 | -1.3918 | -3.3173 | -4.3859 | -3.5132 | 15.9038 | 15.3448 | 14.4474 | 13.704 | 12.5019 | 11.4691 | 10.9744 | 9.991 | 8.9712 | 8.1147 | 5.6528 | 3.2482 | 1.3227 | 0.25413 | 0.93845 | 11.2638 | 10.4552 | 9.5052 | 8.796 | 7.7517 | 6.8745 | 6.627 | 6.3576 | 6.0129 | 5.8213 | 5.1172 | 4.2651 | 3.5716 | 2.9448 | 2.7075 | 15.9038 | 15.0952 | 14.1452 | 13.436 | 12.3917 | 11.5145 | 11.267 | 10.9976 | 10.6529 | 10.4613 | 9.7572 | 8.9051 | 8.2116 | 7.5848 | 7.3343 | 11.2638 | 10.5298 | 9.5339 | 8.688 | 7.4051 | 6.3221 | 5.764 | 4.6915 | 3.6014 | 2.6748 | 0.004158 | -2.564 | -4.6526 | -5.9177 | -5.2822 | 15.9038 | 15.1698 | 14.1739 | 13.328 | 12.0451 | 10.9621 | 10.404 | 9.3315 | 8.2414 | 7.3148 | 4.6442 | 2.076 | -0.012628 | -1.2777 | -0.77859 | 385907 | 402469 | RED BANK | WHITEGATE
| Harwood | 3.1867 | 2.9995 | 2.8974 | 2.7753 | 2.2352 | 1.677 | 1.1581 | 0.70032 | 0.20166 | -0.25858 | -3.0228 | -7.4362 | -10.6075 | -13.8806 | -17.0753 | 7.4867 | 7.2995 | 7.1974 | 7.0753 | 6.5352 | 5.977 | 5.4581 | 5.0003 | 4.5017 | 4.0414 | 1.2772 | -3.1362 | -6.3075 | -9.5806 | -12.9523 | 3.1867 | 3.053 | 2.9737 | 2.8723 | 2.6886 | 2.4606 | 2.1575 | 1.77 | 1.4086 | 1.039 | -0.1051 | -1.2665 | -2.3429 | -3.4382 | -4.1563 | 7.4867 | 7.353 | 7.2737 | 7.1723 | 6.9886 | 6.7606 | 6.4575 | 6.07 | 5.7086 | 5.339 | 4.1949 | 3.0335 | 1.9571 | 0.86182 | 0.25735 | 3.1867 | 3.014 | 2.9473 | 2.884 | 2.411 | 1.9315 | 1.5218 | 1.1926 | 0.82743 | 0.40577 | -2.2081 | -6.4199 | -9.4304 | -12.3845 | -15.1303 | 7.4867 | 7.314 | 7.2473 | 7.184 | 6.711 | 6.2315 | 5.8218 | 5.4926 | 5.1274 | 4.7058 | 2.0919 | -2.1199 | -5.1304 | -8.0845 | -11.0006 | 3.1867 | 3.4222 | 3.4753 | 3.4452 | 2.9618 | 2.4268 | 1.734 | 0.38656 | -1.0261 | -2.4274 | -6.5222 | -10.5634 | -13.3378 | -14.975 | -13.9287 | 7.4867 | 7.7222 | 7.7753 | 7.7452 | 7.2618 | 6.7268 | 6.034 | 4.6866 | 3.2739 | 1.8726 | -2.2222 | -6.2634 | -9.0378 | -10.675 | -9.8579 | 3.1867 | 3.0671 | 3.0414 | 3.059 | 2.7871 | 2.4625 | 2.0984 | 1.721 | 1.238 | 0.75944 | -0.92351 | -2.9166 | -3.9551 | -4.9347 | -5.443 | 7.4867 | 7.3671 | 7.3414 | 7.359 | 7.0871 | 6.7625 | 6.3984 | 6.021 | 5.538 | 5.0594 | 3.3765 | 1.3834 | 0.34493 | -0.63471 | -1.1237 | 3.1867 | 3.2942 | 3.2164 | 3.0483 | 2.4423 | 1.8217 | 1.0293 | -0.44759 | -1.975 | -3.4893 | -7.9107 | -12.2124 | -15.2328 | -17.1644 | -16.4571 | 7.4867 | 7.5942 | 7.5164 | 7.3483 | 6.7423 | 6.1217 | 5.3293 | 3.8524 | 2.325 | 0.81071 | -3.6107 | -7.9124 | -10.9328 | -12.8644 | -12.3118 | 374043 | 410941 | BOLTON | KEARSLEY
| Hattersley | 7.1136 | 4.7058 | 4.0855 | 3.9611 | 3.3459 | 2.6593 | 1.9938 | 1.3633 | 0.64282 | -0.054665 | -2.9834 | -7.0842 | -10.7509 | -13.7714 | -16.2975 | 10.6136 | 8.2058 | 7.5855 | 7.4611 | 6.8459 | 6.1593 | 5.4938 | 4.8633 | 4.1428 | 3.4453 | 0.51665 | -3.5842 | -7.2509 | -10.2714 | -12.8546 | 7.1136 | 6.3047 | 5.98 | 5.7964 | 5.1956 | 4.5361 | 3.8128 | 3.0269 | 2.4515 | 1.8766 | -0.34888 | -2.7199 | -5.0136 | -6.6837 | -7.5859 | 10.6136 | 9.8047 | 9.48 | 9.2964 | 8.6956 | 8.0361 | 7.3128 | 6.5269 | 5.9515 | 5.3766 | 3.1511 | 0.78015 | -1.5136 | -3.1837 | -3.9297 | 7.1136 | 4.3176 | 3.4638 | 3.1846 | 2.5224 | 1.8023 | 1.0605 | 0.36012 | -0.39514 | -1.1679 | -3.8787 | -7.7934 | -11.3071 | -14.1345 | -16.4508 | 10.6136 | 7.8176 | 6.9638 | 6.6846 | 6.0224 | 5.3023 | 4.5605 | 3.8601 | 3.1049 | 2.3321 | -0.37873 | -4.2934 | -7.8071 | -10.6345 | -13.0461 | 7.1136 | 5.2562 | 4.6554 | 4.4738 | 3.8708 | 3.0577 | 2.1222 | 0.71097 | -0.75897 | -2.2184 | -6.0752 | -9.9466 | -13.2684 | -15.0943 | -14.6711 | 10.6136 | 8.7562 | 8.1554 | 7.9738 | 7.3708 | 6.5577 | 5.6222 | 4.211 | 2.741 | 1.2816 | -2.5752 | -6.4466 | -9.7684 | -11.5943 | -11.2736 | 7.1136 | 5.6719 | 5.2807 | 5.2076 | 4.7514 | 4.2472 | 3.697 | 3.1266 | 2.4308 | 1.7307 | -0.48715 | -2.8952 | -4.9121 | -6.1742 | -6.8207 | 10.6136 | 9.1719 | 8.7807 | 8.7076 | 8.2514 | 7.7472 | 7.197 | 6.6266 | 5.9308 | 5.2307 | 3.0129 | 0.60475 | -1.4121 | -2.6742 | -3.2473 | 7.1136 | 4.0342 | 3.1172 | 2.8434 | 2.1658 | 1.2995 | 0.2983 | -1.2078 | -2.7558 | -4.2925 | -8.3784 | -12.4389 | -15.9449 | -17.9955 | -17.8335 | 10.6136 | 7.5342 | 6.6172 | 6.3434 | 5.6658 | 4.7995 | 3.7983 | 2.2922 | 0.74419 | -0.79248 | -4.8784 | -8.9389 | -12.4449 | -14.4955 | -14.3782 | 398419 | 395120 | HYDE | STALYBRIDGE
| Haverthwaite | 4.7543 | 4.445 | 4.329 | 4.2762 | 4.1849 | 4.0848 | 3.9947 | 3.9136 | 3.8194 | 3.7401 | 3.1929 | 2.2265 | 1.3376 | 0.49255 | -0.3274 | 7.2543 | 6.945 | 6.829 | 6.7762 | 6.6849 | 6.5848 | 6.4947 | 6.4136 | 6.3194 | 6.2401 | 5.6929 | 4.7265 | 3.8376 | 2.9926 | 2.1039 | 4.7543 | 4.642 | 4.5417 | 4.4639 | 4.3877 | 4.3337 | 4.2657 | 4.1814 | 4.092 | 4.0041 | 3.7459 | 3.4921 | 3.2136 | 2.8046 | 2.375 | 7.2543 | 7.142 | 7.0417 | 6.9639 | 6.8877 | 6.8337 | 6.7657 | 6.6814 | 6.592 | 6.5041 | 6.2459 | 5.9921 | 5.7136 | 5.3046 | 4.9584 | 4.7543 | 4.4019 | 4.2785 | 4.2251 | 4.1338 | 4.0341 | 3.9439 | 3.8638 | 3.7887 | 3.7299 | 3.2437 | 2.345 | 1.5253 | 0.79157 | 0.12272 | 7.2543 | 6.9019 | 6.7785 | 6.7251 | 6.6338 | 6.5341 | 6.4439 | 6.3638 | 6.2887 | 6.2299 | 5.7437 | 4.845 | 4.0253 | 3.2916 | 2.527 | 4.7543 | 4.555 | 4.4575 | 4.3698 | 4.2713 | 4.1664 | 4.0127 | 3.7035 | 3.3684 | 3.0034 | 1.9602 | 0.99281 | 0.28539 | -0.036328 | 0.3855 | 7.2543 | 7.055 | 6.9575 | 6.8698 | 6.7713 | 6.6664 | 6.5127 | 6.2035 | 5.8684 | 5.5034 | 4.4602 | 3.4928 | 2.7854 | 2.4637 | 2.7871 | 4.7543 | 4.6063 | 4.5163 | 4.4634 | 4.4095 | 4.371 | 4.3298 | 4.2768 | 4.1875 | 4.0989 | 3.7455 | 3.2853 | 2.974 | 2.643 | 2.4519 | 7.2543 | 7.1063 | 7.0163 | 6.9634 | 6.9095 | 6.871 | 6.8298 | 6.7768 | 6.6875 | 6.5989 | 6.2455 | 5.7853 | 5.474 | 5.143 | 4.9286 | 4.7543 | 4.4154 | 4.2781 | 4.1698 | 4.0528 | 3.938 | 3.7767 | 3.4509 | 3.1141 | 2.7852 | 1.7292 | 0.74043 | 0.0018751 | -0.36696 | -0.007701 | 7.2543 | 6.9154 | 6.7781 | 6.6698 | 6.5528 | 6.438 | 6.2767 | 5.9509 | 5.6141 | 5.2852 | 4.2292 | 3.2404 | 2.5019 | 2.133 | 2.4087 | 334234 | 483827 | ULVERSTON | HARKER
| Hawk Green | 12.8649 | 12.7572 | 12.6305 | 12.5104 | 12.3332 | 12.1535 | 11.9901 | 11.8361 | 11.6311 | 11.4498 | 9.9807 | 7.2467 | 4.9299 | 2.379 | 0.19572 | 17.3649 | 17.2572 | 17.1305 | 17.0104 | 16.8332 | 16.6535 | 16.4901 | 16.3361 | 16.1311 | 15.9498 | 14.4807 | 11.7467 | 9.4299 | 6.879 | 4.5713 | 12.8649 | 12.7575 | 12.6468 | 12.524 | 12.3527 | 12.1587 | 11.9039 | 11.5703 | 11.289 | 11.006 | 10.1643 | 9.3279 | 8.4979 | 7.5626 | 6.8853 | 17.3649 | 17.2575 | 17.1468 | 17.024 | 16.8527 | 16.6587 | 16.4039 | 16.0703 | 15.789 | 15.506 | 14.6643 | 13.8279 | 12.9979 | 12.0626 | 11.5019 | 12.8649 | 12.7767 | 12.6751 | 12.5957 | 12.4625 | 12.3338 | 12.2403 | 12.1629 | 12.041 | 11.9296 | 10.6139 | 8.0501 | 5.9196 | 3.636 | 1.6712 | 17.3649 | 17.2767 | 17.1751 | 17.0957 | 16.9625 | 16.8338 | 16.7403 | 16.6629 | 16.541 | 16.4296 | 15.1139 | 12.5501 | 10.4196 | 8.136 | 6.007 | 12.8649 | 13.0224 | 12.9978 | 12.9371 | 12.7942 | 12.6267 | 12.3243 | 11.5241 | 10.6747 | 9.8311 | 7.3818 | 4.9719 | 3.0161 | 1.6939 | 2.4404 | 17.3649 | 17.5224 | 17.4978 | 17.4371 | 17.2942 | 17.1267 | 16.8243 | 16.0241 | 15.1747 | 14.3311 | 11.8818 | 9.4719 | 7.5161 | 6.1939 | 6.7732 | 12.8649 | 12.7855 | 12.704 | 12.6514 | 12.5773 | 12.4723 | 12.3502 | 12.2314 | 12.0394 | 11.8559 | 11.1981 | 10.332 | 9.6155 | 8.915 | 8.4541 | 17.3649 | 17.2855 | 17.204 | 17.1514 | 17.0773 | 16.9723 | 16.8502 | 16.7314 | 16.5394 | 16.3559 | 15.6981 | 14.832 | 14.1155 | 13.415 | 12.9872 | 12.8649 | 12.9577 | 12.8481 | 12.693 | 12.4658 | 12.2429 | 11.8724 | 10.9748 | 10.0519 | 9.1358 | 6.4737 | 3.887 | 1.7568 | 0.20988 | 0.69767 | 17.3649 | 17.4577 | 17.3481 | 17.193 | 16.9658 | 16.7429 | 16.3724 | 15.4748 | 14.5519 | 13.6358 | 10.9737 | 8.387 | 6.2568 | 4.7099 | 5.0876 | 395915 | 387138 | HAZEL GROVE | BREDBURY
| Haydock | 14.4457 | 11.5283 | 10.8197 | 10.4358 | 9.9986 | 9.4907 | 8.9448 | 8.5885 | 8.1276 | 7.6509 | 4.6517 | -0.032615 | -3.8262 | -7.5796 | -10.793 | 19.9457 | 17.0283 | 16.3197 | 15.9358 | 15.4986 | 14.9907 | 14.4448 | 14.0885 | 13.6276 | 13.1509 | 10.1517 | 5.4674 | 1.6738 | -2.0796 | -5.4856 | 14.4457 | 13.5868 | 13.2275 | 13.0105 | 12.7862 | 12.4957 | 12.1355 | 11.7112 | 11.3907 | 11.0503 | 9.7092 | 7.968 | 5.7214 | 3.391 | 1.9108 | 19.9457 | 19.0868 | 18.7275 | 18.5105 | 18.2862 | 17.9957 | 17.6355 | 17.2112 | 16.8907 | 16.5503 | 15.2092 | 13.468 | 11.2214 | 8.891 | 7.6025 | 14.4457 | 11.0599 | 10.2592 | 9.8867 | 9.4565 | 8.9697 | 8.4549 | 8.1453 | 7.781 | 7.4013 | 5.0799 | 0.87895 | -2.9397 | -6.4621 | -9.3335 | 19.9457 | 16.5599 | 15.7592 | 15.3867 | 14.9565 | 14.4697 | 13.9549 | 13.6453 | 13.281 | 12.9013 | 10.5799 | 6.379 | 2.5603 | -0.96212 | -4.0897 | 14.4457 | 12.3042 | 11.7282 | 11.4352 | 11.0686 | 10.5649 | 9.8273 | 8.7084 | 7.4992 | 6.009 | 1.4322 | -2.7684 | -6.0514 | -8.0962 | -6.9754 | 19.9457 | 17.8042 | 17.2282 | 16.9352 | 16.5686 | 16.0649 | 15.3273 | 14.2084 | 12.9992 | 11.509 | 6.9322 | 2.7316 | -0.5514 | -2.5962 | -1.738 | 14.4457 | 12.8907 | 12.5013 | 12.173 | 11.8577 | 11.4663 | 10.9973 | 10.7318 | 10.3672 | 9.9767 | 8.4118 | 5.9852 | 4.0819 | 2.7104 | 2.2425 | 19.9457 | 18.3907 | 18.0013 | 17.673 | 17.3577 | 16.9663 | 16.4973 | 16.2318 | 15.8672 | 15.4767 | 13.9118 | 11.4852 | 9.5819 | 8.2104 | 7.7465 | 14.4457 | 10.841 | 9.8898 | 9.4953 | 9.1112 | 8.5916 | 7.8573 | 6.7151 | 5.3471 | 3.7921 | -1.0077 | -5.6121 | -9.3125 | -11.7481 | -10.9515 | 19.9457 | 16.341 | 15.3898 | 14.9953 | 14.6112 | 14.0916 | 13.3573 | 12.2151 | 10.8471 | 9.2921 | 4.4923 | -0.11209 | -3.8125 | -6.2481 | -5.6465 | 357489 | 397336 | GOLBORNE | BOLD
| HDA No1 & HDA No2 | 13.9779 | 13.9028 | 13.6052 | 13.3538 | 13.1077 | 12.8291 | 12.2258 | 11.5008 | 10.7319 | 9.9531 | 7.7556 | 5.5739 | 3.9784 | 2.7317 | 2.0813 | 20.1979 | 20.1228 | 19.8252 | 19.5738 | 19.3277 | 19.0491 | 18.4458 | 17.7208 | 16.9519 | 16.1731 | 13.9756 | 11.7939 | 10.1984 | 8.9517 | 8.2173 | 13.9779 | 13.8997 | 13.7349 | 13.6158 | 13.5167 | 13.4055 | 13.2734 | 13.1159 | 12.9446 | 12.6086 | 11.1021 | 9.5062 | 8.0859 | 6.7512 | 6.0078 | 20.1979 | 20.1197 | 19.9549 | 19.8358 | 19.7367 | 19.6255 | 19.4934 | 19.3359 | 19.1646 | 18.8286 | 17.3221 | 15.7262 | 14.3059 | 12.9712 | 12.3163 | 13.9779 | 13.9022 | 13.6049 | 13.3539 | 13.11 | 12.7926 | 12.184 | 11.4476 | 10.7308 | 9.9899 | 7.7284 | 5.809 | 4.419 | 3.1439 | 2.5882 | 20.1979 | 20.1222 | 19.8249 | 19.5739 | 19.33 | 19.0126 | 18.404 | 17.6676 | 16.9508 | 16.2099 | 13.9484 | 12.029 | 10.639 | 9.3639 | 8.6965 | 13.9779 | 13.9524 | 13.695 | 13.4682 | 13.2503 | 13.0122 | 12.3963 | 11.6593 | 10.8162 | 9.8985 | 7.2988 | 5.1973 | 3.7808 | 2.9882 | 3.4666 | 20.1979 | 20.1724 | 19.915 | 19.6882 | 19.4703 | 19.2322 | 18.6163 | 17.8793 | 17.0362 | 16.1185 | 13.5188 | 11.4173 | 10.0008 | 9.2082 | 9.5528 | 13.9779 | 13.9173 | 13.6421 | 13.428 | 13.2485 | 13.0534 | 12.7577 | 12.1621 | 11.5267 | 10.858 | 8.7817 | 6.9802 | 5.7213 | 4.812 | 4.5609 | 20.1979 | 20.1373 | 19.8621 | 19.648 | 19.4685 | 19.2734 | 18.9777 | 18.3821 | 17.7467 | 17.078 | 15.0017 | 13.2002 | 11.9413 | 11.032 | 10.7846 | 13.9779 | 13.9209 | 13.619 | 13.3412 | 13.0788 | 12.8208 | 12.4419 | 11.6101 | 10.7137 | 9.7995 | 7.0832 | 4.7804 | 3.1453 | 2.1594 | 2.4716 | 20.1979 | 20.1409 | 19.839 | 19.5612 | 19.2988 | 19.0408 | 18.6619 | 17.8301 | 16.9337 | 16.0195 | 13.3032 | 11.0004 | 9.3653 | 8.3794 | 8.592 | 301743 | 524532 | STAINBURN & SIDDICK | HARKER
| Heady Hill | 9.1036 | 6.8412 | 6.2561 | 6.0928 | 5.8424 | 5.5156 | 4.596 | 4.1938 | 3.7109 | 3.2047 | 0.7421 | -2.7777 | -5.915 | -8.3806 | -10.6862 | 12.6036 | 10.3412 | 9.7561 | 9.5928 | 9.3424 | 9.0156 | 8.096 | 7.6938 | 7.2109 | 6.7047 | 4.2421 | 0.72227 | -2.415 | -4.8806 | -7.1977 | 9.1036 | 8.6255 | 8.4364 | 8.3246 | 8.1489 | 7.9558 | 7.6902 | 7.3053 | 6.9549 | 6.578 | 5.2691 | 3.618 | 1.2945 | -0.9067 | -2.4835 | 12.6036 | 12.1255 | 11.9364 | 11.8246 | 11.6489 | 11.4558 | 11.1902 | 10.8053 | 10.4549 | 10.078 | 8.7691 | 7.118 | 4.7945 | 2.5933 | 1.249 | 9.1036 | 6.4844 | 5.8286 | 5.6691 | 5.427 | 5.1482 | 4.3565 | 4.0714 | 3.7363 | 3.3251 | 0.62349 | -2.8935 | -5.6492 | -8.1352 | -10.3396 | 12.6036 | 9.9844 | 9.3286 | 9.1691 | 8.927 | 8.6482 | 7.8565 | 7.5714 | 7.2363 | 6.8251 | 4.1235 | 0.60652 | -2.1492 | -4.6352 | -6.8712 | 9.1036 | 7.3631 | 6.899 | 6.1684 | 5.3715 | 4.6284 | 4.2878 | 3.4323 | 2.4089 | 1.3488 | -1.948 | -5.2394 | -7.6484 | -9.1223 | -9.0036 | 12.6036 | 10.8631 | 10.399 | 9.6684 | 8.8715 | 8.1284 | 7.7878 | 6.9323 | 5.9089 | 4.8488 | 1.552 | -1.7394 | -4.1484 | -5.6223 | -5.5498 | 9.1036 | 8.2542 | 7.9756 | 7.8658 | 7.7283 | 7.5504 | 6.7859 | 6.4829 | 6.0588 | 5.5959 | 3.8304 | 1.6337 | -0.41502 | -1.6567 | -2.3746 | 12.6036 | 11.7542 | 11.4756 | 11.3658 | 11.2283 | 11.0504 | 10.2859 | 9.9829 | 9.5588 | 9.0959 | 7.3304 | 5.1337 | 3.085 | 1.8433 | 1.2095 | 9.1036 | 6.2768 | 5.5646 | 4.7998 | 3.9783 | 3.2375 | 2.877 | 1.9851 | 0.98255 | -0.062486 | -3.4161 | -6.8875 | -9.6145 | -11.3672 | -11.4589 | 12.6036 | 9.7768 | 9.0646 | 8.2998 | 7.4783 | 6.7375 | 6.377 | 5.4851 | 4.4825 | 3.4375 | 0.083882 | -3.3875 | -6.1145 | -7.8672 | -7.962 | 384370 | 410583 | CASTLETON | ROCHDALE
| Heap Bridge | 4.5816 | 2.7787 | 2.2399 | 2.076 | 1.8305 | 1.5291 | 1.1772 | 0.76135 | 0.27887 | -0.22455 | -1.9329 | -3.6806 | -4.9024 | -5.9034 | -6.7474 | 4.5816 | 2.7787 | 2.2399 | 2.076 | 1.8305 | 1.5291 | 1.1772 | 0.76135 | 0.27887 | -0.22455 | -1.9329 | -3.6806 | -4.9024 | -5.9034 | -6.7398 | 4.5816 | 4.122 | 3.8865 | 3.7734 | 3.6812 | 3.5762 | 3.4455 | 3.2767 | 3.035 | 2.7276 | 1.5962 | 0.31448 | -0.95581 | -2.3477 | -3.3548 | 4.5816 | 4.122 | 3.8865 | 3.7734 | 3.6812 | 3.5762 | 3.4455 | 3.2767 | 3.035 | 2.7276 | 1.5962 | 0.31448 | -0.95581 | -2.3477 | -3.1979 | 4.5816 | 2.4866 | 1.8845 | 1.7029 | 1.4314 | 1.1154 | 0.75196 | 0.32732 | -0.10905 | -0.5647 | -2.2321 | -4.072 | -5.3708 | -6.3313 | -6.9464 | 4.5816 | 2.4866 | 1.8845 | 1.7029 | 1.4314 | 1.1154 | 0.75196 | 0.32732 | -0.10905 | -0.5647 | -2.2321 | -4.072 | -5.3708 | -6.3313 | -6.9488 | 4.5816 | 3.1171 | 2.6658 | 2.5279 | 2.3227 | 2.0089 | 1.6026 | 1.0554 | 0.47231 | -0.13279 | -1.9798 | -3.6586 | -4.7811 | -5.5608 | -5.523 | 4.5816 | 3.1171 | 2.6658 | 2.5279 | 2.3227 | 2.0089 | 1.6026 | 1.0554 | 0.47231 | -0.13279 | -1.9798 | -3.6586 | -4.7811 | -5.5608 | -5.5387 | 4.5816 | 3.7294 | 3.4003 | 3.2721 | 3.1285 | 2.8989 | 2.6083 | 2.2716 | 1.8589 | 1.4182 | -0.058863 | -1.5335 | -2.5848 | -3.4097 | -3.8708 | 4.5816 | 3.7294 | 3.4003 | 3.2721 | 3.1285 | 2.8989 | 2.6083 | 2.2716 | 1.8589 | 1.4182 | -0.058863 | -1.5335 | -2.5848 | -3.4097 | -3.8102 | 4.5816 | 2.2405 | 1.5918 | 1.43 | 1.2081 | 0.91959 | 0.56261 | 0.049844 | -0.4965 | -1.0643 | -2.8749 | -4.6064 | -5.816 | -6.6754 | -6.6603 | 4.5816 | 2.2405 | 1.5918 | 1.43 | 1.2081 | 0.91959 | 0.56261 | 0.049844 | -0.4965 | -1.0643 | -2.8749 | -4.6064 | -5.816 | -6.6754 | -6.686 | 382793 | 410428 | BURY | KEARSLEY
| Heasandford | 14.9645 | 13.7047 | 13.3895 | 13.3322 | 13.2918 | 13.2563 | 13.2359 | 13.2178 | 13.1328 | 13.056 | 12.5651 | 11.7264 | 11.0321 | 10.3218 | 9.8062 | 19.5645 | 18.3047 | 17.9895 | 17.9322 | 17.8918 | 17.8563 | 17.8359 | 17.8178 | 17.7328 | 17.656 | 17.1651 | 16.3264 | 15.6321 | 14.9218 | 14.3319 | 14.9645 | 14.5219 | 14.3566 | 14.31 | 14.2928 | 14.2769 | 14.2584 | 14.2372 | 14.1287 | 14.0223 | 13.7212 | 13.4446 | 13.2226 | 13.0094 | 12.8599 | 19.5645 | 19.1219 | 18.9566 | 18.91 | 18.8928 | 18.8769 | 18.8584 | 18.8372 | 18.7287 | 18.6223 | 18.3212 | 18.0446 | 17.8226 | 17.6094 | 17.475 | 14.9645 | 13.4987 | 13.1481 | 13.0888 | 13.0477 | 13.0116 | 12.99 | 12.9709 | 12.9148 | 12.871 | 12.4848 | 11.765 | 11.1988 | 10.6697 | 10.3909 | 19.5645 | 18.0987 | 17.7481 | 17.6888 | 17.6477 | 17.6116 | 17.59 | 17.5709 | 17.5148 | 17.471 | 17.0848 | 16.365 | 15.7988 | 15.2697 | 14.8724 | 14.9645 | 13.9452 | 13.6837 | 13.6382 | 13.6077 | 13.5736 | 13.4931 | 13.2457 | 12.9602 | 12.6884 | 11.9352 | 11.2491 | 10.7238 | 10.4816 | 11.0016 | 19.5645 | 18.5452 | 18.2837 | 18.2382 | 18.2077 | 18.1736 | 18.0931 | 17.8457 | 17.5602 | 17.2884 | 16.5352 | 15.8491 | 15.3238 | 15.0816 | 15.481 | 14.9645 | 14.1125 | 13.8779 | 13.8393 | 13.834 | 13.8264 | 13.8134 | 13.7945 | 13.7037 | 13.6148 | 13.3443 | 13.0813 | 12.9171 | 12.8017 | 12.8941 | 19.5645 | 18.7125 | 18.4779 | 18.4393 | 18.434 | 18.4264 | 18.4134 | 18.3945 | 18.3037 | 18.2148 | 17.9443 | 17.6813 | 17.5171 | 17.4017 | 17.4552 | 14.9645 | 13.3264 | 12.943 | 12.8785 | 12.8318 | 12.7922 | 12.7083 | 12.4477 | 12.1506 | 11.8682 | 11.0893 | 10.3869 | 9.8383 | 9.5587 | 10.0239 | 19.5645 | 17.9264 | 17.543 | 17.4785 | 17.4318 | 17.3922 | 17.3083 | 17.0477 | 16.7506 | 16.4682 | 15.6893 | 14.9869 | 14.4383 | 14.1587 | 14.5169 | 385349 | 433821 | BURNLEY | ROCHDALE
| Heaton Moor | 5.8512 | 4.4404 | 3.6562 | 2.9256 | 2.1348 | 1.3271 | 0.5142 | -0.31838 | -1.2176 | -2.1147 | -4.4365 | -7.4147 | -9.5721 | -11.5115 | -12.7402 | 15.8512 | 14.4404 | 13.6562 | 12.9256 | 12.1348 | 11.3271 | 10.5142 | 9.6816 | 8.7824 | 7.8853 | 5.5635 | 2.5853 | 0.42789 | -1.5115 | -2.8712 | 5.8512 | 4.777 | 4.1597 | 3.5338 | 2.8424 | 2.1383 | 1.3679 | 0.53132 | -0.25604 | -1.0672 | -2.3666 | -3.7061 | -4.941 | -6.244 | -7.09 | 15.8512 | 14.777 | 14.1597 | 13.5338 | 12.8424 | 12.1383 | 11.3679 | 10.5313 | 9.744 | 8.9328 | 7.6334 | 6.2939 | 5.059 | 3.756 | 3.0347 | 5.8512 | 4.3353 | 3.4822 | 2.7028 | 1.8613 | 1.0057 | 0.16109 | -0.70435 | -1.6457 | -2.6465 | -5.2241 | -8.2652 | -10.3103 | -11.9093 | -12.4904 | 15.8512 | 14.3353 | 13.4822 | 12.7028 | 11.8613 | 11.0057 | 10.1611 | 9.2957 | 8.3543 | 7.3535 | 4.7759 | 1.7348 | -0.31027 | -1.9093 | -2.6183 | 5.8512 | 4.6808 | 3.9498 | 3.2327 | 2.4164 | 1.5311 | 0.51243 | -0.90784 | -2.3601 | -3.8044 | -6.82 | -9.4131 | -10.9977 | -11.7825 | -11.2326 | 15.8512 | 14.6808 | 13.9498 | 13.2327 | 12.4164 | 11.5311 | 10.5124 | 9.0922 | 7.6399 | 6.1956 | 3.18 | 0.58692 | -0.99771 | -1.7825 | -1.3743 | 5.8512 | 4.6491 | 3.9712 | 3.3463 | 2.6901 | 1.9881 | 1.2552 | 0.5096 | -0.32281 | -1.1716 | -2.7599 | -4.4299 | -5.6087 | -6.6581 | -7.2949 | 15.8512 | 14.6491 | 13.9712 | 13.3463 | 12.6901 | 11.9881 | 11.2552 | 10.5096 | 9.6772 | 8.8284 | 7.2401 | 5.5701 | 4.3913 | 3.3419 | 2.7783 | 5.8512 | 4.4447 | 3.5756 | 2.7429 | 1.8326 | 0.9092 | -0.14891 | -1.6472 | -3.1536 | -4.6565 | -7.8523 | -10.6728 | -12.4832 | -13.4961 | -13.1912 | 15.8512 | 14.4447 | 13.5756 | 12.7429 | 11.8326 | 10.9092 | 9.8511 | 8.3528 | 6.8464 | 5.3435 | 2.1477 | -0.67276 | -2.4832 | -3.4961 | -3.2801 | 387623 | 391345 | VERNON PARK | BREDBURY
| Heaton Norris | 5.8187 | 4.0053 | 3.2446 | 2.7633 | 2.261 | -1.0023 | -1.4091 | -1.806 | -2.2583 | -2.7041 | -8.5386 | -11.6195 | -13.4665 | -15.201 | -15.8706 | 12.8187 | 11.0053 | 10.2446 | 9.7633 | 9.261 | 5.9977 | 5.5909 | 5.194 | 4.7417 | 4.2959 | -1.5386 | -4.6195 | -6.4665 | -8.201 | -9.1167 | 5.8187 | 4.9277 | 4.4308 | 4.0449 | 3.6629 | 3.2858 | 2.8694 | 2.4094 | 1.9218 | 1.4241 | 0.56181 | -1.0678 | -2.1282 | -3.2213 | -3.9249 | 12.8187 | 11.9277 | 11.4308 | 11.0449 | 10.6629 | 10.2858 | 9.8694 | 9.4094 | 8.9218 | 8.4241 | 7.5618 | 5.9322 | 4.8718 | 3.7787 | 3.1822 | 5.8187 | 3.7312 | 2.8611 | 2.3025 | 1.7192 | -1.5769 | -2.0741 | -2.6037 | -3.1066 | -3.6267 | -10.0722 | -12.5919 | -14.1973 | -15.4508 | -15.3204 | 12.8187 | 10.7312 | 9.8611 | 9.3025 | 8.7192 | 5.4231 | 4.9259 | 4.3963 | 3.8934 | 3.3733 | -3.0722 | -5.5919 | -7.1973 | -8.4508 | -8.5869 | 5.8187 | 4.2796 | 3.5674 | 3.0658 | 2.5261 | -0.7442 | -1.3497 | -5.276 | -8.3923 | -9.1708 | -11.3087 | -13.4863 | -14.6998 | -15.2034 | -13.9825 | 12.8187 | 11.2796 | 10.5674 | 10.0658 | 9.5261 | 6.2558 | 5.6503 | 1.724 | -1.3923 | -2.1708 | -4.3087 | -6.4863 | -7.6998 | -8.2034 | -7.2571 | 5.8187 | 4.5234 | 3.9046 | 3.4939 | 3.1027 | -0.061805 | -0.40126 | -0.75129 | -1.1895 | -1.6431 | -6.8218 | -8.491 | -9.3203 | -10.1718 | -10.1621 | 12.8187 | 11.5234 | 10.9046 | 10.4939 | 10.1027 | 6.9382 | 6.5987 | 6.2487 | 5.8105 | 5.3569 | 0.17819 | -1.491 | -2.3203 | -3.1718 | -3.2163 | 5.8187 | 3.6268 | 2.7225 | 2.1412 | 1.5327 | -1.7651 | -2.3899 | -6.372 | -9.4988 | -10.3523 | -12.9651 | -15.3105 | -16.6865 | -17.3591 | -16.3581 | 12.8187 | 10.6268 | 9.7225 | 9.1412 | 8.5327 | 5.2349 | 4.6101 | 0.62802 | -2.4988 | -3.3523 | -5.9651 | -8.3105 | -9.6865 | -10.3591 | -9.5801 | 388860 | 391967 | VERNON PARK | BREDBURY
| Helwith Bridge | 0.36033 | 0.13076 | 0.039722 | -0.0029568 | -0.050463 | -0.099773 | -0.14883 | -0.20821 | -0.28474 | -0.35414 | -0.66894 | -1.1268 | -1.4863 | -1.8091 | -2.077 | 8.3603 | 8.1308 | 8.0397 | 7.997 | 7.9495 | 7.9002 | 7.8512 | 7.7918 | 7.7153 | 7.6459 | 7.3311 | 6.8732 | 6.5137 | 6.1909 | 5.8972 | 0.36033 | 0.25968 | 0.19643 | 0.16026 | 0.11711 | 0.057723 | -0.011538 | -0.092025 | -0.17061 | -0.24915 | -0.47535 | -0.67956 | -0.86101 | -1.0637 | -1.227 | 8.3603 | 8.2597 | 8.1964 | 8.1603 | 8.1171 | 8.0577 | 7.9885 | 7.908 | 7.8294 | 7.7509 | 7.5246 | 7.3204 | 7.139 | 6.9363 | 6.7975 | 0.36033 | 0.09627 | -0.00098224 | -0.044268 | -0.092181 | -0.14183 | -0.18407 | -0.22909 | -0.28925 | -0.34156 | -0.60476 | -1.0083 | -1.3126 | -1.5594 | -1.7297 | 8.3603 | 8.0963 | 7.999 | 7.9557 | 7.9078 | 7.8582 | 7.8159 | 7.7709 | 7.7107 | 7.6584 | 7.3952 | 6.9917 | 6.6874 | 6.4406 | 6.2262 | 0.36033 | 0.18669 | 0.11051 | 0.063987 | 0.019773 | -0.030965 | -0.099248 | -0.23163 | -0.37825 | -0.52048 | -0.93237 | -1.3133 | -1.5819 | -1.692 | -1.4874 | 8.3603 | 8.1867 | 8.1105 | 8.064 | 8.0198 | 7.969 | 7.9008 | 7.7684 | 7.6218 | 7.4795 | 7.0676 | 6.6867 | 6.4181 | 6.308 | 6.4653 | 0.36033 | 0.18126 | 0.10313 | 0.068529 | 0.043288 | 0.018207 | -0.009075 | -0.056175 | -0.12958 | -0.20193 | -0.44136 | -0.70418 | -0.87787 | -1.0284 | -1.0695 | 8.3603 | 8.1813 | 8.1031 | 8.0685 | 8.0433 | 8.0182 | 7.9909 | 7.9438 | 7.8704 | 7.7981 | 7.5586 | 7.2958 | 7.1221 | 6.9716 | 6.9168 | 0.36033 | 0.076568 | -0.028804 | -0.088782 | -0.14441 | -0.19848 | -0.26825 | -0.42149 | -0.58606 | -0.74486 | -1.1906 | -1.595 | -1.8826 | -2.0153 | -1.8479 | 8.3603 | 8.0766 | 7.9712 | 7.9112 | 7.8556 | 7.8015 | 7.7318 | 7.5785 | 7.4139 | 7.2551 | 6.8094 | 6.405 | 6.1174 | 5.9847 | 6.1122 | 381025 | 469428 | PADIHAM | PADIHAM | Firm Capacity marginally exceeded in FY28. Review in RIIO-ED2 as the forecast overload is minimal.
| Hensingham | 14.5166 | 14.2929 | 14.3764 | 14.3304 | 14.2089 | 14.0802 | 13.9797 | 13.9098 | 13.8186 | 13.7491 | 12.7487 | 10.714 | 8.9529 | 7.1566 | 5.5667 | 18.6536 | 18.4299 | 18.5134 | 18.4674 | 18.3459 | 18.2172 | 18.1167 | 18.0468 | 17.9556 | 17.8861 | 16.8857 | 14.851 | 13.0899 | 11.2936 | 9.5444 | 14.5166 | 14.3211 | 14.3932 | 14.3294 | 14.2325 | 14.106 | 13.9413 | 13.7416 | 13.605 | 13.469 | 13.071 | 12.6248 | 12.1825 | 11.7174 | 11.4494 | 18.6536 | 18.4581 | 18.5302 | 18.4664 | 18.3695 | 18.243 | 18.0783 | 17.8786 | 17.742 | 17.606 | 17.208 | 16.7618 | 16.3195 | 15.8544 | 15.6208 | 14.5166 | 14.2989 | 14.3993 | 14.3835 | 14.2939 | 14.2021 | 14.1529 | 14.1388 | 14.1125 | 14.0968 | 13.2618 | 11.3655 | 9.729 | 8.0793 | 6.6512 | 18.6536 | 18.4359 | 18.5363 | 18.5205 | 18.4309 | 18.3391 | 18.2899 | 18.2758 | 18.2495 | 18.2338 | 17.3988 | 15.5025 | 13.866 | 12.2163 | 10.5994 | 14.5166 | 14.5036 | 14.6648 | 14.6541 | 14.5498 | 14.4213 | 14.1977 | 13.5762 | 12.9198 | 12.2711 | 10.4036 | 8.6122 | 7.1372 | 6.3568 | 7.2421 | 18.6536 | 18.6406 | 18.8018 | 18.7911 | 18.6868 | 18.5583 | 18.3347 | 17.7132 | 17.0568 | 16.4081 | 14.5406 | 12.7492 | 11.2742 | 10.4938 | 11.1893 | 14.5166 | 14.3523 | 14.4774 | 14.5011 | 14.5155 | 14.5026 | 14.4716 | 14.4366 | 14.3556 | 14.2811 | 13.9468 | 13.3575 | 12.9509 | 12.609 | 12.5061 | 18.6536 | 18.4893 | 18.6144 | 18.6381 | 18.6525 | 18.6396 | 18.6086 | 18.5736 | 18.4926 | 18.4181 | 18.0838 | 17.4945 | 17.0879 | 16.746 | 16.611 | 14.5166 | 14.4308 | 14.5201 | 14.4335 | 14.2603 | 14.0856 | 13.8074 | 13.1094 | 12.3996 | 11.6984 | 9.6766 | 7.758 | 6.1592 | 5.229 | 5.9401 | 18.6536 | 18.5678 | 18.6571 | 18.5705 | 18.3973 | 18.2226 | 17.9444 | 17.2464 | 16.5366 | 15.8354 | 13.8136 | 11.895 | 10.2962 | 9.366 | 9.9253 | 298465 | 517239 | EGREMONT | HARKER
| Heyrod | 9.0174 | 8.8417 | 8.6819 | 8.519 | 8.2513 | 7.9574 | 7.6708 | 7.4161 | 7.1322 | 6.857 | 5.1695 | 2.6006 | 0.66386 | -1.0974 | -2.4606 | 13.6544 | 13.4787 | 13.3189 | 13.156 | 12.8883 | 12.5944 | 12.3078 | 12.0531 | 11.7692 | 11.494 | 9.8065 | 7.2376 | 5.3009 | 3.5396 | 2.0536 | 9.0174 | 8.8759 | 8.7434 | 8.6147 | 8.4491 | 8.273 | 8.0305 | 7.6888 | 7.4416 | 7.1868 | 6.3895 | 5.4992 | 4.5811 | 3.5622 | 2.7891 | 13.6544 | 13.5129 | 13.3804 | 13.2517 | 13.0861 | 12.91 | 12.6675 | 12.3258 | 12.0786 | 11.8238 | 11.0265 | 10.1362 | 9.2181 | 8.1992 | 7.5549 | 9.0174 | 8.778 | 8.5474 | 8.318 | 7.9778 | 7.6093 | 7.2597 | 6.9274 | 6.5888 | 6.2398 | 4.3509 | 1.845 | 0.16869 | -1.1175 | -1.6902 | 13.6544 | 13.415 | 13.1844 | 12.955 | 12.6148 | 12.2463 | 11.8967 | 11.5644 | 11.2258 | 10.8768 | 8.9879 | 6.482 | 4.8057 | 3.5195 | 2.8145 | 9.0174 | 9.0708 | 8.9173 | 8.7191 | 8.3891 | 8.0198 | 7.538 | 6.6562 | 5.7701 | 4.9043 | 2.4218 | 0.33082 | -0.92046 | -1.371 | -0.73463 | 13.6544 | 13.7078 | 13.5543 | 13.3561 | 13.0261 | 12.6568 | 12.175 | 11.2932 | 10.4071 | 9.5413 | 7.0588 | 4.9678 | 3.7165 | 3.266 | 3.7614 | 9.0174 | 8.8609 | 8.7287 | 8.6301 | 8.5044 | 8.3548 | 8.1749 | 7.9675 | 7.6817 | 7.391 | 6.3183 | 5.1603 | 4.3503 | 3.5585 | 3.0063 | 13.6544 | 13.4979 | 13.3657 | 13.2671 | 13.1414 | 12.9918 | 12.8119 | 12.6045 | 12.3187 | 12.028 | 10.9553 | 9.7973 | 8.9873 | 8.1955 | 7.7111 | 9.0174 | 9.0227 | 8.8051 | 8.5352 | 8.1383 | 7.7197 | 7.1751 | 6.2176 | 5.2877 | 4.3651 | 1.7044 | -0.54327 | -1.9472 | -2.5672 | -2.1265 | 13.6544 | 13.6597 | 13.4421 | 13.1722 | 12.7753 | 12.3567 | 11.8121 | 10.8546 | 9.9247 | 9.0021 | 6.3414 | 4.0937 | 2.6898 | 2.0698 | 2.4124 | 397310 | 399981 | HARTSHEAD-HEYROD | STALYBRIDGE
| Heyside | 12.9108 | 11.2764 | 10.7782 | 10.6021 | 10.3951 | 10.1608 | 9.9017 | 9.5249 | 9.0717 | 8.6051 | 6.3919 | 3.7845 | 1.9232 | 0.25338 | -1.1124 | 17.5478 | 15.9134 | 15.4152 | 15.2391 | 15.0321 | 14.7978 | 14.5387 | 14.1619 | 13.7087 | 13.2421 | 11.0289 | 8.4215 | 6.5602 | 4.8904 | 3.5214 | 12.9108 | 12.5122 | 12.2876 | 12.1397 | 11.9815 | 11.799 | 11.5748 | 11.2944 | 11.042 | 10.7768 | 9.5594 | 8.0117 | 6.4703 | 4.7723 | 3.5646 | 17.5478 | 17.1492 | 16.9246 | 16.7767 | 16.6185 | 16.436 | 16.2118 | 15.9314 | 15.679 | 15.4138 | 14.1964 | 12.6487 | 11.1073 | 9.4093 | 8.3935 | 12.9108 | 10.9954 | 10.4147 | 10.09 | 9.5544 | 8.9919 | 8.4039 | 7.7845 | 7.0501 | 6.3845 | 3.7408 | 1.0715 | -0.90296 | -2.4913 | -3.5044 | 17.5478 | 15.6324 | 15.0517 | 14.727 | 14.1914 | 13.6289 | 13.0409 | 12.4215 | 11.6871 | 11.0215 | 8.3778 | 5.7085 | 3.734 | 2.1457 | 1.181 | 12.9108 | 11.6468 | 11.2275 | 10.9487 | 10.4456 | 9.8946 | 9.1795 | 8.084 | 6.9517 | 5.9112 | 2.8523 | 0.51531 | -0.96225 | -1.8158 | -2.0896 | 17.5478 | 16.2838 | 15.8645 | 15.5857 | 15.0826 | 14.5316 | 13.8165 | 12.721 | 11.5887 | 10.5482 | 7.4893 | 5.1523 | 3.6747 | 2.8212 | 2.5846 | 12.9108 | 12.2378 | 11.9574 | 11.825 | 11.6858 | 11.5059 | 11.2841 | 11.0315 | 10.6282 | 10.1865 | 8.483 | 6.6843 | 5.3457 | 4.1909 | 3.3425 | 17.5478 | 16.8748 | 16.5944 | 16.462 | 16.3228 | 16.1429 | 15.9211 | 15.6685 | 15.2652 | 14.8235 | 13.12 | 11.3213 | 9.9827 | 8.8279 | 8.1108 | 12.9108 | 10.8712 | 10.2563 | 9.9283 | 9.3839 | 8.8181 | 8.0997 | 6.9724 | 5.8317 | 4.7798 | 1.6038 | -0.90794 | -2.6147 | -3.6689 | -3.9706 | 17.5478 | 15.5082 | 14.8933 | 14.5653 | 14.0209 | 13.4551 | 12.7367 | 11.6094 | 10.4687 | 9.4168 | 6.2408 | 3.7291 | 2.0223 | 0.96807 | 0.7368 | 393433 | 407129 | ROYTON | WHITEGATE
| Heywood | 7.3772 | 4.5049 | 3.7512 | 3.5145 | 3.2517 | 2.9727 | 2.6979 | 2.4071 | 2.0246 | 1.6417 | -0.18959 | -2.8777 | -5.002 | -7.1721 | -9.1301 | 8.0862 | 5.2139 | 4.4602 | 4.2235 | 3.9607 | 3.6817 | 3.4069 | 3.1161 | 2.7336 | 2.3507 | 0.51941 | -2.1687 | -4.293 | -6.4631 | -8.4939 | 7.3772 | 6.4303 | 6.1021 | 5.9113 | 5.7369 | 5.5562 | 5.3283 | 5.011 | 4.6696 | 4.3199 | 3.2255 | 2.0352 | 0.88798 | -0.40726 | -1.3543 | 8.0862 | 7.1393 | 6.8111 | 6.6203 | 6.4459 | 6.2652 | 6.0373 | 5.72 | 5.3786 | 5.0289 | 3.9345 | 2.7442 | 1.597 | 0.30174 | -0.49512 | 7.3772 | 4.0607 | 3.2181 | 2.8623 | 2.4838 | 2.0926 | 1.6491 | 1.3776 | 1.0633 | 0.75114 | -0.90983 | -3.4729 | -5.4639 | -7.3962 | -9.0112 | 8.0862 | 4.7697 | 3.9271 | 3.5713 | 3.1928 | 2.8016 | 2.3581 | 2.0866 | 1.7723 | 1.4601 | -0.20083 | -2.7639 | -4.7549 | -6.6872 | -8.4354 | 7.3772 | 5.0542 | 4.4429 | 4.1175 | 3.7595 | 3.3671 | 2.7811 | 1.9635 | 1.0755 | 0.19184 | -2.3767 | -4.7993 | -6.7539 | -8.2222 | -7.6754 | 8.0862 | 5.7632 | 5.1519 | 4.8265 | 4.4685 | 4.0761 | 3.4901 | 2.6725 | 1.7845 | 0.90084 | -1.6677 | -4.0903 | -6.0449 | -7.5132 | -7.1069 | 7.3772 | 5.7036 | 5.2141 | 5.0244 | 4.8555 | 4.6646 | 4.4526 | 4.2077 | 3.8407 | 3.4593 | 2.212 | 0.90126 | 0.018714 | -0.74072 | -1.1192 | 8.0862 | 6.4126 | 5.9231 | 5.7334 | 5.5645 | 5.3736 | 5.1616 | 4.9167 | 4.5497 | 4.1683 | 2.921 | 1.6103 | 0.72771 | -0.031719 | -0.38481 | 7.3772 | 3.693 | 2.7653 | 2.3879 | 1.9855 | 1.5746 | 0.97836 | 0.13319 | -0.75846 | -1.6452 | -4.26 | -6.7794 | -8.7154 | -10.1497 | -9.7842 | 8.0862 | 4.402 | 3.4743 | 3.0969 | 2.6945 | 2.2836 | 1.6874 | 0.84219 | -0.049456 | -0.93621 | -3.551 | -6.0704 | -8.0064 | -9.4407 | -9.1735 | 385429 | 410369 | CASTLETON | ROCHDALE
| Higher Mill | 6.4317 | 5.0336 | 4.5605 | 4.3411 | 4.0465 | 3.6597 | 3.266 | 2.8455 | 2.3429 | 1.8616 | -0.4033 | -3.7028 | -6.3318 | -9.0162 | -11.2926 | 13.9317 | 12.5336 | 12.0605 | 11.8411 | 11.5465 | 11.1597 | 10.766 | 10.3455 | 9.8429 | 9.3616 | 7.0967 | 3.7972 | 1.1682 | -1.5162 | -3.8698 | 6.4317 | 5.9885 | 5.7441 | 5.5525 | 5.313 | 5.059 | 4.7313 | 4.2456 | 3.7843 | 3.3052 | 1.7836 | 0.21264 | -1.2407 | -2.7442 | -3.7223 | 13.9317 | 13.4885 | 13.2441 | 13.0525 | 12.813 | 12.559 | 12.2313 | 11.7456 | 11.2843 | 10.8052 | 9.2836 | 7.7126 | 6.2593 | 4.7558 | 3.9296 | 6.4317 | 4.8699 | 4.3926 | 4.2326 | 3.9835 | 3.6619 | 3.3587 | 3.0367 | 2.3687 | 1.8474 | -0.20891 | -3.4065 | -5.9568 | -8.5207 | -10.604 | 13.9317 | 12.3699 | 11.8926 | 11.7326 | 11.4835 | 11.1619 | 10.8587 | 10.5367 | 9.8687 | 9.3474 | 7.2911 | 4.0935 | 1.5432 | -1.0207 | -3.223 | 6.4317 | 5.5112 | 5.1986 | 5.0665 | 4.8366 | 4.5297 | 4.0178 | 3.0407 | 1.702 | 0.50774 | -2.6 | -5.5987 | -7.8979 | -9.4738 | -8.962 | 13.9317 | 13.0112 | 12.6986 | 12.5665 | 12.3366 | 12.0297 | 11.5178 | 10.5407 | 9.202 | 8.0077 | 4.9 | 1.9013 | -0.39793 | -1.9738 | -1.5972 | 6.4317 | 5.7367 | 5.4598 | 5.335 | 5.1925 | 4.9939 | 4.6894 | 4.3704 | 3.9419 | 3.5036 | 2.0113 | 0.39197 | -0.75175 | -1.7708 | -2.3321 | 13.9317 | 13.2367 | 12.9598 | 12.835 | 12.6925 | 12.4939 | 12.1894 | 11.8704 | 11.4419 | 11.0036 | 9.5113 | 7.892 | 6.7482 | 5.7292 | 5.2096 | 6.4317 | 4.8415 | 4.3137 | 4.0805 | 3.765 | 3.3864 | 2.8491 | 1.8011 | 0.41227 | -0.83739 | -4.1641 | -7.3733 | -9.8838 | -11.6849 | -11.4125 | 13.9317 | 12.3415 | 11.8137 | 11.5805 | 11.265 | 10.8864 | 10.3491 | 9.3011 | 7.9123 | 6.6626 | 3.3359 | 0.12675 | -2.3838 | -4.1849 | -3.9959 | 385731 | 388090 | MOSS NOOK | SOUTH MANCHESTER
| Higher Walton | 7.028 | 4.0384 | 1.8007 | 0.098555 | -1.6465 | -3.4192 | -3.6897 | -4.009 | -4.5066 | -5.0144 | -9.0688 | -12.2769 | -14.7737 | -17.2253 | -19.0104 | 11.665 | 8.6754 | 6.4377 | 4.7356 | 2.9905 | 1.2178 | 0.94727 | 0.62803 | 0.13037 | -0.3774 | -4.4318 | -7.6399 | -10.1367 | -12.5883 | -14.5416 | 7.028 | 5.8546 | 4.9467 | 4.2408 | 3.5087 | 2.7407 | 2.4135 | 2.03 | 1.5967 | 1.1407 | -0.33812 | -1.9123 | -3.4218 | -5.0116 | -9.5567 | 11.665 | 10.4916 | 9.5837 | 8.8778 | 8.1457 | 7.3777 | 7.0505 | 6.667 | 6.2337 | 5.7777 | 4.2989 | 2.7247 | 1.2152 | -0.37464 | -4.8025 | 7.028 | 3.5996 | 1.3149 | -0.32117 | -1.9968 | -3.6836 | -3.8333 | -4.0084 | -4.3319 | -4.663 | -8.6745 | -13.3483 | -15.6455 | -17.8244 | -19.0772 | 11.665 | 8.2366 | 5.9519 | 4.3158 | 2.6402 | 0.95339 | 0.80366 | 0.62865 | 0.30512 | -0.02605 | -4.0375 | -8.7113 | -11.0085 | -13.1874 | -14.711 | 7.028 | 4.7816 | 2.7465 | 1.1366 | -0.53581 | -2.2651 | -2.634 | -5.8 | -10.3146 | -11.1522 | -13.9371 | -16.6366 | -18.5987 | -19.7949 | -18.5139 | 11.665 | 9.4186 | 7.3835 | 5.7736 | 4.1012 | 2.3719 | 2.003 | -1.163 | -5.6776 | -6.5152 | -9.3001 | -11.9996 | -13.9617 | -15.1579 | -14.1714 | 7.028 | 4.8797 | 2.8396 | 1.2216 | -0.39461 | -2.0681 | -2.2833 | -2.5412 | -2.9772 | -3.441 | -6.754 | -8.4091 | -9.5088 | -10.3668 | -10.4817 | 11.665 | 9.5167 | 7.4766 | 5.8586 | 4.2424 | 2.5689 | 2.3537 | 2.0958 | 1.6598 | 1.196 | -2.117 | -3.7721 | -4.8718 | -5.7298 | -5.9052 | 7.028 | 3.289 | 0.90745 | -0.81193 | -3.7899 | -5.8682 | -6.5856 | -10.1277 | -14.984 | -15.8613 | -18.8722 | -21.9043 | -24.1917 | -25.684 | -24.6489 | 11.665 | 7.926 | 5.5445 | 3.8251 | 0.84705 | -1.2312 | -1.9486 | -5.4907 | -10.347 | -11.2243 | -14.2352 | -17.2673 | -19.5547 | -21.047 | -20.2549 | 358020 | 427270 | LEYLAND | PENWORTHAM | Firm Capacity exceeded in FY28. HV interconnection with Samlesbury Enterprise Zone will be the immediate solution.
| Hill Top T11 & T12 | 4.6342 | 4.0426 | 3.5476 | 3.1088 | 2.53 | 1.9179 | 1.2999 | 0.65741 | -0.062609 | -0.7458 | -4.149 | -9.0153 | -12.8093 | -16.5329 | -19.6118 | 8.7742 | 8.1826 | 7.6876 | 7.2488 | 6.67 | 6.0579 | 5.4399 | 4.7974 | 4.0774 | 3.3942 | -0.0089811 | -4.8753 | -8.6693 | -12.3929 | -15.6117 | 4.6342 | 4.326 | 4.1137 | 3.8857 | 3.5556 | 3.1736 | 2.6666 | 1.9986 | 1.4083 | 0.76909 | -1.3351 | -3.5034 | -5.5186 | -7.6446 | -8.9597 | 8.7742 | 8.466 | 8.2537 | 8.0257 | 7.6956 | 7.3136 | 6.8066 | 6.1386 | 5.5483 | 4.9091 | 2.8049 | 0.63657 | -1.3786 | -3.5046 | -4.6195 | 4.6342 | 4.026 | 3.5704 | 3.2114 | 2.7257 | 2.2269 | 1.7679 | 1.2627 | 0.64012 | 0.045935 | -3.0579 | -7.8116 | -11.5386 | -15.1346 | -18.0072 | 8.7742 | 8.166 | 7.7104 | 7.3514 | 6.8657 | 6.3669 | 5.9079 | 5.4027 | 4.7801 | 4.1859 | 1.0821 | -3.6716 | -7.3986 | -10.9946 | -14.0497 | 4.6342 | 4.6157 | 4.3329 | 4.0379 | 3.5565 | 2.999 | 2.2221 | 0.68016 | -0.86336 | -2.359 | -6.7517 | -11.1848 | -14.5207 | -16.6965 | -15.8994 | 8.7742 | 8.7557 | 8.4729 | 8.1779 | 7.6965 | 7.139 | 6.3621 | 4.8202 | 3.2766 | 1.781 | -2.6117 | -7.0448 | -10.3807 | -12.5565 | -11.9609 | 4.6342 | 4.2819 | 3.9127 | 3.6177 | 3.2657 | 2.8355 | 2.3439 | 1.8213 | 1.2393 | 0.63887 | -1.6222 | -4.1077 | -5.8029 | -7.2332 | -7.9748 | 8.7742 | 8.4219 | 8.0527 | 7.7577 | 7.4057 | 6.9755 | 6.4839 | 5.9613 | 5.3793 | 4.7789 | 2.5178 | 0.03234 | -1.6629 | -3.0932 | -3.7825 | 4.6342 | 4.3365 | 3.867 | 3.4038 | 2.7776 | 2.1382 | 1.2642 | -0.41945 | -2.0617 | -3.6586 | -8.4695 | -13.2122 | -16.8755 | -19.3832 | -18.9818 | 8.7742 | 8.4765 | 8.007 | 7.5438 | 6.9176 | 6.2782 | 5.4042 | 3.7206 | 2.0783 | 0.48137 | -4.3295 | -9.0722 | -12.7355 | -15.2432 | -14.9561 | 373466 | 403748 | KEARSLEY LOCAL | KEARSLEY
| Hill Top T13 | 3.3712 | 3.1845 | 3.1801 | 3.0947 | 2.9788 | 2.8598 | 2.7508 | 2.6371 | 2.4644 | 2.2975 | 1.1641 | -0.68712 | -2.2225 | -3.8732 | -5.2505 | 3.3712 | 3.1845 | 3.1801 | 3.0947 | 2.9788 | 2.8598 | 2.7508 | 2.6371 | 2.4644 | 2.2975 | 1.1641 | -0.68712 | -2.2225 | -3.8732 | -5.3377 | 3.3712 | 3.1886 | 3.2412 | 3.1782 | 3.1047 | 3.0194 | 2.8982 | 2.7261 | 2.5472 | 2.3658 | 1.8065 | 1.2043 | 0.59679 | -0.067302 | -0.51899 | 3.3712 | 3.1886 | 3.2412 | 3.1782 | 3.1047 | 3.0194 | 2.8982 | 2.7261 | 2.5472 | 2.3658 | 1.8065 | 1.2043 | 0.59679 | -0.067302 | -0.44738 | 3.3712 | 3.1976 | 3.2063 | 3.1457 | 3.0536 | 2.9621 | 2.8934 | 2.8237 | 2.7189 | 2.6048 | 1.6341 | -0.11055 | -1.5512 | -3.0675 | -4.2697 | 3.3712 | 3.1976 | 3.2063 | 3.1457 | 3.0536 | 2.9621 | 2.8934 | 2.8237 | 2.7189 | 2.6048 | 1.6341 | -0.11055 | -1.5512 | -3.0675 | -4.3911 | 3.3712 | 3.3378 | 3.3865 | 3.3348 | 3.2367 | 3.1256 | 2.9219 | 2.3722 | 1.7861 | 1.1912 | -0.56879 | -2.2088 | -3.5119 | -4.3734 | -3.8202 | 3.3712 | 3.3378 | 3.3865 | 3.3348 | 3.2367 | 3.1256 | 2.9219 | 2.3722 | 1.7861 | 1.1912 | -0.56879 | -2.2088 | -3.5119 | -4.3734 | -3.9436 | 3.3712 | 3.2027 | 3.2204 | 3.1696 | 3.1188 | 3.0491 | 2.9651 | 2.8741 | 2.7139 | 2.5534 | 1.9834 | 1.3772 | 0.97642 | 0.63984 | 0.47826 | 3.3712 | 3.2027 | 3.2204 | 3.1696 | 3.1188 | 3.0491 | 2.9651 | 2.8741 | 2.7139 | 2.5534 | 1.9834 | 1.3772 | 0.97642 | 0.63984 | 0.4767 | 3.3712 | 3.3054 | 3.3132 | 3.217 | 3.0798 | 2.9444 | 2.7117 | 2.122 | 1.5104 | 0.88962 | -0.97908 | -2.7312 | -4.1498 | -5.143 | -4.7267 | 3.3712 | 3.3054 | 3.3132 | 3.217 | 3.0798 | 2.9444 | 2.7117 | 2.122 | 1.5104 | 0.88962 | -0.97908 | -2.7312 | -4.1498 | -5.143 | -4.8201 | 373476 | 403758 | KEARSLEY LOCAL | KEARSLEY
| Hindley Green | 17.1756 | 14.842 | 14.0497 | 13.5888 | 12.7264 | 11.8418 | 10.9957 | 10.1657 | 9.1904 | 8.0887 | 3.4627 | -2.4782 | -6.9445 | -11.0274 | -13.8412 | 23.9956 | 21.662 | 20.8697 | 20.4088 | 19.5464 | 18.6618 | 17.8157 | 16.9857 | 16.0104 | 14.9087 | 10.2827 | 4.3418 | -0.12449 | -4.2074 | -7.2493 | 17.1756 | 16.4081 | 16.1038 | 15.8384 | 15.4328 | 14.9506 | 14.3288 | 13.5475 | 12.9305 | 12.2569 | 9.9101 | 7.5866 | 5.3482 | 3.0959 | 1.7105 | 23.9956 | 23.2281 | 22.9238 | 22.6584 | 22.2528 | 21.7706 | 21.1488 | 20.3675 | 19.7505 | 19.0769 | 16.7301 | 14.4066 | 12.1682 | 9.9159 | 8.7408 | 17.1756 | 14.3827 | 13.373 | 12.7611 | 11.5085 | 10.235 | 8.962 | 7.695 | 6.2491 | 4.6644 | -0.89849 | -6.9647 | -11.1385 | -14.5178 | -16.1144 | 23.9956 | 21.2027 | 20.193 | 19.5811 | 18.3285 | 17.055 | 15.782 | 14.515 | 13.0691 | 11.4844 | 5.9215 | -0.1447 | -4.3185 | -7.6978 | -9.4699 | 17.1756 | 15.5821 | 14.8813 | 14.3566 | 13.133 | 11.8245 | 10.1765 | 7.564 | 4.9543 | 2.4425 | -3.9204 | -8.7689 | -12.1025 | -13.8639 | -13.0924 | 23.9956 | 22.4021 | 21.7013 | 21.1766 | 19.953 | 18.6445 | 16.9965 | 14.384 | 11.7743 | 9.2625 | 2.8996 | -1.9489 | -5.2825 | -7.0439 | -6.4699 | 17.1756 | 15.8643 | 15.3684 | 15.0798 | 14.5198 | 13.8663 | 13.1316 | 12.3598 | 11.4807 | 10.4092 | 7.0478 | 3.8756 | 1.628 | -0.45429 | -1.809 | 23.9956 | 22.6843 | 22.1884 | 21.8998 | 21.3398 | 20.6863 | 19.9516 | 19.1798 | 18.3007 | 17.2292 | 13.8678 | 10.6956 | 8.448 | 6.3657 | 5.1835 | 17.1756 | 14.5193 | 13.4437 | 12.7087 | 11.2957 | 9.8656 | 8.0701 | 5.2464 | 2.4727 | -0.20301 | -7.0796 | -12.3694 | -16.0354 | -18.1301 | -17.7892 | 23.9956 | 21.3393 | 20.2637 | 19.5287 | 18.1157 | 16.6856 | 14.8901 | 12.0664 | 9.2927 | 6.617 | -0.25962 | -5.5494 | -9.2154 | -11.3101 | -11.0635 | 363389 | 403254 | ATHERTON | KEARSLEY
| Hollinwood | 13.931 | 13.5736 | 13.4101 | 13.3305 | 13.2318 | 13.1211 | 13.0054 | 12.8834 | 12.7252 | 12.5761 | 11.6272 | 9.8945 | 8.4506 | 7.0236 | 5.6326 | 18.568 | 18.2106 | 18.0471 | 17.9675 | 17.8688 | 17.7581 | 17.6424 | 17.5204 | 17.3622 | 17.2131 | 16.2642 | 14.5315 | 13.0876 | 11.6606 | 10.2079 | 13.931 | 13.7929 | 13.6728 | 13.592 | 13.5089 | 13.4051 | 13.2742 | 13.1157 | 12.9553 | 12.794 | 12.2961 | 11.5822 | 10.9014 | 10.1741 | 9.6554 | 18.568 | 18.4299 | 18.3098 | 18.229 | 18.1459 | 18.0421 | 17.9112 | 17.7527 | 17.5923 | 17.431 | 16.9331 | 16.2192 | 15.5384 | 14.8111 | 14.3755 | 13.931 | 13.5228 | 13.3493 | 13.2693 | 13.1115 | 12.9426 | 12.7682 | 12.5903 | 12.401 | 12.223 | 11.5959 | 10.0497 | 8.7176 | 7.4648 | 6.3479 | 18.568 | 18.1598 | 17.9863 | 17.9063 | 17.7485 | 17.5796 | 17.4052 | 17.2273 | 17.038 | 16.86 | 16.2329 | 14.6867 | 13.3546 | 12.1018 | 10.8881 | 13.931 | 13.7549 | 13.6532 | 13.6117 | 13.4808 | 13.3204 | 13.104 | 12.7407 | 12.3496 | 11.7745 | 10.1723 | 8.5951 | 7.3245 | 6.5623 | 6.9913 | 18.568 | 18.3919 | 18.2902 | 18.2487 | 18.1178 | 17.9574 | 17.741 | 17.3777 | 16.9866 | 16.4115 | 14.8093 | 13.2321 | 11.9615 | 11.1993 | 11.5278 | 13.931 | 13.7379 | 13.6289 | 13.5906 | 13.5576 | 13.4957 | 13.4055 | 13.3035 | 13.1558 | 13.0089 | 12.5241 | 11.8475 | 11.2772 | 10.7758 | 10.5157 | 18.568 | 18.3749 | 18.2659 | 18.2276 | 18.1946 | 18.1327 | 18.0425 | 17.9405 | 17.7928 | 17.6459 | 17.1611 | 16.4845 | 15.9142 | 15.4128 | 15.1683 | 13.931 | 13.5793 | 13.4082 | 13.3216 | 13.1518 | 12.9751 | 12.7478 | 12.3541 | 11.819 | 11.181 | 9.461 | 7.7819 | 6.3909 | 5.4941 | 5.7761 | 18.568 | 18.2163 | 18.0452 | 17.9586 | 17.7888 | 17.6121 | 17.3848 | 16.9911 | 16.456 | 15.818 | 14.098 | 12.4189 | 11.0279 | 10.1311 | 10.3451 | 390287 | 402592 | CHADDERTON | WHITEGATE
| Holme Rd | 8.3728 | 7.7871 | 7.6363 | 7.5898 | 7.4647 | 7.3353 | 7.2174 | 7.0992 | 6.9169 | 6.7633 | 4.9797 | 1.4274 | -1.5862 | -5.0456 | -8.0152 | 12.5098 | 11.9241 | 11.7733 | 11.7268 | 11.6017 | 11.4723 | 11.3544 | 11.2362 | 11.0539 | 10.9003 | 9.1167 | 5.5644 | 2.5508 | -0.90861 | -4.0792 | 8.3728 | 8.1244 | 7.9968 | 7.8818 | 7.7001 | 7.4727 | 7.1707 | 6.8113 | 6.5388 | 6.262 | 5.4311 | 4.5822 | 3.5938 | 2.6138 | 1.9741 | 12.5098 | 12.2614 | 12.1338 | 12.0188 | 11.8371 | 11.6097 | 11.3077 | 10.9483 | 10.6758 | 10.399 | 9.5681 | 8.7192 | 7.7308 | 6.7508 | 6.2051 | 8.3728 | 7.7321 | 7.6019 | 7.6099 | 7.545 | 7.4862 | 7.467 | 7.4551 | 7.3839 | 7.3259 | 5.6678 | 2.2857 | -0.58108 | -3.666 | -6.1903 | 12.5098 | 11.8691 | 11.7389 | 11.7469 | 11.682 | 11.6232 | 11.604 | 11.5921 | 11.5209 | 11.4629 | 9.8048 | 6.4227 | 3.5559 | 0.47097 | -2.3045 | 8.3728 | 8.2758 | 8.2797 | 8.3063 | 8.2204 | 8.1045 | 7.7893 | 6.7626 | 5.6711 | 4.5845 | 1.4124 | -1.6811 | -4.2863 | -6.0538 | -4.9019 | 12.5098 | 12.4128 | 12.4167 | 12.4433 | 12.3574 | 12.2415 | 11.9263 | 10.8996 | 9.8081 | 8.7215 | 5.5494 | 2.4559 | -0.14933 | -1.9168 | -1.0179 | 8.3728 | 8.0586 | 8.0097 | 8.0544 | 8.0698 | 8.0338 | 7.9521 | 7.8671 | 7.7062 | 7.5552 | 6.9292 | 5.6638 | 4.74 | 3.8958 | 3.4922 | 12.5098 | 12.1956 | 12.1467 | 12.1914 | 12.2068 | 12.1708 | 12.0891 | 12.0041 | 11.8432 | 11.6922 | 11.0662 | 9.8008 | 8.877 | 8.0328 | 7.6237 | 8.3728 | 7.9515 | 7.8012 | 7.7022 | 7.5028 | 7.3112 | 6.9025 | 5.7468 | 4.561 | 3.3805 | -0.073936 | -3.3994 | -6.2251 | -8.2581 | -7.3997 | 12.5098 | 12.0885 | 11.9382 | 11.8392 | 11.6398 | 11.4482 | 11.0395 | 9.8838 | 8.698 | 7.5175 | 4.0631 | 0.73765 | -2.0881 | -4.1211 | -3.4519 | 352311 | 429141 | RIBBLE | PENWORTHAM
| Holt St | 5.4618 | 5.1112 | 4.927 | 4.7847 | 4.5525 | 4.3063 | 4.0729 | 3.8194 | 3.4483 | 2.8847 | 0.033315 | -4.0499 | -7.3185 | -10.644 | -13.316 | 8.9618 | 8.6112 | 8.427 | 8.2847 | 8.0525 | 7.8063 | 7.5729 | 7.3194 | 6.9483 | 6.3847 | 3.5333 | -0.54986 | -3.8185 | -7.144 | -9.9444 | 5.4618 | 5.2821 | 5.1537 | 5.0065 | 4.7868 | 4.5195 | 4.1777 | 3.7606 | 3.3871 | 2.998 | 1.6245 | -0.024222 | -1.5975 | -3.2636 | -4.3606 | 8.9618 | 8.7821 | 8.6537 | 8.5065 | 8.2868 | 8.0195 | 7.6777 | 7.2606 | 6.8871 | 6.498 | 5.1245 | 3.4758 | 1.9025 | 0.23636 | -0.70384 | 5.4618 | 5.0999 | 4.9464 | 4.8667 | 4.7068 | 4.5478 | 4.4329 | 4.3175 | 4.0291 | 3.5451 | 0.9444 | -3.4536 | -7.0427 | -10.3954 | -12.9761 | 8.9618 | 8.5999 | 8.4464 | 8.3667 | 8.2068 | 8.0478 | 7.9329 | 7.8175 | 7.5291 | 7.0451 | 4.4444 | 0.046423 | -3.5427 | -6.8954 | -9.4278 | 5.4618 | 5.488 | 5.4575 | 5.423 | 5.2664 | 5.0622 | 4.6637 | 3.5659 | 2.3709 | 1.1524 | -2.5105 | -6.1461 | -9.0578 | -11.0768 | -10.6723 | 8.9618 | 8.988 | 8.9575 | 8.923 | 8.7664 | 8.5622 | 8.1637 | 7.0659 | 5.8709 | 4.6524 | 0.98949 | -2.6461 | -5.5578 | -7.5768 | -7.1657 | 5.4618 | 5.2459 | 5.1514 | 5.11 | 5.034 | 4.895 | 4.706 | 4.4979 | 4.1781 | 3.8384 | 2.0142 | 0.036784 | -1.3491 | -2.7462 | -3.7952 | 8.9618 | 8.7459 | 8.6514 | 8.61 | 8.534 | 8.395 | 8.206 | 7.9979 | 7.6781 | 7.3384 | 5.5142 | 3.5368 | 2.1509 | 0.75376 | -0.16157 | 5.4618 | 5.2754 | 5.101 | 4.9367 | 4.6689 | 4.4 | 3.926 | 2.715 | 1.4266 | 0.10167 | -3.8777 | -7.9112 | -11.2289 | -13.6674 | -13.3067 | 8.9618 | 8.7754 | 8.601 | 8.4367 | 8.1689 | 7.9 | 7.426 | 6.215 | 4.9266 | 3.6017 | -0.37766 | -4.4112 | -7.7289 | -10.1674 | -9.9063 | 378620 | 416362 | BURY | KEARSLEY
| Hurst | 6.8595 | 6.5305 | 6.4645 | 6.4366 | 6.2899 | 6.1169 | 5.9605 | 5.8424 | 5.6574 | 5.432 | 3.8219 | 0.97404 | -1.4306 | -3.8703 | -6.0364 | 10.3595 | 10.0305 | 9.9645 | 9.9366 | 9.7899 | 9.6169 | 9.4605 | 9.3424 | 9.1574 | 8.932 | 7.3219 | 4.474 | 2.0694 | -0.37028 | -2.6768 | 6.8595 | 6.71 | 6.666 | 6.6251 | 6.5263 | 6.4056 | 6.2275 | 6.0006 | 5.7794 | 5.5542 | 4.8528 | 4.0943 | 3.3549 | 2.6153 | 2.1422 | 10.3595 | 10.21 | 10.166 | 10.1251 | 10.0263 | 9.9056 | 9.7275 | 9.5006 | 9.2794 | 9.0542 | 8.3528 | 7.5943 | 6.8549 | 6.1153 | 5.7141 | 6.8595 | 6.5041 | 6.4562 | 6.4694 | 6.3699 | 6.2619 | 6.1938 | 6.1058 | 5.9393 | 5.7694 | 4.3239 | 1.5991 | -0.70515 | -3.0315 | -5.0763 | 10.3595 | 10.0041 | 9.9562 | 9.9694 | 9.8699 | 9.7619 | 9.6938 | 9.6058 | 9.4393 | 9.2694 | 7.8239 | 5.0991 | 2.7948 | 0.46846 | -1.7396 | 6.8595 | 6.9065 | 6.9586 | 6.9909 | 6.8767 | 6.725 | 6.4267 | 5.5765 | 4.6812 | 3.8009 | 1.2431 | -1.2491 | -3.3334 | -4.6491 | -3.884 | 10.3595 | 10.4065 | 10.4586 | 10.4909 | 10.3767 | 10.225 | 9.9267 | 9.0765 | 8.1812 | 7.3009 | 4.7431 | 2.2509 | 0.16657 | -1.1491 | -0.55639 | 6.8595 | 6.6615 | 6.6641 | 6.7266 | 6.7512 | 6.7398 | 6.6803 | 6.6093 | 6.4623 | 6.2638 | 5.4166 | 4.4319 | 3.7152 | 3.0513 | 2.5501 | 10.3595 | 10.1615 | 10.1641 | 10.2266 | 10.2512 | 10.2398 | 10.1803 | 10.1093 | 9.9623 | 9.7638 | 8.9166 | 7.9319 | 7.2152 | 6.5513 | 6.1088 | 6.8595 | 6.7163 | 6.6595 | 6.5996 | 6.3934 | 6.178 | 5.8083 | 4.8727 | 3.9005 | 2.9431 | 0.15546 | -2.5358 | -4.8052 | -6.3403 | -5.8261 | 10.3595 | 10.2163 | 10.1595 | 10.0996 | 9.8934 | 9.678 | 9.3083 | 8.3727 | 7.4005 | 6.4431 | 3.6555 | 0.96421 | -1.3052 | -2.8403 | -2.4393 | 394658 | 400360 | HARTSHEAD-HEYROD | STALYBRIDGE
| Hutton End & Skelton C | 10.2478 | 10.1562 | 9.9644 | 9.7681 | 9.4711 | 9.1882 | 8.7681 | 8 | 7.0473 | 5.9682 | 2.2477 | -1.1666 | -3.3537 | -4.7948 | -5.8006 | 19.8878 | 19.7962 | 19.6044 | 19.4081 | 19.1111 | 18.8282 | 18.4081 | 17.64 | 16.6873 | 15.6082 | 11.8877 | 8.4734 | 6.2863 | 4.8452 | 3.8298 | 10.2478 | 10.1303 | 9.9468 | 9.7541 | 9.5336 | 9.3177 | 9.0441 | 8.715 | 8.4661 | 8.1867 | 6.5233 | 4.1222 | 1.464 | -1.5734 | -3.6983 | 19.8878 | 19.7703 | 19.5868 | 19.3941 | 19.1736 | 18.9577 | 18.6841 | 18.355 | 18.1061 | 17.8267 | 16.1633 | 13.7622 | 11.104 | 8.0666 | 6.2273 | 10.2478 | 10.1745 | 9.9991 | 9.8362 | 9.5791 | 9.3516 | 9.0112 | 8.3954 | 7.6474 | 6.7653 | 3.2203 | -0.56755 | -3.1681 | -4.7893 | -5.6868 | 19.8878 | 19.8145 | 19.6391 | 19.4762 | 19.2191 | 18.9916 | 18.6512 | 18.0354 | 17.2874 | 16.4053 | 12.8603 | 9.0724 | 6.4719 | 4.8507 | 3.9196 | 10.2478 | 10.2449 | 10.0627 | 9.8494 | 9.5828 | 9.2898 | 8.7928 | 7.8431 | 6.6812 | 5.3893 | 1.351 | -1.945 | -3.9302 | -4.9017 | -4.8612 | 19.8878 | 19.8849 | 19.7027 | 19.4894 | 19.2228 | 18.9298 | 18.4328 | 17.4831 | 16.3212 | 15.0293 | 10.991 | 7.695 | 5.7098 | 4.7383 | 4.736 | 10.2478 | 10.1664 | 9.979 | 9.7926 | 9.5706 | 9.4167 | 9.221 | 8.6628 | 7.9305 | 7.0723 | 3.8452 | 0.64092 | -1.464 | -2.8461 | -3.4068 | 19.8878 | 19.8064 | 19.619 | 19.4326 | 19.2106 | 19.0567 | 18.861 | 18.3028 | 17.5705 | 16.7123 | 13.4852 | 10.2809 | 8.176 | 6.7939 | 6.2387 | 10.2478 | 10.2377 | 10.0404 | 9.7655 | 9.4417 | 9.162 | 8.801 | 8.0248 | 7.0363 | 5.9119 | 1.9423 | -1.8233 | -4.3249 | -5.6169 | -5.6676 | 19.8878 | 19.8777 | 19.6804 | 19.4055 | 19.0817 | 18.802 | 18.441 | 17.6648 | 16.6763 | 15.5519 | 11.5823 | 7.8167 | 5.3151 | 4.0231 | 3.944 | 345810 | 538827 | PENRITH & SHAP | HUTTON
| Hyde | 6.3243 | 5.7654 | 5.531 | 5.3862 | 5.139 | 4.8716 | 4.623 | 4.3915 | 4.0972 | 3.8323 | 1.7456 | -2.0577 | -5.2686 | -8.6821 | -11.6568 | 10.9613 | 10.4024 | 10.168 | 10.0232 | 9.776 | 9.5086 | 9.26 | 9.0285 | 8.7342 | 8.4693 | 6.3826 | 2.5793 | -0.63162 | -4.0451 | -7.1893 | 6.3243 | 6.0614 | 5.8516 | 5.6484 | 5.3869 | 5.0963 | 4.713 | 4.2187 | 3.8576 | 3.4929 | 2.3688 | 1.1837 | 0.068243 | -1.1657 | -2.0782 | 10.9613 | 10.6984 | 10.4886 | 10.2854 | 10.0239 | 9.7333 | 9.35 | 8.8557 | 8.4946 | 8.1299 | 7.0058 | 5.8207 | 4.7052 | 3.4713 | 2.7061 | 6.3243 | 5.7262 | 5.5073 | 4.809 | 3.8579 | 2.8945 | 1.9764 | 1.6822 | 1.3552 | 1.0351 | -0.76348 | -4.324 | -7.2817 | -10.3853 | -12.9992 | 10.9613 | 10.3632 | 10.1443 | 9.446 | 8.4949 | 7.5315 | 6.6134 | 6.3192 | 5.9922 | 5.6721 | 3.8735 | 0.31299 | -2.6447 | -5.7483 | -8.595 | 6.3243 | 6.2117 | 6.1331 | 5.4932 | 4.5688 | 3.6038 | 2.4431 | 1.1668 | -0.17537 | -1.5122 | -4.9438 | -8.295 | -10.9863 | -12.7198 | -11.6609 | 10.9613 | 10.8487 | 10.7701 | 10.1302 | 9.2058 | 8.2408 | 7.0801 | 5.8038 | 4.4616 | 3.1248 | -0.30681 | -3.658 | -6.3493 | -8.0828 | -7.2646 | 6.3243 | 6.0761 | 5.9464 | 5.8869 | 5.8005 | 5.6786 | 5.5189 | 5.327 | 5.0261 | 4.7251 | 3.6441 | 2.3871 | 1.3864 | 0.43633 | -0.016662 | 10.9613 | 10.7131 | 10.5834 | 10.5239 | 10.4375 | 10.3156 | 10.1559 | 9.964 | 9.6631 | 9.3621 | 8.2811 | 7.0241 | 6.0234 | 5.0733 | 4.6448 | 6.3243 | 5.9393 | 5.7145 | 4.9547 | 3.9195 | 2.8759 | 1.6205 | 0.21958 | -1.1989 | -2.6128 | -6.2926 | -9.8679 | -12.7948 | -14.8432 | -14.1477 | 10.9613 | 10.5763 | 10.3515 | 9.5917 | 8.5565 | 7.5129 | 6.2575 | 4.8566 | 3.4381 | 2.0242 | -1.6556 | -5.2309 | -8.1578 | -10.2062 | -9.671 | 395215 | 395126 | HYDE | STALYBRIDGE
| Hyndburn Rd | 4.9013 | 4.1824 | 3.8285 | 3.6221 | 3.2468 | 2.86 | 2.7754 | 2.6832 | 2.5589 | 2.4373 | 1.5689 | 0.071745 | -1.1742 | -2.4567 | -3.5689 | 17.2013 | 16.4824 | 16.1285 | 15.9221 | 15.5468 | 15.16 | 15.0754 | 14.9832 | 14.8589 | 14.7373 | 13.8689 | 12.3717 | 11.1258 | 9.8433 | 8.5932 | 4.9013 | 4.5331 | 4.2917 | 4.1209 | 3.8977 | 3.6503 | 3.4635 | 3.2375 | 3.1183 | 2.9969 | 2.6137 | 2.2022 | 1.8218 | 1.4227 | 1.1366 | 17.2013 | 16.8331 | 16.5917 | 16.4209 | 16.1977 | 15.9503 | 15.7635 | 15.5375 | 15.4183 | 15.2969 | 14.9137 | 14.5022 | 14.1218 | 13.7227 | 13.471 | 4.9013 | 4.0697 | 3.6965 | 3.4893 | 3.1151 | 2.731 | 2.6499 | 2.5646 | 2.4776 | 2.3958 | 1.6311 | 0.23375 | -0.9089 | -2.0263 | -2.8743 | 17.2013 | 16.3697 | 15.9965 | 15.7893 | 15.4151 | 15.031 | 14.9499 | 14.8646 | 14.7776 | 14.6958 | 13.9311 | 12.5338 | 11.3911 | 10.2737 | 9.2486 | 4.9013 | 4.4138 | 4.1291 | 3.9569 | 3.612 | 3.2481 | 3.0856 | 2.6183 | 2.1149 | 1.6197 | 0.19934 | -1.1073 | -2.2157 | -2.9567 | -2.1601 | 17.2013 | 16.7138 | 16.4291 | 16.2569 | 15.912 | 15.5481 | 15.3856 | 14.9183 | 14.4149 | 13.9197 | 12.4993 | 11.1927 | 10.0843 | 9.3433 | 9.9601 | 4.9013 | 4.3082 | 3.9889 | 3.8099 | 3.4929 | 3.1603 | 3.1018 | 3.0197 | 2.896 | 2.7658 | 2.3095 | 1.8294 | 1.5055 | 1.2506 | 1.2776 | 17.2013 | 16.6082 | 16.2889 | 16.1099 | 15.7929 | 15.4603 | 15.4018 | 15.3197 | 15.196 | 15.0658 | 14.6095 | 14.1294 | 13.8055 | 13.5506 | 13.5404 | 4.9013 | 4.0498 | 3.6666 | 3.4489 | 3.0609 | 2.6676 | 2.4788 | 1.973 | 1.4631 | 0.96162 | -0.49219 | -1.8554 | -3.1072 | -3.9924 | -3.3609 | 17.2013 | 16.3498 | 15.9666 | 15.7489 | 15.3609 | 14.9676 | 14.7788 | 14.273 | 13.7631 | 13.2616 | 11.8078 | 10.4446 | 9.1928 | 8.3076 | 8.7967 | 375688 | 428877 | HUNCOAT | PADIHAM
| India St | 13.7623 | 12.9595 | 12.6285 | 12.4043 | 12.1208 | 11.8209 | 11.4899 | 11.152 | 10.3271 | 9.9597 | 6.0872 | 3.3698 | 0.70482 | -1.6368 | -3.6602 | 18.3993 | 17.5965 | 17.2655 | 17.0413 | 16.7578 | 16.4579 | 16.1269 | 15.789 | 14.9641 | 14.5967 | 10.7242 | 8.0068 | 5.3418 | 3.0002 | 0.78318 | 13.7623 | 13.4196 | 13.2754 | 13.1586 | 12.9905 | 12.7912 | 12.53 | 12.1929 | 11.5077 | 11.2604 | 10.5112 | 9.7716 | 9.1147 | 8.4259 | 7.9971 | 18.3993 | 18.0566 | 17.9124 | 17.7956 | 17.6275 | 17.4282 | 17.167 | 16.8299 | 16.1447 | 15.8974 | 15.1482 | 14.4086 | 13.7517 | 13.0629 | 12.6949 | 13.7623 | 12.8817 | 12.5301 | 12.3151 | 12.0447 | 11.7566 | 11.4614 | 11.1659 | 10.3961 | 10.0682 | 6.3033 | 2.5091 | 0.38222 | -1.8095 | -3.633 | 18.3993 | 17.5187 | 17.1671 | 16.9521 | 16.6817 | 16.3936 | 16.0984 | 15.8029 | 15.0331 | 14.7052 | 10.9403 | 7.1461 | 5.0192 | 2.8275 | 0.78116 | 13.7623 | 13.2996 | 13.0599 | 12.8933 | 12.6494 | 12.3534 | 11.4197 | 8.5196 | 7.4739 | 5.639 | 2.1427 | -0.35995 | -2.3981 | -3.7156 | -2.6832 | 18.3993 | 17.9366 | 17.6969 | 17.5303 | 17.2864 | 16.9904 | 16.0567 | 13.1566 | 12.1109 | 10.276 | 6.7797 | 4.277 | 2.2389 | 0.92144 | 1.7275 | 13.7623 | 13.0802 | 12.8021 | 12.6321 | 12.4381 | 12.2149 | 11.9602 | 11.6811 | 10.8628 | 10.4841 | 7.3787 | 6.4737 | 5.4134 | 4.8736 | 4.7038 | 18.3993 | 17.7172 | 17.4391 | 17.2691 | 17.0751 | 16.8519 | 16.5972 | 16.3181 | 15.4998 | 15.1211 | 12.0157 | 11.1107 | 10.0504 | 9.5106 | 9.3307 | 13.7623 | 12.9604 | 12.595 | 12.3426 | 12.0205 | 11.6765 | 10.6926 | 7.7128 | 6.6074 | 4.7133 | 1.0777 | -1.5865 | -3.832 | -5.4233 | -4.6982 | 18.3993 | 17.5974 | 17.232 | 16.9796 | 16.6575 | 16.3135 | 15.3296 | 12.3498 | 11.2444 | 9.3503 | 5.7147 | 3.0505 | 0.80501 | -0.78634 | -0.21953 | 369485 | 421865 | LOWER DARWEN | ROCHDALE
| Ingleton | 1.7753 | 1.6705 | 1.6058 | 1.5503 | 1.4734 | 1.3949 | 1.3281 | 1.2638 | 1.1958 | 1.1196 | 0.57958 | -0.15064 | -0.68032 | -1.1168 | -1.4125 | 9.7753 | 9.6705 | 9.6058 | 9.5503 | 9.4734 | 9.3949 | 9.3281 | 9.2638 | 9.1958 | 9.1196 | 8.5796 | 7.8494 | 7.3197 | 6.8832 | 6.5584 | 1.7753 | 1.6972 | 1.6331 | 1.5665 | 1.488 | 1.4038 | 1.3003 | 1.1674 | 1.0883 | 1.0099 | 0.71414 | 0.42037 | 0.16121 | -0.16306 | -0.35505 | 9.7753 | 9.6972 | 9.6331 | 9.5665 | 9.488 | 9.4038 | 9.3003 | 9.1674 | 9.0883 | 9.0099 | 8.7141 | 8.4204 | 8.1612 | 7.8369 | 7.6728 | 1.7753 | 1.6636 | 1.6016 | 1.5525 | 1.4844 | 1.417 | 1.3635 | 1.3165 | 1.268 | 1.2266 | 0.5119 | -0.29371 | -0.88877 | -1.3838 | -1.7119 | 9.7753 | 9.6636 | 9.6016 | 9.5525 | 9.4844 | 9.417 | 9.3635 | 9.3165 | 9.268 | 9.2266 | 8.5119 | 7.7063 | 7.1112 | 6.6162 | 6.2869 | 1.7753 | 1.7274 | 1.6867 | 1.6432 | 1.5837 | 1.5214 | 1.436 | 1.2484 | 1.0491 | 0.8556 | 0.26843 | -0.392 | -0.92166 | -1.2909 | -1.3028 | 9.7753 | 9.7274 | 9.6867 | 9.6432 | 9.5837 | 9.5214 | 9.436 | 9.2484 | 9.0491 | 8.8556 | 8.2684 | 7.608 | 7.0783 | 6.7091 | 6.6873 | 1.7753 | 1.6877 | 1.631 | 1.586 | 1.5376 | 1.4883 | 1.4383 | 1.3821 | 1.3134 | 1.2461 | 0.96741 | 0.37021 | -0.052825 | -0.40423 | -0.57855 | 9.7753 | 9.6877 | 9.631 | 9.586 | 9.5376 | 9.4883 | 9.4383 | 9.3821 | 9.3134 | 9.2461 | 8.9674 | 8.3702 | 7.9472 | 7.5958 | 7.4367 | 1.7753 | 1.6833 | 1.6168 | 1.5495 | 1.467 | 1.3863 | 1.2812 | 1.0655 | 0.85068 | 0.6419 | -0.012671 | -0.63811 | -1.1225 | -1.4435 | -1.4206 | 9.7753 | 9.6833 | 9.6168 | 9.5495 | 9.467 | 9.3863 | 9.2812 | 9.0655 | 8.8507 | 8.6419 | 7.9873 | 7.3619 | 6.8775 | 6.5565 | 6.578 | 368913 | 472337 | KENDAL (PARKSIDE RD) | HUTTON
| Irlam | 6.4374 | 5.4222 | 5.1297 | 5.0218 | 4.7799 | 4.4732 | 4.1281 | 3.7463 | 3.234 | 2.6967 | -0.17827 | -4.4386 | -7.7096 | -10.9238 | -13.6709 | 10.5774 | 9.5622 | 9.2697 | 9.1618 | 8.9199 | 8.6132 | 8.2681 | 7.8863 | 7.374 | 6.8367 | 3.9617 | -0.29864 | -3.5696 | -6.7838 | -9.6864 | 6.4374 | 6.1253 | 5.9251 | 5.7693 | 5.5696 | 5.3274 | 5.0057 | 4.6123 | 4.251 | 3.8588 | 2.4851 | 0.88769 | -0.99473 | -3.2521 | -4.7154 | 10.5774 | 10.2653 | 10.0651 | 9.9093 | 9.7096 | 9.4674 | 9.1457 | 8.7523 | 8.391 | 7.9988 | 6.6251 | 5.0277 | 3.1453 | 0.88794 | -0.38331 | 6.4374 | 5.298 | 5.0039 | 4.95 | 4.7679 | 4.5383 | 4.3104 | 4.0661 | 3.7405 | 3.3612 | 0.82617 | -3.5033 | -6.819 | -9.6432 | -12.0664 | 10.5774 | 9.438 | 9.1439 | 9.09 | 8.9079 | 8.6783 | 8.4504 | 8.2061 | 7.8805 | 7.5012 | 4.9662 | 0.63674 | -2.679 | -5.5032 | -8.1436 | 6.4374 | 5.9311 | 5.7844 | 5.7435 | 5.5388 | 5.254 | 4.7523 | 3.571 | 2.2573 | 0.88379 | -3.212 | -6.9233 | -9.8459 | -11.5568 | -10.6406 | 10.5774 | 10.0711 | 9.9244 | 9.8835 | 9.6788 | 9.394 | 8.8923 | 7.711 | 6.3973 | 5.0238 | 0.92803 | -2.7833 | -5.7059 | -7.4168 | -6.7226 | 6.4374 | 6.0271 | 5.8982 | 5.8868 | 5.8417 | 5.7274 | 5.5301 | 5.2582 | 4.8325 | 4.3619 | 2.5937 | 0.09722 | -1.5865 | -2.7615 | -3.1425 | 10.5774 | 10.1671 | 10.0382 | 10.0268 | 9.9817 | 9.8674 | 9.6701 | 9.3982 | 8.9725 | 8.5019 | 6.7337 | 4.2372 | 2.5535 | 1.3785 | 0.99171 | 6.4374 | 5.4183 | 5.097 | 4.9681 | 4.6902 | 4.3692 | 3.8319 | 2.6092 | 1.3018 | -0.070203 | -4.3317 | -8.3941 | -11.7333 | -13.8036 | -13.1472 | 10.5774 | 9.5583 | 9.237 | 9.1081 | 8.8302 | 8.5092 | 7.9719 | 6.7492 | 5.4418 | 4.0698 | -0.1917 | -4.2541 | -7.5933 | -9.6636 | -9.1756 | 371680 | 393360 | CARRINGTON BSP | CARRINGTON
| James St | 5.3326 | 4.7672 | 4.401 | 4.0891 | 3.7327 | 3.355 | 2.9912 | 2.6168 | 2.2018 | 1.7982 | -0.31086 | -3.3343 | -6.0162 | -8.9411 | -11.2463 | 9.4696 | 8.9042 | 8.538 | 8.2261 | 7.8697 | 7.492 | 7.1282 | 6.7538 | 6.3388 | 5.9352 | 3.8261 | 0.80272 | -1.8792 | -4.8041 | -7.3903 | 5.3326 | 4.9905 | 4.6645 | 4.3874 | 4.096 | 3.764 | 3.352 | 2.8496 | 2.5732 | 2.2932 | 1.4571 | 0.61229 | -0.10378 | -0.78498 | -1.1654 | 9.4696 | 9.1275 | 8.8015 | 8.5244 | 8.233 | 7.901 | 7.489 | 6.9866 | 6.7102 | 6.4302 | 5.5941 | 4.7493 | 4.0332 | 3.352 | 3.0001 | 5.3326 | 4.6986 | 4.3219 | 4.0092 | 3.6554 | 3.2831 | 2.9269 | 2.5654 | 2.2142 | 1.8795 | -0.044405 | -2.895 | -5.2612 | -7.9153 | -9.832 | 9.4696 | 8.8356 | 8.4589 | 8.1462 | 7.7924 | 7.4201 | 7.0639 | 6.7024 | 6.3512 | 6.0165 | 4.0926 | 1.242 | -1.1242 | -3.7783 | -6.0435 | 5.3326 | 5.0745 | 4.8219 | 4.5847 | 4.2959 | 3.9645 | 3.4498 | 2.3473 | 1.1863 | 0.042937 | -3.3222 | -6.4357 | -8.8517 | -10.2012 | -8.6431 | 9.4696 | 9.2115 | 8.9589 | 8.7217 | 8.4329 | 8.1015 | 7.5868 | 6.4843 | 5.3233 | 4.1799 | 0.81476 | -2.2987 | -4.7147 | -6.0642 | -4.8607 | 5.3326 | 4.9609 | 4.6594 | 4.4125 | 4.1834 | 3.9233 | 3.6209 | 3.2774 | 2.8678 | 2.4494 | 1.1654 | 0.15338 | -0.47296 | -0.92937 | -0.79979 | 9.4696 | 9.0979 | 8.7964 | 8.5495 | 8.3204 | 8.0603 | 7.7579 | 7.4144 | 7.0048 | 6.5864 | 5.3024 | 4.2904 | 3.664 | 3.2076 | 3.2501 | 5.3326 | 4.8158 | 4.4452 | 4.1088 | 3.7288 | 3.3408 | 2.7765 | 1.5919 | 0.40656 | -0.75917 | -4.3762 | -7.6329 | -10.2258 | -11.8162 | -10.551 | 9.4696 | 8.9528 | 8.5822 | 8.2458 | 7.8658 | 7.4778 | 6.9135 | 5.7289 | 4.5436 | 3.3778 | -0.23924 | -3.4959 | -6.0888 | -7.6792 | -6.7019 | 340034 | 555418 | CARLISLE | HARKER
| Kay St | 13.9004 | 13.7111 | 13.5983 | 13.5047 | 13.3118 | 13.1152 | 12.9518 | 12.7986 | 12.5875 | 12.3931 | 10.5867 | 7.5674 | 5.0478 | 2.3279 | 0.14955 | 18.0374 | 17.8481 | 17.7353 | 17.6417 | 17.4488 | 17.2522 | 17.0888 | 16.9356 | 16.7245 | 16.5301 | 14.7237 | 11.7044 | 9.1848 | 6.4649 | 4.073 | 13.9004 | 13.7523 | 13.6325 | 13.5101 | 13.3434 | 13.1451 | 12.8928 | 12.5911 | 12.3396 | 12.0736 | 11.2682 | 10.4903 | 9.7149 | 8.9331 | 8.4627 | 18.0374 | 17.8893 | 17.7695 | 17.6471 | 17.4804 | 17.2821 | 17.0298 | 16.7281 | 16.4766 | 16.2106 | 15.4052 | 14.6273 | 13.8519 | 13.0701 | 12.6669 | 13.9004 | 13.7116 | 13.6194 | 13.5643 | 13.4325 | 13.2934 | 13.2067 | 13.1422 | 13.0112 | 12.7833 | 11.1373 | 8.2394 | 5.8189 | 3.3475 | 1.496 | 18.0374 | 17.8486 | 17.7564 | 17.7013 | 17.5695 | 17.4304 | 17.3437 | 17.2792 | 17.1482 | 16.9203 | 15.2743 | 12.3764 | 9.9559 | 7.4845 | 5.422 | 13.9004 | 13.949 | 13.9356 | 13.9116 | 13.7852 | 13.6198 | 13.2901 | 12.3455 | 11.3516 | 10.3644 | 7.5201 | 4.8252 | 2.6022 | 1.1886 | 2.3583 | 18.0374 | 18.086 | 18.0726 | 18.0486 | 17.9222 | 17.7568 | 17.4271 | 16.4825 | 15.4886 | 14.5014 | 11.6571 | 8.9622 | 6.7392 | 5.3256 | 6.238 | 13.9004 | 13.7505 | 13.6825 | 13.6581 | 13.6192 | 13.5304 | 13.4085 | 13.2784 | 13.0751 | 12.8687 | 11.9932 | 10.932 | 10.1813 | 9.5467 | 9.3393 | 18.0374 | 17.8875 | 17.8195 | 17.7951 | 17.7562 | 17.6674 | 17.5455 | 17.4154 | 17.2121 | 17.0057 | 16.1302 | 15.069 | 14.3183 | 13.6837 | 13.4632 | 13.9004 | 13.84 | 13.7369 | 13.6052 | 13.3781 | 13.1551 | 12.76 | 11.7145 | 10.6438 | 9.5806 | 6.4983 | 3.5746 | 1.1167 | -0.59666 | 0.23717 | 18.0374 | 17.977 | 17.8739 | 17.7422 | 17.5151 | 17.2921 | 16.897 | 15.8515 | 14.7808 | 13.7176 | 10.6353 | 7.7116 | 5.2537 | 3.5403 | 4.1911 | 373863 | 427594 | HUNCOAT | PADIHAM
| Kendal | 4.0096 | 3.0725 | 2.6457 | 2.333 | 1.8646 | 1.3322 | 0.82522 | 0.34363 | -0.15381 | -0.59798 | -3.1896 | -7.4588 | -11.0206 | -14.7946 | -18.2167 | 8.1496 | 7.2125 | 6.7857 | 6.473 | 6.0046 | 5.4722 | 4.9652 | 4.4836 | 3.9862 | 3.542 | 0.95036 | -3.3188 | -6.8806 | -10.6546 | -14.2748 | 4.0096 | 3.4505 | 3.1148 | 2.7874 | 2.3729 | 1.9506 | 1.4143 | 0.73733 | 0.31342 | -0.10673 | -1.3736 | -2.6329 | -3.8449 | -5.2171 | -6.2594 | 8.1496 | 7.5905 | 7.2548 | 6.9274 | 6.5129 | 6.0906 | 5.5543 | 4.8773 | 4.4534 | 4.0333 | 2.7664 | 1.5071 | 0.2951 | -1.0771 | -1.9533 | 4.0096 | 2.9931 | 2.5774 | 2.3149 | 1.8989 | 1.4283 | 1.0157 | 0.62941 | 0.25246 | -0.092318 | -2.3866 | -6.4208 | -9.7715 | -13.2803 | -16.3807 | 8.1496 | 7.1331 | 6.7174 | 6.4549 | 6.0389 | 5.5683 | 5.1557 | 4.7694 | 4.3925 | 4.0477 | 1.7534 | -2.2808 | -5.6315 | -9.1403 | -12.4954 | 4.0096 | 3.6559 | 3.3982 | 3.1516 | 2.7397 | 2.2506 | 1.5584 | 0.091768 | -1.4215 | -2.9178 | -7.0829 | -10.8995 | -13.9184 | -15.8223 | -14.6871 | 8.1496 | 7.7959 | 7.5382 | 7.2916 | 6.8797 | 6.3906 | 5.6984 | 4.2318 | 2.7185 | 1.2222 | -2.9429 | -6.7595 | -9.7784 | -11.6823 | -10.8117 | 4.0096 | 3.3017 | 2.9536 | 2.7211 | 2.4319 | 2.0878 | 1.7123 | 1.3031 | 0.81242 | 0.33708 | -1.1442 | -2.6359 | -3.6684 | -4.7076 | -5.2642 | 8.1496 | 7.4417 | 7.0936 | 6.8611 | 6.5719 | 6.2278 | 5.8523 | 5.4431 | 4.9524 | 4.4771 | 2.9958 | 1.5041 | 0.47158 | -0.56762 | -1.1342 | 4.0096 | 3.2408 | 2.8112 | 2.4351 | 1.9024 | 1.3275 | 0.529 | -1.0744 | -2.6684 | -4.2488 | -8.6899 | -12.7364 | -15.9866 | -18.1791 | -17.3768 | 8.1496 | 7.3808 | 6.9512 | 6.5751 | 6.0424 | 5.4675 | 4.669 | 3.0656 | 1.4716 | -0.10881 | -4.5499 | -8.5964 | -11.8466 | -14.0391 | -13.4277 | 351915 | 491858 | KENDAL (PARKSIDE RD) | HUTTON
| Keswick | 5.6079 | 5.4147 | 5.2555 | 5.1351 | 4.9795 | 4.8226 | 4.7001 | 4.5899 | 4.4631 | 4.3558 | 3.5488 | 2.1261 | 0.97448 | -0.14271 | -1.0929 | 8.1079 | 7.9147 | 7.7555 | 7.6351 | 7.4795 | 7.3226 | 7.2001 | 7.0899 | 6.9631 | 6.8558 | 6.0488 | 4.6261 | 3.4745 | 2.3573 | 1.3026 | 5.6079 | 5.4529 | 5.263 | 5.0792 | 4.8794 | 4.6701 | 4.4152 | 4.1001 | 3.937 | 3.7763 | 3.3157 | 2.8926 | 2.522 | 2.102 | 1.7855 | 8.1079 | 7.9529 | 7.763 | 7.5792 | 7.3794 | 7.1701 | 6.9152 | 6.6001 | 6.437 | 6.2763 | 5.8157 | 5.3926 | 5.022 | 4.602 | 4.3301 | 5.6079 | 5.4101 | 5.2589 | 5.1608 | 5.0242 | 4.8886 | 4.796 | 4.719 | 4.6563 | 4.5952 | 3.9545 | 2.6903 | 1.682 | 0.73586 | -0.012309 | 8.1079 | 7.9101 | 7.7589 | 7.6608 | 7.5242 | 7.3886 | 7.296 | 7.219 | 7.1563 | 7.0952 | 6.4545 | 5.1903 | 4.182 | 3.2359 | 2.3448 | 5.6079 | 5.5325 | 5.4306 | 5.3415 | 5.2304 | 5.1141 | 4.9441 | 4.5145 | 4.061 | 3.606 | 2.319 | 1.1093 | 0.20314 | -0.24434 | 0.39738 | 8.1079 | 8.0325 | 7.9306 | 7.8415 | 7.7304 | 7.6141 | 7.4441 | 7.0145 | 6.561 | 6.106 | 4.819 | 3.6093 | 2.7031 | 2.2557 | 2.7508 | 5.6079 | 5.4872 | 5.3498 | 5.2501 | 5.1602 | 5.0749 | 4.9882 | 4.8777 | 4.726 | 4.5771 | 4.0528 | 3.4361 | 3.0411 | 2.6938 | 2.6657 | 8.1079 | 7.9872 | 7.8498 | 7.7501 | 7.6602 | 7.5749 | 7.4882 | 7.3777 | 7.226 | 7.0771 | 6.5528 | 5.9361 | 5.5411 | 5.1938 | 5.1169 | 5.6079 | 5.4432 | 5.2773 | 5.1243 | 4.9503 | 4.7825 | 4.5553 | 4.0509 | 3.5621 | 3.0729 | 1.6887 | 0.40168 | -0.57723 | -1.1133 | -0.57393 | 8.1079 | 7.9432 | 7.7773 | 7.6243 | 7.4503 | 7.2825 | 7.0553 | 6.5509 | 6.0621 | 5.5729 | 4.1887 | 2.9017 | 1.9228 | 1.3867 | 1.8027 | 327022 | 523784 | STAINBURN & SIDDICK | HARKER
| Kingsway | 25.2531 | 23.6702 | 22.9751 | 22.6222 | 22.2821 | 21.934 | 21.8764 | 21.8002 | 21.6579 | 21.5045 | 20.975 | 20.4527 | 20.0956 | 19.8135 | 19.6366 | 40.2531 | 38.6702 | 37.9751 | 37.6222 | 37.2821 | 36.934 | 36.8764 | 36.8002 | 36.6579 | 36.5045 | 35.975 | 35.4527 | 35.0956 | 34.8135 | 34.6238 | 25.2531 | 24.8491 | 24.7016 | 24.6615 | 24.6408 | 24.6173 | 24.5907 | 24.5606 | 24.4627 | 24.358 | 24.0034 | 23.5131 | 22.7723 | 21.9867 | 21.4831 | 40.2531 | 39.8491 | 39.7016 | 39.6615 | 39.6408 | 39.6173 | 39.5907 | 39.5606 | 39.4627 | 39.358 | 39.0034 | 38.5131 | 37.7723 | 36.9867 | 36.5476 | 25.2531 | 23.4099 | 22.6627 | 22.3109 | 21.9749 | 21.6342 | 21.588 | 21.5284 | 21.4256 | 21.3136 | 20.8681 | 20.3771 | 20.0519 | 19.8583 | 19.8349 | 40.2531 | 38.4099 | 37.6627 | 37.3109 | 36.9749 | 36.6342 | 36.588 | 36.5284 | 36.4256 | 36.3136 | 35.8681 | 35.3771 | 35.0519 | 34.8583 | 34.7922 | 25.2531 | 23.9342 | 23.2988 | 22.9507 | 22.6156 | 22.2682 | 22.1967 | 22.0723 | 21.8993 | 21.7179 | 21.1767 | 20.7357 | 20.4671 | 20.3687 | 20.5339 | 40.2531 | 38.9342 | 38.2988 | 37.9507 | 37.6156 | 37.2682 | 37.1967 | 37.0723 | 36.8993 | 36.7179 | 36.1767 | 35.7357 | 35.4671 | 35.3687 | 35.4898 | 25.2531 | 24.4658 | 23.938 | 23.5958 | 23.2722 | 22.9389 | 22.8936 | 22.8345 | 22.7136 | 22.5808 | 22.1335 | 21.7151 | 21.3606 | 21.0727 | 21.0309 | 40.2531 | 39.4658 | 38.938 | 38.5958 | 38.2722 | 37.9389 | 37.8936 | 37.8345 | 37.7136 | 37.5808 | 37.1335 | 36.7151 | 36.3606 | 36.0727 | 36.0273 | 25.2531 | 23.1501 | 22.3492 | 21.994 | 21.6553 | 21.3122 | 21.2502 | 21.136 | 20.9779 | 20.8106 | 20.2717 | 19.7802 | 19.4571 | 19.3277 | 19.4854 | 40.2531 | 38.1501 | 37.3492 | 36.994 | 36.6553 | 36.3122 | 36.2502 | 36.136 | 35.9779 | 35.8106 | 35.2717 | 34.7802 | 34.4571 | 34.3277 | 34.4427 | 391636 | 411724 | BELFIELD | ROCHDALE
| Kinkry Hill | 0.78604 | 0.39093 | 0.2982 | 0.27243 | 0.24129 | 0.20968 | 0.18224 | 0.15733 | 0.12704 | 0.10123 | -0.038946 | -0.2508 | -0.40014 | -0.49831 | -0.55102 | 2.286 | 1.8909 | 1.7982 | 1.7724 | 1.7413 | 1.7097 | 1.6822 | 1.6573 | 1.627 | 1.6012 | 1.4611 | 1.2492 | 1.0999 | 1.0017 | 0.94838 | 0.78604 | 0.73707 | 0.70188 | 0.66851 | 0.62956 | 0.58948 | 0.54277 | 0.49054 | 0.4519 | 0.41284 | 0.27389 | 0.14854 | 0.043971 | -0.060935 | -0.13256 | 2.286 | 2.2371 | 2.2019 | 2.1685 | 2.1296 | 2.0895 | 2.0428 | 1.9905 | 1.9519 | 1.9128 | 1.7739 | 1.6485 | 1.544 | 1.4391 | 1.3783 | 0.78604 | 0.33038 | 0.23012 | 0.21067 | 0.18653 | 0.16345 | 0.14686 | 0.13535 | 0.12033 | 0.064315 | -0.18464 | -0.42886 | -0.59237 | -0.6979 | -0.74989 | 2.286 | 1.8304 | 1.7301 | 1.7107 | 1.6865 | 1.6635 | 1.6469 | 1.6354 | 1.6203 | 1.5643 | 1.3154 | 1.0711 | 0.90763 | 0.8021 | 0.74911 | 0.78604 | 0.46931 | 0.39848 | 0.37714 | 0.35587 | 0.33198 | 0.30731 | 0.2716 | 0.22718 | 0.18197 | 0.049956 | -0.18775 | -0.34396 | -0.44269 | -0.44784 | 2.286 | 1.9693 | 1.8985 | 1.8771 | 1.8559 | 1.832 | 1.8073 | 1.7716 | 1.7272 | 1.682 | 1.55 | 1.3122 | 1.156 | 1.0573 | 1.0482 | 0.78604 | 0.71343 | 0.68029 | 0.65977 | 0.63947 | 0.61934 | 0.59994 | 0.58277 | 0.55729 | 0.52333 | 0.31724 | 0.091323 | -0.06345 | -0.18702 | -0.23892 | 2.286 | 2.2134 | 2.1803 | 2.1598 | 2.1395 | 2.1193 | 2.0999 | 2.0828 | 2.0573 | 2.0233 | 1.8172 | 1.5913 | 1.4365 | 1.313 | 1.2623 | 0.78604 | 0.26952 | 0.15249 | 0.11553 | 0.079346 | 0.04458 | 0.0080075 | -0.045539 | -0.10304 | -0.16064 | -0.32069 | -0.47936 | -0.588 | -0.62394 | -0.5963 | 2.286 | 1.7695 | 1.6525 | 1.6155 | 1.5793 | 1.5446 | 1.508 | 1.4545 | 1.397 | 1.3394 | 1.1793 | 1.0206 | 0.912 | 0.87606 | 0.90086 | 350800 | 575111 | - | HARKER
| Kirkby Lonsdale | 2.8412 | 2.7037 | 2.5959 | 2.5132 | 2.4115 | 2.3092 | 2.2208 | 2.1365 | 2.0317 | 1.939 | 1.4429 | 0.64968 | -0.056581 | -0.79089 | -1.4365 | 6.8412 | 6.7037 | 6.5959 | 6.5132 | 6.4115 | 6.3092 | 6.2208 | 6.1365 | 6.0317 | 5.939 | 5.4429 | 4.6497 | 3.9434 | 3.2091 | 2.5169 | 2.8412 | 2.7218 | 2.5991 | 2.4808 | 2.3471 | 2.2023 | 2.0265 | 1.8125 | 1.6765 | 1.5418 | 1.1516 | 0.7859 | 0.46237 | 0.10993 | -0.14658 | 6.8412 | 6.7218 | 6.5991 | 6.4808 | 6.3471 | 6.2023 | 6.0265 | 5.8125 | 5.6765 | 5.5418 | 5.1516 | 4.7859 | 4.4624 | 4.1099 | 3.893 | 2.8412 | 2.7022 | 2.6022 | 2.5381 | 2.4541 | 2.3724 | 2.3126 | 2.2604 | 2.2048 | 2.1386 | 1.6242 | 0.81157 | 0.18242 | -0.43526 | -0.95373 | 6.8412 | 6.7022 | 6.6022 | 6.5381 | 6.4541 | 6.3724 | 6.3126 | 6.2604 | 6.2048 | 6.1386 | 5.6242 | 4.8116 | 4.1824 | 3.5647 | 2.9872 | 2.8412 | 2.8058 | 2.7456 | 2.6991 | 2.6355 | 2.5659 | 2.4724 | 2.2571 | 1.9838 | 1.677 | 0.80356 | -0.025808 | -0.63917 | -0.97824 | -0.66394 | 6.8412 | 6.8058 | 6.7456 | 6.6991 | 6.6355 | 6.5659 | 6.4724 | 6.2571 | 5.9838 | 5.677 | 4.8036 | 3.9742 | 3.3608 | 3.0218 | 3.2606 | 2.8412 | 2.7254 | 2.6325 | 2.5689 | 2.5067 | 2.44 | 2.3682 | 2.2866 | 2.1719 | 2.0603 | 1.6932 | 1.2881 | 1.0172 | 0.77382 | 0.68476 | 6.8412 | 6.7254 | 6.6325 | 6.5689 | 6.5067 | 6.44 | 6.3682 | 6.2866 | 6.1719 | 6.0603 | 5.6932 | 5.2881 | 5.0172 | 4.7738 | 4.677 | 2.8412 | 2.7403 | 2.6334 | 2.5406 | 2.4326 | 2.3285 | 2.1956 | 1.9277 | 1.661 | 1.3915 | 0.54197 | -0.31179 | -0.96134 | -1.3551 | -1.1194 | 6.8412 | 6.7403 | 6.6334 | 6.5406 | 6.4326 | 6.3285 | 6.1956 | 5.9277 | 5.661 | 5.3915 | 4.542 | 3.6882 | 3.0387 | 2.6449 | 2.8252 | 359833 | 478813 | KENDAL (PARKSIDE RD) | HUTTON
| Kirkby Moor | 2.2947 | 2.2526 | 2.1599 | 2.0673 | 1.9623 | 1.8553 | 1.7544 | 1.6815 | 1.5605 | 1.3856 | 0.809 | 0.18077 | -0.2737 | -0.62883 | -0.86024 | 5.7947 | 5.7526 | 5.6599 | 5.5673 | 5.4623 | 5.3553 | 5.2544 | 5.1815 | 5.0605 | 4.8856 | 4.309 | 3.6808 | 3.2263 | 2.8712 | 2.6342 | 2.2947 | 2.2553 | 2.2023 | 2.1485 | 2.0885 | 2.0254 | 1.9462 | 1.7843 | 1.6814 | 1.5702 | 1.2468 | 0.93239 | 0.67565 | 0.44604 | 0.31788 | 5.7947 | 5.7553 | 5.7023 | 5.6485 | 5.5885 | 5.5254 | 5.4462 | 5.2843 | 5.1814 | 5.0702 | 4.7468 | 4.4324 | 4.1756 | 3.946 | 3.8349 | 2.2947 | 2.252 | 2.1596 | 2.0673 | 1.9632 | 1.8574 | 1.7581 | 1.6121 | 1.4087 | 1.2162 | 0.58369 | -0.10315 | -0.59883 | -0.98093 | -1.221 | 5.7947 | 5.752 | 5.6596 | 5.5673 | 5.4632 | 5.3574 | 5.2581 | 5.1121 | 4.9087 | 4.7162 | 4.0837 | 3.3968 | 2.9012 | 2.5191 | 2.2744 | 2.2947 | 2.2711 | 2.1957 | 2.1111 | 2.0197 | 1.9164 | 1.7901 | 1.6228 | 1.4498 | 1.2817 | 0.66271 | 0.00050161 | -0.46542 | -0.78311 | -0.78508 | 5.7947 | 5.7711 | 5.6957 | 5.6111 | 5.5197 | 5.4164 | 5.2901 | 5.1228 | 4.9498 | 4.7817 | 4.1627 | 3.5005 | 3.0346 | 2.7169 | 2.7029 | 2.2947 | 2.2582 | 2.176 | 2.0993 | 2.0226 | 1.9391 | 1.8483 | 1.7845 | 1.7125 | 1.6085 | 1.0912 | 0.54879 | 0.16725 | -0.14973 | -0.30134 | 5.7947 | 5.7582 | 5.676 | 5.5993 | 5.5226 | 5.4391 | 5.3483 | 5.2845 | 5.2125 | 5.1085 | 4.5912 | 4.0488 | 3.6672 | 3.3503 | 3.2078 | 2.2947 | 2.2554 | 2.1589 | 2.0496 | 1.9368 | 1.8247 | 1.692 | 1.507 | 1.3205 | 1.1401 | 0.49244 | -0.12217 | -0.55216 | -0.8238 | -0.82047 | 5.7947 | 5.7554 | 5.6589 | 5.5496 | 5.4368 | 5.3247 | 5.192 | 5.007 | 4.8205 | 4.6401 | 3.9924 | 3.3778 | 2.9478 | 2.6762 | 2.673 | 326099 | 483011 | ULVERSTON | HARKER
| Kirkby Stephen | 9.8716 | 9.1667 | 8.9523 | 8.8416 | 8.6623 | 8.4692 | 8.2955 | 8.107 | 7.9074 | 7.7212 | 6.7476 | 5.2695 | 4.1114 | 3.0802 | 2.1512 | 12.3716 | 11.6667 | 11.4523 | 11.3416 | 11.1623 | 10.9692 | 10.7955 | 10.607 | 10.4074 | 10.2212 | 9.2476 | 7.7695 | 6.6114 | 5.5802 | 4.5719 | 9.8716 | 9.6933 | 9.5362 | 9.3718 | 9.1803 | 8.999 | 8.7773 | 8.3518 | 8.2225 | 8.0883 | 7.6612 | 7.0815 | 6.5035 | 5.7992 | 5.2253 | 12.3716 | 12.1933 | 12.0362 | 11.8718 | 11.6803 | 11.499 | 11.2773 | 10.8518 | 10.7225 | 10.5883 | 10.1612 | 9.5815 | 9.0035 | 8.2992 | 7.8163 | 9.8716 | 9.0777 | 8.8567 | 8.7655 | 8.6072 | 8.44 | 8.3029 | 8.1759 | 8.058 | 7.9234 | 7.0724 | 5.5118 | 4.3238 | 3.4233 | 2.8253 | 12.3716 | 11.5777 | 11.3567 | 11.2655 | 11.1072 | 10.94 | 10.8029 | 10.6759 | 10.558 | 10.4234 | 9.5724 | 8.0118 | 6.8238 | 5.9233 | 5.2237 | 9.8716 | 9.3666 | 9.2058 | 9.083 | 8.9243 | 8.7557 | 8.5297 | 8.0735 | 7.5844 | 7.0891 | 5.6584 | 4.3462 | 3.4147 | 2.96 | 3.4061 | 12.3716 | 11.8666 | 11.7058 | 11.583 | 11.4243 | 11.2557 | 11.0297 | 10.5735 | 10.0844 | 9.5891 | 8.1584 | 6.8462 | 5.9147 | 5.46 | 5.8012 | 9.8716 | 9.6854 | 9.5629 | 9.4605 | 9.3428 | 9.2394 | 9.1363 | 9.0129 | 8.8379 | 8.6563 | 7.9722 | 7.0768 | 6.216 | 5.5161 | 5.1614 | 12.3716 | 12.1854 | 12.0629 | 11.9605 | 11.8428 | 11.7394 | 11.6363 | 11.5129 | 11.3379 | 11.1563 | 10.4722 | 9.5768 | 8.716 | 8.0161 | 7.6717 | 9.8716 | 9.0337 | 8.7786 | 8.608 | 8.4034 | 8.1988 | 7.9396 | 7.4474 | 6.9421 | 6.4248 | 4.8951 | 3.4606 | 2.4107 | 1.8331 | 2.1644 | 12.3716 | 11.5337 | 11.2786 | 11.108 | 10.9034 | 10.6988 | 10.4396 | 9.9474 | 9.4421 | 8.9248 | 7.3951 | 5.9606 | 4.9107 | 4.3331 | 4.5835 | 376579 | 509136 | PENRITH & SHAP | HUTTON
| Kirkby Thore | 6.7692 | 6.1937 | 6.0534 | 5.9952 | 5.845 | 5.6777 | 5.5225 | 5.3729 | 5.1866 | 5.0191 | 4.2697 | 3.2505 | 2.4673 | 1.88 | 1.23 | 18.0192 | 17.4437 | 17.3034 | 17.2452 | 17.095 | 16.9277 | 16.7725 | 16.6229 | 16.4366 | 16.2691 | 15.5197 | 14.5005 | 13.7173 | 13.13 | 12.4047 | 6.7692 | 6.6204 | 6.517 | 6.4025 | 6.2808 | 6.1841 | 6.0584 | 5.8931 | 5.744 | 5.5941 | 5.1355 | 4.6786 | 4.1858 | 3.511 | 2.4387 | 18.0192 | 17.8704 | 17.767 | 17.6525 | 17.5308 | 17.4341 | 17.3084 | 17.1431 | 16.994 | 16.8441 | 16.3855 | 15.9286 | 15.4358 | 14.761 | 14.2588 | 6.7692 | 6.1245 | 5.9811 | 5.9472 | 5.8184 | 5.6764 | 5.5596 | 5.4195 | 5.2722 | 5.1443 | 4.5292 | 3.1855 | 2.5203 | 2.1134 | 1.712 | 18.0192 | 17.3745 | 17.2311 | 17.1972 | 17.0684 | 16.9264 | 16.8096 | 16.6695 | 16.5222 | 16.3943 | 15.7792 | 14.4355 | 13.7703 | 13.3634 | 12.8391 | 6.7692 | 6.4047 | 6.3124 | 6.2117 | 6.0461 | 5.3386 | 5.1576 | 4.841 | 4.4918 | 4.1494 | 3.126 | 2.1947 | 1.6766 | 1.6207 | 2.1843 | 18.0192 | 17.6547 | 17.5624 | 17.4617 | 17.2961 | 16.5886 | 16.4076 | 16.091 | 15.7418 | 15.3994 | 14.376 | 13.4447 | 12.9266 | 12.8707 | 13.308 | 6.7692 | 6.6072 | 6.5378 | 6.4811 | 6.3813 | 6.2986 | 6.2178 | 6.1235 | 5.963 | 5.8028 | 5.2162 | 4.5673 | 4.1434 | 3.7637 | 3.4854 | 18.0192 | 17.8572 | 17.7878 | 17.7311 | 17.6313 | 17.5486 | 17.4678 | 17.3735 | 17.213 | 17.0528 | 16.4662 | 15.8173 | 15.3934 | 15.0137 | 14.6905 | 6.7692 | 6.1264 | 5.953 | 5.8311 | 5.6529 | 4.9426 | 4.7668 | 4.4451 | 4.1138 | 3.7654 | 2.6954 | 1.6843 | 1.0624 | 0.90164 | 1.3375 | 18.0192 | 17.3764 | 17.203 | 17.0811 | 16.9029 | 16.1926 | 16.0168 | 15.6951 | 15.3638 | 15.0154 | 13.9454 | 12.9343 | 12.3124 | 12.1516 | 12.4905 | 364439 | 526672 | PENRITH & SHAP | HUTTON
| Kirkhall Lane | 6.4081 | 5.1502 | 4.791 | 4.6559 | 4.4296 | 4.1911 | 3.9727 | 3.7837 | 3.5668 | 3.3759 | 1.9332 | -0.72658 | -2.9579 | -5.3179 | -7.5217 | 8.7581 | 7.5002 | 7.141 | 7.0059 | 6.7796 | 6.5411 | 6.3227 | 6.1337 | 5.9168 | 5.7259 | 4.2832 | 1.6234 | -0.60786 | -2.9679 | -5.2582 | 6.4081 | 5.9581 | 5.7965 | 5.7 | 5.5609 | 5.4063 | 5.1897 | 4.8798 | 4.5961 | 4.3116 | 3.4595 | 2.5805 | 1.7287 | 0.7808 | 0.11269 | 8.7581 | 8.3081 | 8.1465 | 8.05 | 7.9109 | 7.7563 | 7.5397 | 7.2298 | 6.9461 | 6.6616 | 5.8095 | 4.9305 | 4.0787 | 3.1308 | 2.5787 | 6.4081 | 4.9781 | 4.6012 | 4.4987 | 4.1865 | 3.8682 | 3.5887 | 3.3407 | 3.0705 | 2.8169 | 1.4473 | -1.054 | -3.1465 | -5.3478 | -7.3787 | 8.7581 | 7.3281 | 6.9512 | 6.8487 | 6.5365 | 6.2182 | 5.9387 | 5.6907 | 5.4205 | 5.1669 | 3.7973 | 1.296 | -0.79653 | -2.9978 | -5.147 | 6.4081 | 5.6106 | 5.383 | 5.3042 | 4.99 | 4.6452 | 4.1861 | 3.2767 | 2.3331 | 1.3989 | -1.0827 | -3.4623 | -5.3849 | -6.6444 | -6.1061 | 8.7581 | 7.9606 | 7.733 | 7.6542 | 7.34 | 6.9952 | 6.5361 | 5.6267 | 4.6831 | 3.7489 | 1.2673 | -1.1123 | -3.0349 | -4.2944 | -3.8801 | 6.4081 | 5.6395 | 5.4111 | 5.3476 | 5.2582 | 5.1411 | 5.0065 | 4.8653 | 4.6516 | 4.4449 | 3.7145 | 2.8114 | 2.1702 | 1.4699 | 1.0071 | 8.7581 | 7.9895 | 7.7611 | 7.6976 | 7.6082 | 7.4911 | 7.3565 | 7.2153 | 7.0016 | 6.7949 | 6.0645 | 5.1614 | 4.5202 | 3.8199 | 3.3984 | 6.4081 | 4.9994 | 4.5875 | 4.4287 | 4.0421 | 3.6513 | 3.1338 | 2.1427 | 1.1337 | 0.13435 | -2.5386 | -5.0644 | -7.1312 | -8.5742 | -8.2566 | 8.7581 | 7.3494 | 6.9375 | 6.7787 | 6.3921 | 6.0013 | 5.4838 | 4.4927 | 3.4837 | 2.4844 | -0.1886 | -2.7144 | -4.7812 | -6.2242 | -5.9811 | 365510 | 401069 | ATHERTON | KEARSLEY
| Kitt Green | 6.3197 | 5.6303 | 5.1005 | 4.7346 | 4.294 | 3.7574 | 3.2232 | 3.0724 | -1.673 | -1.8827 | -7.2379 | -9.3328 | -11.8057 | -13.3719 | -14.2936 | 13.3197 | 12.6303 | 12.1005 | 11.7346 | 11.294 | 10.7574 | 10.2232 | 10.0724 | 5.327 | 5.1173 | -0.2379 | -2.3328 | -4.8057 | -6.3719 | -7.5092 | 6.3197 | 6.1629 | 6.0242 | 5.9682 | 5.9345 | 5.8979 | 5.8335 | 5.7444 | 5.5322 | 5.306 | 4.3945 | 3.3316 | 1.4337 | 0.25616 | -0.44995 | 13.3197 | 13.1629 | 13.0242 | 12.9682 | 12.9345 | 12.8979 | 12.8335 | 12.7444 | 12.5322 | 12.306 | 11.3945 | 10.3316 | 8.4337 | 7.2562 | 6.6369 | 6.3197 | 5.5426 | 5.0059 | 4.6762 | 4.2658 | 3.766 | 3.2899 | 3.2057 | -1.3231 | -1.3908 | -7.321 | -9.2816 | -10.8436 | -12.2132 | -12.8122 | 13.3197 | 12.5426 | 12.0059 | 11.6762 | 11.2658 | 10.766 | 10.2899 | 10.2057 | 5.6769 | 5.6092 | -0.32097 | -2.2816 | -3.8436 | -5.2132 | -6.0893 | 6.3197 | 5.9094 | 5.4508 | 5.1187 | 4.6905 | 4.1585 | 3.5393 | -6.9564 | -7.2381 | -7.6148 | -9.3972 | -11.2621 | -12.597 | -13.2453 | -11.9752 | 13.3197 | 12.9094 | 12.4508 | 12.1187 | 11.6905 | 11.1585 | 10.5393 | 0.043561 | -0.2381 | -0.61481 | -2.3972 | -4.2621 | -5.597 | -6.2453 | -5.2549 | 6.3197 | 6.076 | 5.6542 | 5.352 | 5.0691 | 4.702 | 4.3056 | 4.2366 | -0.43614 | -0.59062 | -5.4047 | -6.4199 | -7.8509 | -8.3571 | -7.8605 | 13.3197 | 13.076 | 12.6542 | 12.352 | 12.0691 | 11.702 | 11.3056 | 11.2366 | 6.5639 | 6.4094 | 1.5953 | 0.58011 | -0.85085 | -1.3571 | -1.0048 | 6.3197 | 5.5599 | 5.0035 | 4.6383 | 4.1838 | 3.6429 | 3.0165 | -7.4866 | -7.7599 | -8.1256 | -9.9624 | -12.0224 | -13.5634 | -14.3809 | -13.2345 | 13.3197 | 12.5599 | 12.0035 | 11.6383 | 11.1838 | 10.6429 | 10.0165 | -0.48662 | -0.75987 | -1.1256 | -2.9624 | -5.0224 | -6.5634 | -7.3809 | -6.4885 | 354934 | 405497 | ORRELL | KIRKBY
| Knott Mill | 9.5182 | 5.1468 | 3.9251 | 3.5392 | 3.1666 | 2.7822 | 2.404 | 2.0076 | 1.5616 | 1.1299 | -0.25725 | -1.8363 | -2.9644 | -4.1297 | -5.3233 | 14.1552 | 9.7838 | 8.5621 | 8.1762 | 7.8036 | 7.4192 | 7.041 | 6.6446 | 6.1986 | 5.7669 | 4.3798 | 2.8007 | 1.6726 | 0.50725 | -0.55528 | 9.5182 | 8.0306 | 7.4365 | 7.0747 | 6.7062 | 6.3359 | 5.9323 | 5.458 | 5.012 | 4.5547 | 3.2661 | 2.0306 | 1.0187 | -0.090078 | -1.1855 | 14.1552 | 12.6676 | 12.0735 | 11.7117 | 11.3432 | 10.9729 | 10.5693 | 10.095 | 9.649 | 9.1917 | 7.9031 | 6.6676 | 5.6557 | 4.5469 | 3.6529 | 9.5182 | 4.4426 | 3.0476 | 2.6307 | 2.2161 | 1.784 | 1.3691 | 0.91972 | 0.45183 | -0.028585 | -1.5883 | -3.2817 | -4.4831 | -5.7389 | -7.0051 | 14.1552 | 9.0796 | 7.6846 | 7.2677 | 6.8531 | 6.421 | 6.0061 | 5.5567 | 5.0888 | 4.6084 | 3.0487 | 1.3553 | 0.15394 | -1.1019 | -2.1864 | 9.5182 | 5.9485 | 4.9007 | 4.5481 | 4.1814 | 3.7726 | 3.3555 | 2.8416 | 2.2825 | 1.7041 | 0.042828 | -1.5536 | -2.6483 | -3.6835 | -4.6169 | 14.1552 | 10.5855 | 9.5377 | 9.1851 | 8.8184 | 8.4096 | 7.9925 | 7.4786 | 6.9195 | 6.3411 | 4.6798 | 3.0834 | 1.9887 | 0.95354 | 0.19107 | 9.5182 | 6.8264 | 5.9743 | 5.6324 | 5.3087 | 4.9586 | 4.6159 | 4.2556 | 3.8218 | 3.3861 | 2.1102 | 0.84731 | -0.064202 | -1.0605 | -2.0645 | 14.1552 | 11.4634 | 10.6113 | 10.2694 | 9.9457 | 9.5956 | 9.2529 | 8.8926 | 8.4588 | 8.0231 | 6.7472 | 5.4843 | 4.5728 | 3.5765 | 2.7514 | 9.5182 | 3.8714 | 2.3483 | 1.9261 | 1.498 | 1.0548 | 0.59206 | 0.016694 | -0.58566 | -1.2077 | -3.0012 | -4.6627 | -5.8162 | -6.9236 | -7.9775 | 14.1552 | 8.5084 | 6.9853 | 6.5631 | 6.135 | 5.6918 | 5.2291 | 4.6537 | 4.0513 | 3.4293 | 1.6358 | -0.025741 | -1.1792 | -2.2866 | -3.1405 | 383136 | 397725 | BLOOM ST | SOUTH MANCHESTER
| Lamberhead | 12.31 | 10.9579 | 10.4686 | 10.2467 | 9.9688 | 9.7039 | 9.5031 | 9.3445 | 9.1013 | 8.8785 | 7.1062 | 3.842 | 1.0523 | -1.8653 | -4.4314 | 16.95 | 15.5979 | 15.1086 | 14.8867 | 14.6088 | 14.3439 | 14.1431 | 13.9845 | 13.7413 | 13.5185 | 11.7462 | 8.482 | 5.6923 | 2.7747 | 0.023316 | 12.31 | 12.0327 | 11.8048 | 11.6331 | 11.4541 | 11.2564 | 11.0145 | 10.7101 | 10.3976 | 10.0832 | 9.1661 | 8.2965 | 7.4361 | 6.5734 | 5.9539 | 16.95 | 16.6727 | 16.4448 | 16.2731 | 16.0941 | 15.8964 | 15.6545 | 15.3501 | 15.0376 | 14.7232 | 13.8061 | 12.9365 | 12.0761 | 11.2134 | 10.6897 | 12.31 | 10.7785 | 10.2737 | 10.1004 | 9.8693 | 9.658 | 9.526 | 9.4492 | 9.327 | 9.1957 | 7.6974 | 4.7013 | 2.1583 | -0.45393 | -2.6613 | 16.95 | 15.4185 | 14.9137 | 14.7404 | 14.5093 | 14.298 | 14.166 | 14.0892 | 13.967 | 13.8357 | 12.3374 | 9.3413 | 6.7983 | 4.1861 | 1.7265 | 12.31 | 11.2864 | 10.9206 | 10.7591 | 10.5209 | 10.2676 | 9.8764 | 8.8867 | 7.8342 | 6.7756 | 3.7379 | 0.85913 | -1.5083 | -2.9559 | -1.8211 | 16.95 | 15.9264 | 15.5606 | 15.3991 | 15.1609 | 14.9076 | 14.5164 | 13.5267 | 12.4742 | 11.4156 | 8.3779 | 5.4991 | 3.1317 | 1.6841 | 2.5656 | 12.31 | 11.8949 | 11.6358 | 11.5002 | 11.392 | 11.2663 | 11.1421 | 11.0213 | 10.7827 | 10.5447 | 9.7478 | 8.8552 | 8.1162 | 7.5118 | 7.3538 | 16.95 | 16.5349 | 16.2758 | 16.1402 | 16.032 | 15.9063 | 15.7821 | 15.6613 | 15.4227 | 15.1847 | 14.3878 | 13.4952 | 12.7562 | 12.1518 | 11.9701 | 12.31 | 10.6137 | 10.0392 | 9.7823 | 9.4579 | 9.1481 | 8.6951 | 7.6087 | 6.484 | 5.3557 | 2.1134 | -0.95901 | -3.5185 | -5.2034 | -4.3355 | 16.95 | 15.2537 | 14.6792 | 14.4223 | 14.0979 | 13.7881 | 13.3351 | 12.2487 | 11.124 | 9.9957 | 6.7534 | 3.681 | 1.1215 | -0.56338 | 0.10994 | 355516 | 404030 | ORRELL | KIRKBY
| Lancaster | 2.7387 | 1.1642 | -0.89408 | -0.98386 | -1.1788 | -1.4058 | -1.6155 | -1.7962 | -2.1551 | -2.4823 | -4.5563 | -9.08 | -11.7815 | -14.3187 | -16.66 | 6.8757 | 5.3012 | 3.2429 | 3.1531 | 2.9582 | 2.7312 | 2.5215 | 2.3408 | 1.9819 | 1.6547 | -0.41934 | -4.943 | -7.6445 | -10.1817 | -12.7294 | 2.7387 | 2.1461 | 1.8971 | 1.7045 | 1.4796 | 1.2441 | 0.93742 | 0.53823 | 0.099302 | -0.33873 | -1.638 | -4.0554 | -5.3123 | -6.6055 | -8.4221 | 6.8757 | 6.2831 | 6.0341 | 5.8415 | 5.6166 | 5.3811 | 5.0744 | 4.6752 | 4.2363 | 3.7983 | 2.499 | 0.081649 | -1.1753 | -2.4685 | -3.2223 | 2.7387 | 0.96677 | -1.0441 | -1.0669 | -1.1967 | -1.3484 | -2.5878 | -2.5784 | -2.7369 | -2.9012 | -5.6279 | -8.9724 | -11.3529 | -13.3001 | -15.1721 | 6.8757 | 5.1038 | 3.0929 | 3.0701 | 2.9403 | 2.7886 | 1.5492 | 1.5586 | 1.4001 | 1.2358 | -1.4909 | -4.8354 | -7.2159 | -9.1631 | -11.3296 | 2.7387 | 1.764 | 1.5174 | -1.4172 | -1.4622 | -1.5688 | -1.8308 | -2.6672 | -3.6996 | -4.7489 | -8.0904 | -11.0025 | -13.1708 | -14.1696 | -12.865 | 6.8757 | 5.901 | 5.6544 | 2.7198 | 2.6748 | 2.5682 | 2.3062 | 1.4698 | 0.43738 | -0.61191 | -3.9534 | -6.8655 | -9.0338 | -10.0326 | -9.0204 | 2.7387 | 1.8028 | -0.10214 | -0.099415 | -0.109 | -0.15726 | -0.24167 | -0.35915 | -0.70784 | -1.0546 | -2.2941 | -4.7928 | -5.8473 | -6.9123 | -7.3256 | 6.8757 | 5.9398 | 4.0349 | 4.0376 | 4.028 | 3.9797 | 3.8953 | 3.7779 | 3.4292 | 3.0824 | 1.8429 | -0.65583 | -1.7103 | -2.7753 | -3.1843 | 2.7387 | 1.0045 | 0.54119 | -2.5023 | -2.6444 | -2.8129 | -3.1503 | -4.0886 | -5.1906 | -6.3104 | -9.9055 | -13.0774 | -15.4997 | -16.7739 | -15.7551 | 6.8757 | 5.1415 | 4.6782 | 1.6347 | 1.4926 | 1.3241 | 0.9867 | 0.048401 | -1.0536 | -2.1734 | -5.7685 | -8.9404 | -11.3627 | -12.6369 | -11.8483 | 348644 | 463628 | LANCASTER | HEYSHAM | Firm Capacity exceeded in FY26. Review n RIIO-ED2 and possibly install a third transformer.
| Langley | 8.8251 | 6.1762 | 5.3403 | 4.9358 | 4.3399 | 3.7063 | 3.0958 | 2.5433 | 1.9721 | 1.4273 | -1.2716 | -5.2946 | -8.3024 | -11.1426 | -13.7439 | 13.4621 | 10.8132 | 9.9773 | 9.5728 | 8.9769 | 8.3433 | 7.7328 | 7.1803 | 6.6091 | 6.0643 | 3.3654 | -0.65762 | -3.6654 | -6.5056 | -9.1201 | 8.8251 | 7.9077 | 7.5501 | 7.332 | 7.0657 | 6.8109 | 6.46 | 5.9249 | 5.4391 | 4.924 | 3.3191 | 1.579 | -0.12154 | -2.1156 | -3.6227 | 13.4621 | 12.5447 | 12.1871 | 11.969 | 11.7027 | 11.4479 | 11.097 | 10.5619 | 10.0761 | 9.561 | 7.9561 | 6.216 | 4.5155 | 2.5214 | 1.2885 | 8.8251 | 5.7025 | 4.6865 | 4.1786 | 3.4772 | 2.7293 | 2.0136 | 1.3341 | 0.64462 | -0.051944 | -3.174 | -7.2398 | -10.0249 | -12.4536 | -14.2643 | 13.4621 | 10.3395 | 9.3235 | 8.8156 | 8.1142 | 7.3663 | 6.6506 | 5.9711 | 5.2816 | 4.5851 | 1.463 | -2.6028 | -5.3879 | -7.8166 | -9.5907 | 8.8251 | 6.8187 | 6.0448 | 5.5502 | 4.8399 | 4.069 | 3.1616 | 1.7492 | 0.34179 | -1.035 | -4.9613 | -8.4852 | -10.7117 | -12.0058 | -12.1777 | 13.4621 | 11.4557 | 10.6818 | 10.1872 | 9.4769 | 8.706 | 7.7986 | 6.3862 | 4.9788 | 3.602 | -0.32426 | -3.8482 | -6.0747 | -7.3688 | -7.5161 | 8.8251 | 7.1753 | 6.5698 | 6.2564 | 5.8885 | 5.4804 | 5.052 | 4.5928 | 4.0161 | 3.4329 | 1.523 | -0.58541 | -2.0647 | -3.6391 | -5.1011 | 13.4621 | 11.8123 | 11.2068 | 10.8934 | 10.5255 | 10.1174 | 9.689 | 9.2298 | 8.6531 | 8.0699 | 6.16 | 4.0516 | 2.5723 | 0.99788 | -0.22808 | 8.8251 | 5.62 | 4.5409 | 3.9485 | 3.1564 | 2.3319 | 1.355 | -0.15021 | -1.6286 | -3.0775 | -7.23 | -10.9382 | -13.3418 | -14.8463 | -15.2809 | 13.4621 | 10.257 | 9.1779 | 8.5855 | 7.7934 | 6.9689 | 5.992 | 4.4868 | 3.0084 | 1.5595 | -2.593 | -6.3012 | -8.7048 | -10.2093 | -10.5613 | 386421 | 406330 | CHADDERTON | WHITEGATE
| Langroyd Rd | 10.548 | 10.4085 | 10.327 | 10.2518 | 10.077 | 9.8838 | 9.7171 | 9.5701 | 9.3878 | 9.2343 | 7.5711 | 4.3209 | 1.5756 | -1.3285 | -3.6706 | 15.188 | 15.0485 | 14.967 | 14.8918 | 14.717 | 14.5238 | 14.3571 | 14.2101 | 14.0278 | 13.8743 | 12.2111 | 8.9609 | 6.2156 | 3.3115 | 0.72949 | 10.548 | 10.4102 | 10.3022 | 10.1894 | 10.0305 | 9.8468 | 9.5949 | 9.2627 | 9.0127 | 8.7622 | 8.0056 | 7.2527 | 6.5704 | 5.8541 | 5.3957 | 15.188 | 15.0502 | 14.9422 | 14.8294 | 14.6705 | 14.4868 | 14.2349 | 13.9027 | 13.6527 | 13.4022 | 12.6456 | 11.8927 | 11.2104 | 10.4941 | 10.1069 | 10.548 | 10.4213 | 10.3605 | 10.3223 | 10.186 | 10.038 | 9.9373 | 9.8594 | 9.7617 | 9.6778 | 8.232 | 5.1694 | 2.5888 | -0.11024 | -2.2302 | 15.188 | 15.0613 | 15.0005 | 14.9623 | 14.826 | 14.678 | 14.5773 | 14.4994 | 14.4017 | 14.3178 | 12.872 | 9.8094 | 7.2288 | 4.5298 | 2.1303 | 10.548 | 10.7298 | 10.7577 | 10.7584 | 10.6379 | 10.4842 | 10.1442 | 9.1103 | 8.0467 | 7.0024 | 4.0178 | 1.1522 | -1.1777 | -2.5941 | -1.2741 | 15.188 | 15.3698 | 15.3977 | 15.3984 | 15.2779 | 15.1242 | 14.7842 | 13.7503 | 12.6867 | 11.6424 | 8.6578 | 5.7922 | 3.4623 | 2.0459 | 3.0822 | 10.548 | 10.4405 | 10.3979 | 10.391 | 10.3581 | 10.295 | 10.1985 | 10.0724 | 9.8708 | 9.6713 | 8.9363 | 8.0863 | 7.5149 | 6.9919 | 6.8832 | 15.188 | 15.0805 | 15.0379 | 15.031 | 14.9981 | 14.935 | 14.8385 | 14.7124 | 14.5108 | 14.3113 | 13.5763 | 12.7263 | 12.1549 | 11.6319 | 11.4852 | 10.548 | 10.6535 | 10.5997 | 10.5103 | 10.3056 | 10.0922 | 9.6785 | 8.5444 | 7.4098 | 6.2929 | 3.0811 | 0.013715 | -2.5531 | -4.3039 | -3.3647 | 15.188 | 15.2935 | 15.2397 | 15.1503 | 14.9456 | 14.7322 | 14.3185 | 13.1844 | 12.0498 | 10.9329 | 7.7211 | 4.6537 | 2.0869 | 0.33614 | 1.0762 | 389077 | 440584 | NELSON | PADIHAM
| Leigh | 3.9483 | 3.1036 | 2.9025 | 2.8794 | 2.827 | 2.7682 | 2.7206 | 2.6798 | 2.6162 | 2.5607 | 1.9161 | 0.64712 | -0.43003 | -1.5817 | -2.5246 | 11.9483 | 11.1036 | 10.9025 | 10.8794 | 10.827 | 10.7682 | 10.7206 | 10.6798 | 10.6162 | 10.5607 | 9.9161 | 8.6471 | 7.57 | 6.4183 | 5.3756 | 3.9483 | 3.6609 | 3.5562 | 3.5101 | 3.4557 | 3.3985 | 3.3187 | 3.211 | 3.1295 | 3.0442 | 2.7845 | 2.5146 | 2.2667 | 2.0038 | 1.8205 | 11.9483 | 11.6609 | 11.5562 | 11.5101 | 11.4557 | 11.3985 | 11.3187 | 11.211 | 11.1295 | 11.0442 | 10.7845 | 10.5146 | 10.2667 | 10.0038 | 9.8466 | 3.9483 | 2.9764 | 2.7546 | 2.7442 | 2.7023 | 2.6553 | 2.6271 | 2.6046 | 2.5767 | 2.5477 | 1.9843 | 0.78297 | -0.22906 | -1.3134 | -2.1478 | 11.9483 | 10.9764 | 10.7546 | 10.7442 | 10.7023 | 10.6553 | 10.6271 | 10.6046 | 10.5767 | 10.5477 | 9.9843 | 8.783 | 7.7709 | 6.6866 | 5.7327 | 3.9483 | 3.3564 | 3.2205 | 3.2254 | 3.1906 | 3.1446 | 3.026 | 2.6306 | 2.2211 | 1.8112 | 0.63337 | -0.50043 | -1.4347 | -2.0108 | -1.465 | 11.9483 | 11.3564 | 11.2205 | 11.2254 | 11.1906 | 11.1446 | 11.026 | 10.6306 | 10.2211 | 9.8112 | 8.6334 | 7.4996 | 6.5653 | 5.9892 | 6.4135 | 3.9483 | 3.4424 | 3.3199 | 3.3183 | 3.3144 | 3.3041 | 3.2842 | 3.2543 | 3.1885 | 3.1227 | 2.8786 | 2.5953 | 2.4049 | 2.2331 | 2.2074 | 11.9483 | 11.4424 | 11.3199 | 11.3183 | 11.3144 | 11.3041 | 11.2842 | 11.2543 | 11.1885 | 11.1227 | 10.8786 | 10.5953 | 10.4049 | 10.2331 | 10.1918 | 3.9483 | 2.9345 | 2.6912 | 2.6675 | 2.6062 | 2.542 | 2.4005 | 1.9757 | 1.5486 | 1.1201 | -0.1216 | -1.3107 | -2.3175 | -3.0023 | -2.5889 | 11.9483 | 10.9345 | 10.6912 | 10.6675 | 10.6062 | 10.542 | 10.4005 | 9.9757 | 9.5486 | 9.1201 | 7.8784 | 6.6893 | 5.6825 | 4.9977 | 5.3195 | 365863 | 399907 | ATHERTON | KEARSLEY
| Levenshulme | 3.025 | 1.699 | 1.2275 | 0.95288 | 0.53291 | 0.085371 | -0.33408 | -0.76653 | -1.2534 | -1.7215 | -4.3065 | -8.1256 | -10.9183 | -13.3194 | -14.7258 | 6.525 | 5.199 | 4.7275 | 4.4529 | 4.0329 | 3.5854 | 3.1659 | 2.7335 | 2.2466 | 1.7785 | -0.80645 | -4.6256 | -7.4183 | -9.8194 | -11.5439 | 3.025 | 2.626 | 2.4202 | 2.241 | 1.9942 | 1.7373 | 1.396 | 0.95744 | 0.62095 | 0.21997 | -1.0027 | -2.2215 | -3.3294 | -4.4366 | -5.1284 | 6.525 | 6.126 | 5.9202 | 5.741 | 5.4942 | 5.2373 | 4.896 | 4.4574 | 4.121 | 3.72 | 2.4973 | 1.2785 | 0.1706 | -0.93659 | -1.5271 | 3.025 | 1.4116 | 0.78504 | 0.39226 | -0.2102 | -0.84284 | -1.4348 | -2.0326 | -2.7665 | -3.4235 | -6.4179 | -10.1991 | -12.6342 | -14.4174 | -14.7713 | 6.525 | 4.9116 | 4.285 | 3.8923 | 3.2898 | 2.6572 | 2.0652 | 1.4674 | 0.73346 | 0.076454 | -2.9179 | -6.6991 | -9.1342 | -10.9174 | -11.561 | 3.025 | 2.1409 | 1.6931 | 1.3482 | 0.76076 | 0.11645 | -0.72805 | -2.2806 | -3.8778 | -5.3276 | -9.1841 | -12.2216 | -13.9947 | -14.4412 | -13.0333 | 6.525 | 5.6409 | 5.1931 | 4.8482 | 4.2608 | 3.6165 | 2.772 | 1.2194 | -0.37783 | -1.8276 | -5.6841 | -8.7216 | -10.4947 | -10.9412 | -9.845 | 3.025 | 2.3477 | 2.0492 | 1.8685 | 1.643 | 1.3918 | 1.105 | 0.75716 | 0.28772 | -0.19561 | -1.8001 | -3.3983 | -4.5202 | -5.5668 | -6.0578 | 6.525 | 5.8477 | 5.5492 | 5.3685 | 5.143 | 4.8918 | 4.605 | 4.2572 | 3.7877 | 3.3044 | 1.6999 | 0.10173 | -1.0202 | -2.0668 | -2.524 | 3.025 | 1.5391 | 0.8847 | 0.42976 | -0.25728 | -0.96873 | -1.8967 | -3.5598 | -5.2302 | -6.7567 | -10.8876 | -14.2776 | -16.3302 | -17.079 | -15.9794 | 6.525 | 5.0391 | 4.3847 | 3.9298 | 3.2427 | 2.5313 | 1.6033 | -0.059837 | -1.7302 | -3.2567 | -7.3876 | -10.7776 | -12.8302 | -13.579 | -12.7025 | 387494 | 394155 | LONGSIGHT | BREDBURY
| Leyland National | 18.2232 | 18.1159 | 17.9812 | 17.8851 | 17.794 | 17.699 | 17.5806 | 17.3563 | 17.0302 | 16.6935 | 15.2893 | 13.6321 | 12.5629 | 11.8012 | 11.4889 | 22.3602 | 22.2529 | 22.1182 | 22.0221 | 21.931 | 21.836 | 21.7176 | 21.4933 | 21.1672 | 20.8305 | 19.4263 | 17.7691 | 16.6999 | 15.9382 | 15.6468 | 18.2232 | 18.1418 | 18.0208 | 17.9376 | 17.8734 | 17.8021 | 17.7205 | 17.6133 | 17.3747 | 17.1184 | 16.2409 | 15.2891 | 14.0251 | 12.5978 | 11.8075 | 22.3602 | 22.2788 | 22.1578 | 22.0746 | 22.0104 | 21.9391 | 21.8575 | 21.7503 | 21.5117 | 21.2554 | 20.3779 | 19.4261 | 18.1621 | 16.7348 | 16.0346 | 18.2232 | 18.1096 | 17.9745 | 17.8795 | 17.7914 | 17.7036 | 17.6276 | 17.5447 | 17.4238 | 17.223 | 15.9625 | 13.8378 | 12.3284 | 11.2327 | 10.7756 | 22.3602 | 22.2466 | 22.1115 | 22.0165 | 21.9284 | 21.8406 | 21.7646 | 21.6817 | 21.5608 | 21.36 | 20.0995 | 17.9748 | 16.4654 | 15.3697 | 14.9462 | 18.2232 | 18.1418 | 18.029 | 17.9445 | 17.8682 | 17.7799 | 17.647 | 17.3623 | 17.0145 | 16.5718 | 15.2761 | 13.8079 | 12.6101 | 11.8057 | 11.5924 | 22.3602 | 22.2788 | 22.166 | 22.0815 | 22.0052 | 21.9169 | 21.784 | 21.4993 | 21.1515 | 20.7088 | 19.4131 | 17.9449 | 16.7471 | 15.9427 | 15.7363 | 18.2232 | 18.1328 | 18.0134 | 17.9417 | 17.896 | 17.8416 | 17.773 | 17.689 | 17.4526 | 17.1646 | 16.1774 | 14.681 | 13.4242 | 12.4563 | 12.0282 | 22.3602 | 22.2698 | 22.1504 | 22.0787 | 22.033 | 21.9786 | 21.91 | 21.826 | 21.5896 | 21.3016 | 20.3144 | 18.818 | 17.5612 | 16.5933 | 16.2033 | 18.2232 | 18.1064 | 17.9659 | 17.8533 | 17.7536 | 17.6549 | 17.5161 | 17.2171 | 16.8777 | 16.4935 | 15.1181 | 13.8528 | 12.7538 | 11.7565 | 11.4119 | 22.3602 | 22.2434 | 22.1029 | 21.9903 | 21.8906 | 21.7919 | 21.6531 | 21.3541 | 21.0147 | 20.6305 | 19.2551 | 17.9898 | 16.8908 | 15.8935 | 15.5741 | 301973 | 525948 | STAINBURN & SIDDICK | HARKER
| Little Hulton | 4.1351 | 2.8655 | 2.2244 | 1.8243 | 1.2144 | 5.543 | 4.8294 | 4.1687 | 3.5886 | 3.1204 | 0.47168 | -3.6728 | -6.9917 | -10.1083 | -13.2036 | 8.1851 | 6.9155 | 6.2744 | 5.8743 | 5.2644 | 9.543 | 8.8294 | 8.1687 | 7.5886 | 7.1204 | 4.4717 | 0.32718 | -2.9917 | -6.1083 | -9.314 | 4.1351 | 3.6673 | 3.4883 | 3.3642 | 3.1803 | 8.0243 | 7.7226 | 7.2736 | 6.8759 | 6.4643 | 5.1338 | 3.469 | 1.699 | -0.3111 | -1.5768 | 8.1851 | 7.7173 | 7.5383 | 7.4142 | 7.2303 | 12.0243 | 11.7226 | 11.2736 | 10.8759 | 10.4643 | 9.1338 | 7.469 | 5.699 | 3.6889 | 2.6144 | 4.1351 | 2.7027 | 2.0506 | 1.6924 | 1.1314 | 5.521 | 4.8996 | 4.3402 | 3.8718 | 3.5033 | 1.1261 | -2.9258 | -6.1524 | -9.1471 | -12.0692 | 8.1851 | 6.7527 | 6.1006 | 5.7424 | 5.1814 | 9.521 | 8.8996 | 8.3402 | 7.8718 | 7.5033 | 5.1261 | 1.0742 | -2.1524 | -5.1471 | -8.2123 | 4.1351 | 3.4183 | 2.9279 | 2.5883 | 2.0112 | 6.3573 | 5.4909 | 4.012 | 2.5688 | 1.2127 | -2.7957 | -6.5784 | -9.5006 | -11.1637 | -10.4928 | 8.1851 | 7.4683 | 6.9779 | 6.6383 | 6.0612 | 10.3573 | 9.4909 | 8.012 | 6.5688 | 5.2127 | 1.2043 | -2.5784 | -5.5006 | -7.1637 | -6.6499 | 4.1351 | 3.375 | 2.872 | 2.5874 | 2.2493 | 6.8566 | 6.3682 | 5.8374 | 5.3008 | 4.8468 | 3.2765 | 1.2343 | -0.20067 | -1.4204 | -2.0934 | 8.1851 | 7.425 | 6.922 | 6.6374 | 6.2993 | 10.8566 | 10.3682 | 9.8374 | 9.3008 | 8.8468 | 7.2765 | 5.2343 | 3.7993 | 2.5796 | 1.9667 | 4.1351 | 2.8168 | 2.1373 | 1.7112 | 1.0585 | 5.3608 | 4.4414 | 2.8945 | 1.4131 | 0.016722 | -4.1851 | -8.2471 | -11.4572 | -13.413 | -13.0281 | 8.1851 | 6.8668 | 6.1873 | 5.7612 | 5.1085 | 9.3608 | 8.4414 | 6.8945 | 5.4131 | 4.0167 | -0.18506 | -4.2471 | -7.4572 | -9.413 | -9.1235 | 372024 | 403826 | KEARSLEY LOCAL | KEARSLEY
| Little Salkeld | 6.9416 | 6.7748 | 6.6554 | 6.5566 | 6.3737 | 6.1695 | 5.9846 | 5.819 | 5.6438 | 5.497 | 4.6298 | 3.3824 | 2.4753 | 1.8617 | 1.3344 | 8.9416 | 8.7748 | 8.6554 | 8.5566 | 8.3737 | 8.1695 | 7.9846 | 7.819 | 7.6438 | 7.497 | 6.6298 | 5.3824 | 4.4753 | 3.8617 | 3.3019 | 6.9416 | 6.8202 | 6.6696 | 6.5076 | 6.3227 | 6.1834 | 6.0167 | 5.8179 | 5.6553 | 5.4845 | 4.967 | 4.4797 | 3.9217 | 3.1022 | 2.2855 | 8.9416 | 8.8202 | 8.6696 | 8.5076 | 8.3227 | 8.1834 | 8.0167 | 7.8179 | 7.6553 | 7.4845 | 6.967 | 6.4797 | 5.9217 | 5.1022 | 4.4283 | 6.9416 | 6.7736 | 6.6657 | 6.5924 | 6.4393 | 6.2731 | 6.1367 | 6.0273 | 5.8308 | 5.517 | 4.3052 | 2.9275 | 1.9157 | 1.2416 | 0.71722 | 8.9416 | 8.7736 | 8.6657 | 8.5924 | 8.4393 | 8.2731 | 8.1367 | 8.0273 | 7.8308 | 7.517 | 6.3052 | 4.9275 | 3.9157 | 3.2416 | 2.6968 | 6.9416 | 6.8839 | 6.7881 | 6.6208 | 6.4375 | 6.2435 | 6.0321 | 5.7157 | 5.3572 | 4.9911 | 3.9343 | 2.7088 | 1.8847 | 1.4593 | 1.5212 | 8.9416 | 8.8839 | 8.7881 | 8.6208 | 8.4375 | 8.2435 | 8.0321 | 7.7157 | 7.3572 | 6.9911 | 5.9343 | 4.7088 | 3.8847 | 3.4593 | 3.4867 | 6.9416 | 6.8374 | 6.7241 | 6.6182 | 6.4949 | 6.41 | 6.3332 | 6.2512 | 6.1185 | 5.9855 | 5.325 | 4.1462 | 3.3176 | 2.559 | 2.0877 | 8.9416 | 8.8374 | 8.7241 | 8.6182 | 8.4949 | 8.41 | 8.3332 | 8.2512 | 8.1185 | 7.9855 | 7.325 | 6.1462 | 5.3176 | 4.559 | 4.088 | 6.9416 | 6.8084 | 6.6607 | 6.4422 | 6.2109 | 5.9789 | 5.7255 | 5.3535 | 4.9591 | 4.5572 | 3.3804 | 2.2983 | 1.6046 | 1.4123 | 1.566 | 8.9416 | 8.8084 | 8.6607 | 8.4422 | 8.2109 | 7.9789 | 7.7255 | 7.3535 | 6.9591 | 6.5572 | 5.3804 | 4.2983 | 3.6046 | 3.4123 | 3.541 | 356221 | 537513 | PENRITH & SHAP | HUTTON
| Littleborough | 3.9275 | 3.3046 | 3.0699 | 2.9622 | 2.7899 | 2.6072 | 2.4433 | 2.2872 | 2.0549 | 1.8451 | 0.22493 | -2.728 | -5.2136 | -7.9035 | -10.1764 | 7.4275 | 6.8046 | 6.5699 | 6.4622 | 6.2899 | 6.1072 | 5.9433 | 5.7872 | 5.5549 | 5.3451 | 3.7249 | 0.77203 | -1.7136 | -4.4035 | -6.8179 | 3.9275 | 3.6486 | 3.4766 | 3.347 | 3.1833 | 2.9946 | 2.7432 | 2.413 | 2.1 | 1.7842 | 0.83376 | -0.13231 | -1.0417 | -2.0449 | -2.7699 | 7.4275 | 7.1486 | 6.9766 | 6.847 | 6.6833 | 6.4946 | 6.2432 | 5.913 | 5.6 | 5.2842 | 4.3338 | 3.3677 | 2.4583 | 1.4551 | 0.84991 | 3.9275 | 3.2418 | 3.0146 | 2.6788 | 2.2784 | 1.8741 | 1.571 | 1.4903 | 1.3596 | 1.2311 | -0.13734 | -2.8694 | -5.1552 | -7.6016 | -9.5908 | 7.4275 | 6.7418 | 6.5146 | 6.1788 | 5.7784 | 5.3741 | 5.071 | 4.9903 | 4.8596 | 4.7311 | 3.3627 | 0.63064 | -1.6552 | -4.1016 | -6.2857 | 3.9275 | 3.6928 | 3.5824 | 3.2799 | 2.8852 | 2.4625 | 1.9536 | 1.0968 | 0.18663 | -0.72347 | -3.3562 | -5.9338 | -8.0157 | -9.3841 | -8.4997 | 7.4275 | 7.1928 | 7.0824 | 6.7799 | 6.3852 | 5.9625 | 5.4536 | 4.5968 | 3.6866 | 2.7765 | 0.14381 | -2.4338 | -4.5157 | -5.8841 | -5.1992 | 3.9275 | 3.5355 | 3.3829 | 3.3405 | 3.2844 | 3.1947 | 3.0778 | 2.951 | 2.7236 | 2.5026 | 1.7301 | 0.67501 | -0.094542 | -0.79814 | -1.1821 | 7.4275 | 7.0355 | 6.8829 | 6.8405 | 6.7844 | 6.6947 | 6.5778 | 6.451 | 6.2236 | 6.0026 | 5.2301 | 4.175 | 3.4055 | 2.7019 | 2.3413 | 3.9275 | 3.3847 | 3.145 | 2.7541 | 2.2784 | 1.8005 | 1.2225 | 0.27168 | -0.70811 | -1.6881 | -4.5359 | -7.2971 | -9.5655 | -11.1765 | -10.572 | 7.4275 | 6.8847 | 6.645 | 6.2541 | 5.7784 | 5.3005 | 4.7225 | 3.7717 | 2.7919 | 1.8119 | -1.0359 | -3.7971 | -6.0655 | -7.6765 | -7.2094 | 393221 | 416124 | BELFIELD | ROCHDALE
| Longford Bridge | 11.0876 | 9.8611 | 8.8642 | 8.221 | 7.7848 | 7.328 | 6.8876 | 6.4822 | 6.0736 | 5.6885 | 3.8806 | 1.1415 | -0.92971 | -2.8452 | -4.2021 | 15.7246 | 14.4981 | 13.5012 | 12.858 | 12.4218 | 11.965 | 11.5246 | 11.1192 | 10.7106 | 10.3255 | 8.5176 | 5.7785 | 3.7073 | 1.7918 | 0.21923 | 11.0876 | 10.674 | 10.3938 | 10.2119 | 9.9852 | 9.7707 | 9.5032 | 9.1784 | 8.9092 | 8.6292 | 7.8793 | 7.1649 | 6.4473 | 5.6412 | 5.0383 | 15.7246 | 15.311 | 15.0308 | 14.8489 | 14.6222 | 14.4077 | 14.1402 | 13.8154 | 13.5462 | 13.2662 | 12.5163 | 11.8019 | 11.0843 | 10.2782 | 9.7781 | 11.0876 | 9.6151 | 8.206 | 7.1855 | 6.3674 | 5.5259 | 4.7103 | 3.9154 | 3.1262 | 2.3376 | -0.60805 | -4.1103 | -6.587 | -7.8713 | -8.3415 | 15.7246 | 14.2521 | 12.843 | 11.8225 | 11.0044 | 10.1629 | 9.3473 | 8.5524 | 7.7632 | 6.9746 | 4.0289 | 0.52674 | -1.95 | -3.2343 | -3.8712 | 11.0876 | 10.2475 | 8.9833 | 7.9851 | 7.1652 | 6.3029 | 5.3056 | 3.8331 | 2.3845 | 0.97345 | -2.7298 | -5.7697 | -7.743 | -8.0011 | -6.9831 | 15.7246 | 14.8845 | 13.6203 | 12.6221 | 11.8022 | 10.9399 | 9.9426 | 8.4701 | 7.0215 | 5.6105 | 1.9072 | -1.1327 | -3.106 | -3.3641 | -2.5202 | 11.0876 | 10.3605 | 9.498 | 8.9252 | 8.6236 | 8.3041 | 7.9716 | 7.6219 | 7.2172 | 6.8079 | 5.7532 | 4.7084 | 3.9409 | 3.1869 | 2.7123 | 15.7246 | 14.9975 | 14.135 | 13.5622 | 13.2606 | 12.9411 | 12.6086 | 12.2589 | 11.8542 | 11.4449 | 10.3902 | 9.3454 | 8.5779 | 7.8239 | 7.3953 | 11.0876 | 9.6751 | 8.234 | 7.1562 | 6.2651 | 5.3568 | 4.3003 | 2.7476 | 1.2406 | -0.22979 | -4.1029 | -7.2844 | -9.4092 | -9.8558 | -8.9601 | 15.7246 | 14.3121 | 12.871 | 11.7932 | 10.9021 | 9.9938 | 8.9373 | 7.3846 | 5.8776 | 4.4072 | 0.53413 | -2.6474 | -4.7722 | -5.2188 | -4.4885 | 380056 | 395083 | STRETFORD | SOUTH MANCHESTER
| Longridge | 11.2307 | 9.9508 | 9.573 | 9.4028 | 9.1387 | 8.858 | 8.5865 | 8.3194 | 8.0278 | 7.7615 | 6.2133 | 3.728 | 1.7713 | -0.17462 | -1.958 | 15.3677 | 14.0878 | 13.71 | 13.5398 | 13.2757 | 12.995 | 12.7235 | 12.4564 | 12.1648 | 11.8985 | 10.3503 | 7.865 | 5.9083 | 3.9624 | 2.1116 | 11.2307 | 10.7084 | 10.451 | 10.2464 | 10.0048 | 9.778 | 9.4688 | 9.0244 | 8.703 | 8.3826 | 7.4141 | 6.3889 | 5.3248 | 4.037 | 3.0658 | 15.3677 | 14.8454 | 14.588 | 14.3834 | 14.1418 | 13.915 | 13.6058 | 13.1614 | 12.84 | 12.5196 | 11.5511 | 10.5259 | 9.4618 | 8.174 | 7.3676 | 11.2307 | 9.7828 | 9.3898 | 9.249 | 9.0142 | 8.7685 | 8.5516 | 8.3405 | 8.1292 | 7.9278 | 6.6136 | 4.2762 | 2.4326 | 0.64556 | -0.96434 | 15.3677 | 13.9198 | 13.5268 | 13.386 | 13.1512 | 12.9055 | 12.6886 | 12.4775 | 12.2662 | 12.0648 | 10.7506 | 8.4132 | 6.5696 | 4.7826 | 3.0692 | 11.2307 | 10.3983 | 10.1289 | 9.9768 | 9.7498 | 9.5109 | 9.1675 | 8.4291 | 7.657 | 6.8851 | 4.653 | 2.4527 | 0.8339 | -0.16719 | 0.31452 | 15.3677 | 14.5353 | 14.2659 | 14.1138 | 13.8868 | 13.6479 | 13.3045 | 12.5661 | 11.794 | 11.0221 | 8.79 | 6.5897 | 4.9709 | 3.9698 | 4.3354 | 11.2307 | 10.4148 | 10.1221 | 9.9687 | 9.7869 | 9.6151 | 9.4245 | 9.1841 | 8.8644 | 8.5465 | 7.4231 | 6.0559 | 5.1367 | 4.2536 | 3.727 | 15.3677 | 14.5518 | 14.2591 | 14.1057 | 13.9239 | 13.7521 | 13.5615 | 13.3211 | 13.0014 | 12.6835 | 11.5601 | 10.1929 | 9.2737 | 8.3906 | 7.8856 | 11.2307 | 9.8021 | 9.378 | 9.1602 | 8.8708 | 8.5835 | 8.18 | 7.3709 | 6.5657 | 5.7583 | 3.3878 | 1.0317 | -0.7479 | -1.934 | -1.6473 | 15.3677 | 13.9391 | 13.515 | 13.2972 | 13.0078 | 12.7205 | 12.317 | 11.5079 | 10.7027 | 9.8953 | 7.5248 | 5.1687 | 3.3891 | 2.203 | 2.4161 | 360581 | 437001 | PRESTON EAST | PENWORTHAM
| Longsight | 5.0795 | 2.382 | 1.0395 | 0.69008 | 0.25199 | -0.21168 | -0.65427 | -1.0624 | -1.5037 | -1.9252 | -3.9962 | -6.9333 | -9.0498 | -10.9241 | -12.3221 | 9.2165 | 6.519 | 5.1765 | 4.8271 | 4.389 | 3.9253 | 3.4827 | 3.0746 | 2.6333 | 2.2118 | 0.14076 | -2.7963 | -4.9128 | -6.7871 | -8.387 | 5.0795 | 4.373 | 3.9957 | 3.7221 | 3.4175 | 3.1023 | 2.7091 | 2.2129 | 1.8329 | 1.4327 | 0.24702 | -0.92899 | -1.9932 | -3.0878 | -3.8682 | 9.2165 | 8.51 | 8.1327 | 7.8591 | 7.5545 | 7.2393 | 6.8461 | 6.3499 | 5.9699 | 5.5697 | 4.384 | 3.208 | 2.1438 | 1.0492 | 0.39172 | 5.0795 | 1.9885 | 0.49181 | 0.051418 | -0.49111 | -1.0654 | -1.607 | -2.135 | -2.6534 | -3.1943 | -5.6223 | -8.6071 | -10.5246 | -11.9206 | -12.4032 | 9.2165 | 6.1255 | 4.6288 | 4.1884 | 3.6459 | 3.0716 | 2.53 | 2.002 | 1.4836 | 0.94274 | -1.4853 | -4.4701 | -6.3876 | -7.7836 | -8.4453 | 5.0795 | 2.8897 | 1.6156 | 1.2311 | 0.71818 | 0.14627 | -0.53603 | -1.645 | -2.7526 | -3.8469 | -6.9038 | -9.4204 | -10.8584 | -11.328 | -10.5501 | 9.2165 | 7.0267 | 5.7526 | 5.3681 | 4.8552 | 4.2833 | 3.601 | 2.492 | 1.3844 | 0.2901 | -2.7668 | -5.2834 | -6.7214 | -7.191 | -6.5732 | 5.0795 | 3.2404 | 2.1102 | 1.8515 | 1.5894 | 1.3042 | 0.99502 | 0.6493 | 0.20811 | -0.24372 | -1.7106 | -3.1674 | -4.1903 | -5.1254 | -5.6265 | 9.2165 | 7.3774 | 6.2472 | 5.9885 | 5.7264 | 5.4412 | 5.132 | 4.7863 | 4.3451 | 3.8933 | 2.4264 | 0.96961 | -0.053331 | -0.98836 | -1.4466 | 5.0795 | 1.9461 | 0.40163 | -0.085659 | -0.69101 | -1.3206 | -2.0719 | -3.2744 | -4.4345 | -5.5839 | -8.8322 | -11.5116 | -13.1166 | -13.7822 | -13.2155 | 9.2165 | 6.0831 | 4.5386 | 4.0513 | 3.446 | 2.8164 | 2.0651 | 0.86261 | -0.29747 | -1.4469 | -4.6952 | -7.3746 | -8.9796 | -9.6452 | -9.2119 | 385535 | 396037 | LONGSIGHT | BREDBURY
| Lostock | 9.7727 | 7.4093 | 7.0597 | 6.8385 | 6.626 | 6.4067 | 6.1927 | 5.9485 | 5.5308 | 5.123 | 3.3264 | 0.78084 | -1.1937 | -3.1117 | -4.6011 | 15.7727 | 13.4093 | 13.0597 | 12.8385 | 12.626 | 12.4067 | 12.1927 | 11.9485 | 11.5308 | 11.123 | 9.3264 | 6.7808 | 4.8063 | 2.8883 | 1.2899 | 9.7727 | 8.8401 | 8.8727 | 8.7647 | 8.6912 | 8.6026 | 8.4786 | 8.2991 | 7.8895 | 7.4704 | 6.2142 | 4.5242 | 2.8906 | 1.2518 | 0.26338 | 15.7727 | 14.8401 | 14.8727 | 14.7647 | 14.6912 | 14.6026 | 14.4786 | 14.2991 | 13.8895 | 13.4704 | 12.2142 | 10.5242 | 8.8906 | 7.2518 | 6.4013 | 9.7727 | 7.0845 | 6.669 | 6.4441 | 6.2334 | 6.0191 | 5.8111 | 5.5788 | 5.2503 | 4.9421 | 3.4187 | 1.1256 | -0.5836 | -2.0963 | -3.0319 | 15.7727 | 13.0845 | 12.669 | 12.4441 | 12.2334 | 12.0191 | 11.8111 | 11.5788 | 11.2503 | 10.9421 | 9.4187 | 7.1256 | 5.4164 | 3.9037 | 2.7532 | 9.7727 | 7.8988 | 7.7042 | 7.5498 | 7.3873 | 7.1662 | 6.8195 | 6.1172 | 5.3102 | 4.5167 | 2.2314 | 0.06275 | -1.4952 | -2.3216 | -1.3931 | 15.7727 | 13.8988 | 13.7042 | 13.5498 | 13.3873 | 13.1662 | 12.8195 | 12.1172 | 11.3102 | 10.5167 | 8.2314 | 6.0627 | 4.5048 | 3.6784 | 4.3794 | 9.7727 | 8.2807 | 8.1603 | 8.0325 | 7.9514 | 7.8171 | 7.6423 | 7.4488 | 7.0665 | 6.6765 | 5.4351 | 4.1294 | 3.275 | 2.4613 | 2.1933 | 15.7727 | 14.2807 | 14.1603 | 14.0325 | 13.9514 | 13.8171 | 13.6423 | 13.4488 | 13.0665 | 12.6765 | 11.4351 | 10.1294 | 9.275 | 8.4613 | 8.1842 | 9.7727 | 6.8852 | 6.4153 | 6.1685 | 5.9317 | 5.6974 | 5.3529 | 4.6076 | 3.7605 | 2.9323 | 0.55217 | -1.687 | -3.3253 | -4.2197 | -3.3953 | 15.7727 | 12.8852 | 12.4153 | 12.1685 | 11.9317 | 11.6974 | 11.3529 | 10.6076 | 9.7605 | 8.9323 | 6.5522 | 4.313 | 2.6747 | 1.7803 | 2.4065 | 365293 | 409079 | WESTHOUGHTON | KEARSLEY
| Lower Darwen | 10.8392 | 10.0132 | 9.585 | 9.3557 | 9.278 | 9.2005 | 9.1259 | 9.0422 | 8.8697 | 8.6975 | 8.0906 | 7.4478 | 6.9701 | 6.5551 | 6.3209 | 17.8392 | 17.0132 | 16.585 | 16.3557 | 16.278 | 16.2005 | 16.1259 | 16.0422 | 15.8697 | 15.6975 | 15.0906 | 14.4478 | 13.9701 | 13.5551 | 13.2556 | 10.8392 | 10.5517 | 10.4061 | 10.3667 | 10.3628 | 10.3545 | 10.339 | 10.3165 | 10.2021 | 10.0858 | 9.7326 | 9.3788 | 9.0646 | 8.7554 | 8.5714 | 17.8392 | 17.5517 | 17.4061 | 17.3667 | 17.3628 | 17.3545 | 17.339 | 17.3165 | 17.2021 | 17.0858 | 16.7326 | 16.3788 | 16.0646 | 15.7554 | 15.5876 | 10.8392 | 9.844 | 9.3612 | 9.0997 | 8.9926 | 8.8874 | 8.7863 | 8.6789 | 8.5209 | 8.3682 | 7.8047 | 7.1891 | 6.8365 | 6.6153 | 6.6473 | 17.8392 | 16.844 | 16.3612 | 16.0997 | 15.9926 | 15.8874 | 15.7863 | 15.6789 | 15.5209 | 15.3682 | 14.8047 | 14.1891 | 13.8365 | 13.6153 | 13.5312 | 10.8392 | 10.1498 | 9.7347 | 9.4884 | 9.3937 | 9.2902 | 9.1523 | 8.9119 | 8.6131 | 8.3193 | 7.5373 | 6.9615 | 6.6563 | 6.621 | 7.134 | 17.8392 | 17.1498 | 16.7347 | 16.4884 | 16.3937 | 16.2902 | 16.1523 | 15.9119 | 15.6131 | 15.3193 | 14.5373 | 13.9615 | 13.6563 | 13.621 | 14.0153 | 10.8392 | 10.2763 | 9.9045 | 9.6943 | 9.6473 | 9.5923 | 9.5262 | 9.4507 | 9.2858 | 9.1172 | 8.6503 | 8.3225 | 8.1316 | 8.0461 | 8.2022 | 17.8392 | 17.2763 | 16.9045 | 16.6943 | 16.6473 | 16.5923 | 16.5262 | 16.4507 | 16.2858 | 16.1172 | 15.6503 | 15.3225 | 15.1316 | 15.0461 | 15.1504 | 10.8392 | 9.7262 | 9.2204 | 8.9521 | 8.8393 | 8.7302 | 8.5907 | 8.341 | 8.0403 | 7.7455 | 6.9485 | 6.3443 | 6.0075 | 5.95 | 6.4427 | 17.8392 | 16.7262 | 16.2204 | 15.9521 | 15.8393 | 15.7302 | 15.5907 | 15.341 | 15.0403 | 14.7455 | 13.9485 | 13.3443 | 13.0075 | 12.95 | 13.3295 | 369695 | 424981 | LOWER DARWEN | ROCHDALE
| Lyons Rd | 12.8629 | 8.8947 | 7.7882 | 7.3125 | 6.8707 | 6.4206 | 5.9612 | 5.4762 | 4.877 | 4.2654 | -1.1718 | -19.2253 | -20.5306 | -22.5462 | -23.4981 | 15.0999 | 11.1317 | 10.0252 | 9.5495 | 9.1077 | 8.6576 | 8.1982 | 7.7132 | 7.114 | 6.5024 | 1.0652 | -16.9883 | -18.2936 | -20.3092 | -21.1636 | 12.8629 | 11.9103 | 11.5736 | 11.4781 | 11.4207 | 11.353 | 11.2767 | 11.1926 | 11.0077 | 10.8128 | 10.1878 | 9.5161 | 8.8812 | 8.2157 | 7.7466 | 15.0999 | 14.1473 | 13.8106 | 13.7151 | 13.6577 | 13.59 | 13.5137 | 13.4296 | 13.2447 | 13.0498 | 12.4248 | 11.7531 | 11.1182 | 10.4527 | 10.0427 | 12.8629 | 8.2716 | 7.0394 | 6.5654 | 6.1289 | 5.6883 | 5.2438 | 4.7802 | 4.2498 | 3.7091 | -33.5936 | -34.6851 | -35.5694 | -37.4213 | -37.144 | 15.0999 | 10.5086 | 9.2764 | 8.8024 | 8.3659 | 7.9253 | 7.4808 | 7.0172 | 6.4868 | 5.9461 | -31.3566 | -32.4481 | -33.3324 | -35.1843 | -35.0534 | 12.8629 | 9.5349 | 8.5791 | 8.1258 | 7.7051 | 7.2624 | 6.7815 | 2.2953 | 1.8035 | 1.2853 | -0.45833 | -2.1947 | -3.6592 | -5.2663 | -6.6098 | 15.0999 | 11.7719 | 10.8161 | 10.3628 | 9.9421 | 9.4994 | 9.0185 | 4.5323 | 4.0405 | 3.5223 | 1.7787 | 0.042273 | -1.4222 | -3.0293 | -4.1455 | 12.8629 | 10.8286 | 10.13 | 9.6805 | 9.2744 | 8.8493 | 8.4044 | 7.9431 | 7.3738 | 6.7889 | 1.4874 | -16.3593 | -17.4853 | -19.2701 | -19.8769 | 15.0999 | 13.0656 | 12.367 | 11.9175 | 11.5114 | 11.0863 | 10.6414 | 10.1801 | 9.6108 | 9.0259 | 3.7244 | -14.1223 | -15.2483 | -17.0331 | -17.5432 | 12.8629 | 7.649 | 6.2886 | 5.8082 | 5.3668 | 4.9223 | 4.4475 | -0.039029 | -0.51911 | -1.0254 | -2.7787 | -4.5806 | -6.1149 | -7.7576 | -9.1114 | 15.0999 | 9.886 | 8.5256 | 8.0452 | 7.6038 | 7.1593 | 6.6845 | 2.198 | 1.7179 | 1.2116 | -0.54172 | -2.3436 | -3.8779 | -5.5206 | -6.6442 | 378253 | 397241 | BARTON | CARRINGTON
| Manchester University | 8.8521 | 8.1123 | 7.7955 | 7.419 | 7.1179 | 6.8308 | 6.4815 | 6.5156 | 6.4092 | 6.3145 | 6.0588 | 5.838 | 5.7235 | 5.6976 | 5.8395 | 12.9891 | 12.2493 | 11.9325 | 11.556 | 11.2549 | 10.9678 | 10.6185 | 10.6526 | 10.5462 | 10.4515 | 10.1958 | 9.975 | 9.8605 | 9.8346 | 9.9122 | 8.8521 | 8.5501 | 8.631 | 8.5645 | 8.5733 | 8.5923 | 8.622 | 8.6595 | 8.4876 | 8.3237 | 7.8859 | 7.522 | 7.2401 | 6.9634 | 6.7534 | 12.9891 | 12.6871 | 12.768 | 12.7015 | 12.7103 | 12.7293 | 12.759 | 12.7965 | 12.6246 | 12.4607 | 12.0229 | 11.659 | 11.3771 | 11.1004 | 10.9189 | 8.8521 | 8.0304 | 7.6966 | 7.3164 | 7.0139 | 6.7259 | 6.3747 | 6.4074 | 6.3575 | 6.3276 | 6.2756 | 6.2727 | 6.3862 | 6.677 | 7.2283 | 12.9891 | 12.1674 | 11.8336 | 11.4534 | 11.1509 | 10.8629 | 10.5117 | 10.5444 | 10.4945 | 10.4646 | 10.4126 | 10.4097 | 10.5232 | 10.814 | 11.2193 | 8.8521 | 8.1962 | 7.9013 | 7.5273 | 7.2298 | 6.9424 | 6.5833 | 6.5894 | 6.5127 | 6.4551 | 6.3582 | 6.3577 | 6.4748 | 6.8041 | 7.4632 | 12.9891 | 12.3332 | 12.0383 | 11.6643 | 11.3668 | 11.0794 | 10.7203 | 10.7264 | 10.6497 | 10.5921 | 10.4952 | 10.4947 | 10.6118 | 10.9411 | 11.4532 | 8.8521 | 8.5066 | 8.2742 | 7.9048 | 7.6127 | 7.33 | 6.9803 | 7.0147 | 6.9085 | 6.8125 | 6.5826 | 6.4309 | 6.3827 | 6.4328 | 6.6743 | 12.9891 | 12.6436 | 12.4112 | 12.0418 | 11.7497 | 11.467 | 11.1173 | 11.1517 | 11.0455 | 10.9495 | 10.7196 | 10.5679 | 10.5197 | 10.5698 | 10.7477 | 8.8521 | 7.9553 | 7.6058 | 7.2242 | 6.9206 | 6.6319 | 6.2725 | 6.2745 | 6.1936 | 6.1324 | 6.0288 | 6.0276 | 6.1442 | 6.4742 | 7.1297 | 12.9891 | 12.0923 | 11.7428 | 11.3612 | 11.0576 | 10.7689 | 10.4095 | 10.4115 | 10.3306 | 10.2694 | 10.1658 | 10.1646 | 10.2812 | 10.6112 | 11.1209 |  |  | LONGSIGHT | BREDBURY
| Marple | 1.3106 | 1.1373 | 0.98694 | 0.86565 | 0.71721 | 0.55906 | 0.47651 | 0.39333 | 0.29291 | 0.20194 | -0.43533 | -1.5722 | -2.5488 | -3.6757 | -4.6649 | 1.3106 | 1.1373 | 0.98694 | 0.86565 | 0.71721 | 0.55906 | 0.47651 | 0.39333 | 0.29291 | 0.20194 | -0.43533 | -1.5722 | -2.5488 | -3.6757 | -4.7063 | 1.3106 | 1.2512 | 1.1783 | 1.1046 | 1.0121 | 0.91436 | 0.80825 | 0.66279 | 0.54043 | 0.41658 | 0.045114 | -0.32961 | -0.69181 | -1.0993 | -1.3931 | 1.3106 | 1.2512 | 1.1783 | 1.1046 | 1.0121 | 0.91436 | 0.80825 | 0.66279 | 0.54043 | 0.41658 | 0.045114 | -0.32961 | -0.69181 | -1.0993 | -1.3416 | 1.3106 | 1.1227 | 0.97679 | 0.86898 | 0.73285 | 0.58708 | 0.48818 | 0.38872 | 0.27902 | 0.17303 | -0.40974 | -1.4857 | -2.4048 | -3.4655 | -4.38 | 1.3106 | 1.1227 | 0.97679 | 0.86898 | 0.73285 | 0.58708 | 0.48818 | 0.38872 | 0.27902 | 0.17303 | -0.40974 | -1.4857 | -2.4048 | -3.4655 | -4.4353 | 1.3106 | 1.2746 | 1.1693 | 1.0745 | 0.94222 | 0.79892 | 0.63222 | 0.24943 | -0.15016 | -0.55239 | -1.6351 | -2.6974 | -3.5681 | -4.1983 | -3.9486 | 1.3106 | 1.2746 | 1.1693 | 1.0745 | 0.94222 | 0.79892 | 0.63222 | 0.24943 | -0.15016 | -0.55239 | -1.6351 | -2.6974 | -3.5681 | -4.1983 | -4.0064 | 1.3106 | 1.2529 | 1.1399 | 1.0429 | 0.93412 | 0.8147 | 0.75209 | 0.6865 | 0.59349 | 0.50381 | 0.19495 | -0.1782 | -0.44338 | -0.71596 | -0.91955 | 1.3106 | 1.2529 | 1.1399 | 1.0429 | 0.93412 | 0.8147 | 0.75209 | 0.6865 | 0.59349 | 0.50381 | 0.19495 | -0.1782 | -0.44338 | -0.71596 | -0.89883 | 1.3106 | 1.188 | 1.0392 | 0.91033 | 0.74672 | 0.57593 | 0.3803 | -0.029751 | -0.44877 | -0.87123 | -2.0252 | -3.1446 | -4.0759 | -4.7902 | -4.6431 | 1.3106 | 1.188 | 1.0392 | 0.91033 | 0.74672 | 0.57593 | 0.3803 | -0.029751 | -0.44877 | -0.87123 | -2.0252 | -3.1446 | -4.0759 | -4.7902 | -4.6778 | 395671 | 388643 | HAZEL GROVE | BREDBURY
| Marton | 10.3072 | 9.0171 | 8.5167 | 8.2318 | 7.8804 | 7.5139 | 7.1599 | 6.8171 | 6.4654 | 6.1348 | 4.4213 | 1.2786 | -1.39 | -4.2857 | -6.8887 | 14.9072 | 13.6171 | 13.1167 | 12.8318 | 12.4804 | 12.1139 | 11.7599 | 11.4171 | 11.0654 | 10.7348 | 9.0213 | 5.8786 | 3.21 | 0.31427 | -2.4516 | 10.3072 | 9.9417 | 9.6772 | 9.4548 | 9.1978 | 8.9014 | 8.5327 | 8.0871 | 7.8975 | 7.7053 | 7.1261 | 6.5581 | 6.0024 | 5.4005 | 4.9413 | 14.9072 | 14.5417 | 14.2772 | 14.0548 | 13.7978 | 13.5014 | 13.1327 | 12.6871 | 12.4975 | 12.3053 | 11.7261 | 11.1581 | 10.6024 | 10.0005 | 9.6188 | 10.3072 | 8.8193 | 8.287 | 8.0047 | 7.0495 | 6.0811 | 5.1257 | 4.1857 | 3.2656 | 2.3699 | 0.78646 | -2.2172 | -4.7406 | -7.4291 | -9.7605 | 14.9072 | 13.4193 | 12.887 | 12.6047 | 11.6495 | 10.6811 | 9.7257 | 8.7857 | 7.8656 | 6.9699 | 5.3865 | 2.3828 | -0.14062 | -2.8291 | -5.3716 | 10.3072 | 9.4146 | 9.0199 | 8.7404 | 7.7746 | 6.7713 | 5.5817 | 3.8067 | 1.9991 | 0.20817 | -2.844 | -5.7055 | -8.0066 | -9.4514 | -8.5023 | 14.9072 | 14.0146 | 13.6199 | 13.3404 | 12.3746 | 11.3713 | 10.1817 | 8.4067 | 6.5991 | 4.8082 | 1.756 | -1.1055 | -3.4066 | -4.8514 | -4.1198 | 10.3072 | 9.7524 | 9.4108 | 9.1932 | 8.9698 | 8.7231 | 8.4397 | 8.1386 | 7.8183 | 7.4969 | 6.7331 | 5.854 | 5.2287 | 4.6152 | 4.3394 | 14.9072 | 14.3524 | 14.0108 | 13.7932 | 13.5698 | 13.3231 | 13.0397 | 12.7386 | 12.4183 | 12.0969 | 11.3331 | 10.454 | 9.8287 | 9.2152 | 8.9094 | 10.3072 | 8.7699 | 8.2011 | 7.8401 | 6.8001 | 5.7534 | 4.5245 | 2.6786 | 0.83432 | -0.99064 | -4.1339 | -7.0695 | -9.4603 | -11.0268 | -10.2448 | 14.9072 | 13.3699 | 12.8011 | 12.4401 | 11.4001 | 10.3534 | 9.1245 | 7.2786 | 5.4343 | 3.6094 | 0.46613 | -2.4695 | -4.8603 | -6.4268 | -5.8219 | 333341 | 433485 | BLACKPOOL | PENWORTHAM
| Maryport | 13.3203 | 13.0873 | 12.8811 | 12.7087 | 12.4581 | 12.206 | 12.0071 | 11.8212 | 11.5722 | 11.3537 | 9.798 | 7.0641 | 4.8355 | 2.6177 | 0.80109 | 17.3203 | 17.0873 | 16.8811 | 16.7087 | 16.4581 | 16.206 | 16.0071 | 15.8212 | 15.5722 | 15.3537 | 13.798 | 11.0641 | 8.8355 | 6.6177 | 4.6097 | 13.3203 | 13.1365 | 12.9551 | 12.78 | 12.5658 | 12.3421 | 12.0559 | 11.6845 | 11.3752 | 11.0684 | 10.1626 | 9.3002 | 8.5396 | 7.7206 | 7.1883 | 17.3203 | 17.1365 | 16.9551 | 16.78 | 16.5658 | 16.3421 | 16.0559 | 15.6845 | 15.3752 | 15.0684 | 14.1626 | 13.3002 | 12.5396 | 11.7206 | 11.2657 | 13.3203 | 13.0914 | 12.9097 | 12.7816 | 12.5775 | 12.3807 | 12.2567 | 12.1568 | 12.0154 | 11.884 | 10.5833 | 8.0733 | 6.0404 | 4.0594 | 2.4788 | 17.3203 | 17.0914 | 16.9097 | 16.7816 | 16.5775 | 16.3807 | 16.2567 | 16.1568 | 16.0154 | 15.884 | 14.5833 | 12.0733 | 10.0404 | 8.0594 | 6.238 | 13.3203 | 13.3232 | 13.2125 | 13.1031 | 12.9249 | 12.7288 | 12.4131 | 11.576 | 10.6922 | 9.8185 | 7.3128 | 4.9381 | 3.0973 | 2.0397 | 3.1659 | 17.3203 | 17.3232 | 17.2125 | 17.1031 | 16.9249 | 16.7288 | 16.4131 | 15.576 | 14.6922 | 13.8185 | 11.3128 | 8.9381 | 7.0973 | 6.0397 | 6.916 | 13.3203 | 13.1325 | 12.964 | 12.8459 | 12.7217 | 12.5873 | 12.4334 | 12.2203 | 11.9026 | 11.5865 | 10.507 | 9.3094 | 8.4967 | 7.7542 | 7.5941 | 17.3203 | 17.1325 | 16.964 | 16.8459 | 16.7217 | 16.5873 | 16.4334 | 16.2203 | 15.9026 | 15.5865 | 14.507 | 13.3094 | 12.4967 | 11.7542 | 11.5564 | 13.3203 | 13.2132 | 13.0053 | 12.7944 | 12.5228 | 12.2635 | 11.8759 | 10.9341 | 9.9756 | 9.0289 | 6.2993 | 3.718 | 1.6882 | 0.40377 | 1.2591 | 17.3203 | 17.2132 | 17.0053 | 16.7944 | 16.5228 | 16.2635 | 15.8759 | 14.9341 | 13.9756 | 13.0289 | 10.2993 | 7.718 | 5.6882 | 4.4038 | 5.0682 | 303716 | 535313 | STAINBURN & SIDDICK | HARKER
| Medipark | 27.8593 | 27.6539 | 27.5647 | 27.5461 | 27.5475 | 22.5529 | 22.5633 | 22.5771 | 22.5515 | 22.5293 | 22.4443 | 22.3339 | 22.2562 | 22.1951 | 22.18 | 33.8593 | 33.6539 | 33.5647 | 33.5461 | 33.5475 | 28.5529 | 28.5633 | 28.5771 | 28.5515 | 28.5293 | 28.4443 | 28.3339 | 28.2562 | 28.1951 | 28.1574 | 27.8593 | 27.8359 | 27.7796 | 27.7559 | 27.7538 | 22.7542 | 22.7561 | 22.7582 | 22.713 | 22.6705 | 22.5573 | 22.4628 | 22.3907 | 22.3194 | 22.2655 | 33.8593 | 33.8359 | 33.7796 | 33.7559 | 33.7538 | 28.7542 | 28.7561 | 28.7582 | 28.713 | 28.6705 | 28.5573 | 28.4628 | 28.3907 | 28.3194 | 28.2714 | 27.8593 | 27.6196 | 27.5233 | 27.5039 | 27.3244 | 22.1489 | 21.9784 | 21.8112 | 21.6224 | 21.439 | 21.2949 | 21.251 | 21.2435 | 21.2805 | 21.3928 | 33.8593 | 33.6196 | 33.5233 | 33.5039 | 33.3244 | 28.1489 | 27.9784 | 27.8112 | 27.6224 | 27.439 | 27.2949 | 27.251 | 27.2435 | 27.2805 | 27.3453 | 27.8593 | 27.6896 | 27.6085 | 27.5893 | 27.4106 | 22.2365 | 22.0602 | 21.8666 | 21.6479 | 21.4345 | 21.24 | 21.197 | 21.1919 | 21.2649 | 21.4762 | 33.8593 | 33.6896 | 33.6085 | 33.5893 | 33.4106 | 28.2365 | 28.0602 | 27.8666 | 27.6479 | 27.4345 | 27.24 | 27.197 | 27.1919 | 27.2649 | 27.4286 | 27.8593 | 27.8217 | 27.7665 | 27.7487 | 27.7537 | 22.7631 | 22.7753 | 22.7884 | 22.7611 | 22.7364 | 22.6762 | 22.6364 | 22.6263 | 22.6424 | 22.7233 | 33.8593 | 33.8217 | 33.7665 | 33.7487 | 33.7537 | 28.7631 | 28.7753 | 28.7884 | 28.7611 | 28.7364 | 28.6762 | 28.6364 | 28.6263 | 28.6424 | 28.7013 | 27.8593 | 27.5871 | 27.4836 | 27.4625 | 27.2817 | 22.1052 | 21.9264 | 21.7301 | 21.5115 | 21.298 | 21.1035 | 21.0604 | 21.055 | 21.1276 | 21.3384 | 33.8593 | 33.5871 | 33.4836 | 33.4625 | 33.2817 | 28.1052 | 27.9264 | 27.7301 | 27.5115 | 27.298 | 27.1035 | 27.0604 | 27.055 | 27.1276 | 27.291 | 380477 | 387810 | ALTRINCHAM | CARRINGTON
| Melling | 1.75 | 1.634 | 1.586 | 1.5516 | 1.496 | 1.4392 | 1.391 | 1.3454 | 1.2771 | 1.2168 | 0.90465 | 0.41089 | 0.019315 | -0.34146 | -0.65941 | 3.75 | 3.634 | 3.586 | 3.5516 | 3.496 | 3.4392 | 3.391 | 3.3454 | 3.2771 | 3.2168 | 2.9046 | 2.4109 | 2.0193 | 1.6585 | 1.3075 | 1.75 | 1.6976 | 1.6483 | 1.5905 | 1.5158 | 1.4344 | 1.3361 | 1.1485 | 1.0986 | 1.0336 | 0.79244 | 0.58598 | 0.41858 | 0.26144 | 0.15661 | 3.75 | 3.6976 | 3.6483 | 3.5905 | 3.5158 | 3.4344 | 3.3361 | 3.1485 | 3.0986 | 3.0336 | 2.7924 | 2.586 | 2.4186 | 2.2614 | 2.1766 | 1.75 | 1.6247 | 1.5807 | 1.5568 | 1.5133 | 1.471 | 1.4421 | 1.4173 | 1.3633 | 1.221 | 0.7289 | 0.15195 | -0.28049 | -0.64685 | -0.90888 | 3.75 | 3.6247 | 3.5807 | 3.5568 | 3.5133 | 3.471 | 3.4421 | 3.4173 | 3.3633 | 3.221 | 2.7289 | 2.1519 | 1.7195 | 1.3532 | 1.0875 | 1.75 | 1.7066 | 1.6881 | 1.6696 | 1.6346 | 1.5956 | 1.5381 | 1.3955 | 1.2401 | 1.087 | 0.65147 | 0.19564 | -0.20999 | -0.49761 | -0.49494 | 3.75 | 3.7066 | 3.6881 | 3.6696 | 3.6346 | 3.5956 | 3.5381 | 3.3955 | 3.2401 | 3.087 | 2.6515 | 2.1956 | 1.79 | 1.5024 | 1.4948 | 1.75 | 1.7049 | 1.6768 | 1.6545 | 1.6254 | 1.5933 | 1.5566 | 1.5171 | 1.4612 | 1.3982 | 1.1843 | 0.8166 | 0.51979 | 0.25913 | 0.12172 | 3.75 | 3.7049 | 3.6768 | 3.6545 | 3.6254 | 3.5933 | 3.5566 | 3.5171 | 3.4612 | 3.3982 | 3.1843 | 2.8166 | 2.5198 | 2.2591 | 2.1321 | 1.75 | 1.6441 | 1.5927 | 1.5452 | 1.4829 | 1.4231 | 1.3415 | 1.1658 | 0.98913 | 0.81525 | 0.32025 | -0.14351 | -0.50503 | -0.7255 | -0.58627 | 3.75 | 3.6441 | 3.5927 | 3.5452 | 3.4829 | 3.4231 | 3.3415 | 3.1658 | 2.9891 | 2.8153 | 2.3203 | 1.8565 | 1.495 | 1.2745 | 1.3822 | 360144 | 471643 | KENDAL (PARKSIDE RD) | HUTTON
| Mereside | 7.8888 | 6.9514 | 6.6652 | 6.5482 | 6.4169 | 6.2776 | 6.137 | 5.9905 | 5.8073 | 5.6337 | 4.8457 | 3.6905 | 2.7763 | 1.7951 | 0.90898 | 19.1488 | 18.2114 | 17.9252 | 17.8082 | 17.6769 | 17.5376 | 17.397 | 17.2505 | 17.0673 | 16.8937 | 16.1057 | 14.9505 | 14.0363 | 13.0551 | 12.1472 | 7.8888 | 7.6424 | 7.5005 | 7.4118 | 7.321 | 7.2162 | 7.0824 | 6.9091 | 6.7234 | 6.5362 | 5.9755 | 5.4158 | 4.9062 | 4.3595 | 3.9663 | 19.1488 | 18.9024 | 18.7605 | 18.6718 | 18.581 | 18.4762 | 18.3424 | 18.1691 | 17.9834 | 17.7962 | 17.2355 | 16.6758 | 16.1662 | 15.6195 | 15.2882 | 7.8888 | 6.8068 | 6.4956 | 6.3781 | 6.2476 | 6.1097 | 5.97 | 5.8265 | 5.6713 | 5.5281 | 4.8287 | 3.7658 | 2.9397 | 2.0987 | 1.4008 | 19.1488 | 18.0668 | 17.7556 | 17.6381 | 17.5076 | 17.3697 | 17.23 | 17.0865 | 16.9313 | 16.7881 | 16.0887 | 15.0258 | 14.1997 | 13.3587 | 12.6034 | 7.8888 | 7.1976 | 6.9837 | 6.9001 | 6.7938 | 6.6593 | 6.4699 | 6.1343 | 5.7718 | 5.4158 | 4.3622 | 3.2699 | 2.454 | 1.9543 | 2.1879 | 19.1488 | 18.4576 | 18.2437 | 18.1601 | 18.0538 | 17.9193 | 17.7299 | 17.3943 | 17.0318 | 16.6758 | 15.6222 | 14.5299 | 13.714 | 13.2143 | 13.3845 | 7.8888 | 7.4693 | 7.2948 | 7.2197 | 7.1514 | 7.058 | 6.9452 | 6.8248 | 6.6531 | 6.482 | 5.9305 | 5.3286 | 4.9199 | 4.5529 | 4.3709 | 19.1488 | 18.7293 | 18.5548 | 18.4797 | 18.4114 | 18.318 | 18.2052 | 18.0848 | 17.9131 | 17.742 | 17.1905 | 16.5886 | 16.1799 | 15.8129 | 15.6384 | 7.8888 | 6.7391 | 6.4099 | 6.2794 | 6.1328 | 5.9823 | 5.7822 | 5.4148 | 5.03 | 4.6544 | 3.5711 | 2.482 | 1.643 | 1.1226 | 1.3136 | 19.1488 | 17.9991 | 17.6699 | 17.5394 | 17.3928 | 17.2423 | 17.0422 | 16.6748 | 16.29 | 15.9144 | 14.8311 | 13.742 | 12.903 | 12.3826 | 12.5225 | 334431 | 434843 | PEEL | PENWORTHAM
| Middleton Junction | 8.727 | 8.248 | 8.2618 | 8.2255 | 8.1161 | 7.9839 | 7.8496 | 7.7168 | 7.5101 | 7.2262 | 5.4639 | 2.6765 | 0.38692 | -2.1068 | -4.4539 | 13.227 | 12.748 | 12.7618 | 12.7255 | 12.6161 | 12.4839 | 12.3496 | 12.2168 | 12.0101 | 11.7262 | 9.9639 | 7.1765 | 4.8869 | 2.3932 | -0.073693 | 8.727 | 8.4739 | 8.5032 | 8.4259 | 8.3161 | 8.1869 | 8.0021 | 7.7602 | 7.5113 | 7.2567 | 6.4558 | 5.4258 | 4.4076 | 3.3257 | 2.5741 | 13.227 | 12.9739 | 13.0032 | 12.9259 | 12.8161 | 12.6869 | 12.5021 | 12.2602 | 12.0113 | 11.7567 | 10.9558 | 9.9258 | 8.9076 | 7.8257 | 7.1908 | 8.727 | 8.2241 | 8.2518 | 8.2552 | 8.1859 | 8.1006 | 8.0376 | 7.9788 | 7.8642 | 7.6299 | 6.0745 | 3.4154 | 1.2373 | -0.97301 | -2.964 | 13.227 | 12.7241 | 12.7518 | 12.7552 | 12.6859 | 12.6006 | 12.5376 | 12.4788 | 12.3642 | 12.1299 | 10.5745 | 7.9154 | 5.7373 | 3.527 | 1.3672 | 8.727 | 8.6268 | 8.7474 | 8.7625 | 8.6761 | 8.5543 | 8.2815 | 7.4753 | 6.6104 | 5.7358 | 3.1692 | 0.66895 | -1.3661 | -2.6962 | -1.9325 | 13.227 | 13.1268 | 13.2474 | 13.2625 | 13.1761 | 13.0543 | 12.7815 | 11.9753 | 11.1104 | 10.2358 | 7.6692 | 5.169 | 3.1339 | 1.8038 | 2.3942 | 8.727 | 8.4892 | 8.5836 | 8.6103 | 8.6157 | 8.5834 | 8.5141 | 8.424 | 8.2351 | 8.0452 | 7.0088 | 5.853 | 5.0388 | 4.3237 | 3.9692 | 13.227 | 12.9892 | 13.0836 | 13.1103 | 13.1157 | 13.0834 | 13.0141 | 12.924 | 12.7351 | 12.5452 | 11.5088 | 10.353 | 9.5388 | 8.8237 | 8.4778 | 8.727 | 8.4446 | 8.4711 | 8.4116 | 8.2585 | 8.094 | 7.7661 | 6.8893 | 5.9755 | 5.0506 | 2.3049 | -0.36752 | -2.5923 | -4.1532 | -3.6119 | 13.227 | 12.9446 | 12.9711 | 12.9116 | 12.7585 | 12.594 | 12.2661 | 11.3893 | 10.4755 | 9.5506 | 6.8049 | 4.1325 | 1.9077 | 0.34682 | 0.76358 | 388606 | 405292 | CHADDERTON | WHITEGATE
| Midway | 9.6984 | 9.5367 | 9.4304 | 9.3419 | 9.2015 | 9.0542 | 8.9268 | 8.8323 | 8.7247 | 8.6333 | 7.8912 | 6.5792 | 5.6095 | 4.8156 | 4.1158 | 12.1984 | 12.0367 | 11.9304 | 11.8419 | 11.7015 | 11.5542 | 11.4268 | 11.3323 | 11.2247 | 11.1333 | 10.3912 | 9.0792 | 8.1095 | 7.3156 | 6.5262 | 9.6984 | 9.5757 | 9.4826 | 9.3828 | 9.2526 | 9.1127 | 8.9406 | 8.7374 | 8.6169 | 8.4948 | 8.1266 | 7.7577 | 7.4054 | 7.0156 | 6.7336 | 12.1984 | 12.0757 | 11.9826 | 11.8828 | 11.7526 | 11.6127 | 11.4406 | 11.2374 | 11.1169 | 10.9948 | 10.6266 | 10.2577 | 9.9054 | 9.5156 | 9.2722 | 9.6984 | 9.5312 | 9.4351 | 9.3686 | 9.2524 | 9.1342 | 9.0467 | 8.9972 | 8.94 | 8.8909 | 7.662 | 6.2241 | 5.1492 | 4.2696 | 3.685 | 12.1984 | 12.0312 | 11.9351 | 11.8686 | 11.7524 | 11.6342 | 11.5467 | 11.4972 | 11.44 | 11.3909 | 10.162 | 8.7241 | 7.6492 | 6.7696 | 6.1671 | 9.6984 | 9.6815 | 9.6328 | 9.5694 | 9.4673 | 9.3506 | 9.1836 | 8.831 | 8.4552 | 8.0847 | 7.0076 | 5.984 | 5.1143 | 4.4767 | 4.5373 | 12.1984 | 12.1815 | 12.1328 | 12.0694 | 11.9673 | 11.8506 | 11.6836 | 11.331 | 10.9552 | 10.5847 | 9.5076 | 8.484 | 7.6143 | 6.9767 | 7.0024 | 9.6984 | 9.567 | 9.4819 | 9.4214 | 9.3482 | 9.2678 | 9.1707 | 9.0743 | 8.9464 | 8.8174 | 8.3275 | 7.3667 | 6.5711 | 5.9009 | 5.6265 | 12.1984 | 12.067 | 11.9819 | 11.9214 | 11.8482 | 11.7678 | 11.6707 | 11.5743 | 11.4464 | 11.3174 | 10.8275 | 9.8667 | 9.0711 | 8.4009 | 8.1364 | 9.6984 | 9.5933 | 9.3286 | 9.051 | 8.7393 | 8.4307 | 8.067 | 7.4998 | 6.9317 | 6.3692 | 5.1944 | 4.0637 | 3.1974 | 2.7143 | 3.1154 | 12.1984 | 12.0933 | 11.8286 | 11.551 | 11.2393 | 10.9307 | 10.567 | 9.9998 | 9.4317 | 8.8692 | 7.6944 | 6.5637 | 5.6974 | 5.2143 | 5.525 | 304525 | 501993 | EGREMONT | HARKER
| Milnrow | 12.4534 | 11.6755 | 11.3937 | 11.2666 | 11.0807 | 10.8853 | 10.7148 | 10.5667 | 10.3565 | 10.1604 | 8.6835 | 6.0179 | 3.7612 | 1.3562 | -0.81145 | 17.0934 | 16.3155 | 16.0337 | 15.9066 | 15.7207 | 15.5253 | 15.3548 | 15.2067 | 14.9965 | 14.8004 | 13.3235 | 10.6579 | 8.4012 | 5.9962 | 3.7187 | 12.4534 | 12.1921 | 12.0198 | 11.9022 | 11.7772 | 11.6463 | 11.4731 | 11.2353 | 10.9895 | 10.7407 | 9.9825 | 9.1885 | 8.3907 | 7.471 | 6.7671 | 17.0934 | 16.8321 | 16.6598 | 16.5422 | 16.4172 | 16.2863 | 16.1131 | 15.8753 | 15.6295 | 15.3807 | 14.6225 | 13.8285 | 13.0307 | 12.111 | 11.5236 | 12.4534 | 11.5802 | 11.2918 | 11.0754 | 10.7977 | 10.5144 | 10.2106 | 10.1137 | 9.9902 | 9.8594 | 8.5745 | 6.0748 | 3.9823 | 1.8038 | -0.092372 | 17.0934 | 16.2202 | 15.9318 | 15.7154 | 15.4377 | 15.1544 | 14.8506 | 14.7537 | 14.6302 | 14.4994 | 13.2145 | 10.7148 | 8.6223 | 6.4438 | 4.3884 | 12.4534 | 11.9589 | 11.759 | 11.5383 | 11.2414 | 10.9244 | 10.4235 | 9.6233 | 8.7778 | 7.9243 | 5.4556 | 3.0773 | 1.1609 | -0.052679 | 0.65175 | 17.0934 | 16.5989 | 16.399 | 16.1783 | 15.8814 | 15.5644 | 15.0635 | 14.2633 | 13.4178 | 12.5643 | 10.0956 | 7.7173 | 5.8009 | 4.5873 | 5.1293 | 12.4534 | 12.0625 | 11.8805 | 11.8052 | 11.7334 | 11.6464 | 11.5494 | 11.4374 | 11.2294 | 11.0191 | 10.2791 | 9.4165 | 8.8171 | 8.2346 | 7.9196 | 17.0934 | 16.7025 | 16.5205 | 16.4452 | 16.3734 | 16.2864 | 16.1894 | 16.0774 | 15.8694 | 15.6591 | 14.9191 | 14.0565 | 13.4571 | 12.8746 | 12.5635 | 12.4534 | 11.585 | 11.2672 | 10.9912 | 10.6439 | 10.2923 | 9.75 | 8.8937 | 8.0116 | 7.1209 | 4.5243 | 2.0148 | -0.051076 | -1.4553 | -0.95232 | 17.0934 | 16.225 | 15.9072 | 15.6312 | 15.2839 | 14.9323 | 14.39 | 13.5337 | 12.6516 | 11.7609 | 9.1643 | 6.6548 | 4.5889 | 3.1847 | 3.5698 | 392351 | 413056 | CASTLETON | ROCHDALE
| Mintsfeet | 3.1835 | 0.84167 | 0.16966 | -0.14283 | -0.50723 | -0.92531 | -1.6604 | -2.0544 | -2.5303 | -3.2027 | -5.0713 | -11.5633 | -14.5038 | -20.0797 | -21.9053 | 9.1835 | 6.8417 | 6.1697 | 5.8572 | 5.4928 | 5.0747 | 4.3396 | 3.9456 | 3.4697 | 2.7973 | 0.92865 | -5.5633 | -8.5038 | -14.0797 | -16.1578 | 3.1835 | 2.3186 | 2.0185 | 1.739 | 1.4239 | 1.0007 | 0.45915 | -0.17035 | -0.60834 | -1.0321 | -2.3211 | -3.8342 | -4.9607 | -9.4802 | -10.2432 | 9.1835 | 8.3186 | 8.0185 | 7.739 | 7.4239 | 7.0007 | 6.4592 | 5.8297 | 5.3917 | 4.9679 | 3.6789 | 2.1658 | 1.0393 | -3.4802 | -4.1886 | 3.1835 | 0.4977 | -0.23373 | -0.54674 | -0.90904 | -1.3227 | -2.0456 | -2.4332 | -3.137 | -3.4395 | -15.3872 | -18.2527 | -20.2046 | -21.2639 | -22.416 | 9.1835 | 6.4977 | 5.7663 | 5.4533 | 5.091 | 4.6773 | 3.9544 | 3.5668 | 2.863 | 2.5605 | -9.3872 | -12.2527 | -14.2046 | -15.2639 | -16.7702 | 3.1835 | 1.3724 | 0.83414 | -4.2783 | -4.3022 | -4.8369 | -5.4585 | -6.2062 | -7.5358 | -8.6806 | -11.8321 | -14.1833 | -15.9806 | -16.7614 | -15.4757 | 9.1835 | 7.3724 | 6.8341 | 1.7217 | 1.6978 | 1.1631 | 0.54154 | -0.20623 | -1.5358 | -2.6806 | -5.8321 | -8.1833 | -9.9806 | -10.7614 | -9.7695 | 3.1835 | 1.8626 | 1.4028 | 1.1602 | 0.93349 | 0.645 | -0.010675 | -0.35205 | -0.80953 | -1.4897 | -2.7093 | -7.5204 | -8.7723 | -12.5472 | -12.3366 | 9.1835 | 7.8626 | 7.4028 | 7.1602 | 6.9335 | 6.645 | 5.9893 | 5.6479 | 5.1905 | 4.5103 | 3.2907 | -1.5204 | -2.7723 | -6.5472 | -6.4742 | 3.1835 | 0.2966 | -0.49146 | -5.6866 | -5.7809 | -6.3404 | -6.9751 | -7.7735 | -9.1368 | -10.3115 | -13.7705 | -16.5129 | -18.5752 | -19.5692 | -18.503 | 9.1835 | 6.2966 | 5.5085 | 0.31338 | 0.21908 | -0.34044 | -0.97513 | -1.7735 | -3.1368 | -4.3115 | -7.7705 | -10.5129 | -12.5752 | -13.5692 | -12.7482 | 351827 | 494315 | KENDAL (PARKSIDE RD) | HUTTON | Firm Capacity exceeded in FY27. Capacity will be released upon the completion of a new RIIO-ED2 connections driven reinforcement project
| Monsall | 6.8632 | 5.6958 | 5.3947 | 5.3255 | 5.0235 | 0.70249 | 0.40028 | 0.13233 | -0.14298 | -0.39663 | -1.7873 | -3.7459 | -5.2404 | -6.5832 | -7.4214 | 10.3632 | 9.1958 | 8.8947 | 8.8255 | 8.5235 | 4.2025 | 3.9003 | 3.6323 | 3.357 | 3.1034 | 1.7127 | -0.24587 | -1.7404 | -3.0832 | -4.1359 | 6.8632 | 6.7057 | 6.6158 | 6.5705 | 6.5216 | 2.4816 | 2.406 | 2.289 | 2.2 | 2.1043 | 1.8352 | 1.5479 | 1.2675 | 0.95461 | 0.71391 | 10.3632 | 10.2057 | 10.1158 | 10.0705 | 10.0216 | 5.9816 | 5.906 | 5.789 | 5.7 | 5.6043 | 5.3352 | 5.0479 | 4.7675 | 4.4546 | 4.25 | 6.8632 | 5.4395 | 5.0103 | 4.845 | 4.4352 | -0.0023226 | -0.40157 | -0.78762 | -1.1503 | -1.5244 | -3.2169 | -5.1468 | -6.3805 | -7.2167 | -7.2246 | 10.3632 | 8.9395 | 8.5103 | 8.345 | 7.9352 | 3.4977 | 3.0984 | 2.7124 | 2.3497 | 1.9756 | 0.28312 | -1.6468 | -2.8805 | -3.7167 | -3.9565 | 6.8632 | 6.0139 | 5.6921 | 5.5259 | 5.1072 | 0.67092 | 0.13484 | -0.82986 | -1.7524 | -2.6448 | -4.9435 | -6.4738 | -7.3045 | -7.3234 | -6.1943 | 10.3632 | 9.5139 | 9.1921 | 9.0259 | 8.6072 | 4.1709 | 3.6348 | 2.6701 | 1.7476 | 0.85516 | -1.4435 | -2.9738 | -3.8045 | -3.8234 | -2.9296 | 6.8632 | 6.5794 | 6.458 | 6.4127 | 6.2071 | 2.0031 | 1.7801 | 1.517 | 1.2014 | 0.88911 | 0.023758 | -0.52683 | -0.87999 | -1.2088 | -1.2666 | 10.3632 | 10.0794 | 9.958 | 9.9127 | 9.7071 | 5.5031 | 5.2801 | 5.017 | 4.7014 | 4.3891 | 3.5238 | 2.9732 | 2.62 | 2.2912 | 2.211 | 6.8632 | 5.4716 | 5.0263 | 4.8427 | 4.4052 | -0.050836 | -0.6178 | -1.6099 | -2.5433 | -3.4507 | -5.8144 | -7.4056 | -8.3167 | -8.4631 | -7.5019 | 10.3632 | 8.9716 | 8.5263 | 8.3427 | 7.9052 | 3.4492 | 2.8822 | 1.8901 | 0.95668 | 0.049349 | -2.3144 | -3.9056 | -4.8167 | -4.9631 | -4.2003 | 386332 | 401003 | STUART ST | STALYBRIDGE
| Monton | 8.013 | 7.2166 | 6.6953 | 6.3547 | 5.9543 | 5.5075 | 5.0329 | 4.5462 | 4.0155 | 3.4935 | 1.401 | -1.1549 | -2.853 | -4.273 | -5.2172 | 11.513 | 10.7166 | 10.1953 | 9.8547 | 9.4543 | 9.0075 | 8.5329 | 8.0462 | 7.5155 | 6.9935 | 4.901 | 2.3451 | 0.64704 | -0.77298 | -1.8086 | 8.013 | 7.7309 | 7.5161 | 7.3115 | 7.0659 | 6.8138 | 6.5007 | 6.0764 | 5.6911 | 5.2889 | 4.056 | 2.8274 | 1.7132 | 0.59366 | -0.10878 | 11.513 | 11.2309 | 11.0161 | 10.8115 | 10.5659 | 10.3138 | 10.0007 | 9.5764 | 9.1911 | 8.7889 | 7.556 | 6.3274 | 5.2132 | 4.0937 | 3.4974 | 8.013 | 7.069 | 6.4765 | 6.0924 | 5.6454 | 5.1135 | 4.5929 | 4.0577 | 3.498 | 2.9211 | 0.63477 | -1.9615 | -3.5625 | -4.7276 | -5.1853 | 11.513 | 10.569 | 9.9765 | 9.5924 | 9.1454 | 8.6135 | 8.0929 | 7.5577 | 6.998 | 6.4211 | 4.1348 | 1.5385 | -0.062489 | -1.2276 | -1.7721 | 8.013 | 7.4466 | 6.9668 | 6.6273 | 6.203 | 5.7352 | 5.1239 | 4.2091 | 3.2761 | 2.3466 | -0.32257 | -2.5862 | -3.852 | -4.4359 | -4.0684 | 11.513 | 10.9466 | 10.4668 | 10.1273 | 9.703 | 9.2352 | 8.6239 | 7.7091 | 6.7761 | 5.8466 | 3.1774 | 0.91382 | -0.35202 | -0.93589 | -0.66287 | 8.013 | 7.578 | 7.1658 | 6.8948 | 6.6083 | 6.2978 | 5.9098 | 5.491 | 5.0009 | 4.4975 | 2.8698 | 1.2678 | 0.27904 | -0.54342 | -1.0082 | 11.513 | 11.078 | 10.6658 | 10.3948 | 10.1083 | 9.7978 | 9.4098 | 8.991 | 8.5009 | 7.9975 | 6.3698 | 4.7678 | 3.779 | 2.9566 | 2.5456 | 8.013 | 7.1028 | 6.4851 | 6.0554 | 5.5507 | 5.0025 | 4.3328 | 3.3386 | 2.3493 | 1.3661 | -1.4852 | -3.9194 | -5.3472 | -6.0736 | -5.8666 | 11.513 | 10.6028 | 9.9851 | 9.5554 | 9.0507 | 8.5025 | 7.8328 | 6.8386 | 5.8493 | 4.8661 | 2.0148 | -0.41943 | -1.8472 | -2.5736 | -2.4227 | 376321 | 399494 | BARTON | CARRINGTON
| Moorside | 8.1847 | 4.5361 | 3.7336 | 3.5474 | 3.3255 | 3.1011 | 2.8915 | 2.6808 | 2.3958 | 2.1139 | 0.98191 | -0.53858 | -1.6321 | -2.6287 | -3.5201 | 11.6847 | 8.0361 | 7.2336 | 7.0474 | 6.8255 | 6.6011 | 6.3915 | 6.1808 | 5.8958 | 5.6139 | 4.4819 | 2.9614 | 1.8679 | 0.87133 | -0.044526 | 8.1847 | 6.6866 | 6.297 | 6.1333 | 5.9427 | 5.7482 | 5.4964 | 5.1485 | 4.8175 | 4.4744 | 3.4437 | 2.4218 | 1.4995 | 0.4675 | -0.20791 | 11.6847 | 10.1866 | 9.797 | 9.6333 | 9.4427 | 9.2482 | 8.9964 | 8.6485 | 8.3175 | 7.9744 | 6.9437 | 5.9218 | 4.9995 | 3.9675 | 3.404 | 8.1847 | 3.9707 | 3.088 | 2.9409 | 2.7588 | 2.5816 | 2.4359 | 2.2993 | 2.1128 | 1.9248 | 1.0446 | -0.28304 | -1.2102 | -1.9982 | -2.6421 | 11.6847 | 7.4707 | 6.588 | 6.4409 | 6.2588 | 6.0816 | 5.9359 | 5.7993 | 5.6128 | 5.4248 | 4.5446 | 3.217 | 2.2898 | 1.5018 | 0.78684 | 8.1847 | 5.2848 | 4.6619 | 4.5327 | 4.369 | 4.1889 | 3.9755 | 3.5978 | 3.1599 | 2.7136 | 1.4333 | 0.18602 | -0.62897 | -1.052 | -0.74017 | 11.6847 | 8.7848 | 8.1619 | 8.0327 | 7.869 | 7.6889 | 7.4755 | 7.0978 | 6.6599 | 6.2136 | 4.9333 | 3.686 | 2.871 | 2.448 | 2.6832 | 8.1847 | 5.3327 | 4.6914 | 4.5438 | 4.3914 | 4.2294 | 4.0595 | 3.8703 | 3.5777 | 3.2838 | 2.298 | 1.2209 | 0.47331 | -0.16926 | -0.47873 | 11.6847 | 8.8327 | 8.1914 | 8.0438 | 7.8914 | 7.7294 | 7.5595 | 7.3703 | 7.0777 | 6.7838 | 5.798 | 4.7209 | 3.9733 | 3.3307 | 3.0321 | 8.1847 | 3.4761 | 2.4793 | 2.2731 | 2.0403 | 1.8146 | 1.5488 | 1.0952 | 0.60552 | 0.10903 | -1.3511 | -2.7669 | -3.7182 | -4.2688 | -4.08 | 11.6847 | 6.9761 | 5.9793 | 5.7731 | 5.5403 | 5.3146 | 5.0488 | 4.5952 | 4.1055 | 3.609 | 2.1489 | 0.73305 | -0.21819 | -0.76879 | -0.63016 | 349331 | 435746 | RIBBLE | PENWORTHAM
| Morton Park & Pirelli | 7.4325 | 1.0018 | -2.3523 | -4.5777 | -6.8528 | 1.6531 | -1.1167 | -3.3556 | -5.6928 | -8.0011 | -17.235 | -28.1232 | -37.056 | -40.2572 | -42.9012 | 11.2325 | 4.8018 | 1.4477 | -0.77774 | -3.0528 | 10.4031 | 7.6333 | 5.3944 | 3.0572 | 0.74886 | -8.485 | -19.3732 | -28.306 | -31.5072 | -34.3981 | 7.4325 | 5.8855 | 3.4197 | 1.2453 | -0.91288 | 7.7185 | 5.4451 | 3.0592 | 0.61757 | -1.8229 | -9.1156 | -16.3916 | -24.9189 | -29.5688 | -30.1292 | 11.2325 | 9.6855 | 7.2197 | 5.0453 | 2.8871 | 16.4685 | 14.1951 | 11.8092 | 9.3676 | 6.9271 | -0.36562 | -7.6416 | -16.1689 | -20.8188 | -21.3054 | 7.4325 | -0.046508 | -3.5815 | -5.808 | -8.0804 | 0.42995 | -2.3232 | -6.459 | -8.656 | -10.825 | -22.8088 | -32.9932 | -41.2529 | -43.7466 | -45.8872 | 11.2325 | 3.7535 | 0.21854 | -2.008 | -4.2804 | 9.1799 | 6.4268 | 2.291 | 0.093993 | -2.075 | -14.0588 | -24.2432 | -32.5029 | -34.9966 | -37.4729 | 7.4325 | 2.3292 | -0.75977 | -3.5204 | -9.9205 | -4.5714 | -8.2544 | -10.8931 | -13.5935 | -16.3052 | -24.9846 | -34.1234 | -42.699 | -43.8978 | -42.3186 | 11.2325 | 6.1292 | 3.0402 | 0.27957 | -6.1205 | 4.1786 | 0.49563 | -2.1431 | -4.8435 | -7.5552 | -16.2346 | -25.3734 | -33.949 | -35.1478 | -33.9093 | 7.4325 | 4.4755 | 1.7579 | -0.38904 | -2.5093 | 6.1373 | 3.4629 | 1.2815 | -1.049 | -3.3748 | -11.859 | -20.4833 | -27.2668 | -28.1033 | -28.1441 | 11.2325 | 8.2755 | 5.5579 | 3.411 | 1.2907 | 14.8873 | 12.2129 | 10.0315 | 7.701 | 5.3752 | -3.109 | -11.7333 | -18.5168 | -19.3533 | -19.5192 | 7.4325 | -0.85333 | -4.5559 | -7.3974 | -13.8673 | -8.5464 | -12.2476 | -14.9433 | -17.6861 | -20.4871 | -29.6598 | -39.0183 | -47.7987 | -49.2149 | -47.8675 | 11.2325 | 2.9467 | -0.75593 | -3.5974 | -10.0673 | 0.20364 | -3.4976 | -6.1933 | -8.9361 | -11.7371 | -20.9098 | -30.2683 | -39.0487 | -40.4649 | -39.4082 | 337826 | 553939 | CARLISLE | HARKER | Firm Capacity exceeded in FY26. Capacity will be released upon completion of the reinforcement of circuits to Morton Park and new 11.5/23MVA transformer at Pirelli in RIIO-ED2
| Mosley Rd | 10.4778 | 8.5831 | 7.8491 | 7.4594 | 7.0917 | 6.695 | 6.2602 | 5.7667 | 5.1405 | 4.4785 | 2.392 | 0.21484 | -3.0722 | -4.3289 | -5.4287 | 10.4778 | 8.5831 | 7.8491 | 7.4594 | 7.0917 | 6.695 | 6.2602 | 5.7667 | 5.1405 | 4.4785 | 2.392 | 0.21484 | -3.0722 | -4.3289 | -5.3294 | 10.4778 | 10.0347 | 9.7682 | 9.6271 | 9.5142 | 9.3772 | 9.2152 | 9.0255 | 8.7919 | 8.5356 | 7.6428 | 6.2304 | 3.3398 | 0.95837 | -0.55215 | 10.4778 | 10.0347 | 9.7682 | 9.6271 | 9.5142 | 9.3772 | 9.2152 | 9.0255 | 8.7919 | 8.5356 | 7.6428 | 6.2304 | 3.3398 | 0.95837 | -0.36165 | 10.4778 | 8.2872 | 7.4953 | 7.11 | 6.7543 | 6.3787 | 5.977 | 5.531 | 5.0038 | 4.4435 | 0.59179 | -2.193 | -3.4996 | -4.5877 | -5.3582 | 10.4778 | 8.2872 | 7.4953 | 7.11 | 6.7543 | 6.3787 | 5.977 | 5.531 | 5.0038 | 4.4435 | 0.59179 | -2.193 | -3.4996 | -4.5877 | -5.3231 | 10.4778 | 8.903 | 8.2562 | 7.89 | 7.5425 | 6.7644 | 4.672 | 4.09 | 2.6982 | 1.9664 | -0.50607 | -2.106 | -3.2494 | -4.0877 | -4.382 | 10.4778 | 8.903 | 8.2562 | 7.89 | 7.5425 | 6.7644 | 4.672 | 4.09 | 2.6982 | 1.9664 | -0.50607 | -2.106 | -3.2494 | -4.0877 | -4.3512 | 10.4778 | 9.6252 | 9.1197 | 8.7606 | 8.4351 | 8.074 | 7.6721 | 7.2306 | 6.6698 | 6.0724 | 4.2177 | 2.2887 | -0.80336 | -1.9082 | -2.4696 | 10.4778 | 9.6252 | 9.1197 | 8.7606 | 8.4351 | 8.074 | 7.6721 | 7.2306 | 6.6698 | 6.0724 | 4.2177 | 2.2887 | -0.80336 | -1.9082 | -2.3934 | 10.4778 | 7.9919 | 7.1383 | 6.747 | 6.3866 | 5.62 | 3.5613 | 3.0217 | 1.6715 | 0.97973 | -1.4873 | -3.2305 | -4.5295 | -5.455 | -5.7704 | 10.4778 | 7.9919 | 7.1383 | 6.747 | 6.3866 | 5.62 | 3.5613 | 3.0217 | 1.6715 | 0.97973 | -1.4873 | -3.2305 | -4.5295 | -5.455 | -5.7354 | 379058 | 396289 | STRETFORD | SOUTH MANCHESTER
| Moss Lane | 2.5064 | 1.2001 | 0.7582 | 0.469 | 0.0059999 | 0.59608 | -0.014517 | -0.53172 | -1.2096 | -2.2578 | -7.2794 | -12.9557 | -17.0833 | -20.6916 | -23.5547 | 6.6434 | 5.3371 | 4.8952 | 4.606 | 4.143 | 0.59608 | -0.014517 | -0.53172 | -1.2096 | -2.2578 | -7.2794 | -12.9557 | -17.0833 | -20.6916 | -23.6462 | 2.5064 | 2.0256 | 1.8318 | 1.6545 | 1.3805 | 2.1854 | 1.7354 | 1.1929 | 0.68298 | 0.13055 | -1.7752 | -4.0002 | -6.9281 | -10.4079 | -12.7227 | 6.6434 | 6.1626 | 5.9688 | 5.7915 | 5.5175 | 2.1854 | 1.7354 | 1.1929 | 0.68298 | 0.13055 | -1.7752 | -4.0002 | -6.9281 | -10.4079 | -12.4173 | 2.5064 | 1.0689 | 0.64108 | 0.44353 | 0.08139 | 0.79896 | 0.37337 | 0.072768 | -0.56734 | -1.6165 | -6.4136 | -12.4211 | -16.9175 | -20.6281 | -23.2669 | 6.6434 | 5.2059 | 4.7781 | 4.5805 | 4.2184 | 0.79896 | 0.37337 | 0.072768 | -0.56734 | -1.6165 | -6.4136 | -12.4211 | -16.9175 | -20.6281 | -23.4065 | 2.5064 | 1.9057 | 1.6912 | 1.5463 | 1.1763 | 1.8134 | 1.0463 | -0.37179 | -1.9749 | -3.7766 | -9.9375 | -15.3318 | -19.1166 | -21.4122 | -20.9103 | 6.6434 | 6.0427 | 5.8282 | 5.6833 | 5.3133 | 1.8134 | 1.0463 | -0.37179 | -1.9749 | -3.7766 | -9.9375 | -15.3318 | -19.1166 | -21.4122 | -21.0691 | 2.5064 | 1.6511 | 1.3759 | 1.2462 | 1.0372 | 1.8457 | 1.4102 | 1.0526 | 0.5093 | -0.21184 | -4.0131 | -7.8037 | -10.3672 | -12.1459 | -12.8261 | 6.6434 | 5.7881 | 5.5129 | 5.3832 | 5.1742 | 1.8457 | 1.4102 | 1.0526 | 0.5093 | -0.21184 | -4.0131 | -7.8037 | -10.3672 | -12.1459 | -12.7914 | 2.5064 | 1.2927 | 0.83165 | 0.51235 | 0.0049611 | 0.57916 | -0.25473 | -1.7681 | -3.4123 | -5.1245 | -10.4688 | -16.2574 | -20.6339 | -23.341 | -23.072 | 6.6434 | 5.4297 | 4.9687 | 4.6493 | 4.142 | 0.57916 | -0.25473 | -1.7681 | -3.4123 | -5.1245 | -10.4688 | -16.2574 | -20.6339 | -23.341 | -23.1799 | 380858 | 405856 | KEARSLEY LOCAL | KEARSLEY
| Moss Nook Primary | 17.6034 | 15.1315 | 14.4027 | 14.1997 | 13.992 | 13.7945 | 13.6368 | 13.5066 | 13.2626 | 13.0363 | 11.6077 | 9.167 | 7.1565 | 5.053 | 3.1456 | 23.6034 | 21.1315 | 20.4027 | 20.1997 | 19.992 | 19.7945 | 19.6368 | 19.5066 | 19.2626 | 19.0363 | 17.6077 | 15.167 | 13.1565 | 11.053 | 9.0382 | 17.6034 | 16.9127 | 16.5776 | 16.4018 | 16.2333 | 16.0615 | 15.8505 | 15.5834 | 15.2635 | 14.9435 | 13.9983 | 13.0874 | 12.243 | 11.3358 | 10.6903 | 23.6034 | 22.9127 | 22.5776 | 22.4018 | 22.2333 | 22.0615 | 21.8505 | 21.5834 | 21.2635 | 20.9435 | 19.9983 | 19.0874 | 18.243 | 17.3358 | 16.7879 | 17.6034 | 14.7673 | 13.9842 | 13.8315 | 13.6675 | 13.5183 | 13.4236 | 13.3663 | 13.2563 | 13.1318 | 12.0208 | 9.8828 | 8.1616 | 6.4275 | 4.9664 | 23.6034 | 20.7673 | 19.9842 | 19.8315 | 19.6675 | 19.5183 | 19.4236 | 19.3663 | 19.2563 | 19.1318 | 18.0208 | 15.8828 | 14.1616 | 12.4275 | 10.776 | 17.6034 | 15.6502 | 15.0804 | 14.941 | 14.773 | 14.5888 | 14.3164 | 13.6608 | 12.9281 | 12.1748 | 10.0078 | 7.9351 | 6.3265 | 5.4011 | 6.2326 | 23.6034 | 21.6502 | 21.0804 | 20.941 | 20.773 | 20.5888 | 20.3164 | 19.6608 | 18.9281 | 18.1748 | 16.0078 | 13.9351 | 12.3265 | 11.4011 | 12.0401 | 17.6034 | 16.3655 | 15.9238 | 15.7912 | 15.6984 | 15.5919 | 15.4961 | 15.4059 | 15.1723 | 14.9431 | 14.165 | 13.3034 | 12.7427 | 12.2588 | 12.1358 | 23.6034 | 22.3655 | 21.9238 | 21.7912 | 21.6984 | 21.5919 | 21.4961 | 21.4059 | 21.1723 | 20.9431 | 20.165 | 19.3034 | 18.7427 | 18.2588 | 18.0974 | 17.6034 | 14.4188 | 13.532 | 13.3047 | 13.0582 | 12.8232 | 12.4947 | 11.7523 | 10.9569 | 10.1382 | 7.7812 | 5.5596 | 3.8181 | 2.7487 | 3.4208 | 23.6034 | 20.4188 | 19.532 | 19.3047 | 19.0582 | 18.8232 | 18.4947 | 17.7523 | 16.9569 | 16.1382 | 13.7812 | 11.5596 | 9.8181 | 8.7487 | 9.2633 | 384084 | 385010 | MOSS NOOK | SOUTH MANCHESTER
| Moss Side (Leyland) & Seven Stars | 3.888 | 0.46385 | -0.33294 | -0.4985 | -0.78051 | -1.1181 | -1.5226 | -1.9586 | -2.6472 | -3.3389 | -6.1244 | -9.5517 | -12.1207 | -14.3414 | -16.0809 | 7.202 | 3.7778 | 2.9811 | 2.8155 | 2.5335 | 2.1959 | 1.7914 | 1.3554 | 0.66684 | -0.024876 | -2.8104 | -6.2377 | -8.8067 | -11.0274 | -12.8826 | 3.888 | 2.4057 | 1.9482 | 1.7841 | 1.5874 | 1.3307 | 1.0034 | 0.56011 | 0.038832 | -0.51004 | -2.293 | -4.2607 | -6.0805 | -7.9423 | -9.1515 | 7.202 | 5.7197 | 5.2622 | 5.0981 | 4.9014 | 4.6447 | 4.3174 | 3.8741 | 3.3528 | 2.804 | 1.021 | -0.94674 | -2.7665 | -4.6283 | -5.6813 | 3.888 | -0.092252 | -0.98407 | -1.1485 | -1.3255 | -1.52 | -1.7332 | -1.9981 | -2.4825 | -3.0155 | -5.4815 | -8.8116 | -11.3224 | -13.3752 | -14.8046 | 7.202 | 3.2217 | 2.3299 | 2.1655 | 1.9885 | 1.794 | 1.5808 | 1.3159 | 0.83146 | 0.2985 | -2.1675 | -5.4976 | -8.0084 | -10.0612 | -11.6712 | 3.888 | 1.2343 | 0.62876 | 0.53866 | 0.4149 | 0.23337 | -0.18215 | -1.0814 | -2.1334 | -3.2649 | -6.6233 | -9.6808 | -11.8725 | -13.0692 | -12.3172 | 7.202 | 4.5483 | 3.9428 | 3.8527 | 3.7289 | 3.5474 | 3.1319 | 2.2326 | 1.1806 | 0.04905 | -3.3093 | -6.3668 | -8.5585 | -9.7552 | -9.1958 | 3.888 | 1.0718 | 0.42269 | 0.33494 | 0.26895 | 0.14997 | -0.07716 | -0.40208 | -0.94623 | -1.5604 | -3.6651 | -5.7836 | -7.2218 | -8.2658 | -8.5637 | 7.202 | 4.3858 | 3.7367 | 3.6489 | 3.583 | 3.464 | 3.2368 | 2.9119 | 2.3678 | 1.7536 | -0.35113 | -2.4696 | -3.9078 | -4.9518 | -5.2624 | 3.888 | -0.48032 | -1.4497 | -1.6251 | -2.4225 | -3.3271 | -4.3807 | -5.9343 | -7.0187 | -8.157 | -11.6691 | -15.0462 | -17.5525 | -18.9917 | -18.4211 | 7.202 | 2.8337 | 1.8643 | 1.6889 | 0.89149 | -0.013065 | -1.0667 | -2.6203 | -3.7047 | -4.843 | -8.3551 | -11.7322 | -14.2385 | -15.6777 | -15.2558 | 352170 | 422970 | LEYLAND | PENWORTHAM | Firm Capacity marginally exceeded in FY26. There is a connections driven reinforcement to install a second 11.5/23MVA in RIIO-ED2.
| Moss Side (Longsight) | 2.9463 | -0.72369 | -1.9145 | -2.3962 | -2.9639 | 4.4396 | 4.005 | 1.9016 | 1.5057 | 1.0901 | -2.614 | -5.9398 | -8.4013 | -10.8707 | -12.6257 | 9.4463 | 5.7763 | 4.5855 | 4.1038 | 3.5361 | 10.9396 | 10.505 | 8.4016 | 8.0057 | 7.5901 | 3.886 | 0.56018 | -1.9013 | -4.3707 | -6.2373 | 2.9463 | 1.8749 | 1.449 | 1.2232 | 0.98517 | 8.7634 | 8.4635 | 8.0095 | 7.5736 | 7.1262 | 5.79 | 4.3631 | 3.0334 | 1.4955 | -0.013812 | 9.4463 | 8.3749 | 7.949 | 7.7232 | 7.4852 | 15.2634 | 14.9635 | 14.5095 | 14.0736 | 13.6262 | 12.29 | 10.8631 | 9.5334 | 7.9955 | 6.7037 | 2.9463 | -1.3684 | -2.7666 | -3.3442 | -4.0314 | 3.2247 | 2.6475 | 0.38542 | -0.15046 | -0.72096 | -5.1424 | -9.9149 | -12.1563 | -14.1944 | -15.1032 | 9.4463 | 5.1316 | 3.7334 | 3.1558 | 2.4686 | 9.7247 | 9.1475 | 6.8854 | 6.3495 | 5.779 | 1.3576 | -3.4149 | -5.6563 | -7.6944 | -8.7106 | 2.9463 | 0.077841 | -1.0178 | -1.5886 | -2.2673 | 5.0035 | 4.2874 | -0.72946 | -3.3685 | -4.4098 | -7.5567 | -10.4234 | -12.1546 | -13.1725 | -12.6598 | 9.4463 | 6.5778 | 5.4822 | 4.9114 | 4.2327 | 11.5035 | 10.7874 | 5.7705 | 3.1315 | 2.0902 | -1.0567 | -3.9234 | -5.6546 | -6.6725 | -6.2707 | 2.9463 | 0.98294 | 0.14836 | -0.29554 | -0.7562 | 6.7753 | 6.4389 | 4.3495 | 3.8819 | 3.3855 | 0.20115 | -1.5234 | -2.6893 | -3.9459 | -4.683 | 9.4463 | 7.4829 | 6.6484 | 6.2045 | 5.7438 | 13.2753 | 12.9389 | 10.8495 | 10.3819 | 9.8855 | 6.7011 | 4.9766 | 3.8107 | 2.5541 | 1.918 | 2.9463 | -1.6184 | -3.0978 | -3.7223 | -4.4547 | 2.7849 | 2.0256 | -3.0289 | -5.705 | -6.788 | -10.0893 | -13.0884 | -14.9712 | -16.2052 | -15.9823 | 9.4463 | 4.8816 | 3.4022 | 2.7777 | 2.0453 | 9.2849 | 8.5256 | 3.4711 | 0.79503 | -0.28804 | -3.5893 | -6.5884 | -8.4712 | -9.7052 | -9.5284 | 384007 | 395893 | LONGSIGHT | BREDBURY | Firm Capacity marginally exceeded in FY25. HV load transfer of ~8MVA to Southern Gateway primary.
| Mossley | 10.8566 | 10.6192 | 10.5261 | 10.4441 | 10.249 | 10.0409 | 9.8556 | 9.6828 | 9.4652 | 9.2747 | 7.1809 | 3.5273 | 0.49447 | -2.8512 | -5.7233 | 15.4936 | 15.2562 | 15.1631 | 15.0811 | 14.886 | 14.6779 | 14.4926 | 14.3198 | 14.1022 | 13.9117 | 11.8179 | 8.1643 | 5.1315 | 1.7858 | -1.2881 | 10.8566 | 10.6988 | 10.6065 | 10.4891 | 10.3013 | 10.0814 | 9.7837 | 9.3985 | 9.1024 | 8.803 | 7.8817 | 6.9054 | 5.8556 | 4.767 | 4.0468 | 15.4936 | 15.3358 | 15.2435 | 15.1261 | 14.9383 | 14.7184 | 14.4207 | 14.0355 | 13.7394 | 13.44 | 12.5187 | 11.5424 | 10.4926 | 9.404 | 8.8 | 10.8566 | 10.6223 | 10.5549 | 10.5182 | 10.3752 | 10.2288 | 10.1308 | 10.0516 | 9.9236 | 9.7774 | 7.8121 | 4.3091 | 1.3998 | -1.6341 | -4.1456 | 15.4936 | 15.2593 | 15.1919 | 15.1552 | 15.0122 | 14.8658 | 14.7678 | 14.6886 | 14.5606 | 14.4144 | 12.4491 | 8.9461 | 6.0368 | 3.0029 | 0.25113 | 10.8566 | 11.01 | 11.0503 | 11.0543 | 10.9169 | 10.7479 | 10.3802 | 9.2713 | 8.1088 | 6.9627 | 3.6268 | 0.36516 | -2.3297 | -4.1431 | -3.0353 | 15.4936 | 15.647 | 15.6873 | 15.6913 | 15.5539 | 15.3849 | 15.0172 | 13.9083 | 12.7458 | 11.5997 | 8.2638 | 5.0022 | 2.3073 | 0.49393 | 1.3572 | 10.8566 | 10.7302 | 10.7022 | 10.6997 | 10.653 | 10.5677 | 10.4443 | 10.3092 | 10.1009 | 9.9003 | 8.9672 | 7.6633 | 6.74 | 5.8812 | 5.3829 | 15.4936 | 15.3672 | 15.3392 | 15.3367 | 15.29 | 15.2047 | 15.0813 | 14.9462 | 14.7379 | 14.5373 | 13.6042 | 12.3003 | 11.377 | 10.5182 | 10.0588 | 10.8566 | 10.8852 | 10.8185 | 10.7146 | 10.4787 | 10.241 | 9.787 | 8.5617 | 7.3134 | 6.0807 | 2.4731 | -1.0339 | -3.9858 | -6.1446 | -5.4343 | 15.4936 | 15.5222 | 15.4555 | 15.3516 | 15.1157 | 14.878 | 14.424 | 13.1987 | 11.9504 | 10.7177 | 7.1101 | 3.6031 | 0.65123 | -1.5076 | -0.95436 | 397437 | 401979 | HARTSHEAD-HEYROD | STALYBRIDGE
| Mount St | 12.7243 | 7.8911 | 6.655 | 6.3055 | 5.8349 | 5.3409 | 4.8634 | 4.4155 | 3.9549 | 3.5126 | 1.2913 | -1.9082 | -4.2479 | -6.3181 | -7.8263 | 17.3612 | 12.528 | 11.2919 | 10.9425 | 10.4718 | 9.9779 | 9.5004 | 9.0525 | 8.5918 | 8.1495 | 5.9282 | 2.7287 | 0.38903 | -1.6812 | -3.343 | 12.7243 | 11.3412 | 10.9229 | 10.715 | 10.4405 | 10.1554 | 9.7913 | 9.3177 | 8.9326 | 8.5306 | 7.287 | 5.9968 | 4.8287 | 3.584 | 2.766 | 17.3612 | 15.9781 | 15.5598 | 15.3519 | 15.0774 | 14.7923 | 14.4282 | 13.9546 | 13.5696 | 13.1676 | 11.9239 | 10.6338 | 9.4657 | 8.2209 | 7.5294 | 12.7243 | 7.0621 | 5.5907 | 5.1606 | 4.6099 | 4.0372 | 3.4939 | 2.3688 | 1.2221 | 0.06917 | -3.6748 | -6.8686 | -8.9737 | -10.5857 | -11.2886 | 17.3612 | 11.699 | 10.2276 | 9.7976 | 9.2468 | 8.6741 | 8.1308 | 7.0057 | 5.859 | 4.7061 | 0.9621 | -2.2316 | -4.3368 | -5.9488 | -6.7947 | 12.7243 | 8.8451 | 7.7704 | 7.388 | 6.8532 | 6.2626 | 5.534 | 3.7296 | 1.9295 | 0.1689 | -4.2652 | -6.9563 | -8.5531 | -9.184 | -8.5107 | 17.3612 | 13.4821 | 12.4073 | 12.0249 | 11.4902 | 10.8996 | 10.171 | 8.3666 | 6.5665 | 4.8058 | 0.37171 | -2.3194 | -3.9161 | -4.5471 | -4.0249 | 12.7243 | 10.1108 | 9.3703 | 9.1172 | 8.8216 | 8.4969 | 8.1462 | 7.7649 | 7.3095 | 6.8382 | 5.2732 | 3.5968 | 2.3028 | 1.1302 | 0.41396 | 17.3612 | 14.7477 | 14.0073 | 13.7541 | 13.4585 | 13.1338 | 12.7831 | 12.4018 | 11.9464 | 11.4751 | 9.9101 | 8.2337 | 6.9398 | 5.7671 | 5.1402 | 12.7243 | 6.5275 | 4.9045 | 4.4218 | 3.7995 | 3.1576 | 2.3669 | 0.4709 | -1.395 | -3.2251 | -7.9065 | -10.8402 | -12.6728 | -13.5718 | -13.1971 | 17.3612 | 11.1645 | 9.5414 | 9.0588 | 8.4365 | 7.7945 | 7.0038 | 5.1078 | 3.2419 | 1.4119 | -3.2696 | -6.2033 | -8.0359 | -8.9349 | -8.648 | 376250 | 397574 | BARTON | CARRINGTON
| Musgrave Rd | 9.4086 | 8.9977 | 8.8284 | 8.726 | 8.5307 | 8.3204 | 8.1366 | 7.969 | 7.7388 | 7.5188 | 5.6589 | 2.2588 | -0.5904 | -3.5523 | -6.0269 | 15.0286 | 14.6177 | 14.4484 | 14.346 | 14.1507 | 13.9404 | 13.7566 | 13.589 | 13.3588 | 13.1388 | 11.2789 | 7.8788 | 5.0296 | 2.0677 | -0.63155 | 9.4086 | 9.2811 | 9.1711 | 9.0646 | 8.9187 | 8.7604 | 8.5453 | 8.2624 | 8.0044 | 7.7346 | 6.8972 | 6.0156 | 5.1371 | 4.1767 | 3.5491 | 15.0286 | 14.9011 | 14.7911 | 14.6846 | 14.5387 | 14.3804 | 14.1653 | 13.8824 | 13.6244 | 13.3546 | 12.5172 | 11.6356 | 10.7571 | 9.7967 | 9.2643 | 9.4086 | 8.9652 | 8.8088 | 8.7479 | 8.5948 | 8.4342 | 8.3221 | 8.2333 | 8.1073 | 7.9716 | 6.3391 | 3.1009 | 0.39109 | -2.4156 | -4.6972 | 15.0286 | 14.5852 | 14.4288 | 14.3679 | 14.2148 | 14.0542 | 13.9421 | 13.8533 | 13.7273 | 13.5916 | 11.9591 | 8.7209 | 6.0111 | 3.2044 | 0.65484 | 9.4086 | 9.3221 | 9.266 | 9.2362 | 9.0862 | 8.8997 | 8.5323 | 7.4845 | 6.3855 | 5.2802 | 2.0868 | -0.96639 | -3.4455 | -4.9773 | -3.7269 | 15.0286 | 14.9421 | 14.886 | 14.8562 | 14.7062 | 14.5197 | 14.1523 | 13.1045 | 12.0055 | 10.9002 | 7.7068 | 4.6536 | 2.1745 | 0.64273 | 1.6206 | 9.4086 | 9.2803 | 9.2059 | 9.1798 | 9.1344 | 9.062 | 8.9649 | 8.8427 | 8.6217 | 8.3876 | 7.5355 | 6.506 | 5.7074 | 5.0425 | 4.8214 | 15.0286 | 14.9003 | 14.8259 | 14.7998 | 14.7544 | 14.682 | 14.5849 | 14.4627 | 14.2417 | 14.0076 | 13.1555 | 12.126 | 11.3274 | 10.6625 | 10.4293 | 9.4086 | 9.1027 | 8.9351 | 8.8182 | 8.5918 | 8.3591 | 7.9367 | 6.8101 | 5.6575 | 4.4974 | 1.1037 | -2.147 | -4.8506 | -6.6946 | -5.7982 | 15.0286 | 14.7227 | 14.5551 | 14.4382 | 14.2118 | 13.9791 | 13.5567 | 12.4301 | 11.2775 | 10.1174 | 6.7237 | 3.473 | 0.76941 | -1.0746 | -0.37209 | 370045 | 409863 | BOLTON | KEARSLEY
| Nelson | 6.1116 | 4.097 | 3.5332 | 3.3467 | 3.1362 | 2.8307 | 2.6712 | 2.4853 | 2.2685 | 2.0628 | 0.80263 | -1.6703 | -4.4448 | -7.3359 | -9.5667 | 10.7516 | 8.737 | 8.1732 | 7.9867 | 7.7762 | 7.4707 | 7.3112 | 7.1253 | 6.9085 | 6.7028 | 5.4426 | 2.9697 | 0.19525 | -2.6959 | -5.1916 | 6.1116 | 5.506 | 5.1472 | 4.8805 | 4.5885 | 4.2082 | 3.7948 | 3.2969 | 3.0824 | 2.865 | 2.2015 | 1.5385 | 0.95783 | 0.39229 | 0.050504 | 10.7516 | 10.146 | 9.7872 | 9.5205 | 9.2285 | 8.8482 | 8.4348 | 7.9369 | 7.7224 | 7.505 | 6.8415 | 6.1785 | 5.5978 | 5.0323 | 4.725 | 6.1116 | 3.7737 | 3.155 | 2.9683 | 2.7611 | 2.4614 | 2.3081 | 2.1342 | 1.9759 | 1.8335 | 0.74377 | -1.5337 | -4.1475 | -6.7934 | -8.6898 | 10.7516 | 8.4137 | 7.795 | 7.6083 | 7.4011 | 7.1014 | 6.9481 | 6.7742 | 6.6159 | 6.4735 | 5.3838 | 3.1063 | 0.49251 | -2.1534 | -4.3745 | 6.1116 | 4.6557 | 4.2637 | 4.1725 | 4.0485 | 3.8065 | 3.5783 | 2.9556 | 2.226 | 1.2923 | -1.8488 | -4.7887 | -7.1426 | -8.5188 | -7.0411 | 10.7516 | 9.2957 | 8.9037 | 8.8125 | 8.6885 | 8.4465 | 8.2183 | 7.5956 | 6.866 | 5.9323 | 2.7912 | -0.14874 | -2.5026 | -3.8788 | -2.733 | 6.1116 | 5.1775 | 4.8346 | 4.7083 | 4.5961 | 4.3647 | 4.2319 | 4.064 | 3.8562 | 3.6438 | 2.919 | 2.1598 | 1.6693 | 1.3096 | 1.4097 | 10.7516 | 9.8175 | 9.4746 | 9.3483 | 9.2361 | 9.0047 | 8.8719 | 8.704 | 8.4962 | 8.2838 | 7.559 | 6.7998 | 6.3093 | 5.9496 | 5.9809 | 6.1116 | 3.6193 | 2.9624 | 2.7605 | 2.5326 | 2.2196 | 1.9262 | 1.2032 | 0.49817 | -0.23967 | -3.5041 | -6.572 | -9.0931 | -10.7092 | -9.53 | 10.7516 | 8.2593 | 7.6024 | 7.4005 | 7.1726 | 6.8596 | 6.5662 | 5.8432 | 5.1382 | 4.4003 | 1.1359 | -1.932 | -4.4531 | -6.0692 | -5.1522 | 386020 | 438507 | NELSON | PADIHAM
| New Moston | 11.869 | 11.5619 | 11.3682 | 11.1824 | 10.8748 | 10.4571 | 10.0574 | 9.6888 | 9.3187 | 8.9766 | 7.2205 | 4.6529 | 2.7561 | 1.1614 | 0.033233 | 16.506 | 16.1989 | 16.0052 | 15.8194 | 15.5118 | 15.0941 | 14.6944 | 14.3258 | 13.9557 | 13.6136 | 11.8575 | 9.2899 | 7.3931 | 5.7984 | 4.5024 | 11.869 | 11.7 | 11.5614 | 11.416 | 11.2167 | 10.9845 | 10.6875 | 10.3247 | 10.0816 | 9.7949 | 8.956 | 8.0766 | 7.2498 | 6.4249 | 5.8948 | 16.506 | 16.337 | 16.1984 | 16.053 | 15.8537 | 15.6215 | 15.3245 | 14.9617 | 14.7186 | 14.4319 | 13.593 | 12.7136 | 11.8868 | 11.0619 | 10.6144 | 11.869 | 11.46 | 11.1924 | 10.9387 | 10.5078 | 9.9748 | 9.4721 | 8.987 | 8.5064 | 8.0315 | 5.9958 | 3.4525 | 1.7926 | 0.62623 | 0.27801 | 16.506 | 16.097 | 15.8294 | 15.5757 | 15.1448 | 14.6118 | 14.1091 | 13.624 | 13.1434 | 12.6685 | 10.6328 | 8.0895 | 6.4296 | 5.2632 | 4.7373 | 11.869 | 11.7929 | 11.609 | 11.3667 | 10.9472 | 10.4707 | 9.8159 | 8.8122 | 7.8265 | 6.873 | 4.2909 | 2.1468 | 0.89845 | 0.54367 | 1.3694 | 16.506 | 16.4299 | 16.246 | 16.0037 | 15.5842 | 15.1077 | 14.4529 | 13.4492 | 12.4635 | 11.51 | 8.9279 | 6.7838 | 5.5354 | 5.1807 | 5.8211 | 11.869 | 11.6357 | 11.4897 | 11.3886 | 11.2586 | 11.0955 | 10.7995 | 10.4923 | 10.1367 | 9.7785 | 8.5858 | 7.3491 | 6.5065 | 5.7437 | 5.3553 | 16.506 | 16.2727 | 16.1267 | 16.0256 | 15.8956 | 15.7325 | 15.4365 | 15.1293 | 14.7737 | 14.4155 | 13.2228 | 11.9861 | 11.1435 | 10.3807 | 10.0131 | 11.869 | 11.6743 | 11.4004 | 11.0715 | 10.5426 | 9.9354 | 9.2257 | 8.1228 | 7.0546 | 6.022 | 3.2234 | 0.93985 | -0.43783 | -0.9288 | -0.29131 | 16.506 | 16.3113 | 16.0374 | 15.7085 | 15.1796 | 14.5724 | 13.8627 | 12.7598 | 11.6916 | 10.659 | 7.8604 | 5.5768 | 4.1992 | 3.7082 | 4.2057 | 388333 | 402657 | CHADDERTON | WHITEGATE
| Newbiggin on Lune | 0.55568 | 0.53843 | 0.50729 | 0.47547 | 0.43589 | 0.39535 | 0.35962 | 0.32581 | 0.28915 | 0.25759 | 0.11958 | -0.083039 | -0.24862 | -0.36616 | -0.45036 | 2.0557 | 2.0384 | 2.0073 | 1.9755 | 1.9359 | 1.8954 | 1.8596 | 1.8258 | 1.7892 | 1.7576 | 1.6196 | 1.417 | 1.2514 | 1.1338 | 1.0462 | 0.55568 | 0.53419 | 0.50123 | 0.46379 | 0.41994 | 0.37561 | 0.3241 | 0.26528 | 0.22424 | 0.18307 | 0.065583 | -0.03266 | -0.12259 | -0.22874 | -0.31648 | 2.0557 | 2.0342 | 2.0012 | 1.9638 | 1.9199 | 1.8756 | 1.8241 | 1.7653 | 1.7242 | 1.6831 | 1.5656 | 1.4673 | 1.3774 | 1.2713 | 1.198 | 0.55568 | 0.54093 | 0.51251 | 0.48585 | 0.45169 | 0.41769 | 0.39024 | 0.36666 | 0.3209 | 0.25198 | 0.036083 | -0.18917 | -0.3661 | -0.48915 | -0.57187 | 2.0557 | 2.0409 | 2.0125 | 1.9858 | 1.9517 | 1.9177 | 1.8902 | 1.8667 | 1.8209 | 1.752 | 1.5361 | 1.3108 | 1.1339 | 1.0108 | 0.92417 | 0.55568 | 0.55194 | 0.53169 | 0.50333 | 0.4733 | 0.43923 | 0.40231 | 0.34801 | 0.28688 | 0.22548 | 0.050681 | -0.15386 | -0.31741 | -0.41498 | -0.40482 | 2.0557 | 2.0519 | 2.0317 | 2.0033 | 1.9733 | 1.9392 | 1.9023 | 1.848 | 1.7869 | 1.7255 | 1.5507 | 1.3461 | 1.1826 | 1.085 | 1.0886 | 0.55568 | 0.54083 | 0.51391 | 0.48787 | 0.46106 | 0.43435 | 0.4084 | 0.38404 | 0.35291 | 0.32289 | 0.21411 | 0.047676 | -0.096772 | -0.21993 | -0.28521 | 2.0557 | 2.0408 | 2.0139 | 1.9879 | 1.9611 | 1.9344 | 1.9084 | 1.884 | 1.8529 | 1.8229 | 1.7141 | 1.5477 | 1.4032 | 1.2801 | 1.2157 | 0.55568 | 0.54193 | 0.50784 | 0.46319 | 0.41791 | 0.37371 | 0.32627 | 0.25507 | 0.18189 | 0.10918 | -0.094941 | -0.27794 | -0.39814 | -0.4413 | -0.41551 | 2.0557 | 2.0419 | 2.0078 | 1.9632 | 1.9179 | 1.8737 | 1.8263 | 1.7551 | 1.6819 | 1.6092 | 1.4051 | 1.2221 | 1.1019 | 1.0587 | 1.0798 | 369770 | 505803 | PENRITH & SHAP | HUTTON
| Newby | 1.7131 | 1.4174 | 1.3149 | 1.2612 | 1.1038 | 0.93548 | 0.788 | 0.65593 | 0.53493 | 0.43421 | -0.15582 | -1.1119 | -1.8927 | -2.5718 | -3.296 | 8.7131 | 8.4174 | 8.3149 | 8.2612 | 8.1038 | 7.9355 | 7.788 | 7.6559 | 7.5349 | 7.4342 | 6.8442 | 5.8881 | 5.1073 | 4.4282 | 3.6416 | 1.7131 | 1.594 | 1.4769 | 1.3578 | 1.22 | 1.1068 | 0.9659 | 0.78636 | 0.69464 | 0.60387 | 0.33685 | 0.079095 | -0.22698 | -0.70606 | -1.1947 | 8.7131 | 8.594 | 8.4769 | 8.3578 | 8.22 | 8.1068 | 7.9659 | 7.7864 | 7.6946 | 7.6039 | 7.3368 | 7.0791 | 6.773 | 6.2939 | 5.8918 | 1.7131 | 1.3858 | 1.2841 | 1.2447 | 1.1012 | 0.94911 | 0.82592 | 0.7195 | 0.63669 | 0.56604 | 0.066922 | -0.81219 | -1.5234 | -2.1148 | -2.7341 | 8.7131 | 8.3858 | 8.2841 | 8.2447 | 8.1012 | 7.9491 | 7.8259 | 7.7195 | 7.6367 | 7.566 | 7.0669 | 6.1878 | 5.4766 | 4.8852 | 4.1847 | 1.7131 | 1.5573 | 1.4853 | 1.3978 | 1.244 | 1.0881 | 0.90642 | 0.57645 | 0.23107 | -0.11498 | -1.074 | -1.9076 | -2.49 | -2.7016 | -2.3274 | 8.7131 | 8.5573 | 8.4853 | 8.3978 | 8.244 | 8.0881 | 7.9064 | 7.5764 | 7.2311 | 6.885 | 5.926 | 5.0924 | 4.51 | 4.2984 | 4.5898 | 1.7131 | 1.6013 | 1.5252 | 1.4663 | 1.3551 | 1.2696 | 1.1904 | 1.0971 | 0.98278 | 0.87043 | 0.44868 | -0.047609 | -0.37311 | -0.73258 | -0.97743 | 8.7131 | 8.6013 | 8.5252 | 8.4663 | 8.3551 | 8.2696 | 8.1904 | 8.0971 | 7.9828 | 7.8704 | 7.4487 | 6.9524 | 6.6269 | 6.2674 | 5.9953 | 1.7131 | 1.4138 | 1.2894 | 1.1662 | 0.97732 | 0.79159 | 0.5744 | 0.20194 | -0.16305 | -0.52912 | -1.5541 | -2.4469 | -3.0865 | -3.3655 | -3.0658 | 8.7131 | 8.4138 | 8.2894 | 8.1662 | 7.9773 | 7.7916 | 7.5744 | 7.2019 | 6.837 | 6.4709 | 5.4459 | 4.5531 | 3.9135 | 3.6345 | 3.8677 | 360520 | 521151 | PENRITH & SHAP | HUTTON
| Newton | 10.7838 | 10.7595 | 10.7011 | 10.6503 | 10.5428 | 10.4187 | 10.2932 | 10.1747 | 10.0208 | 9.8746 | 9.1434 | 8.0211 | 7.0839 | 6.2238 | 5.4913 | 16.5418 | 16.5175 | 16.4591 | 16.4083 | 16.3008 | 16.1767 | 16.0512 | 15.9327 | 15.7788 | 15.6326 | 14.9014 | 13.7791 | 12.8419 | 11.9818 | 11.2204 | 10.7838 | 10.7619 | 10.7163 | 10.6792 | 10.5884 | 10.489 | 10.3606 | 10.1962 | 10.0189 | 9.8399 | 9.2972 | 8.7377 | 8.1882 | 7.7005 | 7.4009 | 16.5418 | 16.5199 | 16.4743 | 16.4372 | 16.3464 | 16.247 | 16.1186 | 15.9542 | 15.7769 | 15.5979 | 15.0552 | 14.4957 | 13.9462 | 13.4585 | 13.2085 | 10.7838 | 10.7587 | 10.7002 | 10.6487 | 10.5414 | 10.4308 | 10.3181 | 10.2012 | 10.0757 | 9.9518 | 9.3722 | 8.2592 | 7.366 | 6.5846 | 5.9832 | 16.5418 | 16.5167 | 16.4582 | 16.4067 | 16.2994 | 16.1888 | 16.0761 | 15.9592 | 15.8337 | 15.7098 | 15.1302 | 14.0172 | 13.124 | 12.3426 | 11.7502 | 10.7838 | 10.8097 | 10.7776 | 10.7479 | 10.6568 | 10.5497 | 10.3917 | 10.1177 | 9.7912 | 9.4527 | 8.4619 | 7.4755 | 6.6763 | 6.2196 | 6.4462 | 16.5418 | 16.5677 | 16.5356 | 16.5059 | 16.4148 | 16.3077 | 16.1497 | 15.8757 | 15.5492 | 15.2107 | 14.2199 | 13.2335 | 12.4343 | 11.9776 | 12.1522 | 10.7838 | 10.7663 | 10.7218 | 10.6938 | 10.6177 | 10.5267 | 10.4236 | 10.3166 | 10.183 | 10.0501 | 9.579 | 9.0299 | 8.611 | 8.2623 | 7.9932 | 16.5418 | 16.5243 | 16.4798 | 16.4518 | 16.3757 | 16.2847 | 16.1816 | 16.0746 | 15.941 | 15.8081 | 15.337 | 14.7879 | 14.369 | 14.0203 | 13.7835 | 10.7838 | 10.7941 | 10.7391 | 10.683 | 10.5693 | 10.4499 | 10.2665 | 9.9255 | 9.5634 | 9.1989 | 8.1124 | 7.0456 | 6.1748 | 5.6407 | 5.7852 | 16.5418 | 16.5521 | 16.4971 | 16.441 | 16.3273 | 16.2079 | 16.0245 | 15.6835 | 15.3214 | 14.9569 | 13.8704 | 12.8036 | 11.9328 | 11.3987 | 11.5091 | 396385 | 396464 | HYDE | STALYBRIDGE
| Newton Heath | 2.2034 | 1.2514 | 1.0917 | 0.85408 | 0.5201 | 0.29059 | 0.072704 | -0.11295 | -0.28732 | -0.44807 | -1.6399 | -3.6306 | -5.1754 | -6.5819 | -7.6276 | 2.2034 | 1.2514 | 1.0917 | 0.85408 | 0.5201 | 0.29059 | 0.072704 | -0.11295 | -0.28732 | -0.44807 | -1.6399 | -3.6306 | -5.1754 | -6.5819 | -7.7731 | 2.2034 | 1.7483 | 1.7825 | 1.6735 | 1.5275 | 1.4095 | 1.25 | 1.0477 | 0.91164 | 0.76611 | 0.32142 | -0.15409 | -0.65484 | -1.1852 | -1.5738 | 2.2034 | 1.7483 | 1.7825 | 1.6735 | 1.5275 | 1.4095 | 1.25 | 1.0477 | 0.91164 | 0.76611 | 0.32142 | -0.15409 | -0.65484 | -1.1852 | -1.5111 | 2.2034 | 1.0983 | 0.85342 | 0.54603 | 0.14016 | -0.16365 | -0.44963 | -0.71602 | -0.97403 | -1.231 | -2.7329 | -4.668 | -5.9875 | -7.009 | -7.4419 | 2.2034 | 1.0983 | 0.85342 | 0.54603 | 0.14016 | -0.16365 | -0.44963 | -0.71602 | -0.97403 | -1.231 | -2.7329 | -4.668 | -5.9875 | -7.009 | -7.5444 | 2.2034 | 1.4936 | 1.3353 | 1.0322 | 0.6152 | 0.29184 | -0.13013 | -0.90035 | -1.6485 | -2.3656 | -4.3468 | -5.9495 | -6.9029 | -7.1438 | -6.5231 | 2.2034 | 1.4936 | 1.3353 | 1.0322 | 0.6152 | 0.29184 | -0.13013 | -0.90035 | -1.6485 | -2.3656 | -4.3468 | -5.9495 | -6.9029 | -7.1438 | -6.6306 | 2.2034 | 1.4792 | 1.3853 | 1.2025 | 0.99016 | 0.88159 | 0.74747 | 0.59083 | 0.40636 | 0.21621 | -0.50896 | -1.3405 | -1.9302 | -2.4985 | -2.8387 | 2.2034 | 1.4792 | 1.3853 | 1.2025 | 0.99016 | 0.88159 | 0.74747 | 0.59083 | 0.40636 | 0.21621 | -0.50896 | -1.3405 | -1.9302 | -2.4985 | -2.8096 | 2.2034 | 1.1988 | 0.94084 | 0.58506 | 0.11918 | -0.23887 | -0.7062 | -1.5335 | -2.3217 | -3.08 | -5.193 | -6.904 | -7.9642 | -8.3345 | -7.7946 | 2.2034 | 1.1988 | 0.94084 | 0.58506 | 0.11918 | -0.23887 | -0.7062 | -1.5335 | -2.3217 | -3.08 | -5.193 | -6.904 | -7.9642 | -8.3345 | -7.8875 | 388030 | 400511 | CHADDERTON | WHITEGATE
| Newton Le Willows | 9.5612 | 8.7717 | 8.3791 | 8.0794 | 7.6399 | 7.1746 | 6.7239 | 6.2852 | 5.7238 | 5.1284 | 2.2917 | -1.8754 | -5.1488 | -8.432 | -11.6011 | 13.6982 | 12.9087 | 12.5161 | 12.2164 | 11.7769 | 11.3116 | 10.8609 | 10.4222 | 9.8608 | 9.2654 | 6.4287 | 2.2616 | -1.0118 | -4.295 | -7.5356 | 9.5612 | 9.2908 | 9.083 | 8.8774 | 8.6111 | 8.3209 | 7.9245 | 7.3459 | 6.8271 | 6.2929 | 4.4618 | 2.4993 | 0.61827 | -1.4136 | -2.711 | 13.6982 | 13.4278 | 13.22 | 13.0144 | 12.7481 | 12.4579 | 12.0615 | 11.4829 | 10.9641 | 10.4299 | 8.5988 | 6.6363 | 4.7553 | 2.7234 | 1.6344 | 9.5612 | 8.7026 | 8.3216 | 8.0725 | 7.6899 | 7.2945 | 6.9449 | 6.6205 | 6.2006 | 5.7215 | 3.1628 | -0.86541 | -4.0383 | -7.1063 | -9.9992 | 13.6982 | 12.8396 | 12.4586 | 12.2095 | 11.8269 | 11.4315 | 11.0819 | 10.7575 | 10.3376 | 9.8585 | 7.2998 | 3.2716 | 0.098689 | -2.9693 | -5.9817 | 9.5612 | 9.2077 | 8.9678 | 8.7705 | 8.4033 | 7.9854 | 7.3927 | 6.1511 | 4.8298 | 3.4967 | -0.40423 | -4.2112 | -7.162 | -9.1327 | -8.6061 | 13.6982 | 13.3447 | 13.1048 | 12.9075 | 12.5403 | 12.1224 | 11.5297 | 10.2881 | 8.9668 | 7.6337 | 3.7328 | -0.074243 | -3.025 | -4.9957 | -4.599 | 9.5612 | 9.2397 | 8.9845 | 8.7856 | 8.5463 | 8.262 | 7.9454 | 7.5946 | 7.1045 | 6.5248 | 4.591 | 2.4965 | 1.0768 | -0.14128 | -0.85817 | 13.6982 | 13.3767 | 13.1215 | 12.9226 | 12.6833 | 12.399 | 12.0824 | 11.7316 | 11.2415 | 10.6618 | 8.728 | 6.6335 | 5.2138 | 3.9957 | 3.3575 | 9.5612 | 8.8622 | 8.4669 | 8.1583 | 7.6925 | 7.2148 | 6.5529 | 5.2148 | 3.832 | 2.4364 | -1.7135 | -5.8058 | -9.0445 | -11.3253 | -11.1176 | 13.6982 | 12.9992 | 12.6039 | 12.2953 | 11.8295 | 11.3518 | 10.6899 | 9.3518 | 7.969 | 6.5734 | 2.4235 | -1.6688 | -4.9075 | -7.1883 | -7.0405 | 357891 | 395944 | GOLBORNE | BOLD
| Newtongate T11 & T12 | 4.9378 | 2.6564 | 2.0724 | 1.7891 | 1.4108 | 0.94277 | 0.39447 | -0.28484 | -1.1553 | -2.6242 | -12.4459 | -17.6984 | -24.5953 | -27.3599 | -28.8294 | 8.9378 | 6.6564 | 6.0724 | 5.7891 | 5.4108 | 4.9428 | 4.3945 | 3.7152 | 2.8447 | 1.3758 | -8.4459 | -13.6984 | -20.5953 | -23.3599 | -25.0053 | 4.9378 | 4.1807 | 3.8862 | 3.6439 | 3.3883 | 3.1141 | 2.7675 | 2.3249 | 1.8194 | 1.2712 | -1.0527 | -4.4878 | -8.1042 | -15.6495 | -21.5465 | 8.9378 | 8.1807 | 7.8862 | 7.6439 | 7.3883 | 7.1141 | 6.7675 | 6.3249 | 5.8194 | 5.2712 | 2.9473 | -0.48777 | -4.1042 | -11.6495 | -17.2886 | 4.9378 | 2.3182 | 1.6811 | 1.4102 | 1.059 | 0.63724 | 0.16049 | -0.41524 | -1.1076 | -1.9336 | -14.8905 | -24.118 | -27.887 | -30.7443 | -31.6799 | 8.9378 | 6.3182 | 5.6811 | 5.4102 | 5.059 | 4.6372 | 4.1605 | 3.5848 | 2.8924 | 2.0664 | -10.8905 | -20.118 | -23.887 | -26.7443 | -27.9615 | 4.9378 | 3.1903 | 2.7466 | 2.4792 | 2.1347 | 1.6701 | 0.98794 | -1.0869 | -14.3265 | -15.8098 | -21.1257 | -25.9273 | -28.8935 | -30.5984 | -29.4161 | 8.9378 | 7.1903 | 6.7466 | 6.4792 | 6.1347 | 5.6701 | 4.9879 | 2.9131 | -10.3265 | -11.8098 | -17.1257 | -21.9273 | -24.8935 | -26.5984 | -25.7132 | 4.9378 | 3.696 | 3.3303 | 3.123 | 2.8948 | 2.5908 | 2.1866 | 1.6673 | 0.94761 | -0.065029 | -8.9732 | -13.2179 | -19.3577 | -21.2328 | -21.3528 | 8.9378 | 7.696 | 7.3303 | 7.123 | 6.8948 | 6.5908 | 6.1866 | 5.6673 | 4.9476 | 3.935 | -4.9732 | -9.2179 | -15.3577 | -17.2328 | -17.4632 | 4.9378 | 2.1231 | 1.426 | 1.0765 | 0.67332 | 0.21485 | -0.42639 | -2.4739 | -15.6337 | -16.4959 | -21.7413 | -27.1476 | -30.7826 | -32.9222 | -31.9152 | 8.9378 | 6.1231 | 5.426 | 5.0765 | 4.6733 | 4.2149 | 3.5736 | 1.5261 | -11.6337 | -12.4959 | -17.7413 | -23.1476 | -26.7826 | -28.9222 | -28.178 | 349973 | 530340 | PENRITH & SHAP | HUTTON
| Newtongate T13 | 6.053 | 3.7885 | 3.0625 | 2.7158 | 2.3101 | 2.1051 | 1.8924 | 1.6563 | 1.392 | 1.123 | -0.17388 | -1.9998 | -3.3778 | -4.7126 | -5.8682 | 10.803 | 8.5385 | 7.8125 | 7.4658 | 7.0601 | 6.8551 | 6.6424 | 6.4063 | 6.142 | 5.873 | 4.5761 | 2.7502 | 1.3722 | 0.037384 | -1.1805 | 6.053 | 5.6339 | 5.3507 | 5.1222 | 4.8722 | 4.6706 | 4.421 | 4.1019 | 3.9609 | 3.8166 | 3.2123 | 2.4038 | 1.6236 | 0.7979 | 0.29696 | 10.803 | 10.3839 | 10.1007 | 9.8722 | 9.6222 | 9.4206 | 9.171 | 8.8519 | 8.7109 | 8.5666 | 7.9623 | 7.1538 | 6.3736 | 5.5479 | 5.1154 | 6.053 | 3.4309 | 2.66 | 2.3364 | 1.9504 | 1.7709 | 1.5993 | 1.409 | 1.214 | 1.0009 | -0.19345 | -2.0193 | -3.406 | -4.6984 | -5.7468 | 10.803 | 8.1809 | 7.41 | 7.0864 | 6.7004 | 6.5209 | 6.3493 | 6.159 | 5.964 | 5.7509 | 4.5566 | 2.7307 | 1.344 | 0.05157 | -1.0794 | 6.053 | 4.2867 | 3.6828 | 3.3673 | 2.9835 | 2.7973 | 2.5254 | 1.9551 | 1.3505 | 0.72878 | -1.0952 | -2.7748 | -3.9842 | -4.7019 | -4.3359 | 10.803 | 9.0367 | 8.4328 | 8.1173 | 7.7335 | 7.5473 | 7.2754 | 6.7051 | 6.1005 | 5.4788 | 3.6548 | 1.9752 | 0.76581 | 0.048062 | 0.3258 | 6.053 | 5.3705 | 4.9298 | 4.6134 | 4.2787 | 4.1534 | 4.0115 | 3.8281 | 3.591 | 3.3381 | 2.4549 | 1.5421 | 0.96613 | 0.5344 | 0.38608 | 10.803 | 10.1205 | 9.6798 | 9.3634 | 9.0287 | 8.9034 | 8.7615 | 8.5781 | 8.341 | 8.0881 | 7.2049 | 6.2921 | 5.7161 | 5.2844 | 5.1314 | 6.053 | 3.1775 | 2.3525 | 2.011 | 1.5984 | 1.3958 | 1.1078 | 0.52136 | -0.071205 | -0.6853 | -2.5617 | -4.3662 | -5.7126 | -6.5607 | -6.3043 | 10.803 | 7.9275 | 7.1025 | 6.761 | 6.3484 | 6.1458 | 5.8578 | 5.2714 | 4.6788 | 4.0647 | 2.1883 | 0.38376 | -0.96261 | -1.8107 | -1.6198 | 349973 | 530340 | PENRITH & SHAP | HUTTON
| Norbreck | 18.6317 | 18.6 | 18.5261 | 18.4655 | 18.4063 | 18.3549 | 18.3176 | 18.2833 | 18.2044 | 18.1345 | 17.5265 | 16.3815 | 15.4002 | 14.2951 | 13.348 | 23.2687 | 23.237 | 23.1631 | 23.1025 | 23.0433 | 22.9919 | 22.9546 | 22.9203 | 22.8414 | 22.7715 | 22.1635 | 21.0185 | 20.0372 | 18.9321 | 17.923 | 18.6317 | 18.6059 | 18.5526 | 18.5065 | 18.4545 | 18.3985 | 18.3296 | 18.248 | 18.1366 | 18.024 | 17.6976 | 17.4034 | 17.1047 | 16.7811 | 16.5417 | 23.2687 | 23.2429 | 23.1896 | 23.1435 | 23.0915 | 23.0355 | 22.9666 | 22.885 | 22.7736 | 22.661 | 22.3346 | 22.0404 | 21.7417 | 21.4181 | 21.2161 | 18.6317 | 18.6108 | 18.5487 | 18.5091 | 18.4709 | 18.4434 | 18.4366 | 18.4385 | 18.4084 | 18.376 | 17.7613 | 16.6165 | 15.7045 | 14.782 | 14.0529 | 23.2687 | 23.2478 | 23.1857 | 23.1461 | 23.1079 | 23.0804 | 23.0736 | 23.0755 | 23.0454 | 23.013 | 22.3983 | 21.2535 | 20.3415 | 19.419 | 18.6849 | 18.6317 | 18.6519 | 18.6096 | 18.5629 | 18.5084 | 18.4482 | 18.3312 | 18.0032 | 17.6456 | 17.2846 | 16.2426 | 15.2491 | 14.4409 | 13.9095 | 14.3119 | 23.2687 | 23.2889 | 23.2466 | 23.1999 | 23.1454 | 23.0852 | 22.9682 | 22.6402 | 22.2826 | 21.9216 | 20.8796 | 19.8861 | 19.0779 | 18.5465 | 18.8609 | 18.6317 | 18.611 | 18.5584 | 18.5278 | 18.5067 | 18.4753 | 18.4465 | 18.4245 | 18.3539 | 18.2855 | 18.0373 | 17.6467 | 17.3542 | 17.0011 | 16.7516 | 23.2687 | 23.248 | 23.1954 | 23.1648 | 23.1437 | 23.1123 | 23.0835 | 23.0615 | 22.9909 | 22.9225 | 22.6743 | 22.2837 | 21.9912 | 21.6381 | 21.4097 | 18.6317 | 18.6277 | 18.5501 | 18.4634 | 18.3736 | 18.2923 | 18.1519 | 17.7848 | 17.3934 | 17.0001 | 15.8696 | 14.8026 | 13.929 | 13.3237 | 13.6453 | 23.2687 | 23.2647 | 23.1871 | 23.1004 | 23.0106 | 22.9293 | 22.7889 | 22.4218 | 22.0304 | 21.6371 | 20.5066 | 19.4396 | 18.566 | 17.9607 | 18.212 | 331831 | 441463 | BISPHAM | PENWORTHAM
| Norbury | 12.7484 | 12.4085 | 12.1903 | 12.0417 | 11.8857 | 11.7358 | 11.5956 | 11.3474 | 11.1128 | 10.8959 | 9.5438 | 6.6068 | 4.4587 | 2.6127 | 0.96959 | 17.3854 | 17.0455 | 16.8273 | 16.6787 | 16.5227 | 16.3728 | 16.2326 | 15.9844 | 15.7498 | 15.5329 | 14.1808 | 11.2438 | 9.0957 | 7.2497 | 5.574 | 12.7484 | 12.5817 | 12.4336 | 12.2994 | 12.1302 | 11.9305 | 11.6818 | 11.2752 | 10.9709 | 10.6613 | 9.7318 | 8.8257 | 7.5115 | 6.4706 | 5.8067 | 17.3854 | 17.2187 | 17.0706 | 16.9364 | 16.7672 | 16.5675 | 16.3188 | 15.9122 | 15.6079 | 15.2983 | 14.3688 | 13.4627 | 12.1485 | 11.1076 | 10.5462 | 12.7484 | 12.3952 | 12.1997 | 12.1021 | 11.9997 | 11.9117 | 11.8519 | 11.6995 | 11.5279 | 11.2095 | 5.8702 | 3.5189 | 1.6063 | -0.41327 | -2.1163 | 17.3854 | 17.0322 | 16.8367 | 16.7391 | 16.6367 | 16.5487 | 16.4889 | 16.3365 | 16.1649 | 15.8465 | 10.5072 | 8.1559 | 6.2433 | 4.2237 | 2.5932 | 12.7484 | 12.6464 | 12.5408 | 12.3549 | 8.0176 | 8.1073 | 8.0836 | 7.7509 | 7.2834 | 6.7916 | 5.0898 | 3.2615 | 1.6366 | -0.036054 | -0.4317 | 17.3854 | 17.2834 | 17.1778 | 16.9919 | 12.6546 | 12.7443 | 12.7206 | 12.3879 | 11.9204 | 11.4286 | 9.7268 | 7.8985 | 6.2736 | 4.6009 | 4.2441 | 12.7484 | 12.5336 | 12.389 | 12.3136 | 12.2392 | 12.1264 | 11.9974 | 11.7767 | 11.5649 | 11.3583 | 10.6517 | 8.3603 | 6.6863 | 5.5528 | 4.7615 | 17.3854 | 17.1706 | 17.026 | 16.9506 | 16.8762 | 16.7634 | 16.6344 | 16.4137 | 16.2019 | 15.9953 | 15.2887 | 12.9973 | 11.3233 | 10.1898 | 9.4928 | 12.7484 | 12.4621 | 12.2395 | 11.95 | 7.5221 | 7.5572 | 7.4709 | 7.0397 | 6.495 | 5.9285 | 4.0104 | 2.0013 | 0.20435 | -1.0514 | -0.90973 | 17.3854 | 17.0991 | 16.8765 | 16.587 | 12.1591 | 12.1942 | 12.1079 | 11.6767 | 11.132 | 10.5655 | 8.6474 | 6.6383 | 4.8413 | 3.5856 | 3.6855 | 392447 | 385492 | HAZEL GROVE | BREDBURY
| Northenden | 8.5201 | 7.7785 | 7.4272 | 7.0868 | 6.6628 | 6.194 | 5.6944 | 5.1615 | 4.569 | 3.556 | 0.18552 | -3.0652 | -5.3038 | -6.9753 | -7.8375 | 12.0201 | 11.2785 | 10.9272 | 10.5868 | 10.1628 | 9.694 | 9.1944 | 8.6615 | 8.069 | 7.056 | 3.6855 | 0.43478 | -1.8038 | -3.4753 | -4.3821 | 8.5201 | 8.2355 | 8.0534 | 7.8752 | 7.6427 | 7.347 | 6.9897 | 6.5718 | 6.1793 | 5.7521 | 4.1619 | 1.4993 | -0.8815 | -3.0429 | -4.2761 | 12.0201 | 11.7355 | 11.5534 | 11.3752 | 11.1427 | 10.847 | 10.4897 | 10.0718 | 9.6793 | 9.2521 | 7.6619 | 4.9993 | 2.6185 | 0.45708 | -0.62427 | 8.5201 | 7.6837 | 7.2882 | 6.93 | 6.4926 | 6.0212 | 5.5406 | 5.0292 | 4.4696 | 3.8662 | 0.55037 | -3.0701 | -5.6519 | -7.8947 | -8.9964 | 12.0201 | 11.1837 | 10.7882 | 10.43 | 9.9926 | 9.5212 | 9.0406 | 8.5292 | 7.9696 | 7.3662 | 4.0504 | 0.42993 | -2.1519 | -4.3947 | -5.446 | 8.5201 | 8.016 | 7.6868 | 7.3533 | 6.9087 | 6.3774 | 5.7409 | 4.8439 | 3.9042 | 2.9212 | -0.78344 | -3.8416 | -5.7904 | -7.0896 | -7.4069 | 12.0201 | 11.516 | 11.1868 | 10.8533 | 10.4087 | 9.8774 | 9.2409 | 8.3439 | 7.4042 | 6.4212 | 2.7166 | -0.34161 | -2.2904 | -3.5896 | -3.9011 | 8.5201 | 8.0808 | 7.8515 | 7.6461 | 7.398 | 7.0885 | 6.7286 | 6.3321 | 5.8518 | 5.3375 | 2.644 | -0.1877 | -2.2323 | -3.873 | -4.6271 | 12.0201 | 11.5808 | 11.3515 | 11.1461 | 10.898 | 10.5885 | 10.2286 | 9.8321 | 9.3518 | 8.8375 | 6.144 | 3.3123 | 1.2677 | -0.373 | -1.0603 | 8.5201 | 7.7441 | 7.3171 | 6.9184 | 6.4309 | 5.9116 | 5.2996 | 4.4017 | 3.4739 | 2.5185 | -0.65889 | -4.1398 | -6.5334 | -8.0982 | -8.3742 | 12.0201 | 11.2441 | 10.8171 | 10.4184 | 9.9309 | 9.4116 | 8.7996 | 7.9017 | 6.9739 | 6.0185 | 2.8411 | -0.63981 | -3.0334 | -4.5982 | -4.8859 | 382555 | 390327 | WEST DIDSBURY | SOUTH MANCHESTER
| NWGB Partington | 11.4973 | 11.4548 | 11.411 | 11.3656 | 11.2352 | 11.0386 | 9.6 | 9.3761 | 9.1093 | 8.7354 | 4.0125 | 0.68661 | -1.4168 | -2.2122 | -3.0659 | 16.4373 | 16.3948 | 16.351 | 16.3056 | 16.1752 | 15.9786 | 14.54 | 14.3161 | 14.0493 | 13.6754 | 8.9525 | 5.6266 | 3.5232 | 2.7278 | 1.8089 | 11.4973 | 11.4469 | 11.3916 | 11.3413 | 11.282 | 11.2098 | 11.1111 | 10.984 | 10.8208 | 10.6324 | 9.9529 | 8.941 | 7.8853 | 1.8418 | -13.792 | 16.4373 | 16.3869 | 16.3316 | 16.2813 | 16.222 | 16.1498 | 16.0511 | 15.924 | 15.7608 | 15.5724 | 14.8929 | 13.881 | 12.8253 | 6.7818 | -8.9359 | 11.4973 | 11.4544 | 11.4115 | 11.3679 | 10.9022 | 10.3941 | 8.6607 | 8.1252 | 7.5626 | 6.9774 | 1.6229 | -8.6931 | -10.817 | -13.2254 | -14.2243 | 16.4373 | 16.3944 | 16.3515 | 16.3079 | 15.8422 | 15.3341 | 13.6007 | 13.0652 | 12.5026 | 11.9174 | 6.5629 | -3.7531 | -5.877 | -8.2854 | -9.3684 | 11.4973 | 11.5436 | 8.2215 | 8.3988 | 8.1337 | 7.7451 | 6.0625 | 5.3413 | 4.4639 | -4.0252 | -7.5919 | -9.4671 | -11.4648 | -13.3986 | -13.0671 | 16.4373 | 16.4836 | 13.1615 | 13.3388 | 13.0737 | 12.6851 | 11.0025 | 10.2813 | 9.4039 | 0.91477 | -2.6519 | -4.5271 | -6.5248 | -8.4586 | -8.2064 | 11.4973 | 11.4615 | 11.4281 | 11.4082 | 11.3786 | 11.3293 | 10.0031 | 9.8535 | 9.6425 | 9.4078 | 5.1069 | 2.4761 | 0.87993 | 0.60533 | 0.50975 | 16.4373 | 16.4015 | 16.3681 | 16.3482 | 16.3186 | 16.2693 | 14.9431 | 14.7935 | 14.5825 | 14.3478 | 10.0469 | 7.4161 | 5.8199 | 5.5453 | 5.4334 | 11.4973 | 11.5294 | 8.1887 | 8.3462 | 8.0596 | 7.6696 | 5.988 | 5.2695 | 4.4069 | -4.0718 | -7.6925 | -9.7127 | -11.8638 | -13.9325 | -13.7004 | 16.4373 | 16.4694 | 13.1287 | 13.2862 | 12.9996 | 12.6096 | 10.928 | 10.2095 | 9.3469 | 0.86822 | -2.7525 | -4.7727 | -6.9238 | -8.9925 | -8.8203 | 372569 | 392079 | CARRINGTON BSP | CARRINGTON
| Offerton | 9.854 | 8.1656 | 7.4357 | 6.8427 | 6.223 | 5.602 | 4.9897 | 4.3879 | 3.7449 | 3.1139 | 1.9007 | -0.37497 | -2.2801 | -4.3278 | -6.1067 | 19.854 | 18.1656 | 17.4357 | 16.8427 | 16.223 | 15.602 | 14.9897 | 14.3879 | 13.7449 | 13.1139 | 11.9007 | 9.625 | 7.7199 | 5.6722 | 3.7856 | 9.854 | 8.6174 | 7.988 | 7.3974 | 6.7913 | 6.1803 | 5.5374 | 4.8556 | 4.1734 | 3.4886 | 2.9593 | 2.2856 | 1.6165 | 0.87476 | 0.34519 | 19.854 | 18.6174 | 17.988 | 17.3974 | 16.7913 | 16.1803 | 15.5374 | 14.8556 | 14.1734 | 13.4886 | 12.9593 | 12.2856 | 11.6165 | 10.8748 | 10.434 | 9.854 | 8.0681 | 7.3297 | 6.7538 | 6.1574 | 5.5652 | 4.9101 | 4.3527 | 3.7601 | 3.181 | 2.2702 | 0.14076 | -1.638 | -3.5331 | -5.137 | 19.854 | 18.0681 | 17.3297 | 16.7538 | 16.1574 | 15.5652 | 14.9101 | 14.3527 | 13.7601 | 13.181 | 12.2702 | 10.1408 | 8.362 | 6.4669 | 4.7217 | 9.854 | 8.3946 | 7.738 | 7.1727 | 6.5719 | 5.9589 | 5.1759 | 4.1621 | 2.9566 | 1.7406 | -0.36809 | -2.3932 | -4.0219 | -5.0984 | -4.4476 | 19.854 | 18.3946 | 17.738 | 17.1727 | 16.5719 | 15.9589 | 15.1759 | 14.1621 | 12.9566 | 11.7406 | 9.6319 | 7.6068 | 5.9781 | 4.9016 | 5.4082 | 9.854 | 8.4735 | 7.8273 | 7.2735 | 6.7186 | 6.1538 | 5.5835 | 5.0085 | 4.3687 | 3.7274 | 3.265 | 2.557 | 2.0646 | 1.5808 | 1.2989 | 19.854 | 18.4735 | 17.8273 | 17.2735 | 16.7186 | 16.1538 | 15.5835 | 15.0085 | 14.3687 | 13.7274 | 13.265 | 12.557 | 12.0646 | 11.5808 | 11.3096 | 9.854 | 8.0574 | 7.2932 | 6.6759 | 6.0281 | 5.3833 | 4.5674 | 3.4406 | 2.1722 | 0.90466 | -1.363 | -3.5368 | -5.314 | -6.5721 | -6.1252 | 19.854 | 18.0574 | 17.2932 | 16.6759 | 16.0281 | 15.3833 | 14.5674 | 13.4406 | 12.1722 | 10.9047 | 8.637 | 6.4632 | 4.686 | 3.4279 | 3.7758 | 391010 | 389489 | VERNON PARK | BREDBURY
| Openshaw | 3.3635 | 2.7644 | 2.3867 | 2.0686 | 1.655 | 1.207 | 0.76475 | 0.32968 | -0.15101 | -0.6713 | -3.2626 | -6.7122 | -9.217 | -11.5442 | -13.2256 | 6.8635 | 6.2644 | 5.8867 | 5.5686 | 5.155 | 4.707 | 4.2647 | 3.8297 | 3.349 | 2.8287 | 0.23739 | -3.2122 | -5.717 | -8.0442 | -9.8856 | 3.3635 | 3.1166 | 2.8477 | 2.3991 | 2.1343 | 1.8045 | 1.4018 | 0.91965 | 0.64844 | 0.37254 | -0.5045 | -2.0192 | -3.4367 | -4.9144 | -5.8751 | 6.8635 | 6.6166 | 6.3477 | 5.8991 | 5.6343 | 5.3045 | 4.9018 | 4.4196 | 4.1484 | 3.8725 | 2.9955 | 1.4808 | 0.063321 | -1.4144 | -2.2297 | 3.3635 | 2.6268 | 2.1062 | 1.6907 | 1.1739 | 0.62053 | 0.086332 | -0.45347 | -1.0209 | -1.6559 | -4.6402 | -8.2327 | -10.6578 | -12.5511 | -13.5114 | 6.8635 | 6.1268 | 5.6062 | 5.1907 | 4.6739 | 4.1205 | 3.5863 | 3.0465 | 2.4791 | 1.8441 | -1.1402 | -4.7327 | -7.1578 | -9.0511 | -10.0773 | 3.3635 | 3.0476 | 2.7087 | 2.3257 | 1.817 | 1.2534 | 0.52598 | -0.74992 | -2.0321 | -3.2925 | -6.827 | -9.8652 | -11.6568 | -12.4079 | -12.1085 | 6.8635 | 6.5476 | 6.2087 | 5.8257 | 5.317 | 4.7534 | 4.026 | 2.7501 | 1.4679 | 0.2075 | -3.327 | -6.3652 | -8.1568 | -8.9079 | -8.6863 | 3.3635 | 3.1074 | 2.8446 | 2.5847 | 2.3512 | 2.0639 | 1.7345 | 1.3446 | 0.85101 | 0.336 | -1.5797 | -3.5463 | -4.9171 | -6.114 | -6.8079 | 6.8635 | 6.6074 | 6.3446 | 6.0847 | 5.8512 | 5.5639 | 5.2345 | 4.8446 | 4.351 | 3.836 | 1.9203 | -0.046257 | -1.4171 | -2.614 | -3.2258 | 3.3635 | 2.7482 | 2.2925 | 1.8226 | 1.2345 | 0.61753 | -0.17502 | -1.5326 | -2.8601 | -4.1688 | -7.9016 | -11.1724 | -13.2211 | -14.2363 | -14.071 | 6.8635 | 6.2482 | 5.7925 | 5.3226 | 4.7345 | 4.1175 | 3.325 | 1.9674 | 0.63993 | -0.66878 | -4.4016 | -7.6724 | -9.7211 | -10.7363 | -10.5958 | 388606 | 397346 | DROYLSDEN | STALYBRIDGE
| Ormskirk | 9.2325 | 8.303 | 7.6337 | 7.2652 | 6.9958 | 6.7215 | 6.4701 | 6.2189 | 5.9231 | 5.6479 | 4.1898 | 1.9919 | 0.36157 | -1.175 | -2.2336 | 13.8695 | 12.94 | 12.2707 | 11.9022 | 11.6328 | 11.3585 | 11.1071 | 10.8559 | 10.5601 | 10.2849 | 8.8268 | 6.6289 | 4.9986 | 3.462 | 2.2715 | 9.2325 | 8.7583 | 8.5064 | 8.3074 | 8.0665 | 7.8067 | 7.4759 | 7.0365 | 6.7479 | 6.4578 | 5.6158 | 4.7712 | 3.9827 | 3.1269 | 2.54 | 13.8695 | 13.3953 | 13.1434 | 12.9444 | 12.7035 | 12.4437 | 12.1129 | 11.6735 | 11.3849 | 11.0948 | 10.2528 | 9.4082 | 8.6197 | 7.7639 | 7.2637 | 9.2325 | 8.1308 | 7.3817 | 6.9617 | 6.6328 | 6.2967 | 5.9944 | 5.6845 | 5.3591 | 5.0246 | 3.4257 | 1.3449 | 0.0010469 | -1.0268 | -1.3146 | 13.8695 | 12.7678 | 12.0187 | 11.5987 | 11.2698 | 10.9337 | 10.6314 | 10.3215 | 9.9961 | 9.6616 | 8.0627 | 5.9819 | 4.638 | 3.6102 | 3.1701 | 9.2325 | 8.6236 | 8.0016 | 7.6212 | 7.3204 | 6.9954 | 6.5836 | 5.8232 | 5.0443 | 4.2819 | 2.1862 | 0.44664 | -0.54077 | -0.84928 | -0.13272 | 13.8695 | 13.2606 | 12.6386 | 12.2582 | 11.9574 | 11.6324 | 11.2206 | 10.4602 | 9.6813 | 8.9189 | 6.8232 | 5.0836 | 4.0962 | 3.7877 | 4.3452 | 9.2325 | 8.459 | 7.8434 | 7.5271 | 7.3505 | 7.1574 | 6.9549 | 6.7289 | 6.4281 | 6.1313 | 5.1665 | 4.1437 | 3.473 | 2.8335 | 2.4904 | 13.8695 | 13.096 | 12.4804 | 12.1641 | 11.9875 | 11.7944 | 11.5919 | 11.3659 | 11.0651 | 10.7683 | 9.8035 | 8.7807 | 8.11 | 7.4705 | 7.1472 | 9.2325 | 8.2006 | 7.4323 | 6.958 | 6.5695 | 6.1806 | 5.6931 | 4.8345 | 4.003 | 3.1882 | 0.93204 | -0.93239 | -2.0335 | -2.4629 | -1.8843 | 13.8695 | 12.8376 | 12.0693 | 11.595 | 11.2065 | 10.8176 | 10.3301 | 9.4715 | 8.64 | 7.8252 | 5.569 | 3.7046 | 2.6035 | 2.1741 | 2.6241 | 341294 | 408158 | SKELMERSDALE | WASHWAY FARM
| Padiham | 18.7324 | 16.1163 | 15.1604 | 14.7121 | 14.243 | 13.7546 | 13.2705 | 13.0698 | 12.7372 | 12.413 | 10.685 | 8.0624 | 5.9176 | 3.4194 | 1.455 | 25.7324 | 23.1163 | 22.1604 | 21.7121 | 21.243 | 20.7546 | 20.2705 | 20.0698 | 19.7372 | 19.413 | 17.685 | 15.0624 | 12.9176 | 10.4194 | 8.2495 | 18.7324 | 17.7622 | 17.4008 | 17.267 | 17.1633 | 17.0464 | 16.8883 | 16.676 | 16.3645 | 16.0502 | 15.071 | 14.0474 | 13.0963 | 12.0268 | 11.09 | 25.7324 | 24.7622 | 24.4008 | 24.267 | 24.1633 | 24.0464 | 23.8883 | 23.676 | 23.3645 | 23.0502 | 22.071 | 21.0474 | 20.0963 | 19.0268 | 18.2222 | 18.7324 | 15.6944 | 14.6664 | 14.2181 | 13.7543 | 13.2757 | 12.8055 | 12.6264 | 12.3785 | 12.1458 | 10.649 | 8.2104 | 6.3186 | 4.338 | 2.8781 | 25.7324 | 22.6944 | 21.6664 | 21.2181 | 20.7543 | 20.2757 | 19.8055 | 19.6264 | 19.3785 | 19.1458 | 17.649 | 15.2104 | 13.3186 | 11.338 | 9.5874 | 18.7324 | 16.7345 | 15.9237 | 15.5172 | 15.0827 | 14.6067 | 13.9813 | 13.1977 | 12.3235 | 11.4642 | 8.8693 | 6.1719 | 4.1347 | 3.0647 | 4.3978 | 25.7324 | 23.7345 | 22.9237 | 22.5172 | 22.0827 | 21.6067 | 20.9813 | 20.1977 | 19.3235 | 18.4642 | 15.8693 | 13.1719 | 11.1347 | 10.0647 | 11.0931 | 18.7324 | 16.9121 | 16.123 | 15.7343 | 15.3813 | 14.9975 | 14.5725 | 14.4093 | 14.0924 | 13.7669 | 12.6716 | 11.5467 | 10.8134 | 10.2687 | 10.2622 | 25.7324 | 23.9121 | 23.123 | 22.7343 | 22.3813 | 21.9975 | 21.5725 | 21.4093 | 21.0924 | 20.7669 | 19.6716 | 18.5467 | 17.8134 | 17.2687 | 17.2031 | 18.7324 | 15.4366 | 14.3511 | 13.8809 | 13.3929 | 12.8984 | 12.2648 | 11.4487 | 10.5621 | 9.6916 | 7.1451 | 4.3381 | 2.0692 | 0.72157 | 1.7629 | 25.7324 | 22.4366 | 21.3511 | 20.8809 | 20.3929 | 19.8984 | 19.2648 | 18.4487 | 17.5621 | 16.6916 | 14.1451 | 11.3381 | 9.0692 | 7.7216 | 8.5256 | 378428 | 433238 | PADIHAM | PADIHAM
| Peel St | 1.632 | 1.2554 | 1.0379 | 0.79302 | 0.49872 | 0.19794 | -2.9907 | -3.273 | -3.7294 | -4.2166 | -7.6192 | -9.9245 | -19.4655 | -21.0392 | -22.2524 | 11.432 | 11.0554 | 10.8379 | 10.593 | 10.2987 | 9.9979 | 6.8093 | 6.527 | 6.0706 | 5.5834 | 2.1808 | -0.12447 | -9.6655 | -11.2392 | -12.4819 | 1.632 | 1.3533 | 1.2034 | 0.99469 | 0.73029 | 0.43309 | 0.032907 | -0.44057 | -0.80321 | -1.1741 | -3.9691 | -5.3279 | -6.5957 | -7.8545 | -8.5759 | 11.432 | 11.1533 | 11.0034 | 10.7947 | 10.5303 | 10.2331 | 9.8329 | 9.3594 | 8.9968 | 8.6259 | 5.8309 | 4.4721 | 3.2043 | 1.9455 | 1.3268 | 1.632 | 1.2475 | 1.0504 | 0.8453 | 0.59809 | 0.35525 | 0.10811 | -0.11906 | -0.54526 | -0.97396 | -11.2035 | -15.3485 | -17.3287 | -19.0196 | -20.2041 | 11.432 | 11.0475 | 10.8504 | 10.6453 | 10.3981 | 10.1553 | 9.9081 | 9.6809 | 9.2547 | 8.826 | -1.4035 | -5.5485 | -7.5287 | -9.2196 | -10.3493 | 1.632 | 1.4632 | 1.3556 | 1.1741 | 0.9609 | 0.71467 | -1.1622 | -1.7881 | -2.4799 | -12.332 | -15.7558 | -17.7832 | -19.5295 | -20.9521 | -21.297 | 11.432 | 11.2632 | 11.1556 | 10.9741 | 10.7609 | 10.5147 | 8.6378 | 8.0119 | 7.3201 | -2.532 | -5.9558 | -7.9832 | -9.7295 | -11.1521 | -11.4653 | 1.632 | 1.3143 | 1.1481 | 0.97282 | 0.77579 | 0.5419 | -2.6075 | -2.8469 | -3.1615 | -3.5802 | -6.5754 | -8.0856 | -17.2438 | -18.4394 | -19.0975 | 11.432 | 11.1143 | 10.9481 | 10.7728 | 10.5758 | 10.3419 | 7.1925 | 6.9531 | 6.6385 | 6.2198 | 3.2246 | 1.7144 | -7.4438 | -8.6394 | -9.2101 | 1.632 | 1.3249 | 1.1143 | 0.83148 | 0.52821 | 0.22541 | -1.7133 | -2.4317 | -3.1824 | -13.0917 | -16.8218 | -19.0408 | -20.7089 | -21.9311 | -21.9268 | 11.432 | 11.1249 | 10.9143 | 10.6315 | 10.3282 | 10.0254 | 8.0867 | 7.3683 | 6.6176 | -3.2917 | -7.0218 | -9.2408 | -10.9089 | -12.1311 | -12.1472 | 374463 | 441514 | PADIHAM | PADIHAM
| Pendleton | 8.6074 | 6.2606 | 5.5412 | 5.0449 | 4.3581 | 3.5067 | 2.5334 | 1.5637 | 0.52406 | 0.1233 | -1.37 | -3.1586 | -4.4722 | -5.7294 | -6.7639 | 13.2444 | 10.8976 | 10.1782 | 9.6819 | 8.9951 | 8.1437 | 7.1704 | 6.2007 | 5.1611 | 4.7603 | 3.267 | 1.4784 | 0.16478 | -1.0924 | -2.1022 | 8.6074 | 7.6744 | 7.4747 | 7.2239 | 6.9931 | 6.7594 | 6.489 | 6.1606 | 5.7994 | 5.4325 | 4.3353 | 3.2232 | 2.2217 | 1.0757 | 0.11919 | 13.2444 | 12.3114 | 12.1117 | 11.8609 | 11.6301 | 11.3964 | 11.126 | 10.7976 | 10.4364 | 10.0695 | 8.9723 | 7.8602 | 6.8587 | 5.7127 | 4.9188 | 8.6074 | 5.8931 | 5.0535 | 4.4918 | 3.737 | 2.8134 | 1.7607 | 0.66192 | -0.41994 | -0.86671 | -2.5391 | -4.3835 | -5.6369 | -6.6858 | -7.3761 | 13.2444 | 10.5301 | 9.6905 | 9.1288 | 8.374 | 7.4504 | 6.3977 | 5.2989 | 4.2171 | 3.7703 | 2.0979 | 0.25346 | -0.99988 | -2.0488 | -2.7202 | 8.6074 | 6.6546 | 5.9951 | 5.4174 | 4.6953 | 3.7892 | 2.695 | 1.4326 | 0.12827 | -0.52956 | -2.4274 | -4.0706 | -5.1182 | -5.8234 | -6.0268 | 13.2444 | 11.2916 | 10.6321 | 10.0544 | 9.3323 | 8.4262 | 7.332 | 6.0696 | 4.7653 | 4.1074 | 2.2096 | 0.56639 | -0.48117 | -1.1864 | -1.3719 | 8.6074 | 7.1463 | 6.6231 | 6.1661 | 5.5539 | 4.778 | 3.8638 | 2.9303 | 1.897 | 1.4885 | 0.21957 | -1.0207 | -1.898 | -2.7926 | -3.4432 | 13.2444 | 11.7833 | 11.2601 | 10.8031 | 10.1909 | 9.415 | 8.5008 | 7.5673 | 6.534 | 6.1255 | 4.8566 | 3.6163 | 2.739 | 1.8444 | 1.2913 | 8.6074 | 5.6935 | 4.8051 | 4.1829 | 3.422 | 2.4974 | 1.3915 | 0.099543 | -1.5177 | -2.4868 | -5.3267 | -7.9273 | -9.9405 | -11.8848 | -13.6462 | 13.2444 | 10.3305 | 9.4421 | 8.8199 | 8.059 | 7.1344 | 6.0285 | 4.7365 | 3.1193 | 2.1502 | -0.6897 | -3.2903 | -5.3035 | -7.2478 | -8.6754 | 381161 | 398842 | FREDERICK RD | KEARSLEY
| Petteril Bank | 9.2883 | 8.5993 | 8.4173 | 8.3181 | 8.0715 | 7.7764 | 7.4748 | 7.0907 | 6.6078 | 6.1268 | 3.9812 | 0.47134 | -2.1509 | -4.6003 | -7.1087 | 13.4253 | 12.7363 | 12.5543 | 12.4551 | 12.2085 | 11.9134 | 11.6118 | 11.2277 | 10.7448 | 10.2638 | 8.1182 | 4.6083 | 1.9861 | -0.46329 | -3.1493 | 9.2883 | 9.0324 | 8.9237 | 8.8297 | 8.6771 | 8.4501 | 8.0559 | 7.5557 | 7.1585 | 6.7417 | 5.4101 | 4.0308 | 2.7202 | 1.4218 | 0.68732 | 13.4253 | 13.1694 | 13.0607 | 12.9667 | 12.8141 | 12.5871 | 12.1929 | 11.6927 | 11.2955 | 10.8787 | 9.5471 | 8.1678 | 6.8572 | 5.5588 | 4.9182 | 9.2883 | 8.5237 | 8.3519 | 8.2978 | 8.1039 | 7.875 | 7.6721 | 7.3645 | 7.0103 | 6.6372 | 4.3993 | 0.74015 | -2.0501 | -4.4289 | -6.2794 | 13.4253 | 12.6607 | 12.4889 | 12.4348 | 12.2409 | 12.012 | 11.8091 | 11.5015 | 11.1473 | 10.7742 | 8.5363 | 4.8772 | 2.0869 | -0.29187 | -2.2747 | 9.2883 | 9.0683 | 9.0108 | 8.9457 | 8.7115 | 8.416 | 7.9574 | 6.924 | 5.8161 | 4.6905 | 1.3726 | -1.7584 | -4.163 | -5.4706 | -4.7911 | 13.4253 | 13.2053 | 13.1478 | 13.0827 | 12.8485 | 12.553 | 12.0944 | 11.061 | 9.9531 | 8.8275 | 5.5096 | 2.3786 | -0.025991 | -1.3336 | -0.79731 | 9.2883 | 8.9236 | 8.8327 | 8.8243 | 8.7725 | 8.67 | 8.4486 | 8.1291 | 7.7202 | 7.2927 | 5.7817 | 4.0065 | 2.653 | 1.6926 | 1.3371 | 13.4253 | 13.0606 | 12.9697 | 12.9613 | 12.9095 | 12.807 | 12.5856 | 12.2661 | 11.8572 | 11.4297 | 9.9187 | 8.1435 | 6.79 | 5.8296 | 5.466 | 9.2883 | 8.7173 | 8.5278 | 8.3723 | 8.0579 | 7.713 | 7.1954 | 6.0879 | 4.9406 | 3.7726 | 0.24312 | -3.1597 | -5.8375 | -7.4172 | -6.6866 | 13.4253 | 12.8543 | 12.6648 | 12.5093 | 12.1949 | 11.85 | 11.3324 | 10.2249 | 9.0776 | 7.9096 | 4.3801 | 0.97727 | -1.7005 | -3.2802 | -2.7127 | 341768 | 553686 | CARLISLE | HARKER
| Phillips Lane | 3.3102 | 2.9855 | 2.8585 | 2.7778 | 2.6645 | 2.5418 | 2.4247 | 2.3053 | 2.1802 | 2.0641 | 1.2744 | -0.29403 | -1.7371 | -3.2576 | -4.5143 | 12.3102 | 11.9855 | 11.8585 | 11.7778 | 11.6645 | 11.5418 | 11.4247 | 11.3053 | 11.1802 | 11.0641 | 10.2744 | 8.706 | 7.2629 | 5.7424 | 4.3793 | 3.3102 | 3.2213 | 3.1339 | 3.0508 | 2.9512 | 2.8373 | 2.6903 | 2.4967 | 2.3748 | 2.2527 | 1.8817 | 1.4998 | 1.1438 | 0.75988 | 0.50235 | 12.3102 | 12.2213 | 12.1339 | 12.0508 | 11.9512 | 11.8373 | 11.6903 | 11.4967 | 11.3748 | 11.2527 | 10.8817 | 10.4998 | 10.1438 | 9.7599 | 9.5472 | 3.3102 | 2.9404 | 2.8056 | 2.7245 | 2.6115 | 2.4896 | 2.3728 | 2.2553 | 2.1466 | 2.048 | 1.3071 | -0.1004 | -1.4775 | -2.9092 | -4.0547 | 12.3102 | 11.9404 | 11.8056 | 11.7245 | 11.6115 | 11.4896 | 11.3728 | 11.2553 | 11.1466 | 11.048 | 10.3071 | 8.8996 | 7.5225 | 6.0908 | 4.8187 | 3.3102 | 3.1277 | 3.0499 | 2.9959 | 2.9035 | 2.7891 | 2.5917 | 2.1342 | 1.6679 | 1.1441 | -0.51347 | -2.0856 | -3.3389 | -4.1273 | -3.5449 | 12.3102 | 12.1277 | 12.0499 | 11.9959 | 11.9035 | 11.7891 | 11.5917 | 11.1342 | 10.6679 | 10.1441 | 8.4865 | 6.9144 | 5.6611 | 4.8727 | 5.3256 | 3.3102 | 3.2202 | 3.1489 | 3.0992 | 3.045 | 2.9743 | 2.8862 | 2.7831 | 2.6578 | 2.532 | 2.1078 | 1.6381 | 1.3225 | 1.0432 | 0.94977 | 12.3102 | 12.2202 | 12.1489 | 12.0992 | 12.045 | 11.9743 | 11.8862 | 11.7831 | 11.6578 | 11.532 | 11.1078 | 10.6381 | 10.3225 | 10.0432 | 9.9416 | 3.3102 | 2.9693 | 2.8334 | 2.739 | 2.6099 | 2.4752 | 2.2606 | 1.7696 | 1.2869 | 0.71235 | -1.0099 | -2.656 | -3.9996 | -4.9201 | -4.4998 | 12.3102 | 11.9693 | 11.8334 | 11.739 | 11.6099 | 11.4752 | 11.2606 | 10.7696 | 10.2869 | 9.7123 | 7.9901 | 6.344 | 5.0004 | 4.0799 | 4.4078 | 387571 | 439522 | NELSON | PADIHAM
| Piccadilly | 12.9185 | 11.9977 | 11.6526 | 11.533 | 11.451 | 11.375 | 11.3112 | 11.2478 | 11.1175 | 10.9974 | 10.5456 | 9.9574 | 9.503 | 9.0453 | 8.6781 | 17.5555 | 16.6347 | 16.2896 | 16.17 | 16.088 | 16.012 | 15.9482 | 15.8848 | 15.7545 | 15.6344 | 15.1826 | 14.5944 | 14.14 | 13.6823 | 13.2898 | 12.9185 | 12.5644 | 12.3081 | 12.1484 | 12.0211 | 11.8833 | 11.7319 | 11.5584 | 11.3918 | 11.227 | 10.779 | 10.3787 | 10.0654 | 9.7414 | 9.4429 | 17.5555 | 17.2014 | 16.9451 | 16.7854 | 16.6581 | 16.5203 | 16.3689 | 16.1954 | 16.0288 | 15.864 | 15.416 | 15.0157 | 14.7024 | 14.3784 | 14.1234 | 12.9185 | 11.8529 | 11.4769 | 11.3526 | 11.2669 | 11.1872 | 11.1236 | 11.061 | 10.9694 | 10.8901 | 10.5664 | 10.1241 | 9.8276 | 9.5934 | 9.5165 | 17.5555 | 16.4899 | 16.1139 | 15.9896 | 15.9039 | 15.8242 | 15.7606 | 15.698 | 15.6064 | 15.5271 | 15.2034 | 14.7611 | 14.4646 | 14.2304 | 14.074 | 12.9185 | 12.1624 | 11.8671 | 11.7637 | 11.6994 | 11.6384 | 11.5655 | 11.4152 | 11.2108 | 11.0173 | 10.5054 | 10.0709 | 9.7877 | 9.7018 | 10.0299 | 17.5555 | 16.7994 | 16.5041 | 16.4007 | 16.3364 | 16.2754 | 16.2025 | 16.0522 | 15.8478 | 15.6543 | 15.1424 | 14.7079 | 14.4247 | 14.3388 | 14.5839 | 12.9185 | 12.345 | 12.0753 | 11.9659 | 11.9031 | 11.8429 | 11.7834 | 11.718 | 11.583 | 11.4547 | 11.1018 | 10.7899 | 10.5992 | 10.4456 | 10.4587 | 17.5555 | 16.982 | 16.7123 | 16.6029 | 16.5401 | 16.4799 | 16.4204 | 16.355 | 16.22 | 16.0917 | 15.7388 | 15.4269 | 15.2362 | 15.0826 | 15.0732 | 12.9185 | 11.7256 | 11.3219 | 11.1923 | 11.1023 | 11.0198 | 10.9253 | 10.7469 | 10.5374 | 10.3396 | 9.8197 | 9.3831 | 9.0974 | 9.009 | 9.327 | 17.5555 | 16.3626 | 15.9589 | 15.8293 | 15.7393 | 15.6568 | 15.5623 | 15.3839 | 15.1744 | 14.9766 | 14.4567 | 14.0201 | 13.7344 | 13.646 | 13.8839 | 384427 | 398261 | BLOOM ST | SOUTH MANCHESTER
| Pimbo | 11.4316 | 10.7998 | 10.231 | 9.6555 | 9.3496 | 9.2064 | 9.0516 | 8.8765 | 8.5377 | 8.1914 | 6.6256 | 3.8245 | 1.8045 | 0.19164 | -0.94021 | 26.4316 | 25.7998 | 25.231 | 24.6555 | 24.3496 | 24.2064 | 24.0516 | 23.8765 | 23.5377 | 23.1914 | 21.6256 | 18.8245 | 16.8045 | 15.1916 | 13.9297 | 11.4316 | 11.3042 | 11.0546 | 10.9447 | 10.8873 | 10.8921 | 10.8798 | 10.7273 | 10.4875 | 10.2444 | 9.4877 | 8.3902 | 7.0859 | 5.6709 | 4.7875 | 26.4316 | 26.3042 | 26.0546 | 25.9447 | 25.8873 | 25.8921 | 25.8798 | 25.7273 | 25.4875 | 25.2444 | 24.4877 | 23.3902 | 22.0859 | 20.6709 | 19.9068 | 11.4316 | 10.6488 | 10.0031 | 9.3745 | 9.0089 | 8.8075 | 8.5946 | 8.3623 | 8.0363 | 7.7036 | 6.138 | 3.4143 | 1.6574 | 0.5391 | 0.097067 | 26.4316 | 25.6488 | 25.0031 | 24.3745 | 24.0089 | 23.8075 | 23.5946 | 23.3623 | 23.0363 | 22.7036 | 21.138 | 18.4143 | 16.6574 | 15.5391 | 15.0182 | 11.4316 | 10.9521 | 10.379 | 9.7646 | 9.4004 | 9.1827 | 8.8799 | 8.3599 | 7.7423 | 6.9058 | 4.1714 | 1.9183 | 0.67348 | 0.37658 | 1.2302 | 26.4316 | 25.9521 | 25.379 | 24.7646 | 24.4004 | 24.1827 | 23.8799 | 23.3599 | 22.7423 | 21.9058 | 19.1714 | 16.9183 | 15.6735 | 15.3766 | 16.0971 | 11.4316 | 11.1417 | 10.6592 | 10.1291 | 9.9154 | 9.861 | 9.7731 | 9.6478 | 9.3454 | 9.0265 | 7.955 | 6.8206 | 5.7793 | 4.914 | 4.4837 | 26.4316 | 26.1417 | 25.6592 | 25.1291 | 24.9154 | 24.861 | 24.7731 | 24.6478 | 24.3454 | 24.0265 | 22.955 | 21.8206 | 20.7793 | 19.914 | 19.5405 | 11.4316 | 10.6507 | 9.9948 | 9.3536 | 8.9709 | 8.7589 | 8.4742 | 7.9652 | 7.2067 | 6.2455 | 3.3796 | 0.88761 | -0.63583 | -1.1375 | -0.39159 | 26.4316 | 25.6507 | 24.9948 | 24.3536 | 23.9709 | 23.7589 | 23.4742 | 22.9652 | 22.2067 | 21.2455 | 18.3796 | 15.8876 | 14.3642 | 13.8625 | 14.4611 | 349148 | 404549 | SKELMERSDALE | WASHWAY FARM
| Portwood | 9.2448 | 6.7554 | 5.537 | 4.4108 | 3.3268 | 2.4082 | 1.5013 | 0.59324 | -0.37171 | -1.2534 | -2.9975 | -4.8211 | -6.0902 | -7.3048 | -8.253 | 13.8818 | 11.3924 | 10.174 | 9.0478 | 7.9638 | 7.0452 | 6.1383 | 5.2302 | 4.2653 | 3.3836 | 1.6395 | -0.18408 | -1.4532 | -2.6678 | -3.6226 | 9.2448 | 7.8797 | 7.0575 | 6.3134 | 5.5755 | 4.8177 | 4.0078 | 3.1335 | 2.3933 | 1.6559 | 0.67906 | -0.2664 | -1.1112 | -2.0088 | -2.7591 | 13.8818 | 12.5167 | 11.6945 | 10.9504 | 10.2125 | 9.4547 | 8.6448 | 7.7705 | 7.0303 | 6.2929 | 5.3161 | 4.3706 | 3.5258 | 2.6282 | 1.9992 | 9.2448 | 6.4344 | 5.1191 | 3.9297 | 2.7761 | 1.7809 | 0.71383 | -0.43565 | -1.5087 | -2.4394 | -4.4062 | -6.2724 | -7.4118 | -8.3638 | -8.8705 | 13.8818 | 11.0714 | 9.7561 | 8.5667 | 7.4131 | 6.4179 | 5.3508 | 4.2014 | 3.1283 | 2.1976 | 0.23077 | -1.6354 | -2.7748 | -3.7268 | -4.256 | 9.2448 | 7.0118 | 5.8661 | 4.7454 | 3.6549 | 2.7005 | 1.6063 | 0.26113 | -1.0477 | -2.2206 | -4.4633 | -6.1513 | -7.1116 | -7.6893 | -7.6417 | 13.8818 | 11.6488 | 10.5031 | 9.3824 | 8.2919 | 7.3375 | 6.2433 | 4.8981 | 3.5893 | 2.4164 | 0.17369 | -1.5143 | -2.4746 | -3.0523 | -3.0387 | 9.2448 | 7.5381 | 6.5044 | 5.4259 | 4.4135 | 3.5479 | 2.6653 | 1.7738 | 0.80841 | -0.087121 | -1.5842 | -2.7694 | -3.5349 | -4.2922 | -4.7973 | 13.8818 | 12.1751 | 11.1414 | 10.0629 | 9.0505 | 8.1849 | 7.3023 | 6.4108 | 5.4454 | 4.5499 | 3.0528 | 1.8676 | 1.1021 | 0.34484 | -0.094522 | 9.2448 | 6.2826 | 4.9286 | 3.7272 | 2.5617 | 1.5597 | 0.42169 | -0.99641 | -2.3257 | -3.4962 | -5.7801 | -7.4896 | -8.4734 | -9.0775 | -9.103 | 13.8818 | 10.9196 | 9.5656 | 8.3642 | 7.1987 | 6.1967 | 5.0587 | 3.6406 | 2.3113 | 1.1408 | -1.1431 | -2.8526 | -3.8364 | -4.4405 | -4.4793 | 389826 | 390619 | VERNON PARK | BREDBURY
| Poulton | 9.0314 | 8.5559 | 8.2568 | 8.0458 | 7.8157 | 7.5761 | 7.34 | 7.0842 | 6.7722 | 6.4748 | 4.8107 | 1.9629 | -0.13337 | -2.0589 | -3.4936 | 11.0114 | 10.5359 | 10.2368 | 10.0258 | 9.7957 | 9.5561 | 9.32 | 9.0642 | 8.7522 | 8.4548 | 6.7907 | 3.9429 | 1.8466 | -0.078867 | -1.5206 | 9.0314 | 8.7609 | 8.5315 | 8.3527 | 8.165 | 7.958 | 7.699 | 7.358 | 7.0572 | 6.7554 | 5.8447 | 4.9372 | 4.0801 | 3.1541 | 2.3163 | 11.0114 | 10.7409 | 10.5115 | 10.3327 | 10.145 | 9.938 | 9.679 | 9.338 | 9.0372 | 8.7354 | 7.8247 | 6.9172 | 6.0601 | 5.1341 | 4.433 | 9.0314 | 8.4973 | 8.1887 | 7.9775 | 7.75 | 7.5151 | 7.2842 | 7.0381 | 6.7769 | 6.5342 | 4.4635 | 1.448 | -0.78079 | -2.7629 | -4.1394 | 11.0114 | 10.4773 | 10.1687 | 9.9575 | 9.73 | 9.4951 | 9.2642 | 9.0181 | 8.7569 | 8.5142 | 6.4435 | 3.428 | 1.1992 | -0.78294 | -2.1836 | 9.0314 | 8.7551 | 8.5385 | 8.369 | 8.1698 | 7.9304 | 7.5753 | 6.8791 | 6.1362 | 5.4065 | 3.2813 | 0.8434 | -1.1817 | -2.6155 | -2.5786 | 11.0114 | 10.7351 | 10.5185 | 10.349 | 10.1498 | 9.9104 | 9.5553 | 8.8591 | 8.1162 | 7.3865 | 5.2613 | 2.8234 | 0.79833 | -0.63552 | -0.64692 | 9.0314 | 8.6411 | 8.3902 | 8.2393 | 8.0978 | 7.922 | 7.7259 | 7.5153 | 7.2271 | 6.9399 | 5.9953 | 4.1493 | 2.7087 | 1.5336 | 0.92789 | 11.0114 | 10.6211 | 10.3702 | 10.2193 | 10.0778 | 9.902 | 9.7059 | 9.4953 | 9.2071 | 8.9199 | 7.9753 | 6.1293 | 4.6887 | 3.5136 | 2.963 | 9.0314 | 8.5335 | 8.2179 | 7.9694 | 7.7011 | 7.4298 | 7.0509 | 6.2992 | 5.5275 | 4.7726 | 2.5776 | 0.44447 | -1.614 | -3.058 | -3.0019 | 11.0114 | 10.5135 | 10.1979 | 9.9494 | 9.6811 | 9.4098 | 9.0309 | 8.2792 | 7.5075 | 6.7526 | 4.5576 | 2.4245 | 0.36605 | -1.078 | -1.049 | 335679 | 439130 | BISPHAM | PENWORTHAM
| Poynton | 9.2201 | 8.434 | 8.2143 | 8.1513 | 7.8366 | 7.7249 | 7.6048 | 7.4694 | 7.2825 | 7.1007 | 5.9018 | 3.9016 | 2.2299 | 0.40234 | -1.16 | 12.7201 | 11.934 | 11.7143 | 11.6513 | 11.3366 | 11.2249 | 11.1048 | 10.9694 | 10.7825 | 10.6007 | 9.4018 | 7.4016 | 5.7299 | 3.9023 | 2.2586 | 9.2201 | 8.9786 | 8.8589 | 8.7665 | 8.6413 | 8.4942 | 8.3036 | 8.0675 | 7.8794 | 7.6848 | 7.0648 | 6.4027 | 5.717 | 4.9514 | 4.3961 | 12.7201 | 12.4786 | 12.3589 | 12.2665 | 12.1413 | 11.9942 | 11.8036 | 11.5675 | 11.3794 | 11.1848 | 10.5648 | 9.9027 | 9.217 | 8.4514 | 7.9813 | 9.2201 | 8.3288 | 8.1024 | 8.0695 | 7.7876 | 7.7153 | 7.6518 | 7.5796 | 7.4682 | 7.3502 | 6.3134 | 4.409 | 2.8157 | 1.1077 | -0.29364 | 12.7201 | 11.8288 | 11.6024 | 11.5695 | 11.2876 | 11.2153 | 11.1518 | 11.0796 | 10.9682 | 10.8502 | 9.8134 | 7.909 | 6.3157 | 4.6077 | 3.0943 | 9.2201 | 8.7591 | 8.6364 | 8.6098 | 8.3139 | 8.2072 | 7.9914 | 7.4186 | 6.7953 | 6.1608 | 4.2866 | 2.4967 | 1.0693 | 0.10192 | 0.59504 | 12.7201 | 12.2591 | 12.1364 | 12.1098 | 11.8139 | 11.7072 | 11.4914 | 10.9186 | 10.2953 | 9.6608 | 7.7866 | 5.9967 | 4.5693 | 3.6019 | 3.9811 | 9.2201 | 8.8447 | 8.7361 | 8.7185 | 8.4686 | 8.4038 | 8.3131 | 8.2101 | 8.049 | 7.8841 | 7.261 | 6.5409 | 6.0397 | 5.5449 | 5.2915 | 12.7201 | 12.3447 | 12.2361 | 12.2185 | 11.9686 | 11.9038 | 11.8131 | 11.7101 | 11.549 | 11.3841 | 10.761 | 10.0409 | 9.5397 | 9.0449 | 8.7939 | 9.2201 | 8.3516 | 8.0963 | 8.006 | 7.655 | 7.5152 | 7.2601 | 6.6342 | 5.9815 | 5.3171 | 3.3196 | 1.386 | -0.18439 | -1.3001 | -0.95011 | 12.7201 | 11.8516 | 11.5963 | 11.506 | 11.155 | 11.0152 | 10.7601 | 10.1342 | 9.4815 | 8.8171 | 6.8196 | 4.886 | 3.3156 | 2.1999 | 2.4666 | 392096 | 383493 | HAZEL GROVE | BREDBURY
| Preesall | 13.4607 | 12.726 | 12.5028 | 12.3367 | 12.0828 | 11.8203 | 11.5833 | 11.3517 | 11.0931 | 10.8612 | 9.6507 | 7.7219 | 6.2123 | 4.7046 | 3.2343 | 17.9607 | 17.226 | 17.0028 | 16.8367 | 16.5828 | 16.3203 | 16.0833 | 15.8517 | 15.5931 | 15.3612 | 14.1507 | 12.2219 | 10.7123 | 9.2046 | 7.7144 | 13.4607 | 13.1377 | 12.9974 | 12.823 | 12.5937 | 12.3561 | 12.0456 | 11.6156 | 11.2948 | 10.9667 | 9.9742 | 8.9675 | 7.9995 | 6.9466 | 6.2405 | 17.9607 | 17.6377 | 17.4974 | 17.323 | 17.0937 | 16.8561 | 16.5456 | 16.1156 | 15.7948 | 15.4667 | 14.4742 | 13.4675 | 12.4995 | 11.4466 | 10.8605 | 13.4607 | 12.6566 | 12.4413 | 12.3127 | 12.1011 | 11.8889 | 11.7223 | 11.5675 | 11.3882 | 11.2249 | 10.2264 | 8.3874 | 6.7367 | 5.2738 | 4.0811 | 17.9607 | 17.1566 | 16.9413 | 16.8127 | 16.6011 | 16.3889 | 16.2223 | 16.0675 | 15.8882 | 15.7249 | 14.7264 | 12.8874 | 11.2367 | 9.7738 | 8.6327 | 13.4607 | 13.065 | 12.9531 | 12.8456 | 12.6585 | 12.4544 | 12.1934 | 11.6517 | 11.078 | 10.5146 | 8.8761 | 7.2183 | 6.006 | 5.2388 | 5.5033 | 17.9607 | 17.565 | 17.4531 | 17.3456 | 17.1585 | 16.9544 | 16.6934 | 16.1517 | 15.578 | 15.0146 | 13.3761 | 11.7183 | 10.506 | 9.7388 | 9.9391 | 13.4607 | 13.0481 | 12.9034 | 12.7787 | 12.6184 | 12.4462 | 12.2529 | 12.0048 | 11.6831 | 11.3633 | 10.278 | 8.9619 | 8.0154 | 7.1329 | 6.7033 | 17.9607 | 17.5481 | 17.4034 | 17.2787 | 17.1184 | 16.9462 | 16.7529 | 16.5048 | 16.1831 | 15.8633 | 14.778 | 13.4619 | 12.5154 | 11.6329 | 11.2291 | 13.4607 | 12.7399 | 12.5041 | 12.3083 | 12.039 | 11.7752 | 11.441 | 10.8016 | 9.5585 | 8.3259 | 4.682 | 1.0627 | -2.0903 | -5.4136 | -8.3204 | 17.9607 | 17.2399 | 17.0041 | 16.8083 | 16.539 | 16.2752 | 15.941 | 15.3016 | 14.0585 | 12.8259 | 9.182 | 5.5627 | 2.4097 | -0.91359 | -3.2477 | 336965 | 446547 | THORNTON | STANAH
| Preston East | 16.3119 | 12.657 | 11.9889 | 11.7904 | 11.5821 | 11.3565 | 11.1189 | 10.8403 | 10.4409 | 10.0423 | 8.3235 | 5.863 | 3.9635 | 2.1727 | 0.70313 | 20.1519 | 16.497 | 15.8289 | 15.6304 | 15.4221 | 15.1965 | 14.9589 | 14.6803 | 14.2809 | 13.8823 | 12.1635 | 9.703 | 7.8035 | 6.0127 | 4.4396 | 16.3119 | 15.7573 | 15.6515 | 15.4799 | 15.3181 | 15.124 | 14.8873 | 14.6073 | 14.2819 | 13.9485 | 12.9148 | 11.8637 | 10.9077 | 9.9404 | 9.3355 | 20.1519 | 19.5973 | 19.4915 | 19.3199 | 19.1581 | 18.964 | 18.7273 | 18.4473 | 18.1219 | 17.7885 | 16.7548 | 15.7037 | 14.7477 | 13.7804 | 13.2464 | 16.3119 | 12.0918 | 11.3272 | 11.1311 | 10.9302 | 10.7175 | 10.4983 | 10.2479 | 9.9358 | 9.6277 | 8.108 | 5.7743 | 4.008 | 2.4747 | 1.3992 | 20.1519 | 15.9318 | 15.1672 | 14.9711 | 14.7702 | 14.5575 | 14.3383 | 14.0879 | 13.7758 | 13.4677 | 11.948 | 9.6143 | 7.848 | 6.3147 | 5.0624 | 16.3119 | 13.3637 | 12.8767 | 12.7479 | 12.5978 | 12.3928 | 12.0872 | 11.3766 | 10.5464 | 9.7178 | 7.3113 | 5.1265 | 3.5407 | 2.6915 | 3.4452 | 20.1519 | 17.2037 | 16.7167 | 16.5879 | 16.4378 | 16.2328 | 15.9272 | 15.2166 | 14.3864 | 13.5578 | 11.1513 | 8.9665 | 7.3807 | 6.5315 | 7.098 | 16.3119 | 15.4876 | 15.353 | 15.2299 | 15.1341 | 14.987 | 14.7873 | 14.5524 | 14.1931 | 13.8211 | 12.6091 | 11.376 | 10.5362 | 9.917 | 9.8667 | 20.1519 | 19.3276 | 19.193 | 19.0699 | 18.9741 | 18.827 | 18.6273 | 18.3924 | 18.0331 | 17.6611 | 16.4491 | 15.216 | 14.3762 | 13.757 | 13.6594 | 16.3119 | 11.6186 | 10.7637 | 10.552 | 10.3338 | 10.1085 | 9.797 | 9.1351 | 8.2938 | 7.4569 | 4.9868 | 2.6978 | 0.99551 | 0.061445 | 0.72983 | 20.1519 | 15.4586 | 14.6037 | 14.392 | 14.1738 | 13.9485 | 13.637 | 12.9751 | 12.1338 | 11.2969 | 8.8268 | 6.5378 | 4.8355 | 3.9014 | 4.4054 | 356777 | 432926 | PRESTON EAST | PENWORTHAM
| Preston Old Rd | 12.2951 | 10.8007 | 10.5481 | 10.5547 | 10.5029 | 10.4364 | 10.373 | 10.3126 | 10.2181 | 10.1443 | 8.9976 | 6.6299 | 4.5942 | 2.3289 | 0.44635 | 16.9321 | 15.4377 | 15.1851 | 15.1917 | 15.1399 | 15.0734 | 15.01 | 14.9496 | 14.8551 | 14.7813 | 13.6346 | 11.2669 | 9.2312 | 6.9659 | 4.9174 | 12.2951 | 11.9019 | 11.8128 | 11.771 | 11.6785 | 11.5677 | 11.4064 | 11.206 | 11.0539 | 10.8971 | 10.4141 | 9.9344 | 9.4287 | 8.8702 | 8.4492 | 16.9321 | 16.5389 | 16.4498 | 16.408 | 16.3155 | 16.2047 | 16.0434 | 15.843 | 15.6909 | 15.5341 | 15.0511 | 14.5714 | 14.0657 | 13.5072 | 13.1533 | 12.2951 | 10.5731 | 10.2986 | 10.337 | 10.3204 | 10.2946 | 10.2901 | 10.2903 | 10.261 | 10.2434 | 9.2752 | 7.0604 | 5.1573 | 3.038 | 1.3122 | 16.9321 | 15.2101 | 14.9356 | 14.974 | 14.9574 | 14.9316 | 14.9271 | 14.9273 | 14.898 | 14.8804 | 13.9122 | 11.6974 | 9.7943 | 7.675 | 5.7553 | 12.2951 | 11.3321 | 11.209 | 11.2454 | 11.2031 | 11.1311 | 10.9193 | 10.2221 | 9.4891 | 8.7612 | 6.636 | 4.552 | 2.8491 | 1.77 | 2.671 | 16.9321 | 15.9691 | 15.846 | 15.8824 | 15.8401 | 15.7681 | 15.5563 | 14.8591 | 14.1261 | 13.3982 | 11.273 | 9.189 | 7.4861 | 6.407 | 7.1104 | 12.2951 | 11.6015 | 11.5215 | 11.5851 | 11.6175 | 11.6182 | 11.5931 | 11.5628 | 11.4824 | 11.407 | 11.0371 | 10.4955 | 10.1027 | 9.6778 | 9.4238 | 16.9321 | 16.2385 | 16.1585 | 16.2221 | 16.2545 | 16.2552 | 16.2301 | 16.1998 | 16.1194 | 16.044 | 15.6741 | 15.1325 | 14.7397 | 14.3148 | 14.0504 | 12.2951 | 10.5543 | 10.2353 | 10.1915 | 10.0764 | 9.9568 | 9.6849 | 8.9053 | 8.109 | 7.318 | 5.0066 | 2.779 | 0.93324 | -0.33109 | 0.34991 | 16.9321 | 15.1913 | 14.8723 | 14.8285 | 14.7134 | 14.5938 | 14.3219 | 13.5423 | 12.746 | 11.955 | 9.6436 | 7.416 | 5.5702 | 4.3059 | 4.8393 | 332562 | 434929 | BLACKPOOL | PENWORTHAM
| Prestwich | 8.1177 | 7.1392 | 6.7375 | 6.4148 | 6.0044 | 5.576 | 5.1551 | 4.7476 | 4.3173 | 3.8822 | 1.7066 | -1.4449 | -3.8095 | -6.0232 | -7.6483 | 12.7547 | 11.7762 | 11.3745 | 11.0518 | 10.6414 | 10.213 | 9.7921 | 9.3846 | 8.9543 | 8.5192 | 6.3436 | 3.1921 | 0.82746 | -1.3862 | -3.135 | 8.1177 | 7.6966 | 7.4749 | 7.2654 | 6.9408 | 6.5886 | 6.1525 | 5.6336 | 5.2429 | 4.8388 | 3.6238 | 2.4319 | 1.3267 | 0.15101 | -0.71317 | 12.7547 | 12.3336 | 12.1119 | 11.9024 | 11.5778 | 11.2256 | 10.7895 | 10.2706 | 9.8799 | 9.4758 | 8.2608 | 7.0689 | 5.9637 | 4.788 | 4.0675 | 8.1177 | 6.9406 | 6.4341 | 6.0342 | 5.5419 | 5.0287 | 4.5369 | 4.0136 | 3.4411 | 2.8758 | 0.35763 | -2.8106 | -4.9674 | -6.7466 | -7.6077 | 12.7547 | 11.5776 | 11.0711 | 10.6712 | 10.1789 | 9.6657 | 9.1739 | 8.6506 | 8.0781 | 7.5128 | 4.9946 | 1.8264 | -0.33044 | -2.1096 | -3.0812 | 8.1177 | 7.5714 | 7.2438 | 6.934 | 6.4894 | 5.9681 | 5.3109 | 4.2089 | 3.1019 | 2.0276 | -1.0408 | -3.7662 | -5.4693 | -6.3428 | -5.8656 | 12.7547 | 12.2084 | 11.8808 | 11.571 | 11.1264 | 10.6051 | 9.9479 | 8.8459 | 7.7389 | 6.6646 | 3.5962 | 0.87076 | -0.83231 | -1.7058 | -1.3517 | 8.1177 | 7.4625 | 7.1956 | 7.0013 | 6.7551 | 6.4498 | 6.1109 | 5.7652 | 5.354 | 4.9379 | 3.4435 | 1.8473 | 0.69948 | -0.44021 | -1.2436 | 12.7547 | 12.0995 | 11.8326 | 11.6383 | 11.3921 | 11.0868 | 10.7479 | 10.4022 | 9.991 | 9.5749 | 8.0805 | 6.4843 | 5.3365 | 4.1968 | 3.4955 | 8.1177 | 7.1265 | 6.5672 | 6.1001 | 5.5199 | 4.9236 | 4.1769 | 2.9352 | 1.7231 | 0.54648 | -2.7887 | -5.6588 | -7.5123 | -8.5511 | -8.3113 | 12.7547 | 11.7635 | 11.2042 | 10.7371 | 10.1569 | 9.5606 | 8.8139 | 7.5722 | 6.3601 | 5.1835 | 1.8483 | -1.0218 | -2.8753 | -3.9141 | -3.74 | 381392 | 404001 | AGECROFT | KEARSLEY
| Pringle St | 9.4781 | 8.5579 | 8.1545 | 7.8465 | 7.4207 | 6.9736 | 6.5432 | 6.1434 | 5.7489 | 5.3713 | 3.5734 | 0.70607 | -1.8277 | -4.3398 | -6.541 | 17.0381 | 16.1179 | 15.7145 | 15.4065 | 14.9807 | 14.5336 | 14.1032 | 13.7034 | 13.3089 | 12.9313 | 11.1334 | 8.2661 | 5.7323 | 3.2202 | 0.86698 | 9.4781 | 9.0335 | 8.8081 | 8.624 | 8.3985 | 8.148 | 7.8381 | 7.4668 | 7.2066 | 6.9411 | 6.2233 | 5.368 | 3.9127 | 2.26 | 1.2671 | 17.0381 | 16.5935 | 16.3681 | 16.184 | 15.9585 | 15.708 | 15.3981 | 15.0268 | 14.7666 | 14.5011 | 13.7833 | 12.928 | 11.4727 | 9.82 | 8.947 | 9.4781 | 8.4695 | 8.0019 | 7.6509 | 7.1881 | 6.7096 | 6.2524 | 5.8357 | 5.4308 | 5.0413 | 3.2463 | 0.65809 | -1.6569 | -4.1119 | -6.1937 | 17.0381 | 16.0295 | 15.5619 | 15.2109 | 14.7481 | 14.2696 | 13.8124 | 13.3957 | 12.9908 | 12.6013 | 10.8063 | 8.2181 | 5.9031 | 3.4481 | 1.1901 | 9.4781 | 8.912 | 8.5479 | 8.2209 | 7.7621 | 7.2707 | 6.6211 | 5.4471 | 4.2466 | 3.0619 | -0.010487 | -2.4408 | -4.6168 | -5.9489 | -5.1478 | 17.0381 | 16.472 | 16.1079 | 15.7809 | 15.3221 | 14.8307 | 14.1811 | 13.0071 | 11.8066 | 10.6219 | 7.5495 | 5.1192 | 2.9432 | 1.6111 | 2.2239 | 9.4781 | 8.684 | 8.3312 | 8.0969 | 7.8368 | 7.5534 | 7.2343 | 6.8778 | 6.4758 | 6.0624 | 4.9963 | 4.0516 | 2.836 | 1.4402 | 0.89165 | 17.0381 | 16.244 | 15.8912 | 15.6569 | 15.3968 | 15.1134 | 14.7943 | 14.4378 | 14.0358 | 13.6224 | 12.5563 | 11.6116 | 10.396 | 9.0002 | 8.4811 | 9.4781 | 8.5833 | 8.1104 | 7.7167 | 7.1977 | 6.6681 | 5.9834 | 4.7467 | 3.5131 | 2.2932 | -0.90135 | -3.4736 | -5.8618 | -7.4755 | -6.9624 | 17.0381 | 16.1433 | 15.6704 | 15.2767 | 14.7577 | 14.2281 | 13.5434 | 12.3067 | 11.0731 | 9.8532 | 6.6586 | 4.0864 | 1.6982 | 0.084533 | 0.46758 | 369088 | 427387 | BLACKBURN | PENWORTHAM
| Queens Park | 10.7872 | 2.7321 | 0.40858 | -0.54481 | -1.6796 | -1.0348 | -2.2044 | -3.4012 | -4.6486 | -5.8943 | -9.7173 | -13.402 | -16.6451 | -20.4188 | -21.9421 | 12.5872 | 4.5321 | 2.2086 | 1.2552 | 0.12044 | -1.0348 | -2.2044 | -3.4012 | -4.6486 | -5.8943 | -9.7173 | -13.402 | -16.6451 | -20.4188 | -21.9935 | 10.7872 | 8.0165 | 6.8383 | 5.9774 | 5.1054 | 6.0121 | 5.0902 | 4.1404 | 3.1412 | 2.13 | -0.92925 | -3.9947 | -6.9847 | -10.7288 | -12.2634 | 12.5872 | 9.8165 | 8.6383 | 7.7774 | 6.9054 | 6.0121 | 5.0902 | 4.1404 | 3.1412 | 2.13 | -0.92925 | -3.9947 | -6.9847 | -10.7288 | -12.1978 | 10.7872 | 1.5748 | -1.0114 | -2.0033 | -3.1754 | -2.5673 | -3.7724 | -5.0038 | -6.2613 | -7.5194 | -11.4152 | -15.1084 | -18.2791 | -21.8655 | -23.0219 | 12.5872 | 3.3748 | 0.78858 | -0.20334 | -1.3754 | -2.5673 | -3.7724 | -5.0038 | -6.2613 | -7.5194 | -11.4152 | -15.1084 | -18.2791 | -21.8655 | -23.0964 | 10.7872 | 3.9385 | 1.8733 | 0.9393 | -0.19181 | 0.41756 | -0.84315 | -2.2535 | -3.6869 | -5.1117 | -9.1679 | -12.6715 | -15.6498 | -18.9345 | -19.6689 | 12.5872 | 5.7385 | 3.6733 | 2.7393 | 1.6082 | 0.41756 | -0.84315 | -2.2535 | -3.6869 | -5.1117 | -9.1679 | -12.6715 | -15.6498 | -18.9345 | -19.7523 | 10.7872 | 6.4873 | 4.9643 | 4.0797 | 3.0421 | 3.756 | 2.6257 | 1.4645 | 0.24016 | -0.99665 | -4.6312 | -7.9257 | -10.8795 | -14.4251 | -15.6512 | 12.5872 | 8.2873 | 6.7643 | 5.8797 | 4.8421 | 3.756 | 2.6257 | 1.4645 | 0.24016 | -0.99665 | -4.6312 | -7.9257 | -10.8795 | -14.4251 | -15.6453 | 10.7872 | 0.53974 | -2.2654 | -3.2641 | -4.4464 | -3.8448 | -5.1013 | -6.536 | -7.989 | -9.4303 | -13.5518 | -17.1308 | -20.1894 | -23.5287 | -24.3308 | 12.5872 | 2.3397 | -0.46538 | -1.4641 | -2.6464 | -3.8448 | -5.1013 | -6.536 | -7.989 | -9.4303 | -13.5518 | -17.1308 | -20.1894 | -23.5287 | -24.3955 | 385893 | 400645 | STUART ST | STALYBRIDGE | Firm Capacity marginally exceeded in FY27. A third transformer to be installed in RIIO-ED2.
| Radcliffe | 8.1587 | 5.8427 | 5.1268 | 4.6325 | 3.9609 | 3.2603 | 2.5865 | 1.927 | 1.087 | 0.27347 | -4.8055 | -11.4301 | -16.4103 | -21.0205 | -24.2178 | 8.5587 | 6.2427 | 5.5268 | 5.0325 | 4.3609 | 3.6603 | 2.9865 | 2.327 | 1.487 | 0.67347 | -4.4055 | -11.0301 | -16.0103 | -20.6205 | -24.0854 | 8.1587 | 7.2647 | 6.9988 | 6.6684 | 6.2126 | 5.6917 | 5.0206 | 4.1918 | 3.4429 | 2.6131 | -0.28102 | -2.9147 | -5.4634 | -8.3863 | -10.1724 | 8.5587 | 7.6647 | 7.3988 | 7.0684 | 6.6126 | 6.0917 | 5.4206 | 4.5918 | 3.8429 | 3.0131 | 0.11898 | -2.5147 | -5.0634 | -7.9863 | -9.4879 | 8.1587 | 5.4113 | 4.4801 | 3.8456 | 3.0264 | 2.1767 | 1.384 | 0.59243 | -0.32288 | -1.2855 | -7.2787 | -13.9736 | -18.539 | -22.1991 | -23.8355 | 8.5587 | 5.8113 | 4.8801 | 4.2456 | 3.4264 | 2.5767 | 1.784 | 0.99243 | 0.077124 | -0.88554 | -6.8787 | -13.5736 | -18.139 | -21.7991 | -23.6715 | 8.1587 | 6.6788 | 6.0846 | 5.1263 | 3.933 | 3.0863 | 1.9263 | -0.28357 | -2.5543 | -4.768 | -11.0144 | -16.2547 | -19.6585 | -21.4917 | -20.4509 | 8.5587 | 7.0788 | 6.4846 | 5.5263 | 4.333 | 3.4863 | 2.3263 | 0.11643 | -2.1543 | -4.368 | -10.6144 | -15.8547 | -19.2585 | -21.0917 | -20.3125 | 8.1587 | 6.7456 | 6.323 | 6.0221 | 5.6552 | 5.1818 | 4.6251 | 4.032 | 3.2245 | 2.3751 | -1.1442 | -4.698 | -7.225 | -9.56 | -11.0388 | 8.5587 | 7.1456 | 6.723 | 6.4221 | 6.0552 | 5.5818 | 5.0251 | 4.432 | 3.6245 | 2.7751 | -0.74418 | -4.298 | -6.825 | -9.16 | -10.463 | 8.1587 | 5.6493 | 4.6546 | 3.446 | 2.031 | 1.045 | -0.28631 | -2.7413 | -5.1987 | -7.5975 | -14.4517 | -20.2335 | -23.9544 | -26.1242 | -25.5549 | 8.5587 | 6.0493 | 5.0546 | 3.846 | 2.431 | 1.445 | 0.11369 | -2.3413 | -4.7987 | -7.1975 | -14.0517 | -19.8335 | -23.5544 | -25.7242 | -25.3016 | 377524 | 406160 | - | KEARSLEY
| Randal St | 4.8698 | 4.5432 | 4.0762 | 3.666 | 3.2787 | 2.8939 | 2.5235 | 2.14 | 1.7211 | 1.3188 | 0.001133 | -1.4963 | -3.5164 | -5.6585 | -7.2823 | 17.5698 | 17.2432 | 16.7762 | 16.366 | 15.9787 | 15.5939 | 15.2235 | 14.84 | 14.4211 | 14.0188 | 12.7011 | 11.2037 | 9.1836 | 7.0415 | 5.2247 | 4.8698 | 4.6487 | 4.2904 | 3.9672 | 3.6446 | 3.2728 | 2.8432 | 2.3514 | 2.0601 | 1.7696 | 1.0341 | 0.49405 | 0.036409 | -0.39671 | -0.66131 | 17.5698 | 17.3487 | 16.9904 | 16.6672 | 16.3446 | 15.9728 | 15.5432 | 15.0514 | 14.7601 | 14.4696 | 13.7341 | 13.194 | 12.7364 | 12.3033 | 12.0681 | 4.8698 | 4.538 | 4.01 | 3.5368 | 3.0886 | 2.6434 | 2.2115 | 1.7674 | 1.3368 | 0.92925 | -0.33685 | -1.6466 | -3.3423 | -5.2099 | -6.4859 | 17.5698 | 17.238 | 16.71 | 16.2368 | 15.7886 | 15.3434 | 14.9115 | 14.4674 | 14.0368 | 13.6292 | 12.3632 | 11.0534 | 9.3577 | 7.4901 | 5.9559 | 4.8698 | 4.6529 | 4.2184 | 3.831 | 3.4602 | 3.0592 | 2.5765 | 1.8351 | 1.0505 | 0.28778 | -2.2368 | -4.3654 | -6.0673 | -7.0567 | -5.896 | 17.5698 | 17.3529 | 16.9184 | 16.531 | 16.1602 | 15.7592 | 15.2765 | 14.5351 | 13.7505 | 12.9878 | 10.4632 | 8.3346 | 6.6327 | 5.6433 | 6.5399 | 4.8698 | 4.564 | 4.1364 | 3.7852 | 3.4778 | 3.1386 | 2.7745 | 2.4023 | 1.9894 | 1.5804 | 0.6369 | 0.057466 | -0.31644 | -0.57732 | -0.45824 | 17.5698 | 17.264 | 16.8364 | 16.4852 | 16.1778 | 15.8386 | 15.4745 | 15.1023 | 14.6894 | 14.2804 | 13.3369 | 12.7575 | 12.3836 | 12.1227 | 12.1771 | 4.8698 | 4.5744 | 4.0461 | 3.5541 | 3.0866 | 2.6246 | 2.0844 | 1.249 | 0.42673 | -0.36979 | -2.945 | -5.1473 | -6.9597 | -8.0845 | -7.0865 | 17.5698 | 17.2744 | 16.7461 | 16.2541 | 15.7866 | 15.3246 | 14.7844 | 13.949 | 13.1267 | 12.3302 | 9.755 | 7.5527 | 5.7403 | 4.6155 | 5.3952 | 368092 | 428515 | BLACKBURN | PENWORTHAM
| Rawtenstall Rd | 10.878 | 10.524 | 10.2349 | 10.0163 | 9.7522 | 9.4684 | 9.1937 | 8.9155 | 8.6033 | 8.3009 | 6.5283 | 3.7845 | 1.6941 | -0.3306 | -1.7393 | 15.515 | 15.161 | 14.8719 | 14.6533 | 14.3892 | 14.1054 | 13.8307 | 13.5525 | 13.2403 | 12.9379 | 11.1653 | 8.4215 | 6.3311 | 4.3064 | 2.7502 | 10.878 | 10.6588 | 10.4662 | 10.3062 | 10.1482 | 9.9767 | 9.7281 | 9.3854 | 9.1468 | 8.9 | 8.1079 | 7.2251 | 6.3646 | 5.3874 | 4.6554 | 15.515 | 15.2958 | 15.1032 | 14.9432 | 14.7852 | 14.6137 | 14.3651 | 14.0224 | 13.7838 | 13.537 | 12.7449 | 11.8621 | 11.0016 | 10.0244 | 9.4166 | 10.878 | 10.4244 | 9.8941 | 9.4405 | 8.931 | 8.3948 | 7.873 | 7.3323 | 6.7817 | 6.2144 | 3.8412 | 1.1225 | -0.70974 | -2.2002 | -2.7872 | 15.515 | 15.0614 | 14.5311 | 14.0775 | 13.568 | 13.0318 | 12.51 | 11.9693 | 11.4187 | 10.8514 | 8.4782 | 5.7595 | 3.9273 | 2.4368 | 1.7035 | 10.878 | 10.7416 | 10.2914 | 9.8668 | 9.3677 | 8.831 | 8.1499 | 6.9818 | 5.8329 | 4.7078 | 1.6862 | -0.58143 | -1.9549 | -2.5266 | -1.8215 | 15.515 | 15.3786 | 14.9284 | 14.5038 | 14.0047 | 13.468 | 12.7869 | 11.6188 | 10.4699 | 9.3448 | 6.3232 | 4.0556 | 2.6821 | 2.1104 | 2.6625 | 10.878 | 10.572 | 10.3164 | 10.1451 | 9.9807 | 9.788 | 9.5665 | 9.316 | 9.002 | 8.6832 | 7.621 | 6.502 | 5.7241 | 4.9394 | 4.3472 | 15.515 | 15.209 | 14.9534 | 14.7821 | 14.6177 | 14.425 | 14.2035 | 13.953 | 13.639 | 13.3202 | 12.258 | 11.139 | 10.3611 | 9.5764 | 9.0615 | 10.878 | 10.6149 | 10.0936 | 9.6058 | 9.0484 | 8.471 | 7.7382 | 6.5046 | 5.3154 | 4.148 | 0.9785 | -1.4252 | -2.9426 | -3.6954 | -3.212 | 15.515 | 15.2519 | 14.7306 | 14.2428 | 13.6854 | 13.108 | 12.3752 | 11.1416 | 9.9524 | 8.785 | 5.6155 | 3.2118 | 1.6944 | 0.94159 | 1.3211 | 379395 | 422143 | ROSSENDALE | PADIHAM
| Reddish Vale | 8.5292 | 8.3776 | 8.237 | 8.0708 | 7.8219 | 7.5738 | 7.3522 | 7.1536 | 6.9156 | 6.7042 | 5.041 | 1.981 | -0.62092 | -3.4646 | -6.0472 | 17.5292 | 17.3776 | 17.237 | 17.0708 | 16.8219 | 16.5738 | 16.3522 | 16.1536 | 15.9156 | 15.7042 | 14.041 | 10.981 | 8.3791 | 5.5354 | 2.8268 | 8.5292 | 8.3654 | 8.2174 | 8.0568 | 7.8436 | 7.6221 | 7.3391 | 6.9836 | 6.6789 | 6.3694 | 5.4507 | 4.5562 | 3.6928 | 2.7335 | 1.9925 | 17.5292 | 17.3654 | 17.2174 | 17.0568 | 16.8436 | 16.6221 | 16.3391 | 15.9836 | 15.6789 | 15.3694 | 14.4507 | 13.5562 | 12.6928 | 11.7335 | 11.1183 | 8.5292 | 8.3938 | 8.2766 | 8.1581 | 7.9548 | 7.7601 | 7.6117 | 7.4934 | 7.2635 | 7.107 | 5.6683 | 2.8126 | 0.35631 | -2.3326 | -4.7056 | 17.5292 | 17.3938 | 17.2766 | 17.1581 | 16.9548 | 16.7601 | 16.6117 | 16.4934 | 16.2635 | 16.107 | 14.6683 | 11.8126 | 9.3563 | 6.6674 | 4.1309 | 8.5292 | 8.6355 | 8.5929 | 8.498 | 8.2942 | 8.0653 | 7.6905 | 6.7626 | 5.7117 | 4.725 | 1.9005 | -0.85671 | -3.1255 | -4.672 | -3.9357 | 17.5292 | 17.6355 | 17.5929 | 17.498 | 17.2942 | 17.0653 | 16.6905 | 15.7626 | 14.7117 | 13.725 | 10.9005 | 8.1433 | 5.8745 | 4.328 | 4.8963 | 8.5292 | 8.4008 | 8.3001 | 8.2247 | 8.1095 | 7.9714 | 7.8165 | 7.6569 | 7.4249 | 7.1967 | 6.3966 | 5.4555 | 4.7709 | 4.0011 | 3.5141 | 17.5292 | 17.4008 | 17.3001 | 17.2247 | 17.1095 | 16.9714 | 16.8165 | 16.6569 | 16.4249 | 16.1967 | 15.3966 | 14.4555 | 13.7709 | 13.0011 | 12.551 | 8.5292 | 8.5777 | 8.4448 | 8.2404 | 7.9446 | 7.6562 | 7.2096 | 6.1771 | 5.0443 | 3.9817 | 0.95524 | -1.9745 | -4.4285 | -6.2172 | -5.7675 | 17.5292 | 17.5777 | 17.4448 | 17.2404 | 16.9446 | 16.6562 | 16.2096 | 15.1771 | 14.0443 | 12.9817 | 9.9552 | 7.0255 | 4.5715 | 2.7828 | 3.1281 | 390147 | 393309 | VERNON PARK | BREDBURY
| Ribblesdale T13 & T14 | 1.9417 | 0.6053 | 0.24415 | 0.10247 | -0.061307 | -0.22874 | -0.38504 | -0.53953 | -0.98047 | -1.1639 | -2.277 | -4.1844 | -5.8982 | -7.6735 | -9.3444 | 4.7417 | 3.4053 | 3.0441 | 2.9025 | 2.7387 | 2.5713 | 2.415 | 2.2605 | 1.8195 | 1.6361 | 0.52301 | -1.3844 | -3.0982 | -4.8735 | -6.6741 | 1.9417 | 1.2732 | 1.0091 | 0.83666 | 0.6781 | 0.52108 | 0.31891 | 0.049826 | -0.18779 | -0.42074 | -1.3122 | -2.0274 | -2.6459 | -3.3612 | -4.0994 | 4.7417 | 4.0732 | 3.8091 | 3.6367 | 3.4781 | 3.3211 | 3.1189 | 2.8498 | 2.6122 | 2.3793 | 1.4878 | 0.77257 | 0.15407 | -0.5612 | -1.2166 | 1.9417 | 0.40814 | 0.012494 | -0.1316 | -0.2956 | -0.46227 | -0.61912 | -1.0103 | -1.1649 | -1.2979 | -2.3088 | -4.4203 | -5.7663 | -7.0934 | -8.3059 | 4.7417 | 3.2081 | 2.8125 | 2.6684 | 2.5044 | 2.3377 | 2.1809 | 1.7897 | 1.6351 | 1.5021 | 0.4912 | -1.6203 | -2.9663 | -4.2934 | -5.689 | 1.9417 | 0.96736 | 0.6938 | 0.57246 | 0.43352 | -0.022568 | -0.26283 | -0.83855 | -1.9065 | -2.4873 | -4.1767 | -5.7798 | -7.2892 | -8.2358 | -7.3248 | 4.7417 | 3.7674 | 3.4938 | 3.3725 | 3.2335 | 2.7774 | 2.5372 | 1.9615 | 0.89353 | 0.31273 | -1.3767 | -2.9798 | -4.4892 | -5.4358 | -4.7336 | 1.9417 | 0.82581 | 0.51345 | 0.39704 | 0.30203 | 0.20763 | 0.096616 | -0.036731 | -0.48483 | -0.68933 | -1.364 | -2.1445 | -2.8217 | -3.2667 | -3.3905 | 4.7417 | 3.6258 | 3.3135 | 3.197 | 3.102 | 3.0076 | 2.8966 | 2.7633 | 2.3152 | 2.1107 | 1.436 | 0.65546 | -0.021691 | -0.46667 | -0.61692 | 1.9417 | 0.35099 | -0.066043 | -0.2349 | -0.41793 | -0.90227 | -1.1673 | -1.7854 | -2.8684 | -3.4631 | -5.1951 | -6.8463 | -8.5176 | -9.6876 | -9.0764 | 4.7417 | 3.151 | 2.734 | 2.5651 | 2.3821 | 1.8977 | 1.6327 | 1.0146 | -0.068357 | -0.66308 | -2.3951 | -4.0463 | -5.7176 | -6.8876 | -6.4191 | 374759 | 443587 | PADIHAM | PADIHAM | Firm Capacity marginally exceeded in FY28. Review in RIIO-ED2 as the forecast overload is minimal.
| Ribbleton | 13.7014 | 11.2145 | 9.2555 | 7.7067 | 6.0555 | 4.3726 | 4.1492 | 3.8879 | 3.5699 | 3.2478 | 1.6144 | -0.709 | -2.5293 | -4.183 | -5.6649 | 17.8384 | 15.3515 | 13.3925 | 11.8437 | 10.1925 | 8.5096 | 8.2862 | 8.0249 | 7.7069 | 7.3848 | 5.7514 | 3.428 | 1.6077 | -0.046036 | -1.6259 | 13.7014 | 13.4514 | 12.8596 | 12.2971 | 11.7007 | 11.0852 | 10.8933 | 10.6364 | 10.4025 | 10.1525 | 9.3118 | 8.3819 | 7.4505 | 6.4739 | 5.8635 | 17.8384 | 17.5884 | 16.9966 | 16.4341 | 15.8377 | 15.2222 | 15.0303 | 14.7734 | 14.5395 | 14.2895 | 13.4488 | 12.5189 | 11.5875 | 10.6109 | 10.0816 | 13.7014 | 10.8198 | 8.8056 | 7.2842 | 5.6632 | 4.0182 | 3.8845 | 3.7005 | 3.4804 | 3.242 | 1.7756 | -0.52417 | -2.345 | -3.9378 | -5.2893 | 17.8384 | 14.9568 | 12.9426 | 11.4212 | 9.8002 | 8.1552 | 8.0215 | 7.8375 | 7.6174 | 7.379 | 5.9126 | 3.6128 | 1.792 | 0.1992 | -1.2762 | 13.7014 | 11.8547 | 10.0381 | 8.5296 | 6.9002 | 5.2294 | 4.9588 | 4.2863 | 3.5377 | 2.7638 | 0.45809 | -1.6572 | -3.2505 | -4.1064 | -3.5403 | 17.8384 | 15.9917 | 14.1751 | 12.6666 | 11.0372 | 9.3664 | 9.0958 | 8.4233 | 7.6747 | 6.9008 | 4.5951 | 2.4798 | 0.88646 | 0.030573 | 0.4669 | 13.7014 | 13.2889 | 11.714 | 10.2287 | 8.7169 | 7.1736 | 7.0604 | 6.8764 | 6.6109 | 6.3243 | 5.2728 | 4.179 | 3.4451 | 2.9057 | 2.7613 | 17.8384 | 17.4259 | 15.851 | 14.3657 | 12.8539 | 11.3106 | 11.1974 | 11.0134 | 10.7479 | 10.4613 | 9.4098 | 8.316 | 7.5821 | 7.0427 | 6.8808 | 13.7014 | 10.5931 | 8.5138 | 6.9505 | 4.0677 | 2.0679 | 1.4638 | 0.47144 | -0.5871 | -1.3754 | -3.8029 | -6.1139 | -7.9097 | -8.9425 | -8.5292 | 17.8384 | 14.7301 | 12.6508 | 11.0875 | 8.2047 | 6.2049 | 5.6008 | 4.6084 | 3.5499 | 2.7616 | 0.33411 | -1.9769 | -3.7727 | -4.8055 | -4.4881 | 356730 | 431506 | PRESTON EAST | PENWORTHAM
| Ringley | 16.1459 | 13.6385 | 13.0913 | 13.0648 | 13.0214 | 12.9684 | 12.9106 | 12.8436 | 12.7508 | 12.6615 | 12.1292 | 11.063 | 9.8435 | 8.5156 | 7.3225 | 16.1459 | 13.6385 | 13.0913 | 13.0648 | 13.0214 | 12.9684 | 12.9106 | 12.8436 | 12.7508 | 12.6615 | 12.1292 | 11.063 | 9.8435 | 8.5156 | 7.2397 | 16.1459 | 15.3798 | 15.1746 | 15.1326 | 15.0856 | 15.0242 | 14.9412 | 14.84 | 14.7559 | 14.6695 | 14.3985 | 14.1174 | 13.8501 | 13.397 | 13.1032 | 16.1459 | 15.3798 | 15.1746 | 15.1326 | 15.0856 | 15.0242 | 14.9412 | 14.84 | 14.7559 | 14.6695 | 14.3985 | 14.1174 | 13.8501 | 13.397 | 13.1427 | 16.1459 | 13.2235 | 12.592 | 12.5654 | 12.5231 | 12.4723 | 12.4169 | 12.3549 | 12.2854 | 12.2207 | 11.7504 | 10.945 | 9.9375 | 8.7607 | 7.6976 | 16.1459 | 13.2235 | 12.592 | 12.5654 | 12.5231 | 12.4723 | 12.4169 | 12.3549 | 12.2854 | 12.2207 | 11.7504 | 10.945 | 9.9375 | 8.7607 | 7.5915 | 16.1459 | 14.1526 | 13.726 | 13.7226 | 13.696 | 13.6489 | 13.5469 | 13.2939 | 13.0184 | 12.7443 | 11.6016 | 10.2385 | 9.1331 | 8.4518 | 8.9286 | 16.1459 | 14.1526 | 13.726 | 13.7226 | 13.696 | 13.6489 | 13.5469 | 13.2939 | 13.0184 | 12.7443 | 11.6016 | 10.2385 | 9.1331 | 8.4518 | 8.8209 | 16.1459 | 14.6647 | 14.3402 | 14.3413 | 14.3435 | 14.3261 | 14.2868 | 14.2347 | 14.1516 | 14.0657 | 13.7626 | 13.4333 | 13.2099 | 13.0324 | 13.0222 | 16.1459 | 14.6647 | 14.3402 | 14.3413 | 14.3435 | 14.3261 | 14.2868 | 14.2347 | 14.1516 | 14.0657 | 13.7626 | 13.4333 | 13.2099 | 13.0324 | 13.0028 | 16.1459 | 12.8895 | 12.182 | 12.1466 | 12.0919 | 12.032 | 11.9213 | 11.647 | 11.3622 | 11.0802 | 9.9164 | 8.4448 | 7.2323 | 6.4383 | 6.8029 | 16.1459 | 12.8895 | 12.182 | 12.1466 | 12.0919 | 12.032 | 11.9213 | 11.647 | 11.3622 | 11.0802 | 9.9164 | 8.4448 | 7.2323 | 6.4383 | 6.7195 | 376120 | 405531 | KEARSLEY LOCAL | KEARSLEY
| Risley | 4.7888 | 2.8315 | 2.4678 | 2.2938 | 2.0817 | 1.8586 | 1.6449 | 1.4138 | 1.0812 | 0.75729 | -0.89255 | -3.4294 | -5.446 | -7.4481 | -9.427 | 15.4888 | 13.5315 | 13.1678 | 12.9938 | 12.7817 | 12.5586 | 12.3449 | 12.1138 | 11.7812 | 11.4573 | 9.8074 | 7.2706 | 5.254 | 3.2519 | 1.1603 | 4.7888 | 4.0079 | 3.9069 | 3.7685 | 3.638 | 3.4823 | 3.2896 | 3.0654 | 2.775 | 2.4779 | 1.5622 | 0.57847 | -0.25717 | -1.1034 | -1.6783 | 15.4888 | 14.7079 | 14.6069 | 14.4685 | 14.338 | 14.1823 | 13.9896 | 13.7654 | 13.475 | 13.1779 | 12.2622 | 11.2785 | 10.4428 | 9.5966 | 9.0901 | 4.7888 | 2.554 | 2.1351 | 1.9614 | 1.7541 | 1.5394 | 1.3366 | 1.1233 | 0.85945 | 0.60959 | -0.85064 | -3.22 | -5.0657 | -6.7865 | -8.1347 | 15.4888 | 13.254 | 12.8351 | 12.6614 | 12.4541 | 12.2394 | 12.0366 | 11.8233 | 11.5594 | 11.3096 | 9.8494 | 7.48 | 5.6343 | 3.9135 | 2.3914 | 4.7888 | 3.2699 | 3.0428 | 2.9271 | 2.7002 | 2.4905 | 2.1483 | 1.4043 | 0.58591 | -0.22314 | -2.5787 | -4.7834 | -6.4989 | -7.5724 | -6.836 | 15.4888 | 13.9699 | 13.7428 | 13.6271 | 13.4002 | 13.1905 | 12.8483 | 12.1043 | 11.2859 | 10.4769 | 8.1213 | 5.9166 | 4.2011 | 3.1276 | 3.6792 | 4.7888 | 3.5348 | 3.3564 | 3.2654 | 3.1967 | 3.0827 | 2.9194 | 2.7187 | 2.3994 | 2.0692 | 0.97297 | -0.21188 | -0.98556 | -1.6051 | -1.6686 | 15.4888 | 14.2348 | 14.0564 | 13.9654 | 13.8967 | 13.7827 | 13.6194 | 13.4187 | 13.0994 | 12.7692 | 11.673 | 10.4881 | 9.7144 | 9.0949 | 8.9875 | 4.7888 | 2.3926 | 1.9263 | 1.73 | 1.4364 | 1.2067 | 0.85651 | 0.070263 | -0.77369 | -1.6045 | -4.0328 | -6.3119 | -8.1892 | -9.4914 | -8.8835 | 15.4888 | 13.0926 | 12.6263 | 12.43 | 12.1364 | 11.9067 | 11.5565 | 10.7703 | 9.9263 | 9.0955 | 6.6672 | 4.3881 | 2.5108 | 1.2086 | 1.6639 | 365181 | 392989 | - | BOLD
| Robert Hall St | 6.2195 | 2.8122 | 1.4163 | 0.63113 | -0.19705 | -1.0265 | -1.9727 | -2.9132 | -3.9093 | -4.4058 | -6.1443 | -8.4144 | -10.1562 | -12.0009 | -13.8566 | 13.2195 | 9.8122 | 8.4163 | 7.6311 | 6.8029 | 5.9735 | 5.0273 | 4.0868 | 3.0907 | 2.5942 | 0.85566 | -1.4144 | -3.1562 | -5.0009 | -6.6772 | 6.2195 | 5.0047 | 4.3847 | 3.951 | 3.5629 | 3.1754 | 2.736 | 2.2018 | 1.6917 | 1.1656 | -0.38891 | -1.9705 | -3.4123 | -5.0767 | -6.7348 | 13.2195 | 12.0047 | 11.3847 | 10.951 | 10.5629 | 10.1754 | 9.736 | 9.2018 | 8.6917 | 8.1656 | 6.6111 | 5.0295 | 3.5877 | 1.9233 | 0.57796 | 6.2195 | 2.2986 | 0.75405 | -0.081182 | -0.97374 | -1.8759 | -4.5489 | -7.5393 | -10.5489 | -11.8791 | -13.8629 | -16.1108 | -17.8944 | -19.7501 | -21.5472 | 13.2195 | 9.2986 | 7.7541 | 6.9188 | 6.0263 | 5.1241 | 2.4511 | -0.53927 | -3.5489 | -4.8791 | -6.8629 | -9.1108 | -10.8944 | -12.7501 | -14.3092 | 6.2195 | 3.4193 | 2.1334 | 1.3484 | 0.49243 | -0.38835 | -3.0828 | -6.2179 | -9.3789 | -10.8785 | -13.1778 | -15.3874 | -16.9595 | -18.3866 | -19.5929 | 13.2195 | 10.4193 | 9.1334 | 8.3484 | 7.4924 | 6.6117 | 3.9172 | 0.78209 | -2.3789 | -3.8785 | -6.1778 | -8.3874 | -9.9595 | -11.3866 | -12.3684 | 6.2195 | 4.099 | 2.9827 | 2.234 | 1.4636 | 0.68465 | -0.22054 | -1.1335 | -2.1338 | -2.6455 | -4.2013 | -5.8557 | -7.1036 | -8.5092 | -9.9676 | 13.2195 | 11.099 | 9.9827 | 9.234 | 8.4636 | 7.6846 | 6.7795 | 5.8665 | 4.8662 | 4.3545 | 2.7987 | 1.1443 | -0.10364 | -1.5092 | -2.7069 | 6.2195 | 1.9639 | 0.33737 | -0.50672 | -1.4164 | -2.3312 | -5.073 | -8.2654 | -11.462 | -12.9759 | -15.3921 | -17.6737 | -19.3161 | -20.8384 | -22.1908 | 13.2195 | 8.9639 | 7.3374 | 6.4933 | 5.5836 | 4.6688 | 1.927 | -1.2654 | -4.462 | -5.9759 | -8.3921 | -10.6737 | -12.3161 | -13.8384 | -14.9325 | 381359 | 397718 | FREDERICK RD | KEARSLEY | Firm Capacity marginally exceeded in FY28. Review in RIIO-ED2 as the forecast overload is minimal.
| Rochdale Central | 23.0311 | 22.2287 | 21.8941 | 21.3947 | 20.7857 | 20.1408 | 19.5007 | 18.87 | 18.1956 | 17.5397 | 14.1551 | 9.2252 | 5.6268 | 1.8854 | -1.3258 | 36.0311 | 35.2287 | 34.8941 | 34.3947 | 33.7857 | 33.1408 | 32.5007 | 31.87 | 31.1956 | 30.5397 | 27.1551 | 22.2252 | 18.6268 | 14.8854 | 11.4616 | 23.0311 | 22.6186 | 22.289 | 21.9847 | 21.6213 | 21.2151 | 20.7075 | 20.0928 | 19.7084 | 19.3141 | 18.0207 | 16.6051 | 15.2862 | 13.4289 | 12.0128 | 36.0311 | 35.6186 | 35.289 | 34.9847 | 34.6213 | 34.2151 | 33.7075 | 33.0928 | 32.7084 | 32.3141 | 31.0207 | 29.6051 | 28.2862 | 26.4289 | 25.2057 | 23.0311 | 22.1433 | 21.8118 | 21.3438 | 20.7787 | 20.151 | 19.5115 | 18.8599 | 18.2218 | 17.6088 | 14.6797 | 10.2126 | 6.8459 | 3.4169 | 0.60401 | 36.0311 | 35.1433 | 34.8118 | 34.3438 | 33.7787 | 33.151 | 32.5115 | 31.8599 | 31.2218 | 30.6088 | 27.6797 | 23.2126 | 19.8459 | 16.4169 | 13.325 | 23.0311 | 22.7125 | 22.545 | 22.1412 | 21.6081 | 21.0217 | 20.1845 | 18.5569 | 16.8442 | 15.152 | 10.2405 | 5.8909 | 2.8698 | 0.95726 | 2.2006 | 36.0311 | 35.7125 | 35.545 | 35.1412 | 34.6081 | 34.0217 | 33.1845 | 31.5569 | 29.8442 | 28.152 | 23.2405 | 18.8909 | 15.8698 | 13.9573 | 14.911 | 23.0311 | 22.5826 | 22.3646 | 21.9589 | 21.5303 | 21.0637 | 20.5458 | 19.956 | 19.2656 | 18.5628 | 16.2875 | 14.1576 | 13.0304 | 12.0198 | 11.2025 | 36.0311 | 35.5826 | 35.3646 | 34.9589 | 34.5303 | 34.0637 | 33.5458 | 32.956 | 32.2656 | 31.5628 | 29.2875 | 27.1576 | 26.0304 | 25.0198 | 24.2902 | 23.0311 | 22.3436 | 22.0054 | 21.476 | 20.8277 | 20.1607 | 19.2446 | 17.497 | 15.7315 | 13.9864 | 8.8698 | 4.2233 | 0.84026 | -1.438 | -0.56835 | 36.0311 | 35.3436 | 35.0054 | 34.476 | 33.8277 | 33.1607 | 32.2446 | 30.497 | 28.7315 | 26.9864 | 21.8698 | 17.2233 | 13.8403 | 11.562 | 12.2249 | 389111 | 413393 | ROCHDALE CENTRAL | ROCHDALE
| Roman Rd | 5.7738 | 5.1745 | 4.7576 | 4.5105 | 4.3909 | 4.2657 | 4.1418 | 4.012 | 3.7848 | 3.5612 | 2.6298 | 1.4277 | 0.11547 | -1.1587 | -2.2206 | 12.7738 | 12.1745 | 11.7576 | 11.5105 | 11.3909 | 11.2657 | 11.1418 | 11.012 | 10.7848 | 10.5612 | 9.6298 | 8.4277 | 7.1155 | 5.8413 | 4.6712 | 5.7738 | 5.5834 | 5.4145 | 5.3446 | 5.3062 | 5.2539 | 5.175 | 5.0663 | 4.8881 | 4.7068 | 4.1606 | 3.6054 | 3.1085 | 2.6103 | 2.3075 | 12.7738 | 12.5834 | 12.4145 | 12.3446 | 12.3062 | 12.2539 | 12.175 | 12.0663 | 11.8881 | 11.7068 | 11.1606 | 10.6054 | 10.1085 | 9.6103 | 9.3402 | 5.7738 | 5.077 | 4.6434 | 4.395 | 4.277 | 4.1556 | 4.0362 | 3.9151 | 3.7474 | 3.5884 | 2.8322 | 1.7901 | 0.6372 | -0.38366 | -1.1238 | 12.7738 | 12.077 | 11.6434 | 11.395 | 11.277 | 11.1556 | 11.0362 | 10.9151 | 10.7474 | 10.5884 | 9.8322 | 8.7901 | 7.6372 | 6.6163 | 5.696 | 5.7738 | 5.3901 | 5.0383 | 4.8254 | 4.7334 | 4.6211 | 4.4426 | 4.0688 | 3.6265 | 3.1896 | 1.6982 | 0.28841 | -0.81693 | -1.3792 | -0.57323 | 12.7738 | 12.3901 | 12.0383 | 11.8254 | 11.7334 | 11.6211 | 11.4426 | 11.0688 | 10.6265 | 10.1896 | 8.6982 | 7.2884 | 6.1831 | 5.6208 | 6.2409 | 5.7738 | 5.4475 | 5.0969 | 4.8896 | 4.8425 | 4.7767 | 4.6847 | 4.5742 | 4.3555 | 4.1309 | 3.4763 | 2.9395 | 2.6082 | 2.3993 | 2.5346 | 12.7738 | 12.4475 | 12.0969 | 11.8896 | 11.8425 | 11.7767 | 11.6847 | 11.5742 | 11.3555 | 11.1309 | 10.4763 | 9.9395 | 9.6082 | 9.3993 | 9.4753 | 5.7738 | 5.0774 | 4.638 | 4.3823 | 4.2536 | 4.1256 | 3.9376 | 3.5383 | 3.0874 | 2.6436 | 1.1907 | -0.26863 | -1.3878 | -2.0157 | -1.2996 | 12.7738 | 12.0774 | 11.638 | 11.3823 | 11.2536 | 11.1256 | 10.9376 | 10.5383 | 10.0874 | 9.6436 | 8.1907 | 6.7314 | 5.6122 | 4.9843 | 5.5363 | 369058 | 426505 | LOWER DARWEN | ROCHDALE
| Romiley | 3.3393 | 2.708 | 2.5444 | 2.4775 | 2.2978 | 2.1015 | 1.9206 | 1.7634 | -0.24171 | -0.38138 | -3.9607 | -7.6277 | -10.6782 | -15.4585 | -18.3986 | 6.8393 | 6.208 | 6.0444 | 5.9775 | 5.7978 | 5.6015 | 5.4206 | 5.2634 | 3.2583 | 3.1186 | -0.46073 | -4.1277 | -7.1782 | -11.9585 | -15.1534 | 3.3393 | 3.0939 | 2.9699 | 2.8622 | 2.6933 | 2.5037 | 2.2428 | 1.9155 | 1.6622 | 1.3883 | 0.553 | -0.28149 | -1.14 | -3.7142 | -4.3424 | 6.8393 | 6.5939 | 6.4699 | 6.3622 | 6.1933 | 6.0037 | 5.7428 | 5.4155 | 5.1622 | 4.8883 | 4.053 | 3.2185 | 2.36 | -0.21422 | -0.74453 | 3.3393 | 2.6401 | 2.4859 | 2.4712 | 2.3429 | 2.1461 | 0.11011 | 0.064988 | -1.7768 | -1.8178 | -5.1346 | -8.5689 | -11.3657 | -14.1635 | -16.8509 | 6.8393 | 6.1401 | 5.9859 | 5.9712 | 5.8429 | 5.6461 | 3.6101 | 3.565 | 1.7232 | 1.6822 | -1.6346 | -5.0689 | -7.8657 | -10.6635 | -13.6512 | 3.3393 | 3.1744 | 3.1441 | -1.4656 | -1.316 | -1.296 | -1.5387 | -2.4986 | -3.8054 | -4.914 | -8.4866 | -11.6687 | -14.2319 | -15.682 | -14.3545 | 6.8393 | 6.6744 | 6.6441 | 2.0344 | 2.184 | 2.204 | 1.9613 | 1.0014 | -0.30545 | -1.414 | -4.9866 | -8.1687 | -10.7319 | -12.182 | -11.1428 | 3.3393 | 3.0235 | 2.9664 | 2.9963 | 2.9787 | 2.9232 | 2.8371 | 2.738 | 0.75138 | 0.60256 | -1.8295 | -2.7395 | -3.2782 | -5.2526 | -5.4088 | 6.8393 | 6.5235 | 6.4664 | 6.4963 | 6.4787 | 6.4232 | 6.3371 | 6.238 | 4.2514 | 4.1026 | 1.6705 | 0.76048 | 0.22176 | -1.7526 | -1.985 | 3.3393 | 2.8344 | 2.6489 | -2.071 | -2.0209 | -2.0662 | -2.3893 | -3.4604 | -4.8489 | -6.0388 | -9.8638 | -13.2653 | -16.0482 | -17.771 | -16.7531 | 6.8393 | 6.3344 | 6.1489 | 1.429 | 1.4791 | 1.4338 | 1.1107 | 0.039574 | -1.3489 | -2.5388 | -6.3638 | -9.7653 | -12.5482 | -14.271 | -13.473 | 393626 | 390716 | VERNON PARK | BREDBURY
| Rossall | 1.5191 | 1.4923 | 1.4588 | 1.4374 | 1.4115 | 1.385 | 1.3648 | 1.3448 | 1.2918 | 1.241 | 0.91682 | 0.37695 | -0.091336 | -0.57862 | -1.0054 | 8.0191 | 7.9923 | 7.9588 | 7.9374 | 7.9115 | 7.885 | 7.8648 | 7.8448 | 7.7918 | 7.741 | 7.4168 | 6.8769 | 6.4087 | 5.9214 | 5.4705 | 1.5191 | 1.4897 | 1.4516 | 1.424 | 1.3975 | 1.3665 | 1.3287 | 1.2854 | 1.2238 | 1.1615 | 0.97275 | 0.78456 | 0.61644 | 0.42131 | 0.27914 | 8.0191 | 7.9897 | 7.9516 | 7.924 | 7.8975 | 7.8665 | 7.8287 | 7.7854 | 7.7238 | 7.6615 | 7.4727 | 7.2846 | 7.1164 | 6.9213 | 6.7953 | 1.5191 | 1.4984 | 1.3754 | 1.2699 | 1.1587 | 1.0484 | 0.94856 | 0.92347 | 0.8775 | 0.83552 | 0.56073 | 0.10096 | -0.26629 | -0.62746 | -0.94263 | 8.0191 | 7.9984 | 7.8754 | 7.7699 | 7.6587 | 7.5484 | 7.4486 | 7.4235 | 7.3775 | 7.3355 | 7.0607 | 6.601 | 6.2337 | 5.8725 | 5.5142 | 1.5191 | 1.5327 | 1.4208 | 1.316 | 1.202 | 1.0841 | 0.94242 | 0.80008 | 0.63578 | 0.46485 | -0.026023 | -0.48224 | -0.83815 | -1.0373 | -0.85883 | 8.0191 | 8.0327 | 7.9208 | 7.816 | 7.702 | 7.5841 | 7.4424 | 7.3001 | 7.1358 | 6.9648 | 6.474 | 6.0178 | 5.6618 | 5.4627 | 5.5975 | 1.5191 | 1.4976 | 1.4719 | 1.4636 | 1.4613 | 1.4535 | 1.4413 | 1.4245 | 1.3729 | 1.3203 | 1.1369 | 0.8594 | 0.64069 | 0.48175 | 0.43632 | 8.0191 | 7.9976 | 7.9719 | 7.9636 | 7.9613 | 7.9535 | 7.9413 | 7.9245 | 7.8729 | 7.8203 | 7.6369 | 7.3594 | 7.1407 | 6.9818 | 6.9368 | 1.5191 | 1.5226 | 1.3967 | 1.2762 | 1.1483 | 1.0215 | 0.86987 | 0.7133 | 0.53976 | 0.3598 | -0.16281 | -0.65239 | -1.042 | -1.284 | -1.1322 | 8.0191 | 8.0226 | 7.8967 | 7.7762 | 7.6483 | 7.5215 | 7.3699 | 7.2133 | 7.0398 | 6.8598 | 6.3372 | 5.8476 | 5.458 | 5.216 | 5.3296 | 331916 | 445505 | THORNTON | STANAH
| Royton | 12.1852 | 11.3671 | 11.0513 | 10.8446 | 10.5256 | 10.186 | 9.8571 | 9.5276 | 9.184 | 8.8562 | 6.8943 | 3.8246 | 1.4458 | -0.83878 | -2.5829 | 16.8222 | 16.0041 | 15.6883 | 15.4816 | 15.1626 | 14.823 | 14.4941 | 14.1646 | 13.821 | 13.4932 | 11.5313 | 8.4616 | 6.0828 | 3.7982 | 1.9132 | 12.1852 | 11.9463 | 11.7979 | 11.6571 | 11.465 | 11.2584 | 10.9899 | 10.6416 | 10.3759 | 10.0973 | 9.23 | 8.2748 | 7.3166 | 6.2463 | 5.4179 | 16.8222 | 16.5833 | 16.4349 | 16.2941 | 16.102 | 15.8954 | 15.6269 | 15.2786 | 15.0129 | 14.7343 | 13.867 | 12.9118 | 11.9536 | 10.8833 | 10.1968 | 12.1852 | 11.1952 | 10.7842 | 10.4267 | 9.9534 | 9.4267 | 8.9167 | 8.4117 | 7.895 | 7.3711 | 4.8666 | 1.696 | -0.38617 | -2.0945 | -2.9011 | 16.8222 | 15.8322 | 15.4212 | 15.0637 | 14.5904 | 14.0637 | 13.5537 | 13.0487 | 12.532 | 12.0081 | 9.5036 | 6.333 | 4.2508 | 2.5425 | 1.5963 | 12.1852 | 11.6831 | 11.3902 | 11.0573 | 10.5722 | 10.0163 | 9.3155 | 8.1126 | 6.9273 | 5.7757 | 2.5261 | -0.15771 | -1.7383 | -2.4231 | -1.7549 | 16.8222 | 16.3201 | 16.0272 | 15.6943 | 15.2092 | 14.6533 | 13.9525 | 12.7496 | 11.5643 | 10.4127 | 7.1631 | 4.4793 | 2.8987 | 2.2139 | 2.736 | 12.1852 | 11.836 | 11.6478 | 11.5122 | 11.3361 | 11.1273 | 10.89 | 10.6118 | 10.2753 | 9.9319 | 8.7578 | 7.5007 | 6.5943 | 5.6596 | 4.9223 | 16.8222 | 16.473 | 16.2848 | 16.1492 | 15.9731 | 15.7643 | 15.527 | 15.2488 | 14.9123 | 14.5689 | 13.3948 | 12.1377 | 11.2313 | 10.2966 | 9.6573 | 12.1852 | 11.3353 | 10.9112 | 10.4988 | 9.9394 | 9.3363 | 8.5765 | 7.2922 | 6.0479 | 4.8357 | 1.3897 | -1.4647 | -3.2124 | -4.0953 | -3.6611 | 16.8222 | 15.9723 | 15.5482 | 15.1358 | 14.5764 | 13.9733 | 13.2135 | 11.9292 | 10.6849 | 9.4727 | 6.0267 | 3.1723 | 1.4246 | 0.54175 | 0.8806 | 392426 | 407533 | ROYTON | WHITEGATE
| S.E. Macclesfield | 9.6261 | 9.3181 | 8.9921 | 8.7099 | 8.3752 | 8.0256 | 7.6875 | 7.3463 | 6.9818 | 6.6391 | 4.4856 | 1.2028 | -1.489 | -4.1918 | -6.5233 | 13.7631 | 13.4551 | 13.1291 | 12.8469 | 12.5122 | 12.1626 | 11.8245 | 11.4833 | 11.1188 | 10.7761 | 8.6226 | 5.3398 | 2.648 | -0.054753 | -2.5223 | 9.6261 | 9.3872 | 9.0921 | 8.7952 | 8.4476 | 8.0779 | 7.6239 | 7.0559 | 6.653 | 6.2464 | 4.9632 | 3.5228 | 2.2026 | 0.80626 | -0.1404 | 13.7631 | 13.5242 | 13.2291 | 12.9322 | 12.5846 | 12.2149 | 11.7609 | 11.1929 | 10.79 | 10.3834 | 9.1002 | 7.6598 | 6.3396 | 4.9433 | 4.1455 | 9.6261 | 9.2975 | 8.9684 | 8.6859 | 8.3537 | 8.0084 | 7.6745 | 7.3418 | 7.0231 | 6.7324 | 5.1553 | 2.241 | -0.17093 | -2.4887 | -4.5262 | 13.7631 | 13.4345 | 13.1054 | 12.8229 | 12.4907 | 12.1454 | 11.8115 | 11.4788 | 11.1601 | 10.8694 | 9.2923 | 6.378 | 3.9661 | 1.6483 | -0.58669 | 9.6261 | 9.535 | 9.3121 | 9.0968 | 8.8225 | 8.4968 | 8.0398 | 7.1822 | 6.275 | 5.2121 | 2.1407 | -0.79106 | -3.0443 | -4.4323 | -3.5631 | 13.7631 | 13.672 | 13.4491 | 13.2338 | 12.9595 | 12.6338 | 12.1768 | 11.3192 | 10.412 | 9.3491 | 6.2777 | 3.3459 | 1.0927 | -0.29533 | 0.36937 | 9.6261 | 9.3908 | 9.1188 | 8.9118 | 8.7068 | 8.4675 | 8.194 | 7.8953 | 7.5386 | 7.183 | 5.9266 | 4.3212 | 3.1614 | 2.1532 | 1.6761 | 13.7631 | 13.5278 | 13.2558 | 13.0488 | 12.8438 | 12.6045 | 12.331 | 12.0323 | 11.6756 | 11.32 | 10.0636 | 8.4582 | 7.2984 | 6.2902 | 5.8334 | 9.6261 | 9.4127 | 9.0886 | 8.7713 | 8.4069 | 8.0371 | 7.5443 | 6.5284 | 5.4056 | 4.261 | 0.92618 | -2.2566 | -4.7521 | -6.4017 | -5.8303 | 13.7631 | 13.5497 | 13.2256 | 12.9083 | 12.5439 | 12.1741 | 11.6813 | 10.6654 | 9.5426 | 8.398 | 5.0632 | 1.8804 | -0.61511 | -2.2647 | -1.8336 | 392001 | 372504 | MACCLESFIELD | MACCLESFIELD
| S.W. Macclesfield | 4.2126 | 2.5844 | 2.0337 | 1.7698 | 1.3719 | 0.95466 | 0.56909 | 0.20667 | -0.21783 | -0.59373 | -3.1836 | -7.7615 | -11.5865 | -15.6412 | -19.2896 | 8.3496 | 6.7214 | 6.1707 | 5.9068 | 5.5089 | 5.0917 | 4.7061 | 4.3437 | 3.9192 | 3.5433 | 0.9534 | -3.6245 | -7.4495 | -11.5042 | -15.3302 | 4.2126 | 3.7088 | 3.4027 | 3.1321 | 2.7798 | 2.3977 | 1.9122 | 1.2999 | 0.78992 | 0.2782 | -1.2441 | -2.7504 | -4.1765 | -5.7637 | -6.9325 | 8.3496 | 7.8458 | 7.5397 | 7.2691 | 6.9168 | 6.5347 | 6.0492 | 5.4369 | 4.9269 | 4.4152 | 2.8929 | 1.3866 | -0.039527 | -1.6267 | -2.6033 | 4.2126 | 2.3856 | 1.8256 | 1.6241 | 1.2919 | 0.9508 | 0.67415 | 0.42772 | 0.14217 | -0.11842 | -2.3539 | -6.6282 | -10.1832 | -13.9115 | -17.1846 | 8.3496 | 6.5226 | 5.9626 | 5.7611 | 5.4289 | 5.0878 | 4.8111 | 4.5647 | 4.2792 | 4.0186 | 1.7831 | -2.4912 | -6.0462 | -9.7745 | -13.2951 | 4.2126 | 3.2892 | 2.9675 | 2.8197 | 2.5061 | 2.1333 | 1.5539 | 0.18751 | -1.2493 | -2.677 | -6.8209 | -10.8894 | -14.144 | -16.2778 | -15.1773 | 8.3496 | 7.4262 | 7.1045 | 6.9567 | 6.6431 | 6.2703 | 5.6909 | 4.3245 | 2.8877 | 1.46 | -2.6839 | -6.7524 | -10.007 | -12.1408 | -11.2975 | 4.2126 | 3.5069 | 3.2097 | 3.0687 | 2.8863 | 2.652 | 2.3791 | 2.087 | 1.676 | 1.2779 | -0.11017 | -1.7467 | -2.8916 | -4.028 | -4.6977 | 8.3496 | 7.6439 | 7.3467 | 7.2057 | 7.0233 | 6.789 | 6.5161 | 6.224 | 5.813 | 5.4149 | 4.0268 | 2.3903 | 1.2454 | 0.10898 | -0.52148 | 4.2126 | 2.4881 | 1.8784 | 1.5654 | 1.1047 | 0.64082 | -0.047796 | -1.5748 | -3.1297 | -4.6735 | -9.1592 | -13.495 | -17.0099 | -19.4584 | -18.7289 | 8.3496 | 6.6251 | 6.0154 | 5.7024 | 5.2417 | 4.7778 | 4.0892 | 2.5622 | 1.0073 | -0.53649 | -5.0222 | -9.358 | -12.8729 | -15.3214 | -14.7654 | 390968 | 373004 | MACCLESFIELD | MACCLESFIELD
| Sale | 11.4512 | 10.0415 | 9.5099 | 9.1987 | 8.8196 | 8.4297 | 8.0604 | 7.7092 | 7.3558 | 7.0267 | 5.2583 | 2.6026 | 0.63053 | -1.2491 | -2.6399 | 16.0912 | 14.6815 | 14.1499 | 13.8387 | 13.4596 | 13.0697 | 12.7004 | 12.3492 | 11.9958 | 11.6667 | 9.8983 | 7.2426 | 5.2705 | 3.3909 | 1.8736 | 11.4512 | 10.9431 | 10.6311 | 10.3407 | 9.9847 | 9.6271 | 9.1964 | 8.6807 | 8.3764 | 8.0605 | 7.1035 | 6.1207 | 5.2354 | 4.2794 | 3.5336 | 16.0912 | 15.5831 | 15.2711 | 14.9807 | 14.6247 | 14.2671 | 13.8364 | 13.3207 | 13.0164 | 12.7005 | 11.7435 | 10.7607 | 9.8754 | 8.9194 | 8.2942 | 11.4512 | 9.7884 | 9.1494 | 8.7733 | 8.3257 | 7.8655 | 7.4361 | 7.0163 | 6.5976 | 6.1789 | 4.1707 | 1.5948 | -0.14645 | -1.6188 | -2.4125 | 16.0912 | 14.4284 | 13.7894 | 13.4133 | 12.9657 | 12.5055 | 12.0761 | 11.6563 | 11.2376 | 10.8189 | 8.8107 | 6.2348 | 4.4936 | 3.0212 | 2.1794 | 11.4512 | 10.4324 | 9.9758 | 9.6713 | 9.2683 | 8.8213 | 8.2659 | 7.312 | 6.3548 | 5.4239 | 2.8217 | 0.64475 | -0.66123 | -1.2397 | -0.84286 | 16.0912 | 15.0724 | 14.6158 | 14.3113 | 13.9083 | 13.4613 | 12.9059 | 11.952 | 10.9948 | 10.0639 | 7.4617 | 5.2848 | 3.9788 | 3.4003 | 3.7383 | 11.4512 | 10.6849 | 10.3287 | 10.0948 | 9.8328 | 9.5509 | 9.2622 | 8.9631 | 8.6216 | 8.2778 | 7.1556 | 5.892 | 4.9332 | 3.9735 | 3.274 | 16.0912 | 15.3249 | 14.9687 | 14.7348 | 14.4728 | 14.1909 | 13.9022 | 13.6031 | 13.2616 | 12.9178 | 11.7956 | 10.532 | 9.5732 | 8.6135 | 8.014 | 11.4512 | 9.7928 | 9.1166 | 8.6946 | 8.1851 | 7.6656 | 7.0239 | 5.9503 | 4.9171 | 3.9111 | 1.0869 | -1.2648 | -2.7348 | -3.5042 | -3.1852 | 16.0912 | 14.4328 | 13.7566 | 13.3346 | 12.8251 | 12.3056 | 11.6639 | 10.5903 | 9.5571 | 8.5511 | 5.7269 | 3.3752 | 1.9052 | 1.1358 | 1.3932 | 378952 | 392177 | SALE | CARRINGTON
| Sale Moor | 2.3351 | 2.2793 | 2.2166 | 2.1468 | 1.9904 | 1.8294 | 1.6892 | 1.5744 | 1.4382 | 1.3265 | 0.29394 | -1.6683 | -3.3342 | -5.0499 | -6.6109 | 2.3351 | 2.2793 | 2.2166 | 2.1468 | 1.9904 | 1.8294 | 1.6892 | 1.5744 | 1.4382 | 1.3265 | 0.29394 | -1.6683 | -3.3342 | -5.0499 | -6.7426 | 2.3351 | 2.2753 | 2.2083 | 2.1335 | 2.0283 | 1.9158 | 1.7542 | 1.5738 | 1.409 | 1.2412 | 0.74534 | 0.29101 | -0.12295 | -0.53569 | -0.81021 | 2.3351 | 2.2753 | 2.2083 | 2.1335 | 2.0283 | 1.9158 | 1.7542 | 1.5738 | 1.409 | 1.2412 | 0.74534 | 0.29101 | -0.12295 | -0.53569 | -0.77058 | 2.3351 | 2.2953 | 2.2513 | 2.2067 | 2.0798 | 1.9527 | 1.8591 | 1.7945 | 1.7176 | 1.6506 | 0.69175 | -1.1703 | -2.7363 | -4.3202 | -5.7134 | 2.3351 | 2.2953 | 2.2513 | 2.2067 | 2.0798 | 1.9527 | 1.8591 | 1.7945 | 1.7176 | 1.6506 | 0.69175 | -1.1703 | -2.7363 | -4.3202 | -5.8497 | 2.3351 | 2.4652 | 2.4756 | 2.4557 | 2.3527 | 2.209 | 1.9665 | 1.3676 | 0.73695 | 0.10957 | -1.7179 | -3.4796 | -4.9567 | -5.8418 | -5.0867 | 2.3351 | 2.4652 | 2.4756 | 2.4557 | 2.3527 | 2.209 | 1.9665 | 1.3676 | 0.73695 | 0.10957 | -1.7179 | -3.4796 | -4.9567 | -5.8418 | -5.2511 | 2.3351 | 2.2971 | 2.2706 | 2.2676 | 2.2536 | 2.1963 | 2.1277 | 2.0619 | 1.9478 | 1.8378 | 1.4355 | 0.90412 | 0.51537 | 0.15954 | 0.031531 | 2.3351 | 2.2971 | 2.2706 | 2.2676 | 2.2536 | 2.1963 | 2.1277 | 2.0619 | 1.9478 | 1.8378 | 1.4355 | 0.90412 | 0.51537 | 0.15954 | 0.018814 | 2.3351 | 2.4204 | 2.3712 | 2.2795 | 2.0971 | 1.9145 | 1.6351 | 0.97177 | 0.28821 | -0.39089 | -2.36 | -4.2225 | -5.7968 | -6.8224 | -6.2538 | 2.3351 | 2.4204 | 2.3712 | 2.2795 | 2.0971 | 1.9145 | 1.6351 | 0.97177 | 0.28821 | -0.39089 | -2.36 | -4.2225 | -5.7968 | -6.8224 | -6.3782 | 379671 | 391133 | SALE | CARRINGTON
| Salford Quays | 11.2734 | 9.4286 | 8.0839 | 6.5232 | 4.7947 | 3.0713 | 0.93594 | -0.29377 | -1.5904 | -2.3963 | -5.0515 | -7.3731 | -8.3263 | -9.3451 | -10.2707 | 18.2734 | 16.4286 | 15.0839 | 13.5232 | 11.7947 | 10.0713 | 7.9359 | 6.7062 | 5.4096 | 4.6037 | 1.9485 | -0.37315 | -1.3263 | -2.3451 | -3.2632 | 11.2734 | 10.7249 | 10.4417 | 10.282 | 10.1458 | 10.0097 | 9.859 | 9.6823 | 9.4504 | 9.2198 | 8.5482 | 7.8882 | 7.272 | 6.5531 | 5.8903 | 18.2734 | 17.7249 | 17.4417 | 17.282 | 17.1458 | 17.0097 | 16.859 | 16.6823 | 16.4504 | 16.2198 | 15.5482 | 14.8882 | 14.272 | 13.5531 | 13.0026 | 11.2734 | 9.1434 | 7.7414 | 6.1784 | 4.4492 | 2.7256 | 0.58881 | -0.64077 | -1.9061 | -2.6759 | -5.2218 | -7.4201 | -8.2378 | -9.0569 | -9.7124 | 18.2734 | 16.1434 | 14.7414 | 13.1784 | 11.4492 | 9.7256 | 7.5888 | 6.3592 | 5.0939 | 4.3241 | 1.7782 | -0.42014 | -1.2378 | -2.0569 | -2.7553 | 11.2734 | 9.7648 | 8.5042 | 6.9606 | 5.2469 | 3.5297 | 1.3435 | -0.09075 | -1.5705 | -2.5561 | -5.4494 | -7.6124 | -8.3841 | -8.9098 | -8.7775 | 18.2734 | 16.7648 | 15.5042 | 13.9606 | 12.2469 | 10.5297 | 8.3435 | 6.9092 | 5.4295 | 4.4439 | 1.5506 | -0.61237 | -1.3841 | -1.9098 | -1.8251 | 11.2734 | 10.3294 | 9.1777 | 7.637 | 5.9452 | 4.2522 | 2.1307 | 0.90677 | -0.3941 | -1.2108 | -3.6641 | -5.4519 | -5.9051 | -6.3524 | -6.6293 | 18.2734 | 17.3294 | 16.1777 | 14.637 | 12.9452 | 11.2522 | 9.1307 | 7.9068 | 6.6059 | 5.7892 | 3.3359 | 1.5481 | 1.0949 | 0.64763 | 0.3991 | 11.2734 | 8.9073 | 7.4533 | 5.8846 | 4.1491 | 2.4222 | 0.22918 | -1.2227 | -3.0135 | -4.3091 | -8.1289 | -11.2161 | -12.9177 | -14.6831 | -16.1093 | 18.2734 | 15.9073 | 14.4533 | 12.8846 | 11.1491 | 9.4222 | 7.2292 | 5.7773 | 3.9865 | 2.6909 | -1.1289 | -4.2161 | -5.9177 | -7.6831 | -8.8426 | 380334 | 397555 | FREDERICK RD | KEARSLEY
| Samlesbury Enterprise Zone | 22.3333 | 22.3333 | 22.2711 | 22.2089 | 22.1468 | 22.0846 | 22.0224 | 21.9602 | 21.9292 | 21.8981 | 21.8981 | 21.8981 | 21.8981 | 21.8981 | 21.8981 | 26.8333 | 26.8333 | 26.7711 | 26.7089 | 26.6468 | 26.5846 | 26.5224 | 26.4602 | 26.4292 | 26.3981 | 26.3981 | 26.3981 | 26.3981 | 26.3981 | 26.3981 | 22.3333 | 22.3333 | 22.3229 | 22.3125 | 22.3022 | 22.2918 | 22.2815 | 22.2711 | 22.2711 | 22.2711 | 22.2711 | 22.2711 | 22.2711 | 22.2711 | 22.2711 | 26.8333 | 26.8333 | 26.8229 | 26.8125 | 26.8022 | 26.7918 | 26.7815 | 26.7711 | 26.7711 | 26.7711 | 26.7711 | 26.7711 | 26.7711 | 26.7711 | 26.7711 | 22.3333 | 22.3333 | 22.2711 | 22.2089 | 22.1468 | 22.0846 | 22.0224 | 21.9602 | 21.9292 | 21.8981 | 21.8981 | 21.8981 | 21.8981 | 21.8981 | 21.8981 | 26.8333 | 26.8333 | 26.7711 | 26.7089 | 26.6468 | 26.5846 | 26.5224 | 26.4602 | 26.4292 | 26.3981 | 26.3981 | 26.3981 | 26.3981 | 26.3981 | 26.3981 | 22.3333 | 22.3333 | 22.2711 | 22.2089 | 22.1468 | 22.0846 | 22.0224 | 21.9602 | 21.9292 | 21.8981 | 21.8981 | 21.8981 | 21.8981 | 21.8981 | 21.8981 | 26.8333 | 26.8333 | 26.7711 | 26.7089 | 26.6468 | 26.5846 | 26.5224 | 26.4602 | 26.4292 | 26.3981 | 26.3981 | 26.3981 | 26.3981 | 26.3981 | 26.3981 | 22.3333 | 22.3333 | 22.2711 | 22.2089 | 22.1468 | 22.0846 | 22.0224 | 21.9602 | 21.9292 | 21.8981 | 21.8981 | 21.8981 | 21.8981 | 21.8981 | 21.8981 | 26.8333 | 26.8333 | 26.7711 | 26.7089 | 26.6468 | 26.5846 | 26.5224 | 26.4602 | 26.4292 | 26.3981 | 26.3981 | 26.3981 | 26.3981 | 26.3981 | 26.3981 | 22.3333 | 22.3333 | 22.2711 | 22.2089 | 22.1468 | 22.0846 | 22.0224 | 21.9602 | 21.9292 | 21.8981 | 21.8981 | 21.8981 | 21.8981 | 21.8981 | 21.8981 | 26.8333 | 26.8333 | 26.7711 | 26.7089 | 26.6468 | 26.5846 | 26.5224 | 26.4602 | 26.4292 | 26.3981 | 26.3981 | 26.3981 | 26.3981 | 26.3981 | 26.3981 | 362105 | 431439 | BLACKBURN | PENWORTHAM
| Sandgate | 11.0782 | 9.6789 | 8.6941 | 7.936 | 6.9391 | 5.9283 | 4.9278 | 3.9408 | 3.3589 | 2.7942 | -0.1877 | -5.366 | -9.0958 | -12.5953 | -15.4347 | 15.5782 | 14.1789 | 13.1941 | 12.436 | 11.4391 | 10.4283 | 9.4278 | 8.4408 | 7.8589 | 7.2942 | 4.3123 | -0.86601 | -4.5958 | -8.0953 | -11.2548 | 11.0782 | 10.3473 | 9.8349 | 9.3869 | 8.8667 | 8.2961 | 7.6215 | 6.8474 | 6.521 | 6.1902 | 5.1978 | 4.2061 | 3.5722 | 3.1238 | 2.9011 | 15.5782 | 14.8473 | 14.3349 | 13.8869 | 13.3667 | 12.7961 | 12.1215 | 11.3474 | 11.021 | 10.6902 | 9.6978 | 8.7061 | 8.0722 | 7.6238 | 7.4203 | 11.0782 | 9.4808 | 8.4781 | 7.751 | 6.7869 | 5.8147 | 4.8724 | 3.9452 | 3.4354 | 2.9318 | 0.11186 | -4.9366 | -8.5516 | -11.9061 | -14.574 | 15.5782 | 13.9808 | 12.9781 | 12.251 | 11.2869 | 10.3147 | 9.3724 | 8.4452 | 7.9354 | 7.4318 | 4.6119 | -0.4366 | -4.0516 | -7.4061 | -10.4229 | 11.0782 | 10.234 | 9.422 | 8.7699 | 7.858 | 6.9185 | 5.7681 | 3.6663 | 1.9263 | 0.20768 | -4.77 | -9.5784 | -12.8911 | -14.6443 | -13.0147 | 15.5782 | 14.734 | 13.922 | 13.2699 | 12.358 | 11.4185 | 10.2681 | 8.1663 | 6.4263 | 4.7077 | -0.26995 | -5.0784 | -8.3911 | -10.1443 | -8.8667 | 11.0782 | 9.9281 | 9.0182 | 8.3248 | 7.453 | 6.5565 | 5.6149 | 4.6441 | 4.0489 | 3.4489 | 1.5188 | -0.50424 | -1.3945 | -1.7519 | -1.6719 | 15.5782 | 14.4281 | 13.5182 | 12.8248 | 11.953 | 11.0565 | 10.1149 | 9.1441 | 8.5489 | 7.9489 | 6.0188 | 3.9958 | 3.1055 | 2.7481 | 2.7566 | 11.0782 | 9.5116 | 8.4816 | 7.7095 | 6.6819 | 5.6504 | 4.4261 | 2.3158 | 0.51483 | -1.2669 | -6.4543 | -11.4611 | -15.0046 | -17.0877 | -15.8511 | 15.5782 | 14.0116 | 12.9816 | 12.2095 | 11.1819 | 10.1504 | 8.9261 | 6.8158 | 5.0148 | 3.2331 | -1.9543 | -6.9611 | -10.5046 | -12.5877 | -11.6145 | 321492 | 468870 | BARROW & SANDGATE | HARKER
| Scarisbrick | 2.2568 | 2.2293 | 2.1738 | 2.1252 | 2.063 | 1.9969 | 1.9344 | 1.8644 | 1.7769 | 1.69 | 1.1184 | 0.42253 | -0.082987 | -0.49374 | -0.77897 | 3.7568 | 3.7293 | 3.6738 | 3.6252 | 3.563 | 3.4969 | 3.4344 | 3.3644 | 3.2769 | 3.19 | 2.6184 | 1.9225 | 1.417 | 1.0063 | 0.68729 | 2.2568 | 2.2322 | 2.1853 | 2.1441 | 2.0992 | 2.0487 | 1.9849 | 1.8944 | 1.8179 | 1.7364 | 1.2915 | 0.88034 | 0.52891 | 0.19746 | 0.019484 | 3.7568 | 3.7322 | 3.6853 | 3.6441 | 3.5992 | 3.5487 | 3.4849 | 3.3944 | 3.3179 | 3.2364 | 2.7915 | 2.3803 | 2.0289 | 1.6975 | 1.5412 | 2.2568 | 2.2288 | 2.1733 | 2.1245 | 2.063 | 1.9982 | 1.9373 | 1.8702 | 1.7973 | 1.7318 | 1.374 | 0.73588 | 0.27502 | -0.14535 | -0.45232 | 3.7568 | 3.7288 | 3.6733 | 3.6245 | 3.563 | 3.4982 | 3.4373 | 3.3702 | 3.2973 | 3.2318 | 2.874 | 2.2359 | 1.775 | 1.3546 | 1.0468 | 2.2568 | 2.2744 | 2.2418 | 2.2073 | 2.1614 | 2.1017 | 2.0137 | 1.8401 | 1.6547 | 1.4749 | 0.95959 | 0.42063 | 0.010844 | -0.19315 | 0.023862 | 3.7568 | 3.7744 | 3.7418 | 3.7073 | 3.6614 | 3.6017 | 3.5137 | 3.3401 | 3.1547 | 2.9749 | 2.4596 | 1.9206 | 1.5108 | 1.3068 | 1.4716 | 2.2568 | 2.2365 | 2.1926 | 2.1625 | 2.1338 | 2.0946 | 2.0415 | 1.9733 | 1.8816 | 1.7894 | 1.3626 | 0.8487 | 0.50495 | 0.25034 | 0.22119 | 3.7568 | 3.7365 | 3.6926 | 3.6625 | 3.6338 | 3.5946 | 3.5415 | 3.4733 | 3.3816 | 3.2894 | 2.8626 | 2.3487 | 2.0049 | 1.7503 | 1.705 | 2.2568 | 2.2588 | 2.2044 | 2.1447 | 2.0771 | 2.0091 | 1.916 | 1.726 | 1.5295 | 1.34 | 0.62667 | -0.043389 | -0.5122 | -0.75942 | -0.58686 | 3.7568 | 3.7588 | 3.7044 | 3.6447 | 3.5771 | 3.5091 | 3.416 | 3.226 | 3.0295 | 2.84 | 2.1267 | 1.4566 | 0.9878 | 0.74058 | 0.87242 | 338069 | 412086 | SKELMERSDALE | WASHWAY FARM
| Sebergham | -0.2988 | -0.46601 | -0.55488 | -0.61686 | -0.706 | -0.80049 | -0.88342 | -0.96148 | -1.0574 | -1.1435 | -1.6076 | -2.3309 | -2.9015 | -3.4011 | -3.8656 | 0.7012 | 0.53399 | 0.44512 | 0.38314 | 0.294 | 0.19951 | 0.11658 | 0.038518 | -0.057446 | -0.14353 | -0.60757 | -1.3309 | -1.9015 | -2.4011 | -2.9083 | -0.2988 | -0.38699 | -0.47544 | -0.5622 | -0.66042 | -0.75358 | -0.86435 | -0.99338 | -1.0924 | -1.193 | -1.4948 | -1.7829 | -2.0664 | -2.4226 | -2.7337 | 0.7012 | 0.61301 | 0.52456 | 0.4378 | 0.33958 | 0.24642 | 0.13565 | 0.0066165 | -0.092395 | -0.193 | -0.49483 | -0.78287 | -1.0664 | -1.4226 | -1.6855 | -0.2988 | -0.4773 | -0.56116 | -0.60777 | -0.68084 | -0.75595 | -0.81291 | -0.85992 | -0.91483 | -0.96788 | -1.3396 | -1.9835 | -2.4838 | -2.8922 | -3.2453 | 0.7012 | 0.5227 | 0.43884 | 0.39223 | 0.31916 | 0.24405 | 0.18709 | 0.14008 | 0.085167 | 0.03212 | -0.3396 | -0.9835 | -1.4838 | -1.8922 | -2.3074 | -0.2988 | -0.39306 | -0.45409 | -0.51815 | -0.59224 | -0.67353 | -0.77694 | -0.97827 | -1.2056 | -1.4377 | -2.1036 | -2.7157 | -3.1398 | -3.3082 | -3.0401 | 0.7012 | 0.60694 | 0.54591 | 0.48185 | 0.40776 | 0.32647 | 0.22306 | 0.02173 | -0.20561 | -0.4377 | -1.1036 | -1.7157 | -2.1398 | -2.3082 | -2.103 | -0.2988 | -0.39053 | -0.46087 | -0.51319 | -0.5674 | -0.61666 | -0.6661 | -0.72059 | -0.80583 | -0.89223 | -1.2256 | -1.6318 | -1.8948 | -2.1417 | -2.2584 | 0.7012 | 0.60947 | 0.53913 | 0.48681 | 0.4326 | 0.38334 | 0.3339 | 0.27941 | 0.19417 | 0.10777 | -0.22556 | -0.63177 | -0.89475 | -1.1417 | -1.2808 | -0.2988 | -0.47183 | -0.57278 | -0.67115 | -0.7771 | -0.88079 | -1.0086 | -1.2449 | -1.4938 | -1.7467 | -2.4795 | -3.1576 | -3.6395 | -3.8624 | -3.6457 | 0.7012 | 0.52817 | 0.42722 | 0.32885 | 0.2229 | 0.11921 | -0.0086372 | -0.2449 | -0.49381 | -0.74671 | -1.4795 | -2.1576 | -2.6395 | -2.8624 | -2.6975 | 335344 | 542653 | CARLISLE | HARKER | Firm Capacity marginally exceeded. Review in RIIO-ED2 as the forecast overload is minimal.
| Sedbergh | 3.0277 | 2.7279 | 2.6091 | 2.506 | 2.3549 | 2.1761 | 1.9796 | 1.7361 | 1.4377 | 1.1249 | -0.90486 | -2.93 | -4.2983 | -5.3362 | -6.0355 | 12.9069 | 12.6071 | 12.4883 | 12.3852 | 12.2341 | 12.0553 | 11.8588 | 11.6153 | 11.3169 | 11.0041 | 8.9743 | 6.9492 | 5.5809 | 4.543 | 3.8258 | 3.0277 | 2.8458 | 2.7338 | 2.6071 | 2.4514 | 2.2757 | 2.0612 | 1.7997 | 1.5895 | 1.3603 | 0.56848 | -0.30587 | -1.5762 | -3.0176 | -3.974 | 12.9069 | 12.725 | 12.613 | 12.4863 | 12.3306 | 12.1549 | 11.9404 | 11.6789 | 11.4687 | 11.2395 | 10.4477 | 9.5733 | 8.303 | 6.8616 | 6.0364 | 3.0277 | 2.704 | 2.5917 | 2.5124 | 2.3897 | 2.2485 | 2.1059 | 1.9406 | 1.737 | 1.3585 | -0.53584 | -2.6862 | -4.2582 | -5.3895 | -6.0454 | 12.9069 | 12.5832 | 12.4709 | 12.3916 | 12.2689 | 12.1277 | 11.9851 | 11.8198 | 11.6162 | 11.2377 | 9.3434 | 7.193 | 5.621 | 4.4897 | 3.8057 | 3.0277 | 2.8597 | 2.797 | 2.7272 | 2.6165 | 2.4685 | 2.2481 | 1.8233 | 1.3345 | 0.81752 | -1.4382 | -3.3922 | -4.6656 | -5.4052 | -5.3368 | 12.9069 | 12.7389 | 12.6762 | 12.6064 | 12.4957 | 12.3477 | 12.1273 | 11.7025 | 11.2137 | 10.6967 | 8.441 | 6.487 | 5.2136 | 4.474 | 4.5069 | 3.0277 | 2.7957 | 2.7071 | 2.6357 | 2.5467 | 2.4301 | 2.2783 | 2.0903 | 1.8392 | 1.5625 | 0.035489 | -1.6705 | -2.8129 | -3.5785 | -3.8631 | 12.9069 | 12.6749 | 12.5863 | 12.5149 | 12.4259 | 12.3093 | 12.1575 | 11.9695 | 11.7184 | 11.4417 | 9.9147 | 8.2087 | 7.0663 | 6.3007 | 6.0311 | 3.0277 | 2.7184 | 2.5916 | 2.472 | 2.3191 | 2.1503 | 1.9134 | 1.4633 | 0.97589 | 0.45711 | -1.4543 | -3.6456 | -5.182 | -6.0964 | -6.1089 | 12.9069 | 12.5976 | 12.4708 | 12.3512 | 12.1983 | 12.0295 | 11.7926 | 11.3425 | 10.8551 | 10.3363 | 8.4249 | 6.2336 | 4.6972 | 3.7828 | 3.7518 | 365151 | 491747 | KENDAL (PARKSIDE RD) | HUTTON
| Selsmire | 1.1663 | 0.46943 | 0.22562 | 0.018774 | -0.32149 | -0.85014 | -1.6258 | -2.6977 | -4.0554 | -5.6187 | -10.7084 | -14.8451 | -17.2984 | -18.7247 | -19.4133 | 1.1663 | 0.46943 | 0.22562 | 0.018774 | -0.32149 | -0.85014 | -1.6258 | -2.6977 | -4.0554 | -5.6187 | -10.7084 | -14.8451 | -17.2984 | -18.7247 | -19.3648 | 1.1663 | 0.85841 | 0.7253 | 0.60052 | 0.43648 | 0.22415 | -0.060661 | -0.43512 | -0.90852 | -1.4982 | -4.0277 | -7.4802 | -11.2362 | -15.3743 | -18.0605 | 1.1663 | 0.85841 | 0.7253 | 0.60052 | 0.43648 | 0.22415 | -0.060661 | -0.43512 | -0.90852 | -1.4982 | -4.0277 | -7.4802 | -11.2362 | -15.3743 | -17.7185 | 1.1663 | 0.36583 | 0.11467 | -0.05851 | -0.33665 | -0.76011 | -1.3692 | -2.2042 | -3.2695 | -4.5568 | -9.4565 | -14.2648 | -17.4599 | -19.3142 | -20.0341 | 1.1663 | 0.36583 | 0.11467 | -0.05851 | -0.33665 | -0.76011 | -1.3692 | -2.2042 | -3.2695 | -4.5568 | -9.4565 | -14.2648 | -17.4599 | -19.3142 | -19.9885 | 1.1663 | 0.61488 | 0.40453 | 0.20028 | -0.1295 | -0.6554 | -1.4457 | -2.5677 | -3.9769 | -5.5955 | -10.7593 | -14.8501 | -17.2364 | -18.5151 | -18.8727 | 1.1663 | 0.61488 | 0.40453 | 0.20028 | -0.1295 | -0.6554 | -1.4457 | -2.5677 | -3.9769 | -5.5955 | -10.7593 | -14.8501 | -17.2364 | -18.5151 | -18.8379 | 1.1663 | 0.6017 | 0.40534 | 0.24491 | -0.0094267 | -0.4082 | -0.99723 | -1.802 | -2.8348 | -4.0603 | -8.5695 | -12.8633 | -15.6829 | -17.347 | -17.9261 | 1.1663 | 0.6017 | 0.40534 | 0.24491 | -0.0094267 | -0.4082 | -0.99723 | -1.802 | -2.8348 | -4.0603 | -8.5695 | -12.8633 | -15.6829 | -17.347 | -17.8729 | 1.1663 | 0.28052 | 0.0077017 | -0.18517 | -0.47257 | -0.90137 | -1.5306 | -2.4325 | -3.5709 | -4.9347 | -9.9631 | -14.7641 | -17.932 | -19.6904 | -20.1573 | 1.1663 | 0.28052 | 0.0077017 | -0.18517 | -0.47257 | -0.90137 | -1.5306 | -2.4325 | -3.5709 | -4.9347 | -9.9631 | -14.7641 | -17.932 | -19.6904 | -20.109 | 361018 | 507505 | PENRITH & SHAP | HUTTON | Firm Capacity marginally exceeded in FY28. Primary to benefit from reinforcement of supply to nearby MSA.
| Settle | 0.75637 | 0.70518 | 0.65885 | 0.62148 | 0.55699 | 0.48517 | 0.42072 | 0.35578 | 0.28781 | 0.22636 | -0.2655 | -1.214 | -2.0027 | -2.8061 | -3.5446 | 8.2564 | 8.2052 | 8.1588 | 8.1215 | 8.057 | 7.9852 | 7.9207 | 7.8558 | 7.7878 | 7.7264 | 7.2345 | 6.286 | 5.4973 | 4.6939 | 3.9095 | 0.75637 | 0.69246 | 0.62303 | 0.55753 | 0.48792 | 0.41773 | 0.32827 | 0.20693 | 0.13763 | 0.069673 | -0.13645 | -0.39668 | -0.66009 | -0.99608 | -1.2782 | 8.2564 | 8.1925 | 8.123 | 8.0575 | 7.9879 | 7.9177 | 7.8283 | 7.7069 | 7.6376 | 7.5697 | 7.3636 | 7.1033 | 6.8399 | 6.5039 | 6.268 | 0.75637 | 0.70405 | 0.65769 | 0.62002 | 0.55577 | 0.48459 | 0.42087 | 0.35759 | 0.30115 | 0.25225 | -0.14023 | -1.0341 | -1.7891 | -2.5394 | -3.2038 | 8.2564 | 8.204 | 8.1577 | 8.12 | 8.0558 | 7.9846 | 7.9209 | 7.8576 | 7.8011 | 7.7523 | 7.3598 | 6.4659 | 5.7109 | 4.9606 | 4.2375 | 0.75637 | 0.77826 | 0.75082 | 0.71351 | 0.65638 | 0.59422 | 0.49254 | 0.24903 | -0.046097 | -0.3582 | -1.259 | -2.1201 | -2.7898 | -3.1951 | -2.9321 | 8.2564 | 8.2783 | 8.2508 | 8.2135 | 8.1564 | 8.0942 | 7.9925 | 7.749 | 7.4539 | 7.1418 | 6.241 | 5.3799 | 4.7102 | 4.3049 | 4.5065 | 0.75637 | 0.71057 | 0.66527 | 0.63231 | 0.59687 | 0.56217 | 0.52029 | 0.46101 | 0.38537 | 0.30977 | 0.044675 | -0.3262 | -0.58529 | -0.84671 | -0.98951 | 8.2564 | 8.2106 | 8.1653 | 8.1323 | 8.0969 | 8.0622 | 8.0203 | 7.961 | 7.8854 | 7.8098 | 7.5447 | 7.1738 | 6.9147 | 6.6533 | 6.5081 | 0.75637 | 0.7662 | 0.72415 | 0.67065 | 0.59775 | 0.52324 | 0.40981 | 0.14062 | -0.17744 | -0.49638 | -1.4309 | -2.3311 | -3.0474 | -3.5157 | -3.3245 | 8.2564 | 8.2662 | 8.2242 | 8.1706 | 8.0978 | 8.0232 | 7.9098 | 7.6406 | 7.3226 | 7.0036 | 6.0691 | 5.1689 | 4.4526 | 3.9843 | 4.1301 | 381588 | 463721 | PADIHAM | PADIHAM
| Shannon St South | 6.4696 | 4.4631 | 4.0681 | 3.9927 | 3.8176 | 3.6097 | 3.4099 | 3.2245 | 3.0423 | 2.8807 | 1.1036 | -3.146 | -6.6444 | -10.3083 | -13.3821 | 11.9696 | 9.9631 | 9.5681 | 9.4927 | 9.3176 | 9.1097 | 8.9099 | 8.7245 | 8.5423 | 8.3807 | 6.6036 | 2.354 | -1.1444 | -4.8083 | -8.1492 | 6.4696 | 5.6201 | 5.294 | 4.9748 | 4.0103 | 2.8377 | 1.4211 | -0.26755 | -0.41172 | -0.55809 | -1.0003 | -1.4174 | -1.7411 | -2.5112 | -3.5168 | 11.9696 | 11.1201 | 10.794 | 10.4748 | 9.5103 | 8.3377 | 6.9211 | 5.2324 | 5.0883 | 4.9419 | 4.4997 | 4.0826 | 3.7589 | 2.9888 | 2.1025 | 6.4696 | 4.1888 | 3.7678 | 3.735 | 3.6034 | 3.4463 | 3.322 | 3.212 | 3.1298 | 3.0466 | 1.5402 | -2.4303 | -5.8355 | -9.3514 | -12.1762 | 11.9696 | 9.6888 | 9.2678 | 9.235 | 9.1034 | 8.9463 | 8.822 | 8.712 | 8.6298 | 8.5466 | 7.0402 | 3.0697 | -0.3355 | -3.8514 | -6.9848 | 6.4696 | 5.1404 | 4.93 | 4.938 | 4.8262 | 4.6758 | 4.3365 | 3.3231 | 2.1338 | 0.8009 | -3.0632 | -6.9003 | -9.9129 | -11.7415 | -10.3887 | 11.9696 | 10.6404 | 10.43 | 10.438 | 10.3262 | 10.1758 | 9.8365 | 8.8231 | 7.6338 | 6.3009 | 2.4368 | -1.4003 | -4.4129 | -6.2415 | -5.2089 | 6.4696 | 5.1501 | 4.9073 | 4.9003 | 4.8563 | 4.8012 | 4.71 | 4.5546 | 4.408 | 4.2318 | 3.506 | 2.0468 | -0.14107 | -1.9763 | -2.8343 | 11.9696 | 10.6501 | 10.4073 | 10.4003 | 10.3563 | 10.3012 | 10.21 | 10.0546 | 9.908 | 9.7318 | 9.006 | 7.5468 | 5.3589 | 3.5237 | 2.7293 | 6.4696 | 4.1566 | 3.6908 | 3.5915 | 3.3777 | 3.1465 | 2.7112 | 1.5826 | 0.41039 | -0.96897 | -5.0207 | -8.9417 | -12.2539 | -14.4623 | -13.5037 | 11.9696 | 9.6566 | 9.1908 | 9.0915 | 8.8777 | 8.6465 | 8.2112 | 7.0826 | 5.9104 | 4.531 | 0.47929 | -3.4417 | -6.7539 | -8.9623 | -8.2444 | 330806 | 435291 | BLACKPOOL | PENWORTHAM
| Shap | 3.3616 | 3.1407 | 3.0502 | 3.029 | 3.0194 | 3.008 | 2.9989 | 2.9871 | 2.9261 | 2.8674 | 0.55227 | 0.095565 | -2.1471 | -2.3748 | -2.588 | 6.1616 | 5.9407 | 5.8502 | 5.829 | 5.8194 | 5.808 | 5.7989 | 5.7871 | 5.7261 | 5.6674 | 3.3523 | 2.8956 | 0.65294 | 0.42518 | 0.16914 | 3.3616 | 3.3377 | 3.2817 | 3.2621 | 3.2649 | 3.2223 | 3.1372 | 3.0345 | 2.9793 | 2.925 | 2.7616 | 2.6047 | 2.4695 | 2.3467 | -1.9115 | 6.1616 | 6.1377 | 6.0817 | 6.0621 | 6.0649 | 6.0223 | 5.9372 | 5.8345 | 5.7793 | 5.725 | 5.5616 | 5.4047 | 5.2695 | 5.1467 | 0.89117 | 3.3616 | 3.1032 | 3.006 | 2.984 | 2.9748 | 2.9647 | 2.9578 | 2.9496 | 2.9146 | 2.8838 | 2.7036 | 0.79127 | -0.87155 | -1.0026 | -1.067 | 6.1616 | 5.9032 | 5.806 | 5.784 | 5.7748 | 5.7647 | 5.7578 | 5.7496 | 5.7146 | 5.6838 | 5.5036 | 3.5913 | 1.9284 | 1.7974 | 1.7141 | 3.3616 | 3.1928 | 3.1134 | 3.0885 | 1.762 | 1.808 | 1.8433 | 1.8313 | 1.7918 | 1.7573 | 0.1884 | -0.17565 | -0.44883 | -0.452 | -0.14217 | 6.1616 | 5.9928 | 5.9134 | 5.8885 | 4.562 | 4.608 | 4.6433 | 4.6313 | 4.5918 | 4.5573 | 2.9884 | 2.6244 | 2.3512 | 2.348 | 2.5883 | 3.3616 | 3.315 | 3.2566 | 3.2397 | 3.2441 | 3.2497 | 3.2524 | 3.2479 | 3.1907 | 3.1327 | 0.87592 | 0.55397 | -1.5581 | -1.5978 | -1.5713 | 6.1616 | 6.115 | 6.0566 | 6.0397 | 6.0441 | 6.0497 | 6.0524 | 6.0479 | 5.9907 | 5.9327 | 3.6759 | 3.354 | 1.2419 | 1.2022 | 1.195 | 3.3616 | 3.0789 | 2.9749 | 2.9438 | 1.6126 | 1.6585 | 1.6959 | 1.6842 | 1.6476 | 1.6159 | 0.038456 | -0.35293 | -0.64679 | -0.66841 | -0.37628 | 6.1616 | 5.8789 | 5.7749 | 5.7438 | 4.4126 | 4.4585 | 4.4959 | 4.4842 | 4.4476 | 4.4159 | 2.8385 | 2.4471 | 2.1532 | 2.1316 | 2.3584 | 356910 | 513357 | PENRITH & SHAP | HUTTON
| Shaw | 11.0815 | 10.8535 | 10.7883 | 10.7558 | 10.6324 | 10.4871 | 10.342 | 10.1929 | 9.9284 | 9.6314 | 7.6675 | 4.3709 | 1.5944 | -1.3619 | -4.02 | 15.7185 | 15.4905 | 15.4253 | 15.3928 | 15.2694 | 15.1241 | 14.979 | 14.8299 | 14.5654 | 14.2684 | 12.3045 | 9.0079 | 6.2314 | 3.2751 | 0.45106 | 11.0815 | 10.9589 | 10.8808 | 10.797 | 10.6564 | 10.482 | 10.2463 | 9.9567 | 9.7242 | 9.4832 | 8.5316 | 7.5019 | 6.5081 | 5.4748 | 4.776 | 15.7185 | 15.5959 | 15.5178 | 15.434 | 15.2934 | 15.119 | 14.8833 | 14.5937 | 14.3612 | 14.1202 | 13.1686 | 12.1389 | 11.1451 | 10.1118 | 9.5161 | 11.0815 | 10.8487 | 10.8051 | 10.7762 | 10.6622 | 10.5357 | 10.4349 | 10.337 | 10.1692 | 9.9603 | 8.1567 | 4.9682 | 2.2998 | -0.46998 | -2.7827 | 15.7185 | 15.4857 | 15.4421 | 15.4132 | 15.2992 | 15.1727 | 15.0719 | 14.974 | 14.8062 | 14.5973 | 12.7937 | 9.6052 | 6.9368 | 4.167 | 1.6496 | 11.0815 | 11.2199 | 11.271 | 11.263 | 11.1373 | 10.9732 | 10.6147 | 9.5897 | 8.5076 | 7.4634 | 4.3988 | 1.4411 | -1.0353 | -2.7424 | -1.8084 | 15.7185 | 15.8569 | 15.908 | 15.9 | 15.7743 | 15.6102 | 15.2517 | 14.2267 | 13.1446 | 12.1004 | 9.0358 | 6.0781 | 3.6017 | 1.8946 | 2.6194 | 11.0815 | 10.9899 | 10.9917 | 11.0325 | 11.0364 | 10.9949 | 10.9072 | 10.7943 | 10.609 | 10.3462 | 9.3158 | 8.1023 | 7.1975 | 6.4111 | 6.0493 | 15.7185 | 15.6269 | 15.6287 | 15.6695 | 15.6734 | 15.6319 | 15.5442 | 15.4313 | 15.246 | 14.9832 | 13.9528 | 12.7393 | 11.8345 | 11.0481 | 10.6934 | 11.0815 | 11.0898 | 11.0443 | 10.9448 | 10.7375 | 10.5207 | 10.0966 | 8.9844 | 7.8423 | 6.7369 | 3.4559 | 0.27537 | -2.471 | -4.4542 | -3.8137 | 15.7185 | 15.7268 | 15.6813 | 15.5818 | 15.3745 | 15.1577 | 14.7336 | 13.6214 | 12.4793 | 11.3739 | 8.0929 | 4.9124 | 2.166 | 0.18283 | 0.67838 | 394298 | 409450 | ROYTON | WHITEGATE
| Siddick | 17.6933 | 17.6686 | 17.5316 | 17.4152 | 17.3018 | 17.1852 | 17.0704 | 16.9478 | 16.78 | 16.608 | 16.1706 | 15.577 | 15.1192 | 14.6792 | 14.3278 | 24.1933 | 24.1686 | 24.0316 | 23.9152 | 23.8018 | 23.6852 | 23.5704 | 23.4478 | 23.28 | 23.108 | 22.6706 | 22.077 | 21.6192 | 21.1792 | 20.7978 | 17.6933 | 17.6729 | 17.6176 | 17.5863 | 17.5714 | 17.5581 | 17.5437 | 17.5275 | 17.4624 | 17.3944 | 17.1738 | 16.9294 | 16.7055 | 16.4706 | 16.3085 | 24.1933 | 24.1729 | 24.1176 | 24.0863 | 24.0714 | 24.0581 | 24.0437 | 24.0275 | 23.9624 | 23.8944 | 23.6738 | 23.4294 | 23.2055 | 22.9706 | 22.8234 | 17.6933 | 17.6677 | 17.5303 | 17.4134 | 17.3008 | 17.1865 | 17.0757 | 16.9591 | 16.8153 | 16.6687 | 16.2891 | 15.7331 | 15.3181 | 14.9638 | 14.7453 | 24.1933 | 24.1677 | 24.0303 | 23.9134 | 23.8008 | 23.6865 | 23.5757 | 23.4591 | 23.3153 | 23.1687 | 22.7891 | 22.2331 | 21.8181 | 21.4638 | 21.1923 | 17.6933 | 17.6733 | 17.539 | 17.4189 | 17.3044 | 17.1847 | 17.0331 | 16.7826 | 16.4998 | 16.2151 | 15.6196 | 15.0997 | 14.7303 | 14.5509 | 14.7641 | 24.1933 | 24.1733 | 24.039 | 23.9189 | 23.8044 | 23.6847 | 23.5331 | 23.2826 | 22.9998 | 22.7151 | 22.1196 | 21.5997 | 21.2303 | 21.0509 | 21.2096 | 17.6933 | 17.6733 | 17.5399 | 17.4315 | 17.3383 | 17.2426 | 17.1387 | 17.0185 | 16.8516 | 16.6772 | 16.3521 | 16.0344 | 15.83 | 15.6865 | 15.7206 | 24.1933 | 24.1733 | 24.0399 | 23.9315 | 23.8383 | 23.7426 | 23.6387 | 23.5185 | 23.3516 | 23.1772 | 22.8521 | 22.5344 | 22.33 | 22.1865 | 22.1971 | 17.6933 | 17.6702 | 17.5315 | 17.4066 | 17.2892 | 17.1717 | 17.0253 | 16.7797 | 16.5047 | 16.2274 | 15.6339 | 15.0903 | 14.6933 | 14.497 | 14.7027 | 24.1933 | 24.1702 | 24.0315 | 23.9066 | 23.7892 | 23.6717 | 23.5253 | 23.2797 | 23.0047 | 22.7274 | 22.1339 | 21.5903 | 21.1933 | 20.997 | 21.15 | 300289 | 530805 | STAINBURN & SIDDICK | HARKER
| Silloth | 24.3542 | 24.2574 | 24.1797 | 24.1274 | 24.0438 | 23.9556 | 23.8843 | 23.8165 | 23.6739 | 23.5274 | 22.7816 | 21.6669 | 20.6927 | 19.7377 | 18.951 | 41.6642 | 41.5674 | 41.4897 | 41.4374 | 41.3538 | 41.2656 | 41.1943 | 41.1265 | 40.9839 | 40.8374 | 40.0916 | 38.9769 | 38.0027 | 37.0477 | 36.1808 | 24.3542 | 24.2543 | 24.1472 | 24.0501 | 23.9407 | 23.8248 | 23.681 | 23.5095 | 23.3848 | 23.2595 | 22.7738 | 22.2902 | 21.8699 | 21.4406 | 21.158 | 41.6642 | 41.5643 | 41.4572 | 41.3601 | 41.2507 | 41.1348 | 40.991 | 40.8195 | 40.6948 | 40.5695 | 40.0838 | 39.6002 | 39.1799 | 38.7506 | 38.5045 | 24.3542 | 24.264 | 24.1971 | 24.1665 | 24.1044 | 24.0415 | 24.0057 | 23.9722 | 23.8958 | 23.8166 | 22.8749 | 21.6904 | 20.8307 | 20.1604 | 19.776 | 41.6642 | 41.574 | 41.5071 | 41.4765 | 41.4144 | 41.3515 | 41.3157 | 41.2822 | 41.2058 | 41.1266 | 40.1849 | 39.0004 | 38.1407 | 37.4704 | 37.0533 | 24.3542 | 24.3753 | 24.3424 | 24.3131 | 24.2595 | 24.1987 | 24.0509 | 23.6863 | 23.298 | 22.9203 | 21.8443 | 20.8481 | 20.0917 | 19.6972 | 20.1825 | 41.6642 | 41.6853 | 41.6524 | 41.6231 | 41.5695 | 41.5087 | 41.3609 | 40.9963 | 40.608 | 40.2303 | 39.1543 | 38.1581 | 37.4017 | 37.0072 | 37.3788 | 24.3542 | 24.2734 | 24.2085 | 24.1757 | 24.1441 | 24.1097 | 24.0646 | 23.9979 | 23.8822 | 23.7396 | 23.1885 | 22.5894 | 21.9856 | 21.4726 | 21.2825 | 41.6642 | 41.5834 | 41.5185 | 41.4857 | 41.4541 | 41.4197 | 41.3746 | 41.3079 | 41.1922 | 41.0496 | 40.4985 | 39.8994 | 39.2956 | 38.7826 | 38.5955 | 24.3542 | 24.3314 | 24.2568 | 24.1829 | 24.0871 | 23.9945 | 23.8456 | 23.469 | 23.08 | 22.6816 | 21.4827 | 20.3612 | 19.4922 | 18.9895 | 19.3794 | 41.6642 | 41.6414 | 41.5668 | 41.4929 | 41.3971 | 41.3045 | 41.1556 | 40.779 | 40.39 | 39.9916 | 38.7927 | 37.6712 | 36.8022 | 36.2995 | 36.5971 | 311307 | 553464 | CARLISLE | HARKER
| Skelmersdale | 8.9243 | 8.1665 | 7.8831 | 7.7605 | 7.5512 | 7.3072 | 7.0516 | 6.7729 | 6.3722 | 5.9622 | 4.051 | 1.5698 | -0.24458 | -1.7855 | -2.8046 | 13.5613 | 12.8035 | 12.5201 | 12.3975 | 12.1882 | 11.9442 | 11.6886 | 11.4099 | 11.0092 | 10.5992 | 8.688 | 6.2068 | 4.3924 | 2.8515 | 1.6924 | 8.9243 | 8.67 | 8.5256 | 8.4527 | 8.3665 | 8.2818 | 8.1438 | 7.931 | 7.6529 | 7.357 | 6.3743 | 5.245 | 4.0781 | 2.7665 | 1.7798 | 13.5613 | 13.307 | 13.1626 | 13.0897 | 13.0035 | 12.9188 | 12.7808 | 12.568 | 12.2899 | 11.994 | 11.0113 | 9.882 | 8.7151 | 7.4035 | 6.5579 | 8.9243 | 8.014 | 7.6563 | 7.4941 | 7.2404 | 6.9562 | 6.6818 | 6.3844 | 6.0165 | 5.6015 | 3.6207 | 1.1885 | -0.47724 | -1.8401 | -2.3438 | 13.5613 | 12.651 | 12.2933 | 12.1311 | 11.8774 | 11.5932 | 11.3188 | 11.0214 | 10.6535 | 10.2385 | 8.2577 | 5.8255 | 4.1598 | 2.7969 | 2.2129 | 8.9243 | 8.4807 | 8.2185 | 8.0473 | 7.7773 | 7.4644 | 7.0394 | 6.2423 | 5.3844 | 4.5047 | 1.9988 | 0.01037 | -1.1642 | -1.5097 | -1.1818 | 13.5613 | 13.1177 | 12.8555 | 12.6843 | 12.4143 | 12.1014 | 11.6764 | 10.8793 | 10.0214 | 9.1417 | 6.6358 | 4.6474 | 3.4728 | 3.1273 | 3.3652 | 8.9243 | 8.4515 | 8.2424 | 8.1662 | 8.0745 | 7.9571 | 7.7997 | 7.5767 | 7.1991 | 6.7967 | 5.3799 | 3.944 | 3.0107 | 2.0908 | 1.63 | 13.5613 | 13.0885 | 12.8794 | 12.8032 | 12.7115 | 12.5941 | 12.4367 | 12.2137 | 11.8361 | 11.4337 | 10.0169 | 8.581 | 7.6477 | 6.7278 | 6.2991 | 8.9243 | 8.1247 | 7.7498 | 7.5282 | 7.2168 | 6.8848 | 6.4384 | 5.6189 | 4.763 | 3.8816 | 1.2632 | -0.94375 | -2.3674 | -2.8819 | -2.6974 | 13.5613 | 12.7617 | 12.3868 | 12.1652 | 11.8538 | 11.5218 | 11.0754 | 10.2559 | 9.4 | 8.5186 | 5.9002 | 3.6933 | 2.2696 | 1.7551 | 1.8807 | 347198 | 407434 | SKELMERSDALE | WASHWAY FARM
| Slipway | 5.4927 | 5.1146 | 5.0067 | 4.9525 | 4.8343 | 4.7048 | 4.5943 | 4.5141 | 4.4487 | 4.403 | 3.6274 | 1.986 | 0.6288 | -0.73743 | -1.9191 | 7.4927 | 7.1146 | 7.0067 | 6.9525 | 6.8343 | 6.7048 | 6.5943 | 6.5141 | 6.4487 | 6.403 | 5.6274 | 3.986 | 2.6288 | 1.2626 | -0.068398 | 5.4927 | 5.3858 | 5.3063 | 5.2249 | 5.116 | 4.9984 | 4.7938 | 4.1544 | 4.0811 | 4.0095 | 3.8038 | 3.6181 | 3.476 | 3.3699 | 3.3121 | 7.4927 | 7.3858 | 7.3063 | 7.2249 | 7.116 | 6.9984 | 6.7938 | 6.1544 | 6.0811 | 6.0095 | 5.8038 | 5.6181 | 5.476 | 5.3699 | 5.3186 | 5.4927 | 5.0639 | 4.9532 | 4.9074 | 4.8009 | 4.6856 | 4.5909 | 4.5321 | 4.4935 | 4.4756 | 3.7846 | 2.2381 | 0.97163 | -0.28153 | -1.3309 | 7.4927 | 7.0639 | 6.9532 | 6.9074 | 6.8009 | 6.6856 | 6.5909 | 6.5321 | 6.4935 | 6.4756 | 5.7846 | 4.2381 | 2.9716 | 1.7185 | 0.49691 | 5.4927 | 5.3429 | 5.3013 | 5.2733 | 5.1732 | 5.0566 | 4.8457 | 4.2965 | 3.733 | 3.1895 | 1.6535 | 0.20513 | -0.92856 | -1.481 | -0.66981 | 7.4927 | 7.3429 | 7.3013 | 7.2733 | 7.1732 | 7.0566 | 6.8457 | 6.2965 | 5.733 | 5.1895 | 3.6535 | 2.2051 | 1.0714 | 0.51896 | 1.1563 | 5.4927 | 5.3909 | 5.344 | 5.3292 | 5.3033 | 5.2751 | 5.2424 | 5.1929 | 5.1172 | 5.0439 | 4.7601 | 4.4058 | 4.1959 | 4.0205 | 4.0995 | 7.4927 | 7.3909 | 7.344 | 7.3292 | 7.3033 | 7.2751 | 7.2424 | 7.1929 | 7.1172 | 7.0439 | 6.7601 | 6.4058 | 6.1959 | 6.0205 | 6.0455 | 5.4927 | 5.1521 | 4.9774 | 4.8377 | 4.6282 | 4.4135 | 4.1033 | 3.4978 | 2.9055 | 2.3343 | 0.71929 | -0.80861 | -2.0305 | -2.706 | -2.0457 | 7.4927 | 7.1521 | 6.9774 | 6.8377 | 6.6282 | 6.4135 | 6.1033 | 5.4978 | 4.9055 | 4.3343 | 2.7193 | 1.1914 | -0.030544 | -0.70603 | -0.18577 | 297180 | 518183 | EGREMONT | HARKER
| Snipe | 9.407 | 8.2967 | 7.9458 | 7.8223 | 7.4779 | 7.116 | 6.7479 | 6.3675 | 5.913 | 5.4744 | 3.5919 | 0.96012 | -1.2477 | -3.4031 | -5.3329 | 14.044 | 12.9337 | 12.5828 | 12.4593 | 12.1149 | 11.753 | 11.3849 | 11.0045 | 10.55 | 10.1114 | 8.2289 | 5.5971 | 3.3893 | 1.2339 | -0.77541 | 9.407 | 9.0308 | 8.8631 | 8.7859 | 8.7027 | 8.6048 | 8.4665 | 8.2804 | 8.0161 | 7.7495 | 6.9297 | 5.9633 | 5.0044 | 3.9457 | 3.1705 | 14.044 | 13.6678 | 13.5001 | 13.4229 | 13.3397 | 13.2418 | 13.1035 | 12.9174 | 12.6531 | 12.3865 | 11.5667 | 10.6003 | 9.6414 | 8.5827 | 7.9325 | 9.407 | 8.1252 | 7.7398 | 7.6148 | 7.2713 | 6.912 | 6.5468 | 6.1723 | 5.7604 | 5.3691 | 3.6175 | 1.1118 | -0.72531 | -2.4929 | -4.092 | 14.044 | 12.7622 | 12.3768 | 12.2518 | 11.9083 | 11.549 | 11.1838 | 10.8093 | 10.3974 | 10.0061 | 8.2545 | 5.7488 | 3.9117 | 2.1441 | 0.41069 | 9.407 | 8.6572 | 8.4128 | 8.3357 | 8.0225 | 7.6615 | 7.1821 | 6.3805 | 5.5299 | 4.6946 | 2.1474 | -0.55647 | -2.4938 | -3.5619 | -2.9667 | 14.044 | 13.2942 | 13.0498 | 12.9727 | 12.6595 | 12.2985 | 11.8191 | 11.0175 | 10.1669 | 9.3316 | 6.7844 | 4.0805 | 2.1432 | 1.0751 | 1.5281 | 9.407 | 8.7333 | 8.5045 | 8.4467 | 8.2076 | 7.9279 | 7.6069 | 7.2613 | 6.8172 | 6.3713 | 4.9375 | 3.4139 | 2.4888 | 1.864 | 1.5855 | 14.044 | 13.3703 | 13.1415 | 13.0837 | 12.8446 | 12.5649 | 12.2439 | 11.8983 | 11.4542 | 11.0083 | 9.5745 | 8.0509 | 7.1258 | 6.501 | 6.2304 | 9.407 | 8.1148 | 7.7121 | 7.5704 | 7.2036 | 6.8279 | 6.3429 | 5.505 | 4.6239 | 3.7614 | 1.0624 | -1.7725 | -3.8839 | -5.1389 | -4.747 | 14.044 | 12.7518 | 12.3491 | 12.2074 | 11.8406 | 11.4649 | 10.9799 | 10.142 | 9.2609 | 8.3984 | 5.6994 | 2.8645 | 0.75311 | -0.50192 | -0.20521 | 391844 | 398322 | DROYLSDEN | STALYBRIDGE
| South Park | 15.2453 | 14.8264 | 14.6471 | 14.5352 | 14.3905 | 14.2422 | 14.1059 | 13.9764 | 13.8287 | 13.6963 | 12.7916 | 11.2131 | 9.9398 | 8.5973 | 7.3883 | 19.7453 | 19.3264 | 19.1471 | 19.0352 | 18.8905 | 18.7422 | 18.6059 | 18.4764 | 18.3287 | 18.1963 | 17.2916 | 15.7131 | 14.4398 | 13.0973 | 11.7923 | 15.2453 | 15.0385 | 14.8881 | 14.7536 | 14.5932 | 14.4312 | 14.2295 | 13.9771 | 13.8015 | 13.6257 | 13.1058 | 12.5934 | 12.1397 | 11.6653 | 11.353 | 19.7453 | 19.5385 | 19.3881 | 19.2536 | 19.0932 | 18.9312 | 18.7295 | 18.4771 | 18.3015 | 18.1257 | 17.6058 | 17.0934 | 16.6397 | 16.1653 | 15.9016 | 15.2453 | 14.7842 | 14.6066 | 14.5144 | 14.3878 | 14.2601 | 14.1551 | 14.0572 | 13.9601 | 13.8663 | 13.0777 | 11.5931 | 10.3849 | 9.0569 | 7.9467 | 19.7453 | 19.2842 | 19.1066 | 19.0144 | 18.8878 | 18.7601 | 18.6551 | 18.5572 | 18.4601 | 18.3663 | 17.5777 | 16.0931 | 14.8849 | 13.5569 | 12.3273 | 15.2453 | 15.0473 | 14.9481 | 14.8988 | 14.7995 | 14.6812 | 14.4888 | 14.0069 | 13.5056 | 13.0034 | 11.4964 | 10.0242 | 8.8639 | 8.1036 | 8.6365 | 19.7453 | 19.5473 | 19.4481 | 19.3988 | 19.2995 | 19.1812 | 18.9888 | 18.5069 | 18.0056 | 17.5034 | 15.9964 | 14.5242 | 13.3639 | 12.6036 | 13.0138 | 15.2453 | 14.9764 | 14.8458 | 14.7725 | 14.6894 | 14.5985 | 14.5008 | 14.4006 | 14.2644 | 14.1333 | 13.7014 | 13.2246 | 12.9169 | 12.6398 | 12.5094 | 19.7453 | 19.4764 | 19.3458 | 19.2725 | 19.1894 | 19.0985 | 19.0008 | 18.9006 | 18.7644 | 18.6333 | 18.2014 | 17.7246 | 17.4169 | 17.1398 | 17.0124 | 15.2453 | 14.8478 | 14.6675 | 14.5589 | 14.4064 | 14.2546 | 14.0231 | 13.4856 | 12.9511 | 12.4158 | 10.8629 | 9.3795 | 8.1621 | 7.2545 | 7.6292 | 19.7453 | 19.3478 | 19.1675 | 19.0589 | 18.9064 | 18.7546 | 18.5231 | 17.9856 | 17.4511 | 16.9158 | 15.3629 | 13.8795 | 12.6621 | 11.7545 | 12.0426 | 336410 | 427512 | LYTHAM | PENWORTHAM
| Spa Rd | 7.7306 | 5.9991 | 5.1773 | 4.6744 | 4.1145 | 3.5317 | 2.9609 | 2.3792 | 1.7349 | 1.0932 | -1.7226 | -5.4945 | -8.3445 | -10.7598 | -12.348 | 7.7306 | 5.9991 | 5.1773 | 4.6744 | 4.1145 | 3.5317 | 2.9609 | 2.3792 | 1.7349 | 1.0932 | -1.7226 | -5.4945 | -8.3445 | -10.7598 | -12.5156 | 7.7306 | 7.1596 | 6.6847 | 6.3048 | 5.8992 | 5.4578 | 4.9317 | 4.3095 | 3.8614 | 3.3856 | 1.9572 | 0.51406 | -0.79223 | -2.0896 | -3.0508 | 7.7306 | 7.1596 | 6.6847 | 6.3048 | 5.8992 | 5.4578 | 4.9317 | 4.3095 | 3.8614 | 3.3856 | 1.9572 | 0.51406 | -0.79223 | -2.0896 | -2.9124 | 7.7306 | 5.6331 | 4.6249 | 3.9664 | 3.2445 | 2.4902 | 1.7335 | 0.9525 | 0.14379 | -0.66685 | -4.0337 | -7.9133 | -10.551 | -12.4404 | -13.0509 | 7.7306 | 5.6331 | 4.6249 | 3.9664 | 3.2445 | 2.4902 | 1.7335 | 0.9525 | 0.14379 | -0.66685 | -4.0337 | -7.9133 | -10.551 | -12.4404 | -13.2376 | 7.7306 | 6.3941 | 5.6152 | 5.0707 | 4.4416 | 3.7324 | 2.8275 | 1.4306 | -0.028408 | -1.4504 | -5.4784 | -8.8581 | -10.9944 | -11.912 | -11.1165 | 7.7306 | 6.3941 | 5.6152 | 5.0707 | 4.4416 | 3.7324 | 2.8275 | 1.4306 | -0.028408 | -1.4504 | -5.4784 | -8.8581 | -10.9944 | -11.912 | -11.3225 | 7.7306 | 6.847 | 6.2505 | 5.8552 | 5.4715 | 5.0386 | 4.5534 | 4.0156 | 3.3714 | 2.6991 | 0.52216 | -1.6309 | -3.2199 | -4.5169 | -5.0767 | 7.7306 | 6.847 | 6.2505 | 5.8552 | 5.4715 | 5.0386 | 4.5534 | 4.0156 | 3.3714 | 2.6991 | 0.52216 | -1.6309 | -3.2199 | -4.5169 | -5.0348 | 7.7306 | 5.6256 | 4.5888 | 3.9084 | 3.1584 | 2.3873 | 1.4509 | -0.039543 | -1.5162 | -2.9749 | -7.1368 | -10.6236 | -12.885 | -13.9425 | -13.3791 | 7.7306 | 5.6256 | 4.5888 | 3.9084 | 3.1584 | 2.3873 | 1.4509 | -0.039543 | -1.5162 | -2.9749 | -7.1368 | -10.6236 | -12.885 | -13.9425 | -13.5259 | 371065 | 409109 | BOLTON | KEARSLEY
| Spadeadam 132/11kV* | 27.3166 | 27.3524 | 27.2794 | 27.2653 | 27.3012 | 27.3448 | 27.3948 | 27.4494 | 27.4215 | 27.3994 | 27.3689 | 27.3817 | 27.4462 | 27.6039 | 27.8925 | 34.3166 | 34.3524 | 34.2794 | 34.2653 | 34.3012 | 34.3448 | 34.3948 | 34.4494 | 34.4215 | 34.3994 | 34.3689 | 34.3817 | 34.4462 | 34.6039 | 34.8278 | 27.3166 | 27.3522 | 27.2825 | 27.2709 | 27.3058 | 27.3434 | 27.3849 | 27.4309 | 27.3636 | 27.2995 | 27.137 | 27.0158 | 26.934 | 26.8873 | 26.9194 | 34.3166 | 34.3522 | 34.2825 | 34.2709 | 34.3058 | 34.3434 | 34.3849 | 34.4309 | 34.3636 | 34.2995 | 34.137 | 34.0158 | 33.934 | 33.8873 | 33.9061 | 27.3166 | 27.35 | 27.2763 | 27.2591 | 27.2939 | 27.3367 | 27.3853 | 27.4387 | 27.4455 | 27.4641 | 27.5589 | 27.7019 | 27.9001 | 28.2396 | 28.7572 | 34.3166 | 34.35 | 34.2763 | 34.2591 | 34.2939 | 34.3367 | 34.3853 | 34.4387 | 34.4455 | 34.4641 | 34.5589 | 34.7019 | 34.9001 | 35.2396 | 35.6467 | 27.3166 | 27.3574 | 27.292 | 27.2844 | 27.3278 | 27.3747 | 27.4265 | 27.4869 | 27.4981 | 27.5204 | 27.6231 | 27.767 | 27.9653 | 28.3032 | 28.8241 | 34.3166 | 34.3574 | 34.292 | 34.2844 | 34.3278 | 34.3747 | 34.4265 | 34.4869 | 34.4981 | 34.5204 | 34.6231 | 34.767 | 34.9653 | 35.3032 | 35.7129 | 27.3166 | 27.3539 | 27.2855 | 27.2779 | 27.32 | 27.3651 | 27.4139 | 27.4706 | 27.4454 | 27.4251 | 27.3952 | 27.4028 | 27.4617 | 27.6109 | 27.8972 | 34.3166 | 34.3539 | 34.2855 | 34.2779 | 34.32 | 34.3651 | 34.4139 | 34.4706 | 34.4454 | 34.4251 | 34.3952 | 34.4028 | 34.4617 | 34.6109 | 34.8326 | 27.3166 | 27.3515 | 27.2779 | 27.2606 | 27.2954 | 27.3383 | 27.387 | 27.44 | 27.4463 | 27.4643 | 27.5586 | 27.7024 | 27.9016 | 28.2429 | 28.7639 | 34.3166 | 34.3515 | 34.2779 | 34.2606 | 34.2954 | 34.3383 | 34.387 | 34.44 | 34.4463 | 34.4643 | 34.5586 | 34.7024 | 34.9016 | 35.2429 | 35.6533 | 361282 | 570359 | - | HARKER
| Spotland | 8.0181 | 7.655 | 7.5277 | 7.4578 | 7.3085 | 7.1555 | 7.0266 | 6.9134 | 6.7616 | 6.6321 | 5.2588 | 2.5578 | 0.21967 | -2.3395 | -4.574 | 11.5181 | 11.155 | 11.0277 | 10.9578 | 10.8085 | 10.6555 | 10.5266 | 10.4134 | 10.2616 | 10.1321 | 8.7588 | 6.0578 | 3.7197 | 1.1605 | -1.2182 | 8.0181 | 7.8721 | 7.7847 | 7.6999 | 7.5701 | 7.4157 | 7.2108 | 6.952 | 6.7315 | 6.5084 | 5.8402 | 5.1777 | 4.4922 | 3.7194 | 3.1987 | 11.5181 | 11.3721 | 11.2847 | 11.1999 | 11.0701 | 10.9157 | 10.7108 | 10.452 | 10.2315 | 10.0084 | 9.3402 | 8.6777 | 7.9922 | 7.2194 | 6.7833 | 8.0181 | 7.6249 | 7.5119 | 7.3271 | 7.067 | 6.8099 | 6.5956 | 6.4023 | 6.1716 | 5.9537 | 4.6272 | 2.102 | -0.083389 | -2.4699 | -4.5192 | 11.5181 | 11.1249 | 11.0119 | 10.8271 | 10.567 | 10.3099 | 10.0956 | 9.9023 | 9.6716 | 9.4537 | 8.1272 | 5.602 | 3.4166 | 1.0301 | -1.1982 | 8.0181 | 7.9655 | 7.9424 | 7.7767 | 7.5088 | 7.2196 | 6.7926 | 5.8295 | 4.826 | 3.8316 | 1.2305 | -1.1645 | -3.1676 | -4.5065 | -3.6817 | 11.5181 | 11.4655 | 11.4424 | 11.2767 | 11.0088 | 10.7196 | 10.2926 | 9.3295 | 8.326 | 7.3316 | 4.7305 | 2.3355 | 0.33243 | -1.0065 | -0.36274 | 8.0181 | 7.8446 | 7.7919 | 7.7895 | 7.7637 | 7.7067 | 7.6258 | 7.5423 | 7.3991 | 7.2631 | 6.7513 | 5.8618 | 5.1903 | 4.5545 | 4.1908 | 11.5181 | 11.3446 | 11.2919 | 11.2895 | 11.2637 | 11.2067 | 11.1258 | 11.0423 | 10.8991 | 10.7631 | 10.2513 | 9.3618 | 8.6903 | 8.0545 | 7.7108 | 8.0181 | 7.7712 | 7.6453 | 7.3963 | 7.0532 | 6.7134 | 6.2229 | 5.1716 | 4.0995 | 3.0367 | 0.23206 | -2.3339 | -4.5082 | -6.0706 | -5.5033 | 11.5181 | 11.2712 | 11.1453 | 10.8963 | 10.5532 | 10.2134 | 9.7229 | 8.6716 | 7.5995 | 6.5367 | 3.7321 | 1.1661 | -1.0082 | -2.5706 | -2.1279 | 387882 | 414309 | ROCHDALE CENTRAL | ROCHDALE
| Spring Cottage | 4.6063 | 4.2499 | 3.9006 | 3.6437 | 3.3828 | 12.2871 | 12.254 | 12.2127 | 12.1141 | 12.0213 | 11.3864 | 10.3032 | 9.4235 | 8.424 | 7.626 | 18.3543 | 17.9979 | 17.6486 | 17.3917 | 17.1308 | 16.7871 | 16.754 | 16.7127 | 16.6141 | 16.5213 | 15.8864 | 14.8032 | 13.9235 | 12.924 | 12.0086 | 4.6063 | 4.551 | 4.4478 | 4.3805 | 4.326 | 13.4853 | 13.4271 | 13.3442 | 13.236 | 13.1279 | 12.7997 | 12.4632 | 12.1646 | 11.8548 | 11.659 | 18.3543 | 18.299 | 18.1958 | 18.1285 | 18.074 | 17.9853 | 17.9271 | 17.8442 | 17.736 | 17.6279 | 17.2997 | 16.9632 | 16.6646 | 16.3548 | 16.1819 | 4.6063 | 4.1926 | 3.8336 | 3.5759 | 3.3159 | 12.2223 | 12.1918 | 12.1551 | 12.0895 | 12.0331 | 11.5 | 10.5138 | 9.736 | 8.889 | 8.3013 | 18.3543 | 17.9406 | 17.5816 | 17.3239 | 17.0639 | 16.7223 | 16.6918 | 16.6551 | 16.5895 | 16.5331 | 16 | 15.0138 | 14.236 | 13.389 | 12.6446 | 4.6063 | 4.4 | 4.0939 | 3.8573 | 3.615 | 12.5305 | 12.4329 | 12.1115 | 11.7524 | 11.4036 | 10.3997 | 9.2748 | 8.4061 | 7.9453 | 8.6635 | 18.3543 | 18.148 | 17.8419 | 17.6053 | 17.363 | 17.0305 | 16.9329 | 16.6115 | 16.2524 | 15.9036 | 14.8997 | 13.7748 | 12.9061 | 12.4453 | 13.0032 | 4.6063 | 4.5407 | 4.2525 | 4.0161 | 3.7968 | 12.7369 | 12.7178 | 12.6804 | 12.578 | 12.4742 | 12.1256 | 11.7588 | 11.5296 | 11.3633 | 11.4245 | 18.3543 | 18.2887 | 18.0005 | 17.7641 | 17.5448 | 17.2369 | 17.2178 | 17.1804 | 17.078 | 16.9742 | 16.6256 | 16.2588 | 16.0296 | 15.8633 | 15.8883 | 4.6063 | 4.2139 | 3.8533 | 3.5881 | 3.3202 | 12.2227 | 12.115 | 11.7724 | 11.4042 | 11.0467 | 10.0226 | 8.9366 | 8.0055 | 7.4525 | 8.0578 | 18.3543 | 17.9619 | 17.6013 | 17.3361 | 17.0682 | 16.7227 | 16.615 | 16.2724 | 15.9042 | 15.5467 | 14.5226 | 13.4366 | 12.5055 | 11.9525 | 12.4238 | 385446 | 437481 | NELSON | PADIHAM
| Spring Garden St 11kV | 19.6133 | 19.4786 | 18.7477 | 18.0242 | 17.2307 | 16.4287 | 15.6486 | 13.209 | 13.1035 | 13.0114 | 11.8586 | 9.5907 | 7.7228 | 5.3517 | 3.5904 | 28.6133 | 28.4786 | 27.7477 | 27.0242 | 26.2307 | 25.4287 | 24.6486 | 22.209 | 22.1035 | 22.0114 | 20.8586 | 18.5907 | 16.7228 | 14.3517 | 12.5898 | 19.6133 | 19.4588 | 19.3058 | 19.151 | 18.9616 | 18.7693 | 18.532 | 18.2324 | 18.0182 | 17.809 | 17.2165 | 16.6297 | 16.1036 | 15.1283 | 14.0093 | 28.6133 | 28.4588 | 28.3058 | 28.151 | 27.9616 | 27.7693 | 27.532 | 27.2324 | 27.0182 | 26.809 | 26.2165 | 25.6297 | 25.1036 | 24.1283 | 23.0692 | 19.6133 | 19.4898 | 18.7705 | 18.0673 | 17.293 | 16.5126 | 15.7684 | 13.4364 | 13.3872 | 13.342 | 11.1154 | 8.5111 | 6.7937 | 5.0816 | 3.5176 | 28.6133 | 28.4898 | 27.7705 | 27.0673 | 26.293 | 25.5126 | 24.7684 | 22.4364 | 22.3872 | 22.342 | 20.1154 | 17.5111 | 15.7937 | 14.0816 | 12.4809 | 19.6133 | 19.7036 | 19.0485 | 17.7776 | 14.1872 | 12.4902 | 11.8386 | 11.351 | 10.7378 | 10.1232 | 8.1305 | 6.1012 | 4.3771 | 3.4795 | 4.2714 | 28.6133 | 28.7036 | 28.0485 | 26.7776 | 23.1872 | 21.4902 | 20.8386 | 20.351 | 19.7378 | 19.1232 | 17.1305 | 15.1012 | 13.3771 | 12.4795 | 13.0975 | 19.6133 | 19.4956 | 18.7859 | 18.1015 | 17.3945 | 16.6819 | 15.9583 | 13.5447 | 13.4373 | 13.33 | 12.846 | 12.2117 | 11.8001 | 11.0035 | 10.6815 | 28.6133 | 28.4956 | 27.7859 | 27.1015 | 26.3945 | 25.6819 | 24.9583 | 22.5447 | 22.4373 | 22.33 | 21.846 | 21.2117 | 20.8001 | 20.0035 | 19.8244 | 19.6133 | 19.6642 | 18.9581 | 17.6302 | 13.9865 | 12.251 | 11.5504 | 11.0013 | 10.3519 | 9.6991 | 7.5811 | 5.4449 | 3.5944 | 2.5078 | 3.0645 | 28.6133 | 28.6642 | 27.9581 | 26.6302 | 22.9865 | 21.251 | 20.5504 | 20.0013 | 19.3519 | 18.6991 | 16.5811 | 14.4449 | 12.5944 | 11.5078 | 11.9438 | 347661 | 461494 | LANCASTER | HEYSHAM
| Spring Garden St 6.6kV | 11.5579 | 11.2828 | 10.9409 | 10.6295 | 10.2906 | 9.9522 | 9.6331 | 9.3182 | 8.9676 | 8.639 | 7.3007 | 5.3403 | 3.5975 | 1.7253 | -0.083318 | 15.6949 | 15.4198 | 15.0779 | 14.7665 | 14.4276 | 14.0892 | 13.7701 | 13.4552 | 13.1046 | 12.776 | 11.4377 | 9.4773 | 7.7345 | 5.8623 | 4.0785 | 11.5579 | 11.2697 | 10.9278 | 10.6066 | 10.2737 | 9.9371 | 9.5507 | 9.0607 | 8.6892 | 8.3296 | 7.3336 | 6.3483 | 5.4521 | 4.2885 | 3.355 | 15.6949 | 15.4067 | 15.0648 | 14.7436 | 14.4107 | 14.0741 | 13.6877 | 13.1977 | 12.8262 | 12.4666 | 11.4706 | 10.4853 | 9.5891 | 8.4255 | 7.6531 | 11.5579 | 11.2792 | 10.9368 | 10.6235 | 10.2842 | 9.9458 | 9.625 | 9.311 | 8.9937 | 8.7021 | 7.4735 | 5.6418 | 4.0218 | 2.3296 | 0.76058 | 15.6949 | 15.4162 | 15.0738 | 14.7605 | 14.4212 | 14.0828 | 13.762 | 13.448 | 13.1307 | 12.8391 | 11.6105 | 9.7788 | 8.1588 | 6.4666 | 4.881 | 11.5579 | 11.4128 | 11.1325 | 10.8687 | 10.5734 | 10.2694 | 9.8943 | 9.2631 | 8.5862 | 7.9324 | 6.0885 | 4.0763 | 2.5714 | 1.4784 | 1.4848 | 15.6949 | 15.5498 | 15.2695 | 15.0057 | 14.7104 | 14.4064 | 14.0313 | 13.4001 | 12.7232 | 12.0694 | 10.2255 | 8.2133 | 6.7084 | 5.6154 | 5.5962 | 11.5579 | 11.304 | 10.9776 | 10.6948 | 10.4156 | 10.1402 | 9.8677 | 9.5775 | 9.2188 | 8.871 | 7.8778 | 6.8764 | 6.2011 | 5.5267 | 4.9346 | 15.6949 | 15.441 | 15.1146 | 14.8318 | 14.5526 | 14.2772 | 14.0047 | 13.7145 | 13.3558 | 13.008 | 12.0148 | 11.0134 | 10.3381 | 9.6637 | 9.1587 | 11.5579 | 11.3736 | 11.0444 | 10.726 | 10.379 | 10.0385 | 9.6299 | 8.9473 | 8.2567 | 7.591 | 5.6678 | 3.604 | 2.0347 | 0.84929 | 0.73002 | 15.6949 | 15.5106 | 15.1814 | 14.863 | 14.516 | 14.1755 | 13.7669 | 13.0843 | 12.3937 | 11.728 | 9.8048 | 7.741 | 6.1717 | 4.9863 | 4.8706 | 347651 | 461484 | LANCASTER | HEYSHAM
| Squires Gate | 11.2871 | 8.2783 | 7.6468 | 7.5265 | 7.3387 | 7.1343 | 6.9195 | 6.6719 | 6.3281 | 5.9905 | 4.6736 | 2.9148 | 1.3148 | -0.31116 | -1.6684 | 15.8871 | 12.8783 | 12.2468 | 12.1265 | 11.9387 | 11.7343 | 11.5195 | 11.2719 | 10.9281 | 10.5905 | 9.2736 | 7.5148 | 5.9148 | 4.2888 | 2.8748 | 11.2871 | 10.183 | 9.8859 | 9.7397 | 9.5001 | 9.2121 | 8.8624 | 8.4496 | 8.1 | 7.7386 | 6.6275 | 5.5252 | 4.5284 | 3.533 | 2.9056 | 15.8871 | 14.783 | 14.4859 | 14.3397 | 14.1001 | 13.8121 | 13.4624 | 13.0496 | 12.7 | 12.3386 | 11.2275 | 10.1252 | 9.1284 | 8.133 | 7.5938 | 11.2871 | 7.8197 | 7.1288 | 7.0516 | 6.9239 | 6.7756 | 6.6387 | 6.407 | 6.11 | 5.7946 | 4.5041 | 2.7942 | 1.1423 | -0.54638 | -1.6351 | 15.8871 | 12.4197 | 11.7288 | 11.6516 | 11.5239 | 11.3756 | 11.2387 | 11.007 | 10.71 | 10.3946 | 9.1041 | 7.3942 | 5.7423 | 4.0536 | 2.8569 | 11.2871 | 8.9664 | 8.506 | 8.4527 | 8.3565 | 8.2349 | 8.0342 | 7.4729 | 6.8334 | 6.1879 | 4.2068 | 2.2389 | 0.74 | -0.33256 | 0.12184 | 15.8871 | 13.5664 | 13.106 | 13.0527 | 12.9565 | 12.8349 | 12.6342 | 12.0729 | 11.4334 | 10.7879 | 8.8068 | 6.8389 | 5.34 | 4.2674 | 4.609 | 11.2871 | 9.2489 | 8.8177 | 8.7506 | 8.6797 | 8.523 | 8.32 | 8.1129 | 7.814 | 7.5094 | 6.4907 | 5.4261 | 4.6724 | 4.066 | 3.8272 | 15.8871 | 13.8489 | 13.4177 | 13.3506 | 13.2797 | 13.123 | 12.92 | 12.7129 | 12.414 | 12.1094 | 11.0907 | 10.0261 | 9.2724 | 8.666 | 8.4342 | 11.2871 | 7.4739 | 6.6922 | 6.5594 | 6.3676 | 6.1593 | 5.8941 | 5.3302 | 4.6494 | 3.9492 | 1.7637 | -0.41369 | -2.0923 | -3.3279 | -3.0215 | 15.8871 | 12.0739 | 11.2922 | 11.1594 | 10.9676 | 10.7593 | 10.4941 | 9.9302 | 9.2494 | 8.5492 | 6.3637 | 4.1863 | 2.5077 | 1.2721 | 1.4965 | 332037 | 432063 | BLACKPOOL | PENWORTHAM
| St Annes | 11.1263 | 10.3681 | 10.1399 | 10.0273 | 9.8701 | 9.7094 | 9.5593 | 9.4222 | 9.2674 | 9.1299 | 8.1843 | 6.5173 | 5.1573 | 3.6889 | 2.3348 | 14.6263 | 13.8681 | 13.6399 | 13.5273 | 13.3701 | 13.2094 | 13.0593 | 12.9222 | 12.7674 | 12.6299 | 11.6843 | 10.0173 | 8.6573 | 7.1889 | 5.7708 | 11.1263 | 10.7518 | 10.5993 | 10.492 | 10.3608 | 10.241 | 10.0899 | 9.8933 | 9.7239 | 9.5466 | 9.0118 | 8.4824 | 7.9725 | 7.4065 | 6.9932 | 14.6263 | 14.2518 | 14.0993 | 13.992 | 13.8608 | 13.741 | 13.5899 | 13.3933 | 13.2239 | 13.0466 | 12.5118 | 11.9824 | 11.4725 | 10.9065 | 10.5622 | 11.1263 | 10.2693 | 10.0345 | 9.9426 | 9.8117 | 9.6779 | 9.5663 | 9.4707 | 9.3662 | 9.2705 | 8.4488 | 6.8817 | 5.6093 | 4.2491 | 3.0216 | 14.6263 | 13.7693 | 13.5345 | 13.4426 | 13.3117 | 13.1779 | 13.0663 | 12.9707 | 12.8662 | 12.7705 | 11.9488 | 10.3817 | 9.1093 | 7.7491 | 6.4335 | 11.1263 | 10.6217 | 10.4653 | 10.3814 | 10.2416 | 10.0864 | 9.8578 | 9.3484 | 8.8152 | 8.2836 | 6.7408 | 5.2446 | 4.0773 | 3.3041 | 3.6972 | 14.6263 | 14.1217 | 13.9653 | 13.8814 | 13.7416 | 13.5864 | 13.3578 | 12.8484 | 12.3152 | 11.7836 | 10.2408 | 8.7446 | 7.5773 | 6.8041 | 7.1065 | 11.1263 | 10.4971 | 10.3108 | 10.235 | 10.1456 | 10.0479 | 9.9515 | 9.8531 | 9.7109 | 9.5724 | 9.0973 | 8.551 | 8.185 | 7.833 | 7.6246 | 14.6263 | 13.9971 | 13.8108 | 13.735 | 13.6456 | 13.5479 | 13.4515 | 13.3531 | 13.2109 | 13.0724 | 12.5973 | 12.051 | 11.685 | 11.333 | 11.1316 | 11.1263 | 10.2628 | 10.0069 | 9.871 | 9.6866 | 9.5038 | 9.2415 | 8.6839 | 8.1146 | 7.5471 | 5.8923 | 4.2992 | 3.0366 | 2.1493 | 2.4113 | 14.6263 | 13.7628 | 13.5069 | 13.371 | 13.1866 | 13.0038 | 12.7415 | 12.1839 | 11.6146 | 11.0471 | 9.3923 | 7.7992 | 6.5366 | 5.6493 | 5.8496 | 331716 | 429849 | LYTHAM | PENWORTHAM
| St Johns | 14.0959 | 12.1918 | 12.1735 | 12.0865 | 12.0029 | 5.157 | 5.0831 | 5.0106 | 4.894 | 4.7826 | 4.2384 | 3.3922 | 2.6885 | 1.9013 | 1.1546 | 18.7329 | 16.8288 | 16.8105 | 16.7235 | 16.6399 | 9.857 | 9.7831 | 9.7106 | 9.594 | 9.4826 | 8.9384 | 8.0922 | 7.3885 | 6.6013 | 5.8507 | 14.0959 | 13.1727 | 13.3259 | 13.2011 | 13.0954 | 6.2256 | 6.1052 | 5.9616 | 5.8114 | 5.663 | 5.2453 | 4.837 | 4.5049 | 4.1328 | 3.7493 | 18.7329 | 17.8097 | 17.9629 | 17.8381 | 17.7324 | 10.9256 | 10.8052 | 10.6616 | 10.5114 | 10.363 | 9.9453 | 9.537 | 9.2049 | 8.8328 | 8.5147 | 14.0959 | 11.9534 | 11.8864 | 11.7974 | 11.7127 | 4.8657 | 4.7889 | 4.7148 | 4.6204 | 4.5341 | 4.0686 | 3.3166 | 2.7148 | 2.072 | 1.4303 | 18.7329 | 16.5904 | 16.5234 | 16.4344 | 16.3497 | 9.5657 | 9.4889 | 9.4148 | 9.3204 | 9.2341 | 8.7686 | 8.0166 | 7.4148 | 6.772 | 6.1083 | 14.0959 | 12.5018 | 12.5498 | 12.4716 | 12.3958 | 5.5619 | 5.4524 | 5.198 | 4.9099 | 4.6292 | 3.8508 | 3.1341 | 2.5739 | 2.1593 | 2.2421 | 18.7329 | 17.1388 | 17.1868 | 17.1086 | 17.0328 | 10.2619 | 10.1524 | 9.898 | 9.6099 | 9.3292 | 8.5508 | 7.8341 | 7.2739 | 6.8593 | 6.9151 | 14.0959 | 12.7753 | 12.8754 | 12.7922 | 12.731 | 5.9106 | 5.8502 | 5.7729 | 5.6407 | 5.508 | 5.1226 | 4.7518 | 4.4888 | 4.2134 | 4.0511 | 18.7329 | 17.4123 | 17.5124 | 17.4292 | 17.368 | 10.6106 | 10.5502 | 10.4729 | 10.3407 | 10.208 | 9.8226 | 9.4518 | 9.1888 | 8.9134 | 8.7677 | 14.0959 | 11.7856 | 11.6805 | 11.5921 | 11.5054 | 4.6596 | 4.5386 | 4.2703 | 3.9816 | 3.7005 | 2.9207 | 2.1935 | 1.6175 | 1.2072 | 1.2854 | 18.7329 | 16.4226 | 16.3175 | 16.2291 | 16.1424 | 9.3596 | 9.2386 | 8.9703 | 8.6816 | 8.4005 | 7.6207 | 6.8935 | 6.3175 | 5.9072 | 5.9704 | 0 | 0 | FREDERICK RD | KEARSLEY
| St Marys | 14.3928 | 13.2665 | 12.0186 | 11.3024 | 10.5969 | 9.8904 | 9.1924 | 8.4985 | 7.8118 | 7.5889 | 6.751 | 5.7407 | 4.9732 | 4.2092 | 3.5095 | 19.0298 | 17.9035 | 16.6556 | 15.9394 | 15.2339 | 14.5274 | 13.8294 | 13.1355 | 12.4488 | 12.2259 | 11.388 | 10.3777 | 9.6102 | 8.8462 | 8.1853 | 14.3928 | 13.9374 | 13.4363 | 13.1254 | 12.8278 | 12.5264 | 12.206 | 11.8488 | 11.5301 | 11.2951 | 10.5977 | 9.898 | 9.244 | 8.518 | 7.854 | 19.0298 | 18.5744 | 18.0733 | 17.7624 | 17.4648 | 17.1634 | 16.843 | 16.4858 | 16.1671 | 15.9321 | 15.2347 | 14.535 | 13.881 | 13.155 | 12.608 | 14.3928 | 13.0612 | 11.759 | 11.0103 | 10.2678 | 9.5195 | 8.7727 | 8.0247 | 7.3084 | 7.0541 | 6.1057 | 5.0739 | 4.3568 | 3.7045 | 3.2162 | 19.0298 | 17.6982 | 16.396 | 15.6473 | 14.9048 | 14.1565 | 13.4097 | 12.6617 | 11.9454 | 11.6911 | 10.7427 | 9.7109 | 8.9938 | 8.3415 | 7.8852 | 14.3928 | 13.4276 | 12.2185 | 11.4938 | 10.7722 | 10.0385 | 9.2748 | 8.4229 | 7.5881 | 7.2213 | 6.1525 | 5.2219 | 4.6111 | 4.1739 | 3.984 | 19.0298 | 18.0646 | 16.8555 | 16.1308 | 15.4092 | 14.6755 | 13.9118 | 13.0599 | 12.2251 | 11.8583 | 10.7895 | 9.8589 | 9.2481 | 8.8109 | 8.6462 | 14.3928 | 13.6318 | 12.4666 | 11.7692 | 11.0981 | 10.4256 | 9.7526 | 9.0724 | 8.3837 | 8.151 | 7.4245 | 6.7104 | 6.1859 | 5.6361 | 5.1698 | 19.0298 | 18.2688 | 17.1036 | 16.4062 | 15.7351 | 15.0626 | 14.3896 | 13.7094 | 13.0207 | 12.788 | 12.0615 | 11.3474 | 10.8229 | 10.2731 | 9.8796 | 14.3928 | 12.9704 | 11.6451 | 10.8894 | 10.1388 | 9.3855 | 8.6038 | 7.7235 | 6.8792 | 6.5041 | 5.4145 | 4.4672 | 3.8361 | 3.3733 | 3.135 | 19.0298 | 17.6074 | 16.2821 | 15.5264 | 14.7758 | 14.0225 | 13.2408 | 12.3605 | 11.5162 | 11.1411 | 10.0515 | 9.1042 | 8.4731 | 8.0103 | 7.8095 | 392582 | 405316 | GREENHILL | WHITEGATE
| St Marys St | 6.7868 | 5.7051 | 4.9313 | 4.3256 | 3.7095 | 3.0874 | 2.4669 | 1.9993 | 1.4976 | 1.0062 | -0.88484 | -2.3327 | -3.3775 | -4.2963 | -4.841 | 10.2868 | 9.2051 | 8.4313 | 7.8256 | 7.2095 | 6.5874 | 5.9669 | 5.4993 | 4.9976 | 4.5062 | 2.6152 | 1.1673 | 0.12246 | -0.79632 | -1.4669 | 6.7868 | 6.3994 | 6.1427 | 5.936 | 5.717 | 5.4927 | 5.2249 | 4.9596 | 4.7811 | 4.5988 | 4.0489 | 3.4937 | 3.0015 | 2.1573 | 1.5499 | 10.2868 | 9.8994 | 9.6427 | 9.436 | 9.217 | 8.9927 | 8.7249 | 8.4596 | 8.2811 | 8.0988 | 7.5489 | 6.9937 | 6.5015 | 5.6573 | 5.1298 | 6.7868 | 5.5176 | 4.668 | 4.0022 | 3.3237 | 2.6351 | 1.9418 | 1.3973 | 0.84688 | 0.30481 | -1.6355 | -2.8412 | -3.6569 | -4.1914 | -4.2066 | 10.2868 | 9.0176 | 8.168 | 7.5022 | 6.8237 | 6.1351 | 5.4418 | 4.8973 | 4.3469 | 3.8048 | 1.8645 | 0.6588 | -0.15693 | -0.69144 | -0.84202 | 6.7868 | 5.9132 | 5.1612 | 4.5318 | 3.8826 | 3.2118 | 2.4718 | 1.697 | 0.86676 | 0.03624 | -2.299 | -3.3904 | -3.9555 | -3.9812 | -3.2908 | 10.2868 | 9.4132 | 8.6612 | 8.0318 | 7.3826 | 6.7118 | 5.9718 | 5.197 | 4.3668 | 3.5362 | 1.201 | 0.10962 | -0.45551 | -0.48123 | 0.067397 | 6.7868 | 6.0597 | 5.3631 | 4.7892 | 4.2295 | 3.661 | 3.0753 | 2.6247 | 2.1219 | 1.6174 | 0.082206 | -0.52529 | -0.93396 | -1.2823 | -1.3659 | 10.2868 | 9.5597 | 8.8631 | 8.2892 | 7.7295 | 7.161 | 6.5753 | 6.1247 | 5.6219 | 5.1174 | 3.5822 | 2.9747 | 2.566 | 2.2177 | 2.1194 | 6.7868 | 5.48 | 4.617 | 3.9411 | 3.2491 | 2.552 | 1.789 | 0.97423 | 0.11037 | -0.73567 | -3.1393 | -4.3248 | -4.9881 | -5.1287 | -4.6398 | 10.2868 | 8.98 | 8.117 | 7.4411 | 6.7491 | 6.052 | 5.289 | 4.4742 | 3.6104 | 2.7643 | 0.36071 | -0.82476 | -1.4881 | -1.6287 | -1.2521 | 354932 | 429640 | RIBBLE | PENWORTHAM
| St Thomas Rd | 14.0369 | 13.8292 | 13.5672 | 13.1668 | 12.7323 | 12.2984 | 11.9004 | 11.5483 | 11.3606 | 11.1995 | 9.9376 | 7.6013 | 5.7529 | 3.7815 | 1.9256 | 18.6739 | 18.4662 | 18.2042 | 17.8038 | 17.3693 | 16.9354 | 16.5374 | 16.1853 | 15.9976 | 15.8365 | 14.5746 | 12.2383 | 10.3899 | 8.4185 | 6.4389 | 14.0369 | 13.7954 | 13.5 | 13.204 | 12.8865 | 12.6138 | 12.2913 | 11.8918 | 11.672 | 11.4543 | 10.8276 | 10.2219 | 9.6838 | 9.0829 | 8.6198 | 18.6739 | 18.4324 | 18.137 | 17.841 | 17.5235 | 17.2508 | 16.9283 | 16.5288 | 16.309 | 16.0913 | 15.4646 | 14.8589 | 14.3208 | 13.7199 | 13.3282 | 14.0369 | 13.8436 | 13.5943 | 13.2191 | 12.806 | 12.3953 | 12.0301 | 11.713 | 11.5939 | 11.4821 | 10.3774 | 8.2002 | 6.5085 | 4.7416 | 3.1376 | 18.6739 | 18.4806 | 18.2313 | 17.8561 | 17.443 | 17.0323 | 16.6671 | 16.35 | 16.2309 | 16.1191 | 15.0144 | 12.8372 | 11.1455 | 9.3786 | 7.6051 | 14.0369 | 13.957 | 13.7639 | 13.4199 | 13.0303 | 12.632 | 12.1398 | 11.2392 | 10.465 | 9.6879 | 7.4689 | 5.3715 | 3.7981 | 2.8419 | 3.5714 | 18.6739 | 18.594 | 18.4009 | 18.0569 | 17.6673 | 17.269 | 16.7768 | 15.8762 | 15.102 | 14.3249 | 12.1059 | 10.0085 | 8.4351 | 7.4789 | 8.0373 | 14.0369 | 13.8515 | 13.6093 | 13.2446 | 12.8828 | 12.5591 | 12.2722 | 11.9825 | 11.8059 | 11.6335 | 11.0819 | 10.4761 | 10.1012 | 9.7295 | 9.5626 | 18.6739 | 18.4885 | 18.2463 | 17.8816 | 17.5198 | 17.1961 | 16.9092 | 16.6195 | 16.4429 | 16.2705 | 15.7189 | 15.1131 | 14.7382 | 14.3665 | 14.1909 | 14.0369 | 13.9062 | 13.6501 | 13.2364 | 12.7794 | 12.3253 | 11.7698 | 10.7886 | 9.9793 | 9.1668 | 6.84 | 4.6426 | 2.9596 | 1.848 | 2.3846 | 18.6739 | 18.5432 | 18.2871 | 17.8734 | 17.4164 | 16.9623 | 16.4068 | 15.4256 | 14.6163 | 13.8038 | 11.477 | 9.2796 | 7.5966 | 6.485 | 6.8936 | 332713 | 428643 | LYTHAM | PENWORTHAM
| Stainburn | 9.3204 | 8.9911 | 8.7794 | 8.619 | 8.4397 | 8.2611 | 8.1017 | 7.9351 | 7.7394 | 7.4893 | 6.3664 | 4.7385 | 3.4713 | 2.2563 | 1.3264 | 11.8204 | 11.4911 | 11.2794 | 11.119 | 10.9397 | 10.7611 | 10.6017 | 10.4351 | 10.2394 | 9.9893 | 8.8664 | 7.2385 | 5.9713 | 4.7563 | 3.7468 | 9.3204 | 9.2567 | 9.1561 | 9.0712 | 8.9823 | 8.8839 | 8.763 | 8.5748 | 8.2965 | 8.009 | 7.1853 | 6.4601 | 5.834 | 5.2091 | 4.8813 | 11.8204 | 11.7567 | 11.6561 | 11.5712 | 11.4823 | 11.3839 | 11.263 | 11.0748 | 10.7965 | 10.509 | 9.6853 | 8.9601 | 8.334 | 7.7091 | 7.4283 | 9.3204 | 8.9477 | 8.7286 | 8.5677 | 8.3887 | 8.2108 | 8.0522 | 7.887 | 7.7152 | 7.5624 | 6.7614 | 5.2361 | 4.0745 | 3.0063 | 2.1577 | 11.8204 | 11.4477 | 11.2286 | 11.0677 | 10.8887 | 10.7108 | 10.5522 | 10.387 | 10.2152 | 10.0624 | 9.2614 | 7.7361 | 6.5745 | 5.5063 | 4.608 | 9.3204 | 9.0867 | 8.9281 | 8.8004 | 8.6244 | 8.4457 | 8.2147 | 7.8031 | 7.3823 | 6.9709 | 5.4677 | 4.0157 | 2.9378 | 2.3001 | 2.7737 | 11.8204 | 11.5867 | 11.4281 | 11.3004 | 11.1244 | 10.9457 | 10.7147 | 10.3031 | 9.8823 | 9.4709 | 7.9677 | 6.5157 | 5.4378 | 4.8001 | 5.1632 | 9.3204 | 9.2245 | 9.0817 | 8.9718 | 8.871 | 8.745 | 8.6033 | 8.4498 | 8.2541 | 8.0604 | 7.2165 | 6.3181 | 5.7163 | 5.2125 | 5.0945 | 11.8204 | 11.7245 | 11.5817 | 11.4718 | 11.371 | 11.245 | 11.1033 | 10.9498 | 10.7541 | 10.5604 | 9.7165 | 8.8181 | 8.2163 | 7.7125 | 7.574 | 9.3204 | 8.9272 | 8.6972 | 8.5114 | 8.2865 | 8.0936 | 7.8554 | 7.4077 | 6.8238 | 6.2411 | 4.5796 | 3.0305 | 1.8673 | 1.1469 | 1.5084 | 11.8204 | 11.4272 | 11.1972 | 11.0114 | 10.7865 | 10.5936 | 10.3554 | 9.9077 | 9.3238 | 8.7411 | 7.0796 | 5.5305 | 4.3673 | 3.6469 | 3.9268 | 302535 | 529330 | STAINBURN & SIDDICK | HARKER
| Standish | 7.894 | 7.418 | 7.1712 | 6.9467 | 6.6192 | 6.2802 | 5.9546 | 5.6244 | 5.1699 | 4.6095 | 1.9322 | -2.0779 | -5.2772 | -8.6209 | -11.8339 | 12.394 | 11.918 | 11.6712 | 11.4467 | 11.1192 | 10.7802 | 10.4546 | 10.1244 | 9.6699 | 9.1095 | 6.4322 | 2.4221 | -0.77725 | -4.1209 | -7.4185 | 7.894 | 7.6307 | 7.4764 | 7.3196 | 7.0821 | 6.8055 | 6.4193 | 5.8707 | 5.3565 | 4.8364 | 3.23 | 1.3579 | -0.37031 | -2.1694 | -3.2994 | 12.394 | 12.1307 | 11.9764 | 11.8196 | 11.5821 | 11.3055 | 10.9193 | 10.3707 | 9.8565 | 9.3364 | 7.73 | 5.8579 | 4.1297 | 2.3306 | 1.3822 | 7.894 | 7.4029 | 7.1844 | 7.028 | 6.6494 | 6.2732 | 5.9437 | 5.6228 | 5.0936 | 4.517 | 2.0553 | -1.7915 | -4.8643 | -8.0461 | -10.7425 | 12.394 | 11.9029 | 11.6844 | 11.528 | 11.1494 | 10.7732 | 10.4437 | 10.1228 | 9.5936 | 9.017 | 6.5553 | 2.7085 | -0.36427 | -3.5461 | -6.3268 | 7.894 | 7.9154 | 7.8075 | 7.6891 | 7.3169 | 6.9008 | 6.3049 | 5.0491 | 3.7028 | 2.3564 | -1.2835 | -4.8731 | -7.7105 | -9.7239 | -9.1068 | 12.394 | 12.4154 | 12.3075 | 12.1891 | 11.8169 | 11.4008 | 10.8049 | 9.5491 | 8.2028 | 6.8564 | 3.2165 | -0.37311 | -3.2105 | -5.2239 | -4.7555 | 7.894 | 7.5928 | 7.4316 | 7.3181 | 7.1499 | 6.9242 | 6.6654 | 6.3985 | 5.9953 | 5.577 | 3.8048 | 1.8034 | 0.42496 | -0.828 | -1.6492 | 12.394 | 12.0928 | 11.9316 | 11.8181 | 11.6499 | 11.4242 | 11.1654 | 10.8985 | 10.4953 | 10.077 | 8.3048 | 6.3034 | 4.925 | 3.672 | 2.9399 | 7.894 | 7.7048 | 7.4434 | 7.1867 | 6.6914 | 6.1987 | 5.5097 | 4.1208 | 2.672 | 1.2242 | -2.7353 | -6.6106 | -9.715 | -12.0227 | -11.7192 | 12.394 | 12.2048 | 11.9434 | 11.6867 | 11.1914 | 10.6987 | 10.0097 | 8.6208 | 7.172 | 5.7242 | 1.7647 | -2.1106 | -5.215 | -7.5227 | -7.2995 | 356139 | 410059 | WRIGHTINGTON | PENWORTHAM
| Strangeways | 6.0928 | 2.8975 | 1.896 | 1.6425 | 1.3699 | 1.0877 | 0.82478 | 0.56572 | 0.25808 | -0.040692 | -1.3773 | -3.1956 | -4.5686 | -5.842 | -6.8307 | 15.5928 | 12.3975 | 11.396 | 11.1425 | 10.8699 | 10.5877 | 10.3248 | 10.0657 | 9.7581 | 9.4593 | 8.1227 | 6.3044 | 4.9314 | 3.658 | 2.6123 | 6.0928 | 5.1998 | 4.7667 | 4.491 | 4.2135 | 3.9116 | 3.5606 | 3.1477 | 2.8433 | 2.5333 | 1.6389 | 0.77418 | 0.045515 | -0.72121 | -1.3923 | 15.5928 | 14.6998 | 14.2667 | 13.991 | 13.7135 | 13.4116 | 13.0606 | 12.6477 | 12.3433 | 12.0333 | 11.1389 | 10.2742 | 9.5455 | 8.7788 | 8.2143 | 6.0928 | 2.3699 | 1.2323 | 0.92048 | 0.59094 | 0.25269 | -0.075279 | -0.39424 | -0.73653 | -1.0717 | -2.488 | -4.2545 | -5.4478 | -6.3913 | -6.8281 | 15.5928 | 11.8699 | 10.7323 | 10.4205 | 10.0909 | 9.7527 | 9.4247 | 9.1058 | 8.7635 | 8.4283 | 7.012 | 5.2455 | 4.0522 | 3.1087 | 2.5995 | 6.0928 | 3.4916 | 2.6075 | 2.3492 | 2.0558 | 1.7433 | 1.3539 | 0.71457 | 0.035327 | -0.61515 | -2.3946 | -3.9398 | -4.8774 | -5.2998 | -4.9936 | 15.5928 | 12.9916 | 12.1075 | 11.8492 | 11.5558 | 11.2433 | 10.8539 | 10.2146 | 9.5353 | 8.8848 | 7.1054 | 5.5602 | 4.6226 | 4.2002 | 4.4263 | 6.0928 | 4.4252 | 3.7349 | 3.525 | 3.3379 | 3.1357 | 2.9195 | 2.668 | 2.3303 | 1.9857 | 0.91699 | -0.12635 | -0.84577 | -1.5225 | -1.8937 | 15.5928 | 13.9252 | 13.2349 | 13.025 | 12.8379 | 12.6357 | 12.4195 | 12.168 | 11.8303 | 11.4857 | 10.417 | 9.3736 | 8.6542 | 7.9775 | 7.6461 | 6.0928 | 2.0262 | 0.80033 | 0.46797 | 0.11005 | -0.25278 | -0.69349 | -1.4051 | -2.1147 | -2.7938 | -4.7158 | -6.3483 | -7.3741 | -7.8928 | -7.705 | 15.5928 | 11.5262 | 10.3003 | 9.968 | 9.61 | 9.2472 | 8.8065 | 8.0949 | 7.3853 | 6.7062 | 4.7842 | 3.1517 | 2.1259 | 1.6072 | 1.7415 | 383780 | 399743 | RED BANK | WHITEGATE
| Strawberry Bank | 13.777 | 9.6874 | 8.2256 | 7.4922 | 6.7332 | 5.9641 | 5.1979 | 4.4217 | 4.2112 | 4.009 | 2.8335 | 0.74374 | -1.2343 | -3.1929 | -4.777 | 17.914 | 13.8244 | 12.3626 | 11.6292 | 10.8702 | 10.1011 | 9.3349 | 8.5587 | 8.3482 | 8.146 | 6.9705 | 4.8807 | 2.9027 | 0.94414 | -0.78446 | 13.777 | 12.4761 | 12.1458 | 12.0646 | 11.9849 | 11.8705 | 11.6925 | 11.4702 | 11.2782 | 11.0133 | 10.1184 | 9.2185 | 8.3219 | 7.506 | 7.0162 | 17.914 | 16.6131 | 16.2828 | 16.2016 | 16.1219 | 16.0075 | 15.8295 | 15.6072 | 15.4152 | 15.1503 | 14.2554 | 13.3555 | 12.4589 | 11.643 | 11.2199 | 13.777 | 9.0149 | 7.4375 | 6.7046 | 5.9488 | 5.1848 | 4.4247 | 3.5788 | 3.4167 | 3.2658 | 2.2244 | 0.44718 | -0.99758 | -2.739 | -4.0483 | 17.914 | 13.1519 | 11.5745 | 10.8416 | 10.0858 | 9.3218 | 8.5617 | 7.7158 | 7.5537 | 7.4028 | 6.3614 | 4.5842 | 3.1394 | 1.398 | -0.10758 | 13.777 | 10.4923 | 9.2067 | 8.4209 | 7.7019 | 6.9478 | 6.0813 | 4.8808 | 4.2684 | 3.6664 | 1.6033 | -0.39143 | -1.9677 | -2.9175 | -2.0252 | 17.914 | 14.6293 | 13.3437 | 12.5579 | 11.8389 | 11.0848 | 10.2183 | 9.0178 | 8.4054 | 7.8034 | 5.7403 | 3.7456 | 2.1693 | 1.2195 | 1.9125 | 13.777 | 11.2459 | 10.0826 | 9.4015 | 8.7309 | 8.0309 | 7.2998 | 6.5515 | 6.3541 | 6.1521 | 5.4327 | 4.487 | 3.7715 | 3.2952 | 3.2005 | 17.914 | 15.3829 | 14.2196 | 13.5385 | 12.8679 | 12.1679 | 11.4368 | 10.6885 | 10.4911 | 10.2891 | 9.5697 | 8.624 | 7.9085 | 7.4322 | 7.3215 | 13.777 | 8.447 | 6.7634 | 5.9214 | 5.1549 | 4.3838 | 3.5077 | 2.2726 | 1.6366 | 0.94069 | -1.3051 | -3.4591 | -5.2037 | -6.3598 | -5.691 | 17.914 | 12.584 | 10.9004 | 10.0584 | 9.2919 | 8.5208 | 7.6447 | 6.4096 | 5.7736 | 5.0777 | 2.8319 | 0.67788 | -1.0667 | -2.2228 | -1.7042 | 376338 | 429396 | HUNCOAT | PADIHAM
| Stuart St | 10.4389 | 7.1489 | 6.3697 | 6.2322 | 6.018 | 5.7803 | 5.5507 | 5.3447 | 5.1033 | 4.8629 | 3.541 | 1.7647 | 0.42892 | -0.675 | -1.4474 | 17.4389 | 14.1489 | 13.3697 | 13.2322 | 13.018 | 12.7803 | 12.5507 | 12.3447 | 12.1033 | 11.8629 | 10.541 | 8.7647 | 7.4289 | 6.325 | 5.4265 | 10.4389 | 9.6641 | 9.4219 | 9.3338 | 9.235 | 9.1285 | 8.9901 | 8.8194 | 8.6325 | 8.4316 | 7.7484 | 6.9918 | 6.2908 | 5.5806 | 5.0854 | 17.4389 | 16.6641 | 16.4219 | 16.3338 | 16.235 | 16.1285 | 15.9901 | 15.8194 | 15.6325 | 15.4316 | 14.7484 | 13.9918 | 13.2908 | 12.5806 | 12.1567 | 10.4389 | 6.5687 | 5.6217 | 5.4261 | 5.1495 | 4.8484 | 4.583 | 4.3313 | 4.0674 | 3.7745 | 2.3042 | 0.48491 | -0.70247 | -1.5015 | -1.7059 | 17.4389 | 13.5687 | 12.6217 | 12.4261 | 12.1495 | 11.8484 | 11.583 | 11.3313 | 11.0674 | 10.7745 | 9.3042 | 7.4849 | 6.2975 | 5.4985 | 5.1771 | 10.4389 | 7.8022 | 7.1105 | 6.9245 | 6.6434 | 6.3294 | 5.9558 | 5.2973 | 4.6139 | 3.9382 | 2.0614 | 0.57879 | -0.2612 | -0.42696 | 0.11521 | 17.4389 | 14.8022 | 14.1105 | 13.9245 | 13.6434 | 13.3294 | 12.9558 | 12.2973 | 11.6139 | 10.9382 | 9.0614 | 7.5788 | 6.7388 | 6.573 | 6.9929 | 10.4389 | 8.9497 | 8.5532 | 8.4672 | 8.3726 | 8.2587 | 8.1185 | 7.9442 | 7.6978 | 7.4329 | 6.4354 | 5.4762 | 4.8307 | 4.2997 | 4.094 | 17.4389 | 15.9497 | 15.5532 | 15.4672 | 15.3726 | 15.2587 | 15.1185 | 14.9442 | 14.6978 | 14.4329 | 13.4354 | 12.4762 | 11.8307 | 11.2997 | 11.0999 | 10.4389 | 6.2012 | 5.1551 | 4.9317 | 4.6177 | 4.2841 | 3.8845 | 3.1948 | 2.5139 | 1.8207 | -0.16117 | -1.7696 | -2.7393 | -3.0439 | -2.6181 | 17.4389 | 13.2012 | 12.1551 | 11.9317 | 11.6177 | 11.2841 | 10.8845 | 10.1948 | 9.5139 | 8.8207 | 6.8388 | 5.2304 | 4.2607 | 3.9561 | 4.2908 | 387190 | 398835 | STUART ST | STALYBRIDGE
| Stubbins | 12.1296 | 11.7379 | 11.5315 | 11.4937 | 11.4975 | 11.4989 | 8.4857 | 8.6875 | 8.6327 | 8.5799 | 7.9776 | 6.9393 | 6.2038 | 5.463 | 5.0907 | 29.1296 | 28.7379 | 28.5315 | 28.4937 | 28.4975 | 28.4989 | 25.4857 | 25.6875 | 25.6327 | 25.5799 | 24.9776 | 23.9393 | 23.2038 | 22.463 | 21.9485 | 12.1296 | 11.9853 | 11.7979 | 11.7137 | 11.6799 | 11.6477 | 11.5974 | 11.4661 | 11.2842 | 11.1021 | 10.5585 | 10.0348 | 9.5693 | 9.1003 | 6.706 | 29.1296 | 28.9853 | 28.7979 | 28.7137 | 28.6799 | 28.6477 | 28.5974 | 28.4661 | 28.2842 | 28.1021 | 27.5585 | 27.0348 | 26.5693 | 26.1003 | 23.7391 | 12.1296 | 11.6967 | 11.4891 | 11.4854 | 11.5085 | 11.4934 | 8.6162 | 8.8016 | 8.8077 | 8.8267 | 3.816 | 3.1264 | 2.879 | 2.8513 | 3.1028 | 29.1296 | 28.6967 | 28.4891 | 28.4854 | 28.5085 | 28.4934 | 25.6162 | 25.8016 | 25.8077 | 25.8267 | 20.816 | 20.1264 | 19.879 | 19.8513 | 19.8363 | 12.1296 | 11.9248 | 11.7746 | 11.7873 | 8.8338 | 9.0158 | 9.132 | 9.0836 | 8.6529 | 8.4374 | 7.1885 | 6.5635 | 6.1652 | 6.2752 | 7.2887 | 29.1296 | 28.9248 | 28.7746 | 28.7873 | 25.8338 | 26.0158 | 26.132 | 26.0836 | 25.6529 | 25.4374 | 24.1885 | 23.5635 | 23.1652 | 23.2752 | 24.067 | 12.1296 | 11.9053 | 11.7422 | 11.7218 | 11.7603 | 11.7941 | 8.8001 | 9.016 | 8.9691 | 8.9195 | 8.628 | 8.3183 | 8.2286 | 8.2104 | 8.4817 | 29.1296 | 28.9053 | 28.7422 | 28.7218 | 28.7603 | 28.7941 | 25.8001 | 26.016 | 25.9691 | 25.9195 | 25.628 | 25.3183 | 25.2286 | 25.2104 | 25.4019 | 12.1296 | 11.7071 | 11.4899 | 11.4729 | 8.5088 | 8.6753 | 8.7782 | 8.707 | 8.2698 | 8.048 | 6.7074 | 6.0006 | 5.528 | 5.5445 | 6.4562 | 29.1296 | 28.7071 | 28.4899 | 28.4729 | 25.5088 | 25.6753 | 25.7782 | 25.707 | 25.2698 | 25.048 | 23.7074 | 23.0006 | 22.528 | 22.5445 | 23.257 | 379112 | 418005 | ROSSENDALE | PADIHAM
| Swinton | 13.6608 | 13.5743 | 13.4719 | 13.3819 | 13.246 | 13.0926 | 12.9368 | 12.7772 | 12.5957 | 12.4245 | 11.1175 | 8.7765 | 6.8479 | 4.8628 | 3.1458 | 18.1608 | 18.0743 | 17.9719 | 17.8819 | 17.746 | 17.5926 | 17.4368 | 17.2772 | 17.0957 | 16.9245 | 15.6175 | 13.2765 | 11.3479 | 9.3628 | 7.5126 | 13.6608 | 13.5651 | 13.4494 | 13.3471 | 13.2117 | 13.0456 | 12.8264 | 12.5553 | 12.3805 | 12.197 | 11.5899 | 10.923 | 10.2742 | 9.4892 | 8.996 | 18.1608 | 18.0651 | 17.9494 | 17.8471 | 17.7117 | 17.5456 | 17.3264 | 17.0553 | 16.8805 | 16.697 | 16.0899 | 15.423 | 14.7742 | 13.9892 | 13.5621 | 13.6608 | 13.5728 | 13.4708 | 13.3815 | 13.2481 | 12.7972 | 12.3443 | 11.8921 | 11.4409 | 11.3035 | 10.2867 | 8.1978 | 6.3283 | 4.4442 | 2.8778 | 18.1608 | 18.0728 | 17.9708 | 17.8815 | 17.7481 | 17.2972 | 16.8443 | 16.3921 | 15.9409 | 15.8035 | 14.7867 | 12.6978 | 10.8283 | 8.9442 | 7.2165 | 13.6608 | 13.7419 | 13.6962 | 13.638 | 13.5227 | 13.0716 | 12.5071 | 11.6099 | 10.6572 | 9.8887 | 7.649 | 5.5416 | 3.8745 | 2.8681 | 3.5997 | 18.1608 | 18.2419 | 18.1962 | 18.138 | 18.0227 | 17.5716 | 17.0071 | 16.1099 | 15.1572 | 14.3887 | 12.149 | 10.0416 | 8.3745 | 7.3681 | 7.9347 | 13.6608 | 13.5878 | 13.5098 | 13.466 | 13.416 | 13.3422 | 13.2397 | 13.1122 | 12.9401 | 12.7624 | 12.1427 | 11.3159 | 10.6423 | 10.101 | 9.9376 | 18.1608 | 18.0878 | 18.0098 | 17.966 | 17.916 | 17.8422 | 17.7397 | 17.6122 | 17.4401 | 17.2624 | 16.6427 | 15.8159 | 15.1423 | 14.601 | 14.4249 | 13.6608 | 13.7107 | 13.6219 | 13.5148 | 13.3571 | 12.8874 | 12.3107 | 11.3677 | 10.28 | 9.4847 | 7.1152 | 4.8488 | 3.0131 | 1.8152 | 2.3522 | 18.1608 | 18.2107 | 18.1219 | 18.0148 | 17.8571 | 17.3874 | 16.8107 | 15.8677 | 14.78 | 13.9847 | 11.6152 | 9.3488 | 7.5131 | 6.3152 | 6.7289 | 378367 | 401718 | AGECROFT | KEARSLEY
| Tame Valley | 8.8149 | 7.5875 | 7.0917 | 6.879 | 6.5281 | 6.14 | 5.7502 | 5.3679 | 4.9469 | 4.5306 | 2.0806 | -1.6815 | -4.5422 | -7.1665 | -9.0487 | 13.4519 | 12.2245 | 11.7287 | 11.516 | 11.1651 | 10.777 | 10.3872 | 10.0049 | 9.5839 | 9.1676 | 6.7176 | 2.9555 | 0.094836 | -2.5295 | -4.6075 | 8.8149 | 8.4223 | 8.2323 | 8.0722 | 7.8508 | 7.6076 | 7.2822 | 6.869 | 6.5701 | 6.2509 | 5.2054 | 4.0383 | 2.8689 | 1.5712 | 0.59239 | 13.4519 | 13.0593 | 12.8693 | 12.7092 | 12.4878 | 12.2446 | 11.9192 | 11.506 | 11.2071 | 10.8879 | 9.8424 | 8.6753 | 7.5059 | 6.2082 | 5.3835 | 8.8149 | 7.0456 | 5.9622 | 5.193 | 4.2817 | 3.634 | 2.9998 | 2.3614 | 1.6965 | 1.0082 | -1.7788 | -5.4314 | -8.0652 | -10.1307 | -11.0819 | 13.4519 | 11.6826 | 10.5992 | 9.83 | 8.9187 | 8.271 | 7.6368 | 6.9984 | 6.3335 | 5.6452 | 2.8582 | -0.79438 | -3.4282 | -5.4937 | -6.5658 | 8.8149 | 7.6863 | 6.7538 | 6.0144 | 5.1057 | 4.4423 | 3.5838 | 2.0975 | 0.6063 | -0.85599 | -4.545 | -7.5577 | -9.3681 | -10.0941 | -9.4555 | 13.4519 | 12.3233 | 11.3908 | 10.6514 | 9.7427 | 9.0793 | 8.2208 | 6.7345 | 5.2433 | 3.781 | 0.091975 | -2.9207 | -4.7311 | -5.4571 | -4.9505 | 8.8149 | 8.0606 | 7.694 | 7.5603 | 7.3776 | 7.1539 | 6.8774 | 6.5512 | 6.1416 | 5.7105 | 4.1525 | 2.1989 | 0.82532 | -0.39738 | -1.1707 | 13.4519 | 12.6976 | 12.331 | 12.1973 | 12.0146 | 11.7909 | 11.5144 | 11.1882 | 10.7786 | 10.3475 | 8.7895 | 6.8359 | 5.4623 | 4.2396 | 3.5624 | 8.8149 | 7.1954 | 6.0935 | 5.2631 | 4.2713 | 3.5508 | 2.6228 | 1.0515 | -0.48393 | -1.9937 | -5.8895 | -9.1422 | -11.2501 | -12.2501 | -11.7117 | 13.4519 | 11.8324 | 10.7305 | 9.9001 | 8.9083 | 8.1878 | 7.2598 | 5.6885 | 4.1531 | 2.6433 | -1.2525 | -4.5052 | -6.6131 | -7.6131 | -7.1504 | 395148 | 398108 | HARTSHEAD-HEYROD | STALYBRIDGE
| Tardy Gate | 11.8553 | 11.2125 | 10.5014 | 9.8831 | 9.2097 | 8.6864 | 8.4788 | 8.2781 | 8.0006 | 7.7362 | 6.0746 | 3.274 | 0.96972 | -1.4796 | -3.6183 | 15.9923 | 15.3495 | 14.6384 | 14.0201 | 13.3467 | 12.8234 | 12.6158 | 12.4151 | 12.1376 | 11.8732 | 10.2116 | 7.411 | 5.1067 | 2.6574 | 0.41021 | 11.8553 | 11.6113 | 11.407 | 11.217 | 10.9932 | 10.8021 | 10.5445 | 10.1969 | 9.8718 | 9.5408 | 8.537 | 7.511 | 6.508 | 5.4182 | 4.6655 | 15.9923 | 15.7483 | 15.544 | 15.354 | 15.1302 | 14.9391 | 14.6815 | 14.3339 | 14.0088 | 13.6778 | 12.674 | 11.648 | 10.645 | 9.5552 | 8.9211 | 11.8553 | 11.1514 | 10.4514 | 9.8768 | 9.2501 | 8.7824 | 8.6522 | 8.5391 | 8.369 | 8.1932 | 6.7795 | 4.1712 | 2.0315 | -0.20763 | -2.0845 | 15.9923 | 15.2884 | 14.5884 | 14.0138 | 13.3871 | 12.9194 | 12.7892 | 12.6761 | 12.506 | 12.3302 | 10.9165 | 8.3082 | 6.1685 | 3.9294 | 1.8944 | 11.8553 | 11.5392 | 10.9383 | 10.3808 | 9.7448 | 9.2388 | 8.9057 | 8.0978 | 7.2254 | 6.3444 | 3.7846 | 1.3145 | -0.62931 | -1.8884 | -1.1789 | 15.9923 | 15.6762 | 15.0753 | 14.5178 | 13.8818 | 13.3758 | 13.0427 | 12.2348 | 11.3624 | 10.4814 | 7.9216 | 5.4515 | 3.5077 | 2.2486 | 2.7964 | 11.8553 | 11.5279 | 10.9076 | 10.3569 | 9.7969 | 9.3619 | 9.2088 | 9.0483 | 8.7846 | 8.5183 | 7.5955 | 6.546 | 5.8374 | 5.2109 | 4.9007 | 15.9923 | 15.6649 | 15.0446 | 14.4939 | 13.9339 | 13.4989 | 13.3458 | 13.1853 | 12.9216 | 12.6553 | 11.7325 | 10.683 | 9.9744 | 9.3479 | 9.0386 | 11.8553 | 11.2344 | 10.5116 | 9.8654 | 9.1498 | 8.5923 | 8.1983 | 7.3044 | 6.3718 | 5.4312 | 2.6714 | 0.0020344 | -2.1333 | -3.6233 | -3.1507 | 15.9923 | 15.3714 | 14.6486 | 14.0024 | 13.2868 | 12.7293 | 12.3353 | 11.4414 | 10.5088 | 9.5682 | 6.8084 | 4.139 | 2.0037 | 0.51371 | 0.8752 | 353958 | 426066 | RIBBLE | PENWORTHAM
| Tarleton | 5.636 | 5.2395 | 4.9853 | 4.825 | 4.6092 | 4.3945 | 4.2162 | 4.0135 | 3.6643 | 3.34 | 1.7027 | -0.77568 | -2.716 | -4.5747 | -6.0856 | 10.273 | 9.8765 | 9.6223 | 9.462 | 9.2462 | 9.0315 | 8.8532 | 8.6505 | 8.3013 | 7.977 | 6.3397 | 3.8613 | 1.921 | 0.062318 | -1.5858 | 5.636 | 5.395 | 5.1733 | 4.9852 | 4.758 | 4.5016 | 4.1705 | 3.7504 | 3.3484 | 2.9429 | 1.6522 | 0.40492 | -0.73629 | -1.9273 | -2.6849 | 10.273 | 10.032 | 9.8103 | 9.6222 | 9.395 | 9.1386 | 8.8075 | 8.3874 | 7.9854 | 7.5799 | 6.2892 | 5.0419 | 3.9007 | 2.7097 | 2.0609 | 5.636 | 5.2263 | 5.0008 | 4.908 | 4.7609 | 4.6271 | 4.5613 | 4.5072 | 4.3433 | 4.1613 | 2.8906 | -0.38984 | -2.7702 | -4.7204 | -6.0141 | 10.273 | 9.8633 | 9.6378 | 9.545 | 9.3979 | 9.2641 | 9.1983 | 9.1442 | 8.9803 | 8.7983 | 7.5276 | 4.2472 | 1.8668 | -0.08343 | -1.3785 | 5.636 | 5.5987 | 5.4899 | 5.437 | 5.3143 | 5.1666 | 4.9458 | 4.3425 | 3.6205 | 2.877 | 0.74252 | -1.2748 | -2.7363 | -3.7719 | -3.849 | 10.273 | 10.2357 | 10.1269 | 10.074 | 9.9513 | 9.8036 | 9.5828 | 8.9795 | 8.2575 | 7.514 | 5.3795 | 3.3622 | 1.9007 | 0.86512 | 0.7492 | 5.636 | 5.3249 | 5.1327 | 5.0515 | 4.973 | 4.8623 | 4.7202 | 4.5403 | 4.1815 | 3.818 | 2.593 | 1.2637 | 0.37367 | -0.98199 | -1.651 | 10.273 | 9.9619 | 9.7697 | 9.6885 | 9.61 | 9.4993 | 9.3572 | 9.1773 | 8.8185 | 8.455 | 7.23 | 5.9007 | 5.0107 | 3.655 | 3.0416 | 5.636 | 5.3694 | 5.1204 | 4.9376 | 4.6971 | 4.4708 | 4.1563 | 3.4033 | 2.5821 | 1.7458 | -0.68296 | -2.9759 | -4.6802 | -5.6307 | -4.8631 | 10.273 | 10.0064 | 9.7574 | 9.5746 | 9.3341 | 9.1078 | 8.7933 | 8.0403 | 7.2191 | 6.3828 | 3.954 | 1.6611 | -0.04315 | -0.9937 | -0.40076 | 344741 | 422417 | WRIGHTINGTON | PENWORTHAM
| The Height | 6.1362 | 5.5324 | 5.2316 | 4.9885 | 4.6413 | 4.2638 | 3.7954 | 3.4129 | 2.9973 | 2.5157 | 0.078313 | -3.0772 | -5.3222 | -7.2768 | -8.5745 | 16.8362 | 16.2324 | 15.9316 | 15.6885 | 15.3413 | 14.9638 | 14.4954 | 14.1129 | 13.6973 | 13.2157 | 10.7783 | 7.6228 | 5.3778 | 3.4232 | 1.9972 | 6.1362 | 5.9092 | 5.7641 | 5.617 | 5.4165 | 5.2136 | 4.855 | 4.4822 | 4.1824 | 3.8647 | 2.7899 | 1.5103 | 0.18541 | -1.2062 | -2.1212 | 16.8362 | 16.6092 | 16.4641 | 16.317 | 16.1165 | 15.9136 | 15.555 | 15.1822 | 14.8824 | 14.5647 | 13.4899 | 12.2103 | 10.8854 | 9.4938 | 8.719 | 6.1362 | 5.3934 | 4.9987 | 4.6747 | 4.2449 | 3.7843 | 3.2535 | 2.7928 | 2.3131 | 1.6797 | -1.1007 | -4.4057 | -6.5961 | -8.2626 | -8.9678 | 16.8362 | 16.0934 | 15.6987 | 15.3747 | 14.9449 | 14.4843 | 13.9535 | 13.4928 | 13.0131 | 12.3797 | 9.5993 | 6.2943 | 4.1039 | 2.4374 | 1.6267 | 6.1362 | 5.8021 | 5.5086 | 5.1235 | 4.7019 | 4.2287 | 3.599 | 2.4762 | 1.3606 | 0.23686 | -2.9922 | -5.6956 | -7.3869 | -8.1984 | -7.7414 | 16.8362 | 16.5021 | 16.2086 | 15.8235 | 15.4019 | 14.9287 | 14.299 | 13.1762 | 12.0606 | 10.9369 | 7.7078 | 5.0044 | 3.3131 | 2.5016 | 2.8438 | 6.1362 | 5.7949 | 5.5756 | 5.3956 | 5.1711 | 4.9182 | 4.5472 | 4.2195 | 3.8243 | 3.3818 | 1.6199 | -0.20084 | -1.4324 | -2.4754 | -3.094 | 16.8362 | 16.4949 | 16.2756 | 16.0956 | 15.8711 | 15.6182 | 15.2472 | 14.9195 | 14.5243 | 14.0818 | 12.3199 | 10.4992 | 9.2676 | 8.2246 | 7.6811 | 6.1362 | 5.5671 | 5.1683 | 4.7087 | 4.2213 | 3.7077 | 3.0278 | 1.8419 | 0.68899 | -0.48777 | -3.9116 | -6.8276 | -8.7431 | -9.7676 | -9.5393 | 16.8362 | 16.2671 | 15.8683 | 15.4087 | 14.9213 | 14.4077 | 13.7278 | 12.5419 | 11.389 | 10.2122 | 6.7884 | 3.8724 | 1.9569 | 0.93237 | 1.0983 | 379792 | 400497 | AGECROFT | KEARSLEY
| Thorley Ln | 31.5387 | 31.5387 | 31.4766 | 31.4144 | 31.3522 | 31.29 | 31.2279 | 31.1035 | 31.1035 | 31.1035 | 31.1035 | 31.1035 | 31.1035 | 31.1035 | 31.1035 | 37.5387 | 37.5387 | 37.4766 | 37.4144 | 37.3522 | 37.29 | 37.2279 | 37.1035 | 37.1035 | 37.1035 | 37.1035 | 37.1035 | 37.1035 | 37.1035 | 37.1035 | 31.5387 | 31.5387 | 31.5387 | 31.5387 | 31.5387 | 31.5387 | 31.5387 | 31.5387 | 31.5387 | 31.5387 | 31.5387 | 31.5387 | 31.5387 | 31.5387 | 31.5387 | 37.5387 | 37.5387 | 37.5387 | 37.5387 | 37.5387 | 37.5387 | 37.5387 | 37.5387 | 37.5387 | 37.5387 | 37.5387 | 37.5387 | 37.5387 | 37.5387 | 37.5387 | 31.5387 | 31.5387 | 31.4766 | 31.4144 | 31.3522 | 31.29 | 31.2279 | 31.1035 | 31.1035 | 31.1035 | 31.1035 | 31.1035 | 31.1035 | 31.1035 | 31.1035 | 37.5387 | 37.5387 | 37.4766 | 37.4144 | 37.3522 | 37.29 | 37.2279 | 37.1035 | 37.1035 | 37.1035 | 37.1035 | 37.1035 | 37.1035 | 37.1035 | 37.1035 | 31.5387 | 31.5387 | 31.4766 | 31.4144 | 31.3522 | 31.29 | 31.2279 | 31.1035 | 31.1035 | 31.1035 | 31.1035 | 31.1035 | 31.1035 | 31.1035 | 31.1035 | 37.5387 | 37.5387 | 37.4766 | 37.4144 | 37.3522 | 37.29 | 37.2279 | 37.1035 | 37.1035 | 37.1035 | 37.1035 | 37.1035 | 37.1035 | 37.1035 | 37.1035 | 31.5387 | 31.5387 | 31.4766 | 31.4144 | 31.3522 | 31.29 | 31.2279 | 31.1035 | 31.1035 | 31.1035 | 31.1035 | 31.1035 | 31.1035 | 31.1035 | 31.1035 | 37.5387 | 37.5387 | 37.4766 | 37.4144 | 37.3522 | 37.29 | 37.2279 | 37.1035 | 37.1035 | 37.1035 | 37.1035 | 37.1035 | 37.1035 | 37.1035 | 37.1035 | 31.5387 | 31.5387 | 31.4766 | 31.4144 | 31.3211 | 31.2279 | 31.1346 | 30.9792 | 30.9792 | 30.9792 | 30.9792 | 30.9792 | 30.9792 | 30.9792 | 30.9792 | 37.5387 | 37.5387 | 37.4766 | 37.4144 | 37.3211 | 37.2279 | 37.1346 | 36.9792 | 36.9792 | 36.9792 | 36.9792 | 36.9792 | 36.9792 | 36.9792 | 36.9792 | 381499 | 386063 | MOSS NOOK | SOUTH MANCHESTER
| Thornton | 10.8967 | 9.54 | 9.2495 | 9.1842 | 9.0469 | 8.8938 | 8.7371 | 8.5746 | 8.3689 | 3.7598 | 2.3721 | -0.42296 | -4.604 | -7.0125 | -9.1856 | 14.0337 | 12.677 | 12.3865 | 12.3212 | 12.1839 | 12.0308 | 11.8741 | 11.7116 | 11.5059 | 6.8968 | 5.5091 | 2.714 | -1.467 | -3.8755 | -6.1474 | 10.8967 | 10.5541 | 10.4334 | 10.3413 | 10.1881 | 10.0091 | 9.7617 | 9.428 | 9.1585 | 8.8859 | 8.0437 | 6.9253 | 4.9395 | 3.9313 | 3.2779 | 14.0337 | 13.6911 | 13.5704 | 13.4783 | 13.3251 | 13.1461 | 12.8987 | 12.565 | 12.2955 | 12.0229 | 11.1807 | 10.0623 | 8.0765 | 7.0683 | 6.5182 | 10.8967 | 9.3516 | 8.9602 | 8.8446 | 8.6624 | 8.4726 | 8.3037 | 8.2241 | 8.103 | 7.9951 | 5.7732 | -2.1018 | -4.0987 | -6.3235 | -8.2981 | 14.0337 | 12.4886 | 12.0972 | 11.9816 | 11.7994 | 11.6096 | 11.4407 | 11.3611 | 11.24 | 11.1321 | 8.9102 | 1.0352 | -0.9617 | -3.1865 | -5.2953 | 10.8967 | 10.0918 | 9.8581 | 9.7628 | 9.3014 | 9.0917 | 8.7495 | 6.9947 | 1.8581 | 0.14569 | -2.0839 | -4.3098 | -6.1172 | -7.4237 | -6.8154 | 14.0337 | 13.2288 | 12.9951 | 12.8998 | 12.4384 | 12.2287 | 11.8865 | 10.1317 | 4.9951 | 3.2827 | 1.0531 | -1.1728 | -2.9802 | -4.2867 | -3.8163 | 10.8967 | 10.3642 | 10.2543 | 10.2535 | 10.2129 | 10.131 | 10.0206 | 9.902 | 9.7176 | 5.1148 | 4.4786 | 3.2617 | 0.54607 | -0.1159 | -0.5551 | 14.0337 | 13.5012 | 13.3913 | 13.3905 | 13.3499 | 13.268 | 13.1576 | 13.039 | 12.8546 | 8.2518 | 7.6156 | 6.3987 | 3.6831 | 3.0211 | 2.6009 | 10.8967 | 9.4071 | 8.9827 | 8.7952 | 8.2505 | 7.9847 | 7.5709 | 5.7223 | 0.51823 | -1.2619 | -3.7046 | -6.1175 | -8.121 | -9.621 | -9.2213 | 14.0337 | 12.5441 | 12.1197 | 11.9322 | 11.3875 | 11.1217 | 10.7079 | 8.8593 | 3.6552 | 1.8751 | -0.56758 | -2.9805 | -4.984 | -6.484 | -6.1769 | 334207 | 442111 | BISPHAM | PENWORTHAM
| Townley St | 7.721 | 5.7227 | 5.2166 | 5.1203 | 5.0138 | 4.902 | 4.7925 | 4.6791 | 4.5363 | 4.406 | 3.6903 | 2.5346 | 1.5715 | 0.57001 | -0.32651 | 23.979 | 21.9807 | 21.4746 | 21.3783 | 21.2718 | 21.16 | 21.0505 | 20.9371 | 20.7943 | 20.664 | 19.9483 | 18.7926 | 17.8295 | 16.828 | 15.8771 | 7.721 | 7.4933 | 7.3566 | 7.2696 | 7.179 | 7.0732 | 6.6921 | 6.2448 | 6.1093 | 5.9735 | 5.5738 | 5.2085 | 4.8934 | 4.5404 | 4.3408 | 23.979 | 23.7513 | 23.6146 | 23.5276 | 23.437 | 23.3312 | 22.9501 | 22.5028 | 22.3673 | 22.2315 | 21.8318 | 21.4665 | 21.1514 | 20.7984 | 20.624 | 7.721 | 5.3991 | 4.8277 | 4.7314 | 4.6258 | 4.5154 | 4.4065 | 4.2953 | 4.1772 | 4.0734 | 3.4391 | 2.3738 | 1.5065 | 0.64069 | -0.083591 | 23.979 | 21.6571 | 21.0857 | 20.9894 | 20.8838 | 20.7734 | 20.6645 | 20.5533 | 20.4352 | 20.3314 | 19.6971 | 18.6318 | 17.7645 | 16.8987 | 16.0862 | 7.721 | 6.1423 | 5.7491 | 5.6844 | 5.6006 | 5.4897 | 5.3148 | 4.958 | 4.5796 | 4.2112 | 3.1469 | 2.1032 | 1.227 | 0.68502 | 1.0679 | 23.979 | 22.4003 | 22.0071 | 21.9424 | 21.8586 | 21.7477 | 21.5728 | 21.216 | 20.8376 | 20.4692 | 19.4049 | 18.3612 | 17.485 | 16.943 | 17.2332 | 7.721 | 7.3374 | 7.1832 | 7.1298 | 7.0845 | 7.015 | 6.9258 | 6.831 | 6.6977 | 6.5672 | 6.1401 | 5.6752 | 5.3457 | 5.0499 | 4.9523 | 23.979 | 23.5954 | 23.4412 | 23.3878 | 23.3425 | 23.273 | 23.1838 | 23.089 | 22.9557 | 22.8252 | 22.3981 | 21.9332 | 21.6037 | 21.3079 | 21.1986 | 7.721 | 5.1447 | 4.5118 | 4.3977 | 4.2711 | 4.1425 | 3.9546 | 3.5622 | 3.1581 | 2.7668 | 1.6517 | 0.60743 | -0.23372 | -0.80865 | -0.48619 | 23.979 | 21.4027 | 20.7698 | 20.6557 | 20.5291 | 20.4005 | 20.2126 | 19.8202 | 19.4161 | 19.0248 | 17.9097 | 16.8654 | 16.0243 | 15.4494 | 15.6955 | 387242 | 405960 | CHADDERTON | WHITEGATE
| Trafford | 6.3274 | 5.7716 | 4.6065 | 3.4082 | 2.2549 | 1.0872 | 0.055042 | -0.71368 | -1.6625 | -2.6358 | -5.1717 | -6.5916 | -7.6062 | -8.4701 | -9.0559 | 13.3274 | 12.7716 | 11.6065 | 10.4082 | 9.2549 | 8.0872 | 7.055 | 6.2863 | 5.3375 | 4.3642 | 1.8283 | 0.40835 | -0.60623 | -1.4701 | -2.1006 | 6.3274 | 6.1115 | 5.797 | 5.5331 | 5.3313 | 5.1227 | 4.9582 | 4.8889 | 4.6301 | 4.3547 | 3.451 | 2.4226 | 0.98737 | -0.53847 | -1.5432 | 13.3274 | 13.1115 | 12.797 | 12.5331 | 12.3313 | 12.1227 | 11.9582 | 11.8889 | 11.6301 | 11.3547 | 10.451 | 9.4226 | 7.9874 | 6.4615 | 5.5834 | 6.3274 | 5.7392 | 4.5691 | 3.2217 | 1.9261 | 0.77396 | -0.98781 | -2.475 | -4.0757 | -5.6949 | -7.9922 | -9.2818 | -10.1591 | -10.7316 | -10.8526 | 13.3274 | 12.7392 | 11.5691 | 10.2217 | 8.9261 | 7.774 | 6.0122 | 4.525 | 2.9243 | 1.3051 | -0.99219 | -2.2818 | -3.1591 | -3.7316 | -3.9866 | 6.3274 | 5.8162 | 4.6784 | 3.3432 | 2.0537 | 0.88718 | -0.94814 | -2.6415 | -4.4631 | -6.3024 | -8.9208 | -10.0985 | -10.847 | -11.1294 | -10.6055 | 13.3274 | 12.8162 | 11.6784 | 10.3432 | 9.0537 | 7.8872 | 6.0519 | 4.3585 | 2.5369 | 0.69761 | -1.9208 | -3.0985 | -3.847 | -4.1294 | -3.7433 | 6.3274 | 5.8579 | 4.7261 | 3.5588 | 2.4542 | 1.3276 | 0.32353 | -0.40921 | -1.3137 | -2.2462 | -4.5441 | -5.5761 | -6.2495 | -6.676 | -6.6359 | 13.3274 | 12.8579 | 11.7261 | 10.5588 | 9.4542 | 8.3276 | 7.3235 | 6.5908 | 5.6863 | 4.7538 | 2.4559 | 1.4239 | 0.75045 | 0.32395 | 0.3179 | 6.3274 | 5.7089 | 4.5296 | 3.171 | 1.8666 | 0.70745 | -1.1085 | -2.7847 | -4.5767 | -6.3872 | -9.0051 | -10.2927 | -11.1601 | -11.5086 | -11.0016 | 13.3274 | 12.7089 | 11.5296 | 10.171 | 8.8666 | 7.7075 | 5.8915 | 4.2153 | 2.4233 | 0.61278 | -2.0051 | -3.2927 | -4.1601 | -4.5086 | -4.1358 | 380714 | 396551 | STRETFORD | SOUTH MANCHESTER
| Trafford Park North | 1.3294 | 1.2539 | 1.0891 | 0.89732 | 0.73352 | 0.5596 | 0.36928 | 0.15592 | -3.7173 | -7.8944 | -12.7149 | -13.9049 | -14.3618 | -14.1475 | -14.2249 | 6.5794 | 6.5039 | 6.3391 | 6.1473 | 5.9835 | 5.8096 | 5.6193 | 5.4059 | 1.5327 | -2.6444 | -7.4649 | -8.6549 | -9.1118 | -8.8975 | -8.9717 | 1.3294 | 1.3267 | 1.2419 | 1.2036 | 1.1978 | 1.1889 | 1.1778 | 1.1644 | 1.0474 | 0.92085 | 0.40982 | -0.45977 | -1.373 | -2.38 | -3.0353 | 6.5794 | 6.5767 | 6.4919 | 6.4536 | 6.4478 | 6.4389 | 6.4278 | 6.4144 | 6.2974 | 6.1709 | 5.6598 | 4.7902 | 3.877 | 2.87 | 2.299 | 1.3294 | 1.2526 | 1.0884 | 0.89737 | 0.7385 | 0.57372 | 0.39767 | 0.20515 | -3.3929 | -7.1067 | -11.5593 | -12.8048 | -13.352 | -13.1577 | -13.1013 | 6.5794 | 6.5026 | 6.3384 | 6.1474 | 5.9885 | 5.8237 | 5.6477 | 5.4552 | 1.8571 | -1.8567 | -6.3093 | -7.5548 | -8.102 | -7.9077 | -7.8776 | 1.3294 | 1.2583 | 1.1018 | -3.4741 | -11.901 | -11.2658 | -10.7232 | -10.2375 | -10.2789 | -10.3519 | -11.5572 | -12.939 | -13.2702 | -12.975 | -12.8976 | 6.5794 | 6.5083 | 6.3518 | 1.7759 | -6.651 | -6.0158 | -5.4732 | -4.9875 | -5.0289 | -5.1019 | -6.3072 | -7.689 | -8.0202 | -7.725 | -7.6765 | 1.3294 | 1.2569 | 1.0993 | 0.91931 | 0.7698 | 0.60786 | 0.43136 | 0.24246 | -3.5998 | -7.6066 | -12.3006 | -13.5488 | -14.1186 | -13.9834 | -14.0689 | 6.5794 | 6.5069 | 6.3493 | 6.1693 | 6.0198 | 5.8579 | 5.6814 | 5.4925 | 1.6502 | -2.3566 | -7.0506 | -8.2988 | -8.8686 | -8.7334 | -8.8165 | 1.3294 | 1.2526 | 1.0881 | -3.4953 | -11.9255 | -11.2835 | -10.7275 | -10.2237 | -10.2459 | -10.3005 | -11.3353 | -12.8689 | -13.3699 | -13.1766 | -13.1209 | 6.5794 | 6.5026 | 6.3381 | 1.7547 | -6.6755 | -6.0335 | -5.4775 | -4.9737 | -4.9959 | -5.0505 | -6.0853 | -7.6189 | -8.1199 | -7.9266 | -7.8971 | 378738 | 397694 | BARTON | CARRINGTON
| Trimpell | 20.2625 | 19.8509 | 18.4744 | 17.1685 | 15.8474 | 14.5136 | 13.169 | 13.0453 | 12.8724 | 12.688 | 11.938 | 10.9655 | 10.1152 | 9.3333 | 8.6813 | 20.2625 | 19.8509 | 18.4744 | 17.1685 | 15.8474 | 14.5136 | 13.169 | 13.0453 | 12.8724 | 12.688 | 11.938 | 10.9655 | 10.1152 | 9.3333 | 8.6711 | 20.2625 | 20.1124 | 20.0302 | 19.9788 | 19.9312 | 19.88 | 19.8176 | 19.7387 | 19.6316 | 19.5178 | 19.0138 | 18.2843 | 17.4148 | 16.4614 | 15.8596 | 20.2625 | 20.1124 | 20.0302 | 19.9788 | 19.9312 | 19.88 | 19.8176 | 19.7387 | 19.6316 | 19.5178 | 19.0138 | 18.2843 | 17.4148 | 16.4614 | 15.9382 | 20.2625 | 19.7907 | 18.4047 | 17.1007 | 15.7843 | 14.459 | 13.1275 | 13.0231 | 12.8853 | 12.7363 | 12.0439 | 11.1298 | 10.3313 | 9.5749 | 9.0203 | 20.2625 | 19.7907 | 18.4047 | 17.1007 | 15.7843 | 14.459 | 13.1275 | 13.0231 | 12.8853 | 12.7363 | 12.0439 | 11.1298 | 10.3313 | 9.5749 | 8.9929 | 20.2625 | 19.9391 | 18.5821 | 17.2764 | 15.9562 | 14.6212 | 13.2369 | 12.9646 | 12.6505 | 12.3258 | 11.3678 | 10.4594 | 9.7046 | 9.2394 | 9.3221 | 20.2625 | 19.9391 | 18.5821 | 17.2764 | 15.9562 | 14.6212 | 13.2369 | 12.9646 | 12.6505 | 12.3258 | 11.3678 | 10.4594 | 9.7046 | 9.2394 | 9.2924 | 20.2625 | 20.0121 | 18.668 | 17.3736 | 16.0798 | 14.7755 | 13.4542 | 13.3513 | 13.1978 | 13.0305 | 12.4604 | 11.8982 | 11.4671 | 11.1038 | 10.9755 | 20.2625 | 20.0121 | 18.668 | 17.3736 | 16.0798 | 14.7755 | 13.4542 | 13.3513 | 13.1978 | 13.0305 | 12.4604 | 11.8982 | 11.4671 | 11.1038 | 10.9788 | 20.2625 | 19.754 | 18.3585 | 17.0461 | 15.7225 | 14.3919 | 13.0178 | 12.7573 | 12.4621 | 12.1553 | 11.2018 | 10.1845 | 9.3088 | 8.7587 | 8.8029 | 20.2625 | 19.754 | 18.3585 | 17.0461 | 15.7225 | 14.3919 | 13.0178 | 12.7573 | 12.4621 | 12.1553 | 11.2018 | 10.1845 | 9.3088 | 8.7587 | 8.78 | 341861 | 458979 | - | HEYSHAM
| Trinity | 28.4786 | 24.4707 | 22.3653 | 20.7843 | 19.1169 | 17.3875 | 16.029 | 14.6634 | 13.2648 | 12.3579 | 10.0743 | 8.875 | 7.9759 | 6.9697 | 5.9072 | 41.4786 | 37.4707 | 35.3653 | 33.7843 | 32.1169 | 30.3875 | 29.029 | 27.6634 | 26.2648 | 25.3579 | 23.0743 | 21.875 | 20.9759 | 19.9697 | 19.0391 | 28.4786 | 27.0338 | 26.5987 | 26.3175 | 26.0743 | 25.8348 | 25.5821 | 25.2977 | 24.9129 | 24.5028 | 23.3062 | 22.1124 | 21.0711 | 19.8939 | 18.6858 | 41.4786 | 40.0338 | 39.5987 | 39.3175 | 39.0743 | 38.8348 | 38.5821 | 38.2977 | 37.9129 | 37.5028 | 36.3062 | 35.1124 | 34.0711 | 32.8939 | 31.9062 | 28.4786 | 23.8576 | 21.6108 | 20.0207 | 18.3304 | 16.5737 | 14.2812 | 11.6652 | 9.0756 | 8.1661 | 5.8367 | 4.5683 | 3.6385 | 2.6964 | 1.8069 | 41.4786 | 36.8576 | 34.6108 | 33.0207 | 31.3304 | 29.5737 | 27.2812 | 24.6652 | 22.0756 | 21.1661 | 18.8367 | 17.5683 | 16.6385 | 15.6964 | 14.9408 | 28.4786 | 25.1369 | 23.16 | 21.5879 | 19.9093 | 18.1592 | 15.856 | 13.1845 | 10.5377 | 9.5731 | 7.2029 | 6.024 | 5.1871 | 4.3976 | 3.6923 | 41.4786 | 38.1369 | 36.16 | 34.5879 | 32.9093 | 31.1592 | 28.856 | 26.1845 | 23.5377 | 22.5731 | 20.2029 | 19.024 | 18.1871 | 17.3976 | 16.8179 | 28.4786 | 25.9573 | 24.1614 | 22.5937 | 20.9467 | 19.2359 | 17.8941 | 16.5451 | 15.1559 | 14.2547 | 12.0456 | 10.9924 | 10.2074 | 9.3815 | 8.5512 | 41.4786 | 38.9573 | 37.1614 | 35.5937 | 33.9467 | 32.2359 | 30.8941 | 29.5451 | 28.1559 | 27.2547 | 25.0456 | 23.9924 | 23.2074 | 22.3815 | 21.7091 | 28.4786 | 23.3192 | 20.9575 | 19.3655 | 17.6692 | 15.9085 | 13.5874 | 10.8996 | 8.2457 | 7.2705 | 4.8387 | 3.609 | 2.7208 | 1.8741 | 1.0931 | 41.4786 | 36.3192 | 33.9575 | 32.3655 | 30.6692 | 28.9085 | 26.5874 | 23.8996 | 21.2457 | 20.2705 | 17.8387 | 16.609 | 15.7208 | 14.8741 | 14.2358 | 382649 | 398230 | FREDERICK RD | KEARSLEY
| Tulketh | 9.6719 | 8.3109 | 7.9503 | 7.7901 | 7.5046 | 7.2137 | 6.9716 | 6.7704 | 6.5332 | 6.3361 | 4.1867 | -0.040615 | -3.6376 | -7.4672 | -10.7638 | 13.8089 | 12.4479 | 12.0873 | 11.9271 | 11.6416 | 11.3507 | 11.1086 | 10.9074 | 10.6702 | 10.4731 | 8.3237 | 4.0964 | 0.49945 | -3.3302 | -6.919 | 9.6719 | 9.1693 | 8.9642 | 8.8006 | 8.5733 | 8.3342 | 8.0222 | 7.6338 | 7.3261 | 7.017 | 6.1051 | 5.238 | 4.38 | 3.5276 | 3.0102 | 13.8089 | 13.3063 | 13.1012 | 12.9376 | 12.7103 | 12.4712 | 12.1592 | 11.7708 | 11.4631 | 11.154 | 10.2421 | 9.375 | 8.517 | 7.6646 | 7.2235 | 9.6719 | 8.1327 | 7.7682 | 7.6588 | 7.4281 | 7.2014 | 7.048 | 6.9433 | 6.8127 | 6.704 | 4.8185 | 0.81768 | -2.5836 | -6.1889 | -9.2366 | 13.8089 | 12.2697 | 11.9052 | 11.7958 | 11.5651 | 11.3384 | 11.185 | 11.0803 | 10.9497 | 10.841 | 8.9555 | 4.9547 | 1.5534 | -2.0519 | -5.4382 | 9.6719 | 8.8478 | 8.6534 | 8.5763 | 8.3427 | 8.074 | 7.585 | 6.2369 | 4.8375 | 3.4567 | -0.51481 | -4.3033 | -7.4154 | -9.3675 | -7.7861 | 13.8089 | 12.9848 | 12.7904 | 12.7133 | 12.4797 | 12.211 | 11.722 | 10.3739 | 8.9745 | 7.5937 | 3.6222 | -0.16626 | -3.2784 | -5.2305 | -3.9934 | 9.6719 | 8.845 | 8.6309 | 8.5762 | 8.4941 | 8.3864 | 8.2609 | 8.1247 | 7.9018 | 7.6857 | 6.8969 | 5.8581 | 5.1093 | 4.3692 | 4.1097 | 13.8089 | 12.982 | 12.7679 | 12.7132 | 12.6311 | 12.5234 | 12.3979 | 12.2617 | 12.0388 | 11.8227 | 11.0339 | 9.9951 | 9.2463 | 8.5062 | 8.224 | 9.6719 | 8.1579 | 7.7503 | 7.5535 | 7.2128 | 6.8759 | 6.3048 | 4.8359 | 3.3462 | 1.8743 | -2.3792 | -6.4187 | -9.7949 | -12.1016 | -10.9338 | 13.8089 | 12.2949 | 11.8873 | 11.6905 | 11.3498 | 11.0129 | 10.4418 | 8.9729 | 7.4832 | 6.0113 | 1.7578 | -2.2817 | -5.6579 | -7.9646 | -7.0498 | 352393 | 431036 | RIBBLE | PENWORTHAM
| Ulverston | 5.5903 | 5.153 | 4.8476 | 4.6175 | 4.2525 | 3.8874 | 3.5644 | 3.2655 | 2.9355 | 2.6262 | 0.77531 | -2.313 | -5.0018 | -7.7446 | -10.1306 | 8.5903 | 8.153 | 7.8476 | 7.6175 | 7.2525 | 6.8874 | 6.5644 | 6.2655 | 5.9355 | 5.6262 | 3.7753 | 0.68698 | -2.0018 | -4.7446 | -7.2263 | 5.5903 | 5.3749 | 5.1485 | 4.9467 | 4.7263 | 4.4986 | 4.2204 | 3.875 | 3.6286 | 3.3843 | 2.6714 | 1.9887 | 1.3183 | 0.55183 | -0.064692 | 8.5903 | 8.3749 | 8.1485 | 7.9467 | 7.7263 | 7.4986 | 7.2204 | 6.875 | 6.6286 | 6.3843 | 5.6714 | 4.9887 | 4.3183 | 3.5518 | 3.0378 | 5.5903 | 5.1154 | 4.8153 | 4.6144 | 4.2761 | 3.9415 | 3.6612 | 3.4096 | 3.1597 | 2.91 | 1.243 | -1.6708 | -4.1968 | -6.7356 | -8.8784 | 8.5903 | 8.1154 | 7.8153 | 7.6144 | 7.2761 | 6.9415 | 6.6612 | 6.4096 | 6.1597 | 5.91 | 4.243 | 1.3292 | -1.1968 | -3.7356 | -6.0187 | 5.5903 | 5.3592 | 5.129 | 4.932 | 4.5928 | 4.2415 | 3.7648 | 2.7733 | 1.7554 | 0.73947 | -2.1874 | -4.9862 | -7.3339 | -8.8633 | -8.259 | 8.5903 | 8.3592 | 8.129 | 7.932 | 7.5928 | 7.2415 | 6.7648 | 5.7733 | 4.7554 | 3.7395 | 0.81258 | -1.9862 | -4.3339 | -5.8633 | -5.4024 | 5.5903 | 5.3369 | 5.0849 | 4.9011 | 4.6437 | 4.3825 | 4.1172 | 3.8377 | 3.4959 | 3.1563 | 2.0458 | 0.83518 | -0.13885 | -0.98932 | -1.5068 | 8.5903 | 8.3369 | 8.0849 | 7.9011 | 7.6437 | 7.3825 | 7.1172 | 6.8377 | 6.4959 | 6.1563 | 5.0458 | 3.8352 | 2.8611 | 2.0107 | 1.5322 | 5.5903 | 5.1485 | 4.8269 | 4.5581 | 4.1507 | 3.7484 | 3.2136 | 2.1421 | 1.0773 | 0.014653 | -3.0547 | -5.9851 | -8.4737 | -10.1943 | -9.815 | 8.5903 | 8.1485 | 7.8269 | 7.5581 | 7.1507 | 6.7484 | 6.2136 | 5.1421 | 4.0773 | 3.0147 | -0.054744 | -2.9851 | -5.4737 | -7.1943 | -6.9077 | 327495 | 477808 | ULVERSTON | HARKER
| Union Rd | 7.6994 | 7.4504 | 7.1448 | 6.8456 | 6.4632 | 6.0567 | 5.6546 | 4.7249 | 4.286 | 3.85 | 1.4372 | -2.2433 | -5.4762 | -7.8591 | -9.5655 | 12.3364 | 12.0874 | 11.7818 | 11.4826 | 11.1002 | 10.6937 | 10.2916 | 9.3619 | 8.923 | 8.487 | 6.0742 | 2.3937 | -0.83925 | -3.2221 | -5.0931 | 7.6994 | 7.5306 | 7.3306 | 7.1467 | 6.9315 | 6.6939 | 6.3927 | 6.0088 | 5.6926 | 5.3417 | 4.0367 | 2.4069 | 0.38334 | -1.1804 | -2.7704 | 12.3364 | 12.1676 | 11.9676 | 11.7837 | 11.5685 | 11.3309 | 11.0297 | 10.6458 | 10.3296 | 9.9787 | 8.6737 | 7.0439 | 5.0203 | 3.4566 | 2.4444 | 7.6994 | 7.3454 | 6.9266 | 6.5004 | 5.9845 | 4.8542 | 4.3027 | 3.7361 | 3.1511 | 2.5582 | -0.94725 | -4.397 | -7.0341 | -9.3566 | -10.832 | 12.3364 | 11.9824 | 11.5636 | 11.1374 | 10.6215 | 9.4912 | 8.9397 | 8.3731 | 7.7881 | 7.1952 | 3.6898 | 0.24003 | -2.3971 | -4.7196 | -6.1286 | 7.6994 | 7.6084 | 7.291 | 5.6314 | 4.6462 | 4.1959 | 3.583 | 2.5588 | 1.485 | 0.43421 | -3.0572 | -6.163 | -8.0249 | -9.0975 | -8.9688 | 12.3364 | 12.2454 | 11.928 | 10.2684 | 9.2832 | 8.8329 | 8.22 | 7.1958 | 6.122 | 5.0712 | 1.5798 | -1.526 | -3.3879 | -4.4605 | -4.3085 | 7.6994 | 7.4773 | 7.216 | 6.9998 | 6.7638 | 6.4837 | 6.1585 | 5.2767 | 4.8592 | 4.4042 | 2.9288 | 1.0334 | -1.0437 | -2.4949 | -3.4973 | 12.3364 | 12.1143 | 11.853 | 11.6368 | 11.4008 | 11.1207 | 10.7955 | 9.9137 | 9.4962 | 9.0412 | 7.5658 | 5.6704 | 3.5933 | 2.1421 | 1.2872 | 7.6994 | 7.5524 | 7.156 | 5.4056 | 4.3533 | 3.8744 | 3.2439 | 2.1598 | 1.0419 | -0.049011 | -3.9307 | -7.3226 | -9.4695 | -10.844 | -10.9099 | 12.3364 | 12.1894 | 11.793 | 10.0426 | 8.9903 | 8.5114 | 7.8809 | 6.7968 | 5.6789 | 4.588 | 0.7063 | -2.6856 | -4.8325 | -6.207 | -6.2961 | 372174 | 410598 | BOLTON | KEARSLEY
| Upholland | 4.3154 | 4.0305 | 3.8892 | 3.7954 | 3.618 | 3.4353 | 3.2756 | 3.1262 | 2.9118 | 2.7293 | 0.98562 | -2.2415 | -4.9911 | -8.012 | -10.6604 | 7.8154 | 7.5305 | 7.3892 | 7.2954 | 7.118 | 6.9353 | 6.7756 | 6.6262 | 6.4118 | 6.2293 | 4.4856 | 1.2585 | -1.4911 | -4.512 | -7.3164 | 4.3154 | 4.1527 | 4.0372 | 3.9204 | 3.744 | 3.5368 | 3.2593 | 2.9045 | 2.5956 | 2.285 | 1.3644 | 0.35233 | -0.64817 | -1.6683 | -2.3233 | 7.8154 | 7.6527 | 7.5372 | 7.4204 | 7.244 | 7.0368 | 6.7593 | 6.4045 | 6.0956 | 5.785 | 4.8644 | 3.8523 | 2.8518 | 1.8317 | 1.2779 | 4.3154 | 4.0262 | 3.9115 | 3.8702 | 3.7504 | 3.6352 | 3.5688 | 3.5213 | 3.4153 | 3.3256 | 1.6716 | -1.371 | -3.9017 | -6.5396 | -8.7253 | 7.8154 | 7.5262 | 7.4115 | 7.3702 | 7.2504 | 7.1352 | 7.0688 | 7.0213 | 6.9153 | 6.8256 | 5.1716 | 2.129 | -0.40174 | -3.0396 | -5.4149 | 4.3154 | 4.41 | 4.403 | 4.3841 | 4.2628 | 4.1131 | 3.7951 | 2.8554 | 1.8617 | 0.88083 | -1.9585 | -4.774 | -7.1052 | -8.6557 | -7.6852 | 7.8154 | 7.91 | 7.903 | 7.8841 | 7.7628 | 7.6131 | 7.2951 | 6.3554 | 5.3617 | 4.3808 | 1.5415 | -1.274 | -3.6052 | -5.1557 | -4.4003 | 4.3154 | 4.1438 | 4.0705 | 4.057 | 4.0164 | 3.9379 | 3.8176 | 3.647 | 3.3744 | 3.1057 | 2.1412 | 0.61386 | -0.50186 | -1.5205 | -1.8962 | 7.8154 | 7.6438 | 7.5705 | 7.557 | 7.5164 | 7.4379 | 7.3176 | 7.147 | 6.8744 | 6.6057 | 5.6412 | 4.1139 | 2.9981 | 1.9795 | 1.5995 | 4.3154 | 4.2483 | 4.1194 | 3.9822 | 3.7537 | 3.5329 | 3.1276 | 2.0645 | 0.9748 | -0.10061 | -3.2589 | -6.3244 | -8.8714 | -10.6769 | -9.9915 | 7.8154 | 7.7483 | 7.6194 | 7.4822 | 7.2537 | 7.0329 | 6.6276 | 5.5645 | 4.4748 | 3.3994 | 0.24105 | -2.8244 | -5.3714 | -7.1769 | -6.6438 | 352531 | 404369 | ORRELL | KIRKBY
| Urmston | 12.0463 | 11.7868 | 11.7439 | 11.6606 | 11.5067 | 11.334 | 11.16 | 10.9908 | 10.8008 | 10.6372 | 9.2271 | 6.5705 | 4.284 | 1.7473 | -0.5489 | 16.6833 | 16.4238 | 16.3809 | 16.2976 | 16.1437 | 15.971 | 15.797 | 15.6278 | 15.4378 | 15.2742 | 13.8641 | 11.2075 | 8.921 | 6.3843 | 3.9905 | 12.0463 | 11.8517 | 11.8183 | 11.7212 | 11.574 | 11.403 | 11.1752 | 10.8877 | 10.6534 | 10.4158 | 9.6997 | 8.987 | 8.2768 | 7.4786 | 6.8706 | 16.6833 | 16.4887 | 16.4553 | 16.3582 | 16.211 | 16.04 | 15.8122 | 15.5247 | 15.2904 | 15.0528 | 14.3367 | 13.624 | 12.9138 | 12.1156 | 11.6102 | 12.0463 | 11.7845 | 11.7561 | 11.7017 | 11.5781 | 11.4402 | 11.3189 | 11.2023 | 11.0742 | 10.9628 | 9.7211 | 7.2068 | 5.048 | 2.6623 | 0.53635 | 16.6833 | 16.4215 | 16.3931 | 16.3387 | 16.2151 | 16.0772 | 15.9559 | 15.8393 | 15.7112 | 15.5998 | 14.3581 | 11.8438 | 9.685 | 7.2993 | 5.0444 | 12.0463 | 12.1052 | 12.1678 | 12.1401 | 12.0156 | 11.8476 | 11.5339 | 10.7331 | 9.9059 | 9.0852 | 6.6822 | 4.2888 | 2.3072 | 0.92446 | 1.5089 | 16.6833 | 16.7422 | 16.8048 | 16.7771 | 16.6526 | 16.4846 | 16.1709 | 15.3701 | 14.5429 | 13.7222 | 11.3192 | 8.9258 | 6.9442 | 5.5615 | 6.0114 | 12.0463 | 11.8514 | 11.8612 | 11.8509 | 11.8096 | 11.7256 | 11.6093 | 11.4826 | 11.3068 | 11.1382 | 10.5022 | 9.7009 | 9.1127 | 8.4945 | 8.1024 | 16.6833 | 16.4884 | 16.4982 | 16.4879 | 16.4466 | 16.3626 | 16.2463 | 16.1196 | 15.9438 | 15.7752 | 15.1392 | 14.3379 | 13.7497 | 13.1315 | 12.7563 | 12.0463 | 11.9963 | 11.9694 | 11.8523 | 11.6481 | 11.4338 | 11.0631 | 10.1775 | 9.2848 | 8.3997 | 5.8142 | 3.2983 | 1.1959 | -0.33867 | 0.055004 | 16.6833 | 16.6333 | 16.6064 | 16.4893 | 16.2851 | 16.0708 | 15.7001 | 14.8145 | 13.9218 | 13.0367 | 10.4512 | 7.9353 | 5.8329 | 4.2983 | 4.6016 | 377117 | 395709 | STRETFORD | SOUTH MANCHESTER
| Victoria Park | 6.4879 | 5.1335 | 4.6712 | 4.578 | 4.558 | 12.5498 | 12.5518 | 12.5572 | 12.4452 | 12.3462 | 12.0819 | 11.7011 | 11.333 | 11.0288 | 10.8886 | 12.9879 | 11.6335 | 11.1712 | 11.078 | 11.058 | 19.0498 | 19.0518 | 19.0572 | 18.9452 | 18.8462 | 18.5819 | 18.2011 | 17.833 | 17.5288 | 17.3214 | 6.4879 | 6.0815 | 5.7961 | 5.6757 | 5.6169 | 13.5537 | 13.4847 | 13.4063 | 13.2352 | 13.0721 | 12.635 | 12.2758 | 11.9979 | 11.7329 | 11.5495 | 12.9879 | 12.5815 | 12.2961 | 12.1757 | 12.1169 | 20.0537 | 19.9847 | 19.9063 | 19.7352 | 19.5721 | 19.135 | 18.7758 | 18.4979 | 18.2329 | 18.0725 | 6.4879 | 4.9075 | 4.2782 | 4.06 | 3.9174 | 11.7873 | 11.6666 | 11.6705 | 11.6137 | 11.5791 | 11.5169 | 11.3774 | 11.2368 | 11.2511 | 11.5248 | 12.9879 | 11.4075 | 10.7782 | 10.56 | 10.4174 | 18.2873 | 18.1666 | 18.1705 | 18.1137 | 18.0791 | 18.0169 | 17.8774 | 17.7368 | 17.7511 | 17.8767 | 6.4879 | 5.377 | 4.8619 | 4.668 | 4.5481 | 12.4339 | 12.3219 | 12.3226 | 12.2459 | 12.1609 | 11.7625 | 11.4637 | 11.3349 | 11.4817 | 12.1332 | 12.9879 | 11.877 | 11.3619 | 11.168 | 11.0481 | 18.9339 | 18.8219 | 18.8226 | 18.7459 | 18.6609 | 18.2625 | 17.9637 | 17.8349 | 17.9817 | 18.4831 | 6.4879 | 5.7367 | 5.4042 | 5.3224 | 5.3148 | 13.312 | 13.3132 | 13.3212 | 13.2124 | 13.1138 | 12.8724 | 12.7073 | 12.6498 | 12.6407 | 12.8411 | 12.9879 | 12.2367 | 11.9042 | 11.8224 | 11.8148 | 19.812 | 19.8132 | 19.8212 | 19.7124 | 19.6138 | 19.3724 | 19.2073 | 19.1498 | 19.1407 | 19.2785 | 6.4879 | 4.6914 | 4.0172 | 3.7977 | 3.6541 | 11.5237 | 11.3958 | 11.3723 | 11.2877 | 11.2249 | 10.8769 | 10.5752 | 10.444 | 10.5904 | 11.2337 | 12.9879 | 11.1914 | 10.5172 | 10.2977 | 10.1541 | 18.0237 | 17.8958 | 17.8723 | 17.7877 | 17.7249 | 17.3769 | 17.0752 | 16.944 | 17.0904 | 17.5866 | 385373 | 395948 | LONGSIGHT | BREDBURY
| Warbreck | 7.7168 | 7.1324 | 7.0363 | 7.0262 | 6.9187 | 6.7835 | 6.6455 | 6.523 | 6.323 | 6.099 | 4.6761 | 2.3446 | 0.43198 | -1.5355 | -3.4831 | 11.2168 | 10.6324 | 10.5363 | 10.5262 | 10.4187 | 10.2835 | 10.1455 | 10.023 | 9.823 | 9.599 | 8.1761 | 5.8446 | 3.932 | 1.9645 | -0.10035 | 7.7168 | 7.6228 | 7.5861 | 7.5502 | 7.471 | 7.376 | 7.2314 | 7.0414 | 6.8884 | 6.7258 | 6.0961 | 5.3575 | 4.6108 | 3.8188 | 3.2931 | 11.2168 | 11.1228 | 11.0861 | 11.0502 | 10.971 | 10.876 | 10.7314 | 10.5414 | 10.3884 | 10.2258 | 9.5961 | 8.8575 | 8.1108 | 7.3188 | 6.8706 | 7.7168 | 7.0549 | 6.9607 | 6.9797 | 6.9046 | 6.8087 | 6.7301 | 6.669 | 6.5032 | 6.3367 | 5.0507 | 2.7743 | 0.89977 | -0.93706 | -2.6159 | 11.2168 | 10.5549 | 10.4607 | 10.4797 | 10.4046 | 10.3087 | 10.2301 | 10.169 | 10.0032 | 9.8367 | 8.5507 | 6.2743 | 4.3998 | 2.5629 | 0.74087 | 7.7168 | 7.489 | 7.486 | 7.5066 | 7.4097 | 7.2741 | 7.0116 | 6.3072 | 5.5598 | 4.8065 | 2.5839 | 0.44232 | -1.29 | -2.3252 | -1.654 | 11.2168 | 10.989 | 10.986 | 11.0066 | 10.9097 | 10.7741 | 10.5116 | 9.8072 | 9.0598 | 8.3065 | 6.0839 | 3.9423 | 2.21 | 1.1748 | 1.6986 | 7.7168 | 7.612 | 7.6265 | 7.6794 | 7.6993 | 7.6883 | 7.6444 | 7.5763 | 7.4133 | 7.2047 | 6.4046 | 5.4866 | 4.8371 | 4.2782 | 4.0342 | 11.2168 | 11.112 | 11.1265 | 11.1794 | 11.1993 | 11.1883 | 11.1444 | 11.0763 | 10.9133 | 10.7047 | 9.9046 | 8.9866 | 8.3371 | 7.7782 | 7.5295 | 7.7168 | 7.1721 | 7.0643 | 7.0216 | 6.8685 | 6.6979 | 6.3916 | 5.631 | 4.8479 | 4.0577 | 1.6917 | -0.60128 | -2.4864 | -3.6869 | -3.1864 | 11.2168 | 10.6721 | 10.5643 | 10.5216 | 10.3685 | 10.1979 | 9.8916 | 9.131 | 8.3479 | 7.5577 | 5.1917 | 2.8987 | 1.0136 | -0.1869 | 0.20327 | 331775 | 438420 | BISPHAM | PENWORTHAM
| Wardleworth | 11.5727 | 10.6463 | 10.3348 | 10.1999 | 9.9976 | 9.781 | 9.5771 | 9.3882 | 9.1389 | 8.9106 | 7.4161 | 4.8263 | 2.6951 | 0.46096 | -1.5606 | 16.2097 | 15.2833 | 14.9718 | 14.8369 | 14.6346 | 14.418 | 14.2141 | 14.0252 | 13.7759 | 13.5476 | 12.0531 | 9.4633 | 7.3321 | 5.098 | 2.9898 | 11.5727 | 11.1916 | 10.9838 | 10.8357 | 10.6644 | 10.486 | 10.2531 | 9.9341 | 9.6359 | 9.3341 | 8.4153 | 7.4326 | 6.5114 | 5.4873 | 4.7304 | 16.2097 | 15.8286 | 15.6208 | 15.4727 | 15.3014 | 15.123 | 14.8901 | 14.5711 | 14.2729 | 13.9711 | 13.0523 | 12.0696 | 11.1484 | 10.1243 | 9.4939 | 11.5727 | 10.519 | 10.1938 | 10.0768 | 9.8996 | 9.7139 | 9.5451 | 9.41 | 9.247 | 9.1044 | 7.7942 | 5.4707 | 3.5172 | 1.4846 | -0.29429 | 16.2097 | 15.156 | 14.8308 | 14.7138 | 14.5366 | 14.3509 | 14.1821 | 14.047 | 13.884 | 13.7414 | 12.4312 | 10.1077 | 8.1542 | 6.1216 | 4.2107 | 11.5727 | 11.0043 | 10.7951 | 10.7007 | 10.5273 | 10.3329 | 10.0104 | 9.2582 | 8.4556 | 7.6695 | 5.4014 | 3.1195 | 1.3215 | 0.17177 | 0.76667 | 16.2097 | 15.6413 | 15.4321 | 15.3377 | 15.1643 | 14.9699 | 14.6474 | 13.8952 | 13.0926 | 12.3065 | 10.0384 | 7.7565 | 5.9585 | 4.8088 | 5.2659 | 11.5727 | 10.988 | 10.7669 | 10.6805 | 10.5824 | 10.4716 | 10.3488 | 10.2083 | 9.9795 | 9.7333 | 8.8652 | 7.7495 | 6.9724 | 6.2516 | 5.8353 | 16.2097 | 15.625 | 15.4039 | 15.3175 | 15.2194 | 15.1086 | 14.9858 | 14.8453 | 14.6165 | 14.3703 | 13.5022 | 12.3865 | 11.6094 | 10.8886 | 10.5083 | 11.5727 | 10.5713 | 10.2271 | 10.0704 | 9.8393 | 9.6026 | 9.2367 | 8.4173 | 7.5718 | 6.7178 | 4.21 | 1.7704 | -0.18883 | -1.5408 | -1.1772 | 16.2097 | 15.2083 | 14.8641 | 14.7074 | 14.4763 | 14.2396 | 13.8737 | 13.0543 | 12.2088 | 11.3548 | 8.847 | 6.4074 | 4.4482 | 3.0962 | 3.3733 | 390339 | 414050 | BELFIELD | ROCHDALE
| Warton | 11.3605 | 10.6707 | 10.2783 | 10.032 | 9.7211 | 9.3509 | 9.0685 | 8.7948 | 8.498 | 8.219 | 7.4082 | 6.3879 | 5.6509 | 4.9433 | 4.3069 | 15.9975 | 15.3077 | 14.9153 | 14.669 | 14.3581 | 13.9879 | 13.7055 | 13.4318 | 13.135 | 12.856 | 12.0452 | 11.0249 | 10.2879 | 9.5803 | 8.9412 | 11.3605 | 11.0434 | 10.805 | 10.6622 | 10.5424 | 10.4385 | 10.3071 | 10.1114 | 9.8201 | 9.5335 | 8.7013 | 7.8188 | 7.0798 | 6.2449 | 4.2997 | 15.9975 | 15.6804 | 15.442 | 15.2992 | 15.1794 | 15.0755 | 14.9441 | 14.7484 | 14.4571 | 14.1705 | 13.3383 | 12.4558 | 11.7168 | 10.8819 | 9.0416 | 11.3605 | 10.6104 | 10.218 | 9.9179 | 9.626 | 9.3467 | 9.0846 | 8.8395 | 8.611 | 8.4048 | 6.5775 | 5.7267 | 5.1706 | 4.7174 | 4.4022 | 15.9975 | 15.2474 | 14.855 | 14.5549 | 14.263 | 13.9837 | 13.7216 | 13.4765 | 13.248 | 13.0418 | 11.2145 | 10.3637 | 9.8076 | 9.3544 | 8.9726 | 11.3605 | 10.8771 | 10.4712 | 10.2525 | 9.9714 | 8.2235 | 7.9947 | 7.6714 | 7.3378 | 7.0225 | 6.2023 | 5.4111 | 4.9102 | 4.6813 | 4.9823 | 15.9975 | 15.5141 | 15.1082 | 14.8895 | 14.6084 | 12.8605 | 12.6317 | 12.3084 | 11.9748 | 11.6595 | 10.8393 | 10.0481 | 9.5472 | 9.3183 | 9.5456 | 11.3605 | 10.7739 | 10.4099 | 10.1882 | 9.9182 | 9.5857 | 9.3253 | 9.0465 | 8.7175 | 8.395 | 7.5942 | 6.7979 | 6.2701 | 5.7977 | 5.6024 | 15.9975 | 15.4109 | 15.0469 | 14.8252 | 14.5552 | 14.2227 | 13.9623 | 13.6835 | 13.3545 | 13.032 | 12.2312 | 11.4349 | 10.9071 | 10.4347 | 10.2466 | 11.3605 | 10.6109 | 10.1314 | 9.8854 | 9.5752 | 7.8088 | 7.5612 | 7.2055 | 6.8481 | 6.5102 | 5.6264 | 4.7542 | 4.1928 | 3.9007 | 4.1233 | 15.9975 | 15.2479 | 14.7684 | 14.5224 | 14.2122 | 12.4458 | 12.1982 | 11.8425 | 11.4851 | 11.1472 | 10.2634 | 9.3912 | 8.8298 | 8.5377 | 8.7039 | 341290 | 428540 | PEEL | PENWORTHAM
| Waterhead | 15.4682 | 15.3052 | 15.1376 | 14.9652 | 14.7222 | 14.4692 | 14.2345 | 14.0176 | 13.7883 | 13.571 | 12.1872 | 9.9728 | 8.2637 | 6.6492 | 5.5067 | 20.1052 | 19.9422 | 19.7746 | 19.6022 | 19.3592 | 19.1062 | 18.8715 | 18.6546 | 18.4253 | 18.208 | 16.8242 | 14.6098 | 12.9007 | 11.2862 | 10.0065 | 15.4682 | 15.3602 | 15.2562 | 15.1501 | 15.0124 | 14.8649 | 14.6759 | 14.4337 | 14.2373 | 14.0312 | 13.4041 | 12.7659 | 12.1318 | 11.4244 | 10.8856 | 20.1052 | 19.9972 | 19.8932 | 19.7871 | 19.6494 | 19.5019 | 19.3129 | 19.0707 | 18.8743 | 18.6682 | 18.0411 | 17.4029 | 16.7688 | 16.0614 | 15.6157 | 15.4682 | 15.2416 | 15.0093 | 14.772 | 14.3989 | 14.0123 | 13.6478 | 13.2922 | 12.9293 | 12.5606 | 10.7695 | 8.6084 | 7.1586 | 6.0262 | 5.6289 | 20.1052 | 19.8786 | 19.6463 | 19.409 | 19.0359 | 18.6493 | 18.2848 | 17.9292 | 17.5663 | 17.1976 | 15.4065 | 13.2454 | 11.7956 | 10.6632 | 10.1211 | 15.4682 | 15.424 | 15.2456 | 15.0256 | 14.6532 | 14.2516 | 13.7409 | 12.8487 | 11.9752 | 11.1304 | 8.7731 | 6.9743 | 5.8961 | 5.5261 | 6.2251 | 20.1052 | 20.061 | 19.8826 | 19.6626 | 19.2902 | 18.8886 | 18.3779 | 17.4857 | 16.6122 | 15.7674 | 13.4101 | 11.6113 | 10.5331 | 10.1631 | 10.714 | 15.4682 | 15.322 | 15.1827 | 15.0628 | 14.9227 | 14.7611 | 14.5836 | 14.393 | 14.16 | 13.9223 | 13.1161 | 12.2647 | 11.6621 | 11.0408 | 10.6025 | 20.1052 | 19.959 | 19.8197 | 19.6998 | 19.5597 | 19.3981 | 19.2206 | 19.03 | 18.797 | 18.5593 | 17.7531 | 16.9017 | 16.2991 | 15.6778 | 15.2901 | 15.4682 | 15.3848 | 15.1518 | 14.8699 | 14.4411 | 14.0013 | 13.4438 | 12.4863 | 11.5642 | 10.6705 | 8.1623 | 6.2322 | 5.0238 | 4.4928 | 4.9971 | 20.1052 | 20.0218 | 19.7888 | 19.5069 | 19.0781 | 18.6383 | 18.0808 | 17.1233 | 16.2012 | 15.3075 | 12.7993 | 10.8692 | 9.6608 | 9.1298 | 9.5287 | 394942 | 405940 | GREENHILL | WHITEGATE
| Waterswallows | 13.2189 | 12.9914 | 12.8059 | 12.7034 | 12.6189 | 12.5215 | 12.4105 | 12.272 | 12.0322 | 11.7841 | 10.3964 | 8.757 | 7.6664 | 6.7919 | 6.3806 | 17.8559 | 17.6284 | 17.4429 | 17.3404 | 17.2559 | 17.1585 | 17.0475 | 16.909 | 16.6692 | 16.4211 | 15.0334 | 13.394 | 12.3034 | 11.4289 | 10.9688 | 13.2189 | 13.1527 | 13.019 | 12.9427 | 12.8971 | 12.8486 | 12.7909 | 12.6448 | 12.4114 | 12.1633 | 11.3461 | 10.4171 | 9.2662 | 7.9853 | 7.224 | 17.8559 | 17.7897 | 17.656 | 17.5797 | 17.5341 | 17.4856 | 17.4279 | 17.2818 | 17.0484 | 16.8003 | 15.9831 | 15.0541 | 13.9032 | 12.6223 | 11.9591 | 13.2189 | 12.9585 | 12.7668 | 12.6647 | 12.5844 | 12.4953 | 12.3973 | 12.2786 | 12.1004 | 11.9172 | 10.6466 | 8.6904 | 7.3951 | 6.5391 | 6.2137 | 17.8559 | 17.5955 | 17.4038 | 17.3017 | 17.2214 | 17.1323 | 17.0343 | 16.9156 | 16.7374 | 16.5542 | 15.2836 | 13.3274 | 12.0321 | 11.1761 | 10.8192 | 13.2189 | 13.0659 | 12.9121 | 12.8267 | 12.6699 | 12.5798 | 12.4376 | 12.1393 | 11.7201 | 11.2934 | 9.8764 | 8.6597 | 7.6555 | 7.0154 | 7.0892 | 17.8559 | 17.7029 | 17.5491 | 17.4637 | 17.3069 | 17.2168 | 17.0746 | 16.7763 | 16.3571 | 15.9304 | 14.5134 | 13.2967 | 12.2925 | 11.6524 | 11.6802 | 13.2189 | 13.1164 | 12.9714 | 12.8954 | 12.8498 | 12.7846 | 12.6968 | 12.5889 | 12.3805 | 12.1591 | 11.2524 | 9.887 | 8.8857 | 8.0576 | 7.8084 | 17.8559 | 17.7534 | 17.6084 | 17.5324 | 17.4868 | 17.4216 | 17.3338 | 17.2259 | 17.0175 | 16.7961 | 15.8894 | 14.524 | 13.5227 | 12.6946 | 12.46 | 13.2189 | 12.9566 | 12.7604 | 12.6495 | 12.4743 | 12.387 | 12.2568 | 11.9973 | 11.5991 | 11.1886 | 9.8543 | 8.2677 | 7.1574 | 6.5898 | 6.8643 | 17.8559 | 17.5936 | 17.3974 | 17.2865 | 17.1113 | 17.024 | 16.8938 | 16.6343 | 16.2361 | 15.8256 | 14.4913 | 12.9047 | 11.7944 | 11.2268 | 11.4239 | 407734 | 375459 | BUXTON | STALYBRIDGE
| Weaste | 5.8371 | 5.5131 | 5.221 | 5.0535 | 4.9357 | 4.8088 | 4.3638 | 3.8905 | 3.3112 | 2.7294 | 0.84351 | -1.6277 | -2.84 | -3.9728 | -5.0046 | 12.8371 | 12.5131 | 12.221 | 12.0535 | 11.9357 | 11.8088 | 11.3638 | 10.8905 | 10.3112 | 9.7294 | 7.8435 | 5.3723 | 4.16 | 3.0272 | 1.9279 | 5.8371 | 5.6382 | 5.345 | 5.133 | 4.9547 | 4.7487 | 4.5104 | 4.2384 | 3.9792 | 3.716 | 2.902 | 2.0834 | 1.3383 | 0.20666 | -0.60565 | 12.8371 | 12.6382 | 12.345 | 12.133 | 11.9547 | 11.7487 | 11.5104 | 11.2384 | 10.9792 | 10.716 | 9.902 | 9.0834 | 8.3383 | 7.2067 | 6.5094 | 5.8371 | 5.4731 | 5.1735 | 5.0057 | 4.8918 | 4.7727 | 4.3392 | 3.8838 | 3.3812 | 2.8818 | 1.167 | -1.1622 | -2.224 | -3.0958 | -3.6812 | 12.8371 | 12.4731 | 12.1735 | 12.0057 | 11.8918 | 11.7727 | 11.3392 | 10.8838 | 10.3812 | 9.8818 | 8.167 | 5.8378 | 4.776 | 3.9042 | 3.1788 | 5.8371 | 5.6347 | 5.4061 | 5.2933 | 5.2262 | 5.1344 | 4.7126 | 4.0761 | 3.251 | 2.4305 | 0.027432 | -2.2028 | -3.1762 | -3.7134 | -3.1199 | 12.8371 | 12.6347 | 12.4061 | 12.2933 | 12.2262 | 12.1344 | 11.7126 | 11.0761 | 10.251 | 9.4305 | 7.0274 | 4.7972 | 3.8238 | 3.2866 | 3.7358 | 5.8371 | 5.6139 | 5.3614 | 5.2251 | 5.1409 | 5.0328 | 4.5984 | 4.1516 | 3.605 | 3.0528 | 1.3617 | -0.25785 | -0.7994 | -1.2973 | -1.4052 | 12.8371 | 12.6139 | 12.3614 | 12.2251 | 12.1409 | 12.0328 | 11.5984 | 11.1516 | 10.605 | 10.0528 | 8.3617 | 6.7421 | 6.2006 | 5.7027 | 5.5817 | 5.8371 | 5.4829 | 5.1821 | 5.0152 | 4.9001 | 4.7816 | 4.3398 | 3.793 | 2.9683 | 2.1493 | -0.28366 | -2.5891 | -3.754 | -4.4003 | -3.9069 | 12.8371 | 12.4829 | 12.1821 | 12.0152 | 11.9001 | 11.7816 | 11.3398 | 10.793 | 9.9683 | 9.1493 | 6.7163 | 4.4109 | 3.246 | 2.5997 | 2.9711 | 378751 | 398897 | FREDERICK RD | KEARSLEY
| Werneth | 14.0728 | 13.7091 | 13.4744 | 13.2488 | 12.9198 | 12.5551 | 12.1862 | 11.8243 | 11.3988 | 10.9409 | 8.9026 | 6.0829 | 3.9403 | 1.9912 | 0.55928 | 18.7098 | 18.3461 | 18.1114 | 17.8858 | 17.5568 | 17.1921 | 16.8232 | 16.4613 | 16.0358 | 15.5779 | 13.5396 | 10.7199 | 8.5773 | 6.6282 | 5.143 | 14.0728 | 13.8827 | 13.7394 | 13.5893 | 13.3891 | 13.1712 | 12.8928 | 12.5227 | 12.2348 | 11.9332 | 10.8788 | 9.6242 | 8.407 | 7.0048 | 6.0242 | 18.7098 | 18.5197 | 18.3764 | 18.2263 | 18.0261 | 17.8082 | 17.5298 | 17.1597 | 16.8718 | 16.5702 | 15.5158 | 14.2612 | 13.044 | 11.6418 | 10.824 | 14.0728 | 13.626 | 13.3211 | 13.0283 | 12.5697 | 12.073 | 11.5821 | 11.087 | 10.5388 | 9.9278 | 7.5638 | 4.7008 | 2.6348 | 0.90519 | -0.073043 | 18.7098 | 18.263 | 17.9581 | 17.6653 | 17.2067 | 16.71 | 16.2191 | 15.724 | 15.1758 | 14.5648 | 12.2008 | 9.3378 | 7.2718 | 5.5422 | 4.5425 | 14.0728 | 13.922 | 13.6944 | 13.4271 | 12.972 | 12.4535 | 11.8089 | 10.7544 | 9.7123 | 8.6983 | 5.9904 | 3.5147 | 1.861 | 0.90173 | 0.97735 | 18.7098 | 18.559 | 18.3314 | 18.0641 | 17.609 | 17.0905 | 16.4459 | 15.3914 | 14.3493 | 13.3353 | 10.6274 | 8.1517 | 6.498 | 5.5387 | 5.5794 | 14.0728 | 13.8375 | 13.6563 | 13.4926 | 13.2849 | 13.0439 | 12.7664 | 12.45 | 12.082 | 11.6605 | 10.1342 | 8.5443 | 7.3178 | 6.1396 | 5.2874 | 18.7098 | 18.4745 | 18.2933 | 18.1296 | 17.9219 | 17.6809 | 17.4034 | 17.087 | 16.719 | 16.2975 | 14.7712 | 13.1813 | 11.9548 | 10.7766 | 10.0448 | 14.0728 | 13.8177 | 13.5176 | 13.1835 | 12.6655 | 12.1102 | 11.4198 | 10.3025 | 9.2176 | 8.1569 | 5.2712 | 2.6367 | 0.78123 | -0.39813 | -0.57038 | 18.7098 | 18.4547 | 18.1546 | 17.8205 | 17.3025 | 16.7472 | 16.0568 | 14.9395 | 13.8546 | 12.7939 | 9.9082 | 7.2737 | 5.4182 | 4.2389 | 4.0851 | 391273 | 403453 | GREENHILL | WHITEGATE
| Wesley Place Bacup | 12.6855 | 12.5608 | 12.2364 | 11.9385 | 11.643 | 11.4162 | 11.2102 | 11.005 | 10.7606 | 10.5276 | 8.7287 | 5.437 | 2.6866 | -0.23794 | -2.8012 | 17.3225 | 17.1978 | 16.8734 | 16.5755 | 16.28 | 16.0532 | 15.8472 | 15.642 | 15.3976 | 15.1646 | 13.3657 | 10.074 | 7.3236 | 4.3991 | 1.7009 | 12.6855 | 12.564 | 12.3554 | 12.2037 | 12.0704 | 11.8801 | 11.6254 | 11.2635 | 10.9625 | 10.6576 | 9.7258 | 8.7301 | 7.7617 | 6.6416 | 5.8321 | 17.3225 | 17.201 | 16.9924 | 16.8407 | 16.7074 | 16.5171 | 16.2624 | 15.9005 | 15.5995 | 15.2946 | 14.3628 | 13.3671 | 12.3987 | 11.2786 | 10.6037 | 12.6855 | 12.559 | 12.2347 | 11.9361 | 11.6418 | 11.4174 | 11.2136 | 11.0136 | 10.8046 | 10.6103 | 9.222 | 6.1947 | 3.5967 | 0.87651 | -1.4304 | 17.3225 | 17.196 | 16.8717 | 16.5731 | 16.2788 | 16.0544 | 15.8506 | 15.6506 | 15.4416 | 15.2473 | 13.859 | 10.8317 | 8.2337 | 5.5135 | 3.0257 | 12.6855 | 12.6939 | 12.4189 | 12.1422 | 11.8622 | 11.6371 | 11.2721 | 10.4329 | 9.4155 | 8.3469 | 5.273 | 2.3086 | -0.073667 | -1.6429 | -0.83962 | 17.3225 | 17.3309 | 17.0559 | 16.7792 | 16.4992 | 16.2741 | 15.9091 | 15.0699 | 14.0525 | 12.9839 | 9.91 | 6.9456 | 4.5633 | 2.9941 | 3.6121 | 12.6855 | 12.5809 | 12.2787 | 12.0258 | 11.8347 | 11.7064 | 11.5582 | 11.3793 | 11.1272 | 10.8704 | 10.0148 | 8.9058 | 8.1476 | 7.4202 | 7.0217 | 17.3225 | 17.2179 | 16.9157 | 16.6628 | 16.4717 | 16.3434 | 16.1952 | 16.0163 | 15.7642 | 15.5074 | 14.6518 | 13.5428 | 12.7846 | 12.0572 | 11.6796 | 12.6855 | 12.6629 | 12.3463 | 12.0221 | 11.6997 | 11.4526 | 11.0702 | 10.0811 | 8.97 | 7.8589 | 4.6336 | 1.5042 | -1.0618 | -2.8793 | -2.3596 | 17.3225 | 17.2999 | 16.9833 | 16.6591 | 16.3367 | 16.0896 | 15.7072 | 14.7181 | 13.607 | 12.4959 | 9.2706 | 6.1412 | 3.5752 | 1.7577 | 2.1552 | 386475 | 422130 | ROSSENDALE | PADIHAM
| West Didsbury | 8.2949 | 7.2109 | 6.6928 | 6.3058 | 5.8261 | 5.3313 | 4.8664 | 4.4527 | 4.0388 | 3.6626 | 1.9329 | -0.49356 | -2.1697 | -3.5298 | -4.6047 | 15.2949 | 14.2109 | 13.6928 | 13.3058 | 12.8261 | 12.3313 | 11.8664 | 11.4527 | 11.0388 | 10.6626 | 8.9329 | 6.5064 | 4.8303 | 3.4702 | 2.2712 | 8.2949 | 7.8976 | 7.6384 | 7.3914 | 7.0832 | 6.7964 | 6.4495 | 6.0307 | 5.6553 | 5.2709 | 4.1661 | 3.1498 | 2.2979 | 1.4678 | 0.92234 | 15.2949 | 14.8976 | 14.6384 | 14.3914 | 14.0832 | 13.7964 | 13.4495 | 13.0307 | 12.6553 | 12.2709 | 11.1661 | 10.1498 | 9.2979 | 8.4678 | 8.0085 | 8.2949 | 7.0126 | 6.3984 | 5.9483 | 5.4017 | 4.839 | 4.3164 | 3.8301 | 3.356 | 2.8921 | 0.92761 | -1.4757 | -2.9757 | -4.0442 | -4.5158 | 15.2949 | 14.0126 | 13.3984 | 12.9483 | 12.4017 | 11.839 | 11.3164 | 10.8301 | 10.356 | 9.8921 | 7.9276 | 5.5243 | 4.0243 | 2.9558 | 2.3652 | 8.2949 | 7.5587 | 7.1222 | 6.7667 | 6.279 | 5.7183 | 5.0958 | 4.2006 | 3.3067 | 2.4359 | -5.4311e-05 | -2.0698 | -3.2367 | -3.6492 | -3.1148 | 15.2949 | 14.5587 | 14.1222 | 13.7667 | 13.279 | 12.7183 | 12.0958 | 11.2006 | 10.3067 | 9.4359 | 6.9999 | 4.9302 | 3.7633 | 3.3508 | 3.7569 | 8.2949 | 7.6341 | 7.2637 | 6.9966 | 6.7013 | 6.3857 | 6.0664 | 5.7432 | 5.3555 | 4.9712 | 3.7623 | 2.5332 | 1.7157 | 0.94483 | 0.45853 | 15.2949 | 14.6341 | 14.2637 | 13.9966 | 13.7013 | 13.3857 | 13.0664 | 12.7432 | 12.3555 | 11.9712 | 10.7623 | 9.5332 | 8.7157 | 7.9448 | 7.5149 | 8.2949 | 7.0675 | 6.4318 | 5.9463 | 5.3486 | 4.7378 | 4.0587 | 3.0592 | 2.0773 | 1.1221 | -1.5377 | -3.738 | -5.0238 | -5.5653 | -5.224 | 15.2949 | 14.0675 | 13.4318 | 12.9463 | 12.3486 | 11.7378 | 11.0587 | 10.0592 | 9.0773 | 8.1221 | 5.4623 | 3.262 | 1.9762 | 1.4347 | 1.6946 | 383306 | 392514 | WEST DIDSBURY | SOUTH MANCHESTER
| Westgate | 3.0704 | 2.6946 | 2.4458 | 2.2069 | 1.8348 | 1.4372 | 1.0629 | 0.70165 | 0.2956 | -0.084015 | -2.9662 | -7.4688 | -11.2094 | -15.0951 | -18.4384 | 6.5704 | 6.1946 | 5.9458 | 5.7069 | 5.3348 | 4.9372 | 4.5629 | 4.2016 | 3.7956 | 3.416 | 0.53381 | -3.9688 | -7.7094 | -11.5951 | -15.1681 | 3.0704 | 2.7551 | 2.4798 | 2.1905 | 1.8146 | 1.4351 | 0.96627 | 0.39933 | 0.012587 | -0.38485 | -1.6358 | -2.9906 | -4.6358 | -6.3418 | -7.4034 | 6.5704 | 6.2551 | 5.9798 | 5.6905 | 5.3146 | 4.9351 | 4.4663 | 3.8993 | 3.5126 | 3.1152 | 1.8642 | 0.50938 | -1.1358 | -2.8418 | -3.762 | 3.0704 | 2.7008 | 2.4812 | 2.3056 | 1.998 | 1.6787 | 1.4139 | 1.1752 | 0.91451 | 0.65443 | -1.9331 | -7.1023 | -11.1968 | -14.8423 | -17.4129 | 6.5704 | 6.2008 | 5.9812 | 5.8056 | 5.498 | 5.1787 | 4.9139 | 4.6752 | 4.4145 | 4.1544 | 1.5669 | -3.6023 | -7.6968 | -11.3423 | -13.9403 | 3.0704 | 3.0531 | 2.938 | 2.7844 | 2.4857 | 2.1251 | 1.5407 | 0.13677 | -1.3462 | -2.8325 | -7.1645 | -11.3266 | -14.5727 | -16.6037 | -15.3365 | 6.5704 | 6.5531 | 6.438 | 6.2844 | 5.9857 | 5.6251 | 5.0407 | 3.6368 | 2.1538 | 0.6675 | -3.6645 | -7.8266 | -11.0727 | -13.1037 | -12.1303 | 3.0704 | 2.7612 | 2.5699 | 2.4339 | 2.2534 | 2.0504 | 1.82 | 1.5427 | 1.1706 | 0.78793 | -0.66257 | -2.808 | -5.0362 | -7.0993 | -8.0835 | 6.5704 | 6.2612 | 6.0699 | 5.9339 | 5.7534 | 5.5504 | 5.32 | 5.0427 | 4.6706 | 4.2879 | 2.8374 | 0.69196 | -1.5362 | -3.5993 | -4.4973 | 3.0704 | 2.9042 | 2.6705 | 2.3979 | 1.9741 | 1.5413 | 0.87604 | -0.64059 | -2.1816 | -3.7311 | -8.3062 | -12.8036 | -16.4111 | -18.8632 | -18.0075 | 6.5704 | 6.4042 | 6.1705 | 5.8979 | 5.4741 | 5.0413 | 4.376 | 2.8594 | 1.3184 | -0.23112 | -4.8062 | -9.3036 | -12.9111 | -15.3632 | -14.7194 | 343077 | 463204 | LANCASTER | HEYSHAM
| Westhoughton | 4.9086 | 2.6988 | 1.7875 | 1.281 | 0.5956 | -0.11613 | -0.80344 | -1.4843 | -2.2502 | -3.0009 | -6.8701 | -11.9839 | -16.0536 | -20.3237 | -24.1242 | 9.5456 | 7.3358 | 6.4245 | 5.918 | 5.2326 | 4.5209 | 3.8336 | 3.1527 | 2.3868 | 1.6361 | -2.2331 | -7.3469 | -11.4166 | -15.6867 | -19.6889 | 4.9086 | 4.2465 | 4.0219 | 3.88 | 3.645 | 3.3661 | 2.9834 | 2.4775 | 2.0265 | 1.5538 | 0.077452 | -1.4906 | -2.9893 | -4.6907 | -5.7728 | 9.5456 | 8.8835 | 8.6589 | 8.517 | 8.282 | 8.0031 | 7.6204 | 7.1145 | 6.6635 | 6.1908 | 4.7145 | 3.1464 | 1.6477 | -0.053718 | -0.97229 | 4.9086 | 2.388 | 1.4485 | 1.0079 | 0.39754 | -0.22326 | -0.77941 | -1.316 | -1.93 | -2.5464 | -6.0493 | -10.9156 | -14.7859 | -18.7992 | -22.291 | 9.5456 | 7.025 | 6.0855 | 5.6449 | 5.0345 | 4.4137 | 3.8576 | 3.321 | 2.707 | 2.0906 | -1.4123 | -6.2786 | -10.1489 | -14.1622 | -17.9125 | 4.9086 | 3.5449 | 2.8823 | 2.504 | 1.9064 | 1.2512 | 0.35921 | -1.4342 | -3.3165 | -5.208 | -10.7647 | -15.3477 | -18.8627 | -21.1701 | -19.9792 | 9.5456 | 8.1819 | 7.5193 | 7.141 | 6.5434 | 5.8882 | 4.9962 | 3.2028 | 1.3205 | -0.57095 | -6.1277 | -10.7107 | -14.2257 | -16.5331 | -15.6103 | 4.9086 | 3.798 | 3.1733 | 2.7949 | 2.3536 | 1.8462 | 1.2769 | 0.66509 | -0.080381 | -0.8424 | -3.3677 | -5.2568 | -6.4027 | -7.5704 | -8.2126 | 9.5456 | 8.435 | 7.8103 | 7.4319 | 6.9906 | 6.4832 | 5.9139 | 5.3021 | 4.5566 | 3.7946 | 1.2693 | -0.61983 | -1.7657 | -2.9334 | -3.5278 | 4.9086 | 2.431 | 1.4306 | 0.90582 | 0.17794 | -0.55798 | -1.5489 | -3.4797 | -5.4628 | -7.4559 | -13.3646 | -18.2958 | -22.1563 | -24.8566 | -24.0838 | 9.5456 | 7.068 | 6.0676 | 5.5428 | 4.8149 | 4.079 | 3.0881 | 1.1573 | -0.82585 | -2.8189 | -8.7276 | -13.6588 | -17.5193 | -20.2196 | -19.6232 | 365831 | 407025 | WESTHOUGHTON | KEARSLEY
| Westlinton | 7.7245 | 5.4642 | 4.9665 | 4.8399 | 4.637 | 4.3641 | 3.9008 | 3.0574 | 2.0202 | 0.84722 | -3.1253 | -6.6539 | -8.8573 | -10.2583 | -11.1434 | 10.2245 | 7.9642 | 7.4665 | 7.3399 | 7.137 | 6.8641 | 6.4008 | 5.5574 | 4.5202 | 3.3472 | -0.62527 | -4.1539 | -6.3573 | -7.7583 | -8.6455 | 7.7245 | 7.2408 | 7.0481 | 6.893 | 6.7047 | 6.5178 | 6.2747 | 5.9633 | 5.6938 | 5.2374 | 3.2481 | 0.60381 | -2.273 | -5.5094 | -7.6951 | 10.2245 | 9.7408 | 9.5481 | 9.393 | 9.2047 | 9.0178 | 8.7747 | 8.4633 | 8.1938 | 7.7374 | 5.7481 | 3.1038 | 0.22701 | -3.0094 | -4.9062 | 7.7245 | 5.1001 | 4.5427 | 4.4256 | 4.2416 | 4.001 | 3.7099 | 3.1101 | 2.2925 | 1.3286 | -2.4742 | -6.4472 | -9.1432 | -10.7953 | -11.6302 | 10.2245 | 7.6001 | 7.0427 | 6.9256 | 6.7416 | 6.501 | 6.2099 | 5.6101 | 4.7925 | 3.8286 | 0.025807 | -3.9472 | -6.6432 | -8.2953 | -9.1474 | 7.7245 | 5.922 | 5.515 | 5.3664 | 5.1694 | 4.8957 | 4.4024 | 3.4176 | 2.2197 | 0.87546 | -3.351 | -6.7825 | -8.8251 | -9.8499 | -9.8801 | 10.2245 | 8.422 | 8.015 | 7.8664 | 7.6694 | 7.3957 | 6.9024 | 5.9176 | 4.7197 | 3.3755 | -0.85102 | -4.2825 | -6.3251 | -7.3499 | -7.4072 | 7.7245 | 6.839 | 6.5894 | 6.4848 | 6.3493 | 6.1744 | 5.8472 | 5.2209 | 4.4229 | 3.4872 | 0.018094 | -3.3864 | -5.6133 | -7.0182 | -7.5517 | 10.2245 | 9.339 | 9.0894 | 8.9848 | 8.8493 | 8.6744 | 8.3472 | 7.7209 | 6.9229 | 5.9872 | 2.5181 | -0.8864 | -3.1133 | -4.5182 | -5.037 | 7.7245 | 4.8049 | 4.1779 | 4.0004 | 3.7876 | 3.5302 | 3.1828 | 2.4537 | 1.4406 | 0.27031 | -3.8798 | -7.8335 | -10.4511 | -11.8375 | -11.9764 | 10.2245 | 7.3049 | 6.6779 | 6.5004 | 6.2876 | 6.0302 | 5.6828 | 4.9537 | 3.9406 | 2.7703 | -1.3798 | -5.3335 | -7.9511 | -9.3375 | -9.4861 | 339551 | 564489 | CARLISLE | HARKER
| Whalley | 10.8081 | 10.0426 | 9.7029 | 9.4747 | 9.1549 | 8.8325 | 8.5403 | 8.2535 | 7.9194 | 7.6147 | 6.0499 | 3.5764 | 1.6305 | -0.3258 | -2.1098 | 15.4451 | 14.6796 | 14.3399 | 14.1117 | 13.7919 | 13.4695 | 13.1773 | 12.8905 | 12.5564 | 12.2517 | 10.6869 | 8.2134 | 6.2675 | 4.3112 | 2.4723 | 10.8081 | 10.4334 | 10.1961 | 9.9824 | 9.7207 | 9.4544 | 9.0999 | 8.6007 | 8.1963 | 7.7946 | 6.6049 | 5.4015 | 4.2885 | 3.0264 | 2.1481 | 15.4451 | 15.0704 | 14.8331 | 14.6194 | 14.3577 | 14.0914 | 13.7369 | 13.2377 | 12.8333 | 12.4316 | 11.2419 | 10.0385 | 8.9255 | 7.6634 | 6.9361 | 10.8081 | 9.9701 | 9.6384 | 9.3898 | 9.0516 | 8.7186 | 8.4999 | 8.2924 | 8.0551 | 7.8307 | 6.5057 | 4.2268 | 2.4501 | 0.70035 | -0.84613 | 15.4451 | 14.6071 | 14.2754 | 14.0268 | 13.6886 | 13.3556 | 13.1369 | 12.9294 | 12.6921 | 12.4677 | 11.1427 | 8.8638 | 7.0871 | 5.3373 | 3.6906 | 10.8081 | 10.4334 | 10.223 | 10.0134 | 9.7101 | 9.3917 | 9.0537 | 8.3333 | 7.5723 | 6.8172 | 4.6415 | 2.4882 | 0.89013 | -0.1277 | 0.33781 | 15.4451 | 15.0704 | 14.86 | 14.6504 | 14.3471 | 14.0287 | 13.6907 | 12.9703 | 12.2093 | 11.4542 | 9.2785 | 7.1252 | 5.5271 | 4.5093 | 4.8641 | 10.8081 | 10.2824 | 10.0112 | 9.8342 | 9.6304 | 9.4153 | 9.1759 | 8.8933 | 8.5158 | 8.1456 | 6.9381 | 5.5882 | 4.6691 | 3.7954 | 3.306 | 15.4451 | 14.9194 | 14.6482 | 14.4712 | 14.2674 | 14.0523 | 13.8129 | 13.5303 | 13.1528 | 12.7826 | 11.5751 | 10.2252 | 9.3061 | 8.4324 | 7.982 | 10.8081 | 10.0866 | 9.7411 | 9.4354 | 9.0442 | 8.6647 | 8.2522 | 7.4314 | 6.6044 | 5.7835 | 3.4011 | 1.0692 | -0.70793 | -1.932 | -1.6781 | 15.4451 | 14.7236 | 14.3781 | 14.0724 | 13.6812 | 13.3017 | 12.8892 | 12.0684 | 11.2414 | 10.4205 | 8.0381 | 5.7062 | 3.9291 | 2.705 | 2.895 | 373376 | 436176 | PADIHAM | PADIHAM
| Whalley Range | 5.8106 | 5.1725 | 4.6874 | 4.2316 | 3.6627 | 4.0715 | 3.5173 | 3.0174 | 2.5101 | 2.025 | -0.55233 | -4.3899 | -7.1317 | -9.5768 | -11.2039 | 14.9476 | 14.3095 | 13.8244 | 13.3686 | 12.7997 | 13.2115 | 12.6573 | 12.1574 | 11.6501 | 11.165 | 8.5877 | 4.7501 | 2.0083 | -0.43682 | -2.3473 | 5.8106 | 5.481 | 5.1651 | 4.8165 | 4.3767 | 4.9683 | 4.4677 | 3.8563 | 3.4318 | 2.9931 | 1.7121 | 0.49606 | -0.56862 | -1.6592 | -2.4105 | 14.9476 | 14.618 | 14.3021 | 13.9535 | 13.5137 | 14.1083 | 13.6077 | 12.9963 | 12.5718 | 12.1331 | 10.8521 | 9.6361 | 8.5714 | 7.4808 | 6.8501 | 5.8106 | 5.0111 | 4.3912 | 3.8111 | 3.1091 | 3.3787 | 2.697 | 1.9858 | 1.3037 | 0.62853 | -2.4631 | -6.3376 | -8.8134 | -10.6936 | -11.299 | 14.9476 | 14.1481 | 13.5282 | 12.9481 | 12.2461 | 12.5187 | 11.837 | 11.1258 | 10.4437 | 9.7685 | 6.6769 | 2.8024 | 0.32658 | -1.5536 | -2.4103 | 5.8106 | 5.503 | 5.0534 | 4.5748 | 3.9333 | 4.2126 | 3.3258 | 1.8217 | 0.34989 | -1.0669 | -4.9811 | -8.2316 | -10.1071 | -10.7947 | -9.6466 | 14.9476 | 14.64 | 14.1904 | 13.7118 | 13.0703 | 13.3526 | 12.4658 | 10.9617 | 9.4899 | 8.0731 | 4.1589 | 0.90843 | -0.96713 | -1.6547 | -0.76969 | 5.8106 | 5.3833 | 5.0036 | 4.6645 | 4.2772 | 4.883 | 4.4876 | 4.0671 | 3.5796 | 3.0538 | 1.3583 | -0.34846 | -1.4988 | -2.5851 | -3.1853 | 14.9476 | 14.5203 | 14.1406 | 13.8015 | 13.4142 | 14.023 | 13.6276 | 13.2071 | 12.7196 | 12.1938 | 10.4983 | 8.7915 | 7.6412 | 6.5549 | 6.01 | 5.8106 | 5.2704 | 4.6499 | 4.0089 | 3.2229 | 3.4136 | 2.4205 | 0.76032 | -0.8224 | -2.3492 | -6.5823 | -10.0172 | -12.0738 | -13.0111 | -12.2193 | 14.9476 | 14.4074 | 13.7869 | 13.1459 | 12.3599 | 12.5536 | 11.5605 | 9.9003 | 8.3176 | 6.7908 | 2.5577 | -0.87717 | -2.9338 | -3.8711 | -3.2587 | 382923 | 394645 | WEST DIDSBURY | SOUTH MANCHESTER
| Whasset | 3.2936 | 2.461 | 2.1878 | 2.0971 | -0.75386 | -0.72888 | -2.9526 | -2.8002 | -2.8975 | -2.9878 | -3.883 | -5.3901 | -6.4578 | -7.2307 | -8.0883 | 7.2936 | 6.461 | 6.1878 | 6.0971 | 3.2461 | 3.2711 | 1.0474 | 1.1998 | 1.1025 | 1.0122 | 0.11701 | -1.3901 | -2.4578 | -3.2307 | -4.2431 | 3.2936 | 2.9072 | 2.6735 | 2.524 | 2.3779 | 2.2308 | 2.0451 | 1.8186 | 1.6148 | 1.411 | 0.79388 | 0.1841 | -0.39767 | -1.0736 | -1.5976 | 7.2936 | 6.9072 | 6.6735 | 6.524 | 6.3779 | 6.2308 | 6.0451 | 5.8186 | 5.6148 | 5.411 | 4.7939 | 4.1841 | 3.6023 | 2.9264 | 2.4805 | 3.2936 | 2.3375 | 2.0518 | 1.9749 | -0.74265 | -0.708 | -2.7954 | -2.6065 | -2.6235 | -2.6298 | -5.2149 | -6.5449 | -7.3879 | -7.7853 | -8.2505 | 7.2936 | 6.3375 | 6.0518 | 5.9749 | 3.2574 | 3.292 | 1.2046 | 1.3935 | 1.3765 | 1.3702 | -1.2149 | -2.5449 | -3.3879 | -3.7853 | -4.4805 | 3.2936 | 2.7344 | 2.5361 | -0.09047 | -2.5877 | -2.3865 | -2.291 | -2.4546 | -3.0101 | -3.3986 | -5.0073 | -6.1659 | -6.9024 | -6.9273 | -5.943 | 7.2936 | 6.7344 | 6.5361 | 3.9095 | 1.4123 | 1.6135 | 1.709 | 1.5454 | 0.98994 | 0.60141 | -1.0073 | -2.1659 | -2.9024 | -2.9273 | -2.16 | 3.2936 | 2.6611 | 2.4333 | 2.3642 | -0.4144 | -0.30653 | -2.4804 | -2.3214 | -2.4388 | -2.5675 | -3.2206 | -3.9845 | -4.3569 | -4.4327 | -4.3757 | 7.2936 | 6.6611 | 6.4333 | 6.3642 | 3.5856 | 3.6935 | 1.5196 | 1.6786 | 1.5612 | 1.4325 | 0.77937 | 0.015489 | -0.35689 | -0.43271 | -0.47649 | 3.2936 | 2.3146 | 2.0005 | -0.68184 | -3.2314 | -3.055 | -2.9911 | -3.205 | -3.7814 | -4.1898 | -5.8724 | -7.1251 | -7.9591 | -8.0892 | -7.2171 | 7.2936 | 6.3146 | 6.0005 | 3.3182 | 0.76862 | 0.94503 | 1.0089 | 0.79499 | 0.21856 | -0.18983 | -1.8724 | -3.1251 | -3.9591 | -4.0892 | -3.4088 | 350648 | 481468 | KENDAL (PARKSIDE RD) | HUTTON | Firm Capacity marginally exceeded in FY28. HV load transfer to Arnside primary.
| Whittle Le Woods | 7.535 | 6.9296 | 6.6557 | 6.445 | 6.1323 | 5.8152 | 5.5264 | 5.2601 | 4.9635 | 4.6775 | 2.988 | 0.16586 | -2.1142 | -4.4847 | -6.7236 | 11.035 | 10.4296 | 10.1557 | 9.945 | 9.6323 | 9.3152 | 9.0264 | 8.7601 | 8.4635 | 8.1775 | 6.488 | 3.6659 | 1.3858 | -0.98466 | -3.2775 | 7.535 | 7.3389 | 7.187 | 7.0294 | 6.8235 | 6.6057 | 6.3117 | 5.8902 | 5.5286 | 5.1666 | 4.0273 | 2.846 | 1.7535 | 0.55873 | -0.22791 | 11.035 | 10.8389 | 10.687 | 10.5294 | 10.3235 | 10.1057 | 9.8117 | 9.3902 | 9.0286 | 8.6666 | 7.5273 | 6.346 | 5.2535 | 4.0587 | 3.4069 | 7.535 | 6.8764 | 6.6136 | 6.44 | 6.168 | 5.8984 | 5.6766 | 5.4826 | 5.2637 | 5.0613 | 3.5416 | 0.88747 | -1.2131 | -3.337 | -5.4259 | 11.035 | 10.3764 | 10.1136 | 9.94 | 9.668 | 9.3984 | 9.1766 | 8.9826 | 8.7637 | 8.5613 | 7.0416 | 4.3875 | 2.2869 | 0.16303 | -2.0157 | 7.535 | 7.271 | 7.1144 | 6.9798 | 6.722 | 6.4408 | 6.0551 | 5.2232 | 4.3527 | 3.4914 | 0.98889 | -1.5158 | -3.4809 | -4.8093 | -4.4029 | 11.035 | 10.771 | 10.6144 | 10.4798 | 10.222 | 9.9408 | 9.5551 | 8.7232 | 7.8527 | 6.9914 | 4.4889 | 1.9842 | 0.019053 | -1.3093 | -0.99993 | 7.535 | 7.319 | 7.1478 | 7.0099 | 6.8419 | 6.6483 | 6.4388 | 6.2207 | 5.9248 | 5.6373 | 4.6227 | 3.3413 | 2.4257 | 1.5736 | 1.011 | 11.035 | 10.819 | 10.6478 | 10.5099 | 10.3419 | 10.1483 | 9.9388 | 9.7207 | 9.4248 | 9.1373 | 8.1227 | 6.8413 | 5.9257 | 5.0736 | 4.5758 | 7.535 | 7.0016 | 6.7288 | 6.5049 | 6.1664 | 5.8317 | 5.3801 | 4.4562 | 3.5176 | 2.5889 | -0.13467 | -2.8241 | -4.9476 | -6.4543 | -6.2598 | 11.035 | 10.5016 | 10.2288 | 10.0049 | 9.6664 | 9.3317 | 8.8801 | 7.9562 | 7.0176 | 6.0889 | 3.3653 | 0.67593 | -1.4476 | -2.9543 | -2.8111 | 357874 | 421203 | LEYLAND | PENWORTHAM
| Whitworth | 5.0725 | 5.0164 | 4.9411 | 4.866 | 4.7741 | 4.6826 | 4.6014 | 4.5234 | 4.4232 | 4.326 | 3.7361 | 2.8215 | 2.0988 | 1.3606 | 0.76411 | 6.5725 | 6.5164 | 6.4411 | 6.366 | 6.2741 | 6.1826 | 6.1014 | 6.0234 | 5.9232 | 5.826 | 5.2361 | 4.3215 | 3.5988 | 2.8606 | 2.2397 | 5.0725 | 5.0246 | 4.9696 | 4.9107 | 4.8363 | 4.7521 | 4.6476 | 4.5105 | 4.3825 | 4.253 | 3.8544 | 3.4385 | 3.0667 | 2.6856 | 2.4488 | 6.5725 | 6.5246 | 6.4696 | 6.4107 | 6.3363 | 6.2521 | 6.1476 | 6.0105 | 5.8825 | 5.753 | 5.3544 | 4.9385 | 4.5667 | 4.1856 | 3.9881 | 5.0725 | 5.0229 | 4.9575 | 4.8992 | 4.8258 | 4.7562 | 4.7035 | 4.631 | 4.5494 | 4.4706 | 3.634 | 2.6174 | 1.8429 | 1.1162 | 0.55941 | 6.5725 | 6.5229 | 6.4575 | 6.3992 | 6.3258 | 6.2562 | 6.2035 | 6.131 | 6.0494 | 5.9706 | 5.134 | 4.1174 | 3.3429 | 2.6162 | 2.0688 | 5.0725 | 5.0834 | 5.0447 | 4.9998 | 4.9306 | 4.8517 | 4.7382 | 4.4833 | 4.2095 | 3.9388 | 3.1633 | 2.4056 | 1.7692 | 1.1994 | 1.1298 | 6.5725 | 6.5834 | 6.5447 | 6.4998 | 6.4306 | 6.3517 | 6.2382 | 5.9833 | 5.7095 | 5.4388 | 4.6633 | 3.9056 | 3.2692 | 2.6994 | 2.629 | 5.0725 | 5.0288 | 4.9718 | 4.9238 | 4.8713 | 4.8067 | 4.7389 | 4.671 | 4.5719 | 4.4744 | 4.1132 | 3.6432 | 3.1784 | 2.7418 | 2.4827 | 6.5725 | 6.5288 | 6.4718 | 6.4238 | 6.3713 | 6.3067 | 6.2389 | 6.171 | 6.0719 | 5.9744 | 5.6132 | 5.1432 | 4.6784 | 4.2418 | 4.015 | 5.0725 | 5.0576 | 4.986 | 4.9041 | 4.8012 | 4.7001 | 4.5609 | 4.2666 | 3.9609 | 3.6592 | 2.7953 | 1.9621 | 1.2519 | 0.74586 | 0.81612 | 6.5725 | 6.5576 | 6.486 | 6.4041 | 6.3012 | 6.2001 | 6.0609 | 5.7666 | 5.4609 | 5.1592 | 4.2953 | 3.4621 | 2.7519 | 2.2459 | 2.2972 | 388779 | 419157 | ROCHDALE CENTRAL | ROCHDALE
| Wigton | 3.5153 | 3.1203 | 2.7605 | 2.5164 | 2.2105 | 11.0336 | 10.6229 | 7.7911 | 7.219 | 6.6454 | 4.8241 | 3.1584 | 0.21281 | -1.21 | -2.2946 | 3.5153 | 3.1203 | 2.7605 | 2.5164 | 2.2105 | 11.0336 | 10.6229 | 7.7911 | 7.219 | 6.6454 | 4.8241 | 3.1584 | 0.21281 | -1.21 | -2.4762 | 3.5153 | 3.2465 | 2.8819 | 2.5761 | 2.2841 | 11.1839 | 10.7065 | 10.1005 | 9.7014 | 9.1495 | 7.3515 | 5.5595 | 4.0828 | 2.81 | 2.1999 | 3.5153 | 3.2465 | 2.8819 | 2.5761 | 2.2841 | 11.1839 | 10.7065 | 10.1005 | 9.7014 | 9.1495 | 7.3515 | 5.5595 | 4.0828 | 2.81 | 2.2597 | 3.5153 | 3.1156 | 2.7762 | 2.5898 | 2.3331 | 11.212 | 10.9397 | 8.3049 | 7.9019 | 7.4817 | 5.914 | 3.5624 | 0.23311 | -1.4407 | -2.4375 | 3.5153 | 3.1156 | 2.7762 | 2.5898 | 2.3331 | 11.212 | 10.9397 | 8.3049 | 7.9019 | 7.4817 | 5.914 | 3.5624 | 0.23311 | -1.4407 | -2.5131 | 3.5153 | 3.2849 | 2.987 | 2.7023 | 2.4271 | 8.8303 | 8.6129 | 6.8874 | 6.2487 | 5.5621 | 3.3445 | 1.3045 | -0.096345 | -1.18 | -0.86884 | 3.5153 | 3.2849 | 2.987 | 2.7023 | 2.4271 | 8.8303 | 8.6129 | 6.8874 | 6.2487 | 5.5621 | 3.3445 | 1.3045 | -0.096345 | -1.18 | -0.98162 | 3.5153 | 3.2186 | 2.8764 | 2.6418 | 2.4468 | 11.4446 | 11.2826 | 8.5598 | 8.1085 | 7.6251 | 5.8926 | 4.1325 | 1.9398 | 0.97375 | 0.28498 | 3.5153 | 3.2186 | 2.8764 | 2.6418 | 2.4468 | 11.4446 | 11.2826 | 8.5598 | 8.1085 | 7.6251 | 5.8926 | 4.1325 | 1.9398 | 0.97375 | 0.2823 | 3.5153 | 3.1059 | 2.7079 | 2.3336 | 1.9738 | 8.3126 | 8.0259 | 6.2037 | 5.5154 | 4.7852 | 2.377 | 0.12696 | -1.4208 | -2.079 | -1.4309 | 3.5153 | 3.1059 | 2.7079 | 2.3336 | 1.9738 | 8.3126 | 8.0259 | 6.2037 | 5.5154 | 4.7852 | 2.377 | 0.12696 | -1.4208 | -2.079 | -1.5962 | 325814 | 549933 | CARLISLE | HARKER
| Willow Hey | 13.1722 | 12.2091 | 11.6048 | 11.3054 | 11.062 | 10.7931 | 10.5149 | 10.2256 | 9.91 | 9.602 | 8.2132 | 6.3801 | 5.0381 | 3.9012 | 3.1333 | 17.8092 | 16.8461 | 16.2418 | 15.9424 | 15.699 | 15.4301 | 15.1519 | 14.8626 | 14.547 | 14.239 | 12.8502 | 11.0171 | 9.6751 | 8.5382 | 7.6655 | 13.1722 | 12.9914 | 12.7603 | 12.601 | 12.4676 | 12.3118 | 12.1152 | 11.8834 | 11.7033 | 11.5151 | 10.9261 | 10.3191 | 9.6956 | 9.0073 | 8.5191 | 17.8092 | 17.6284 | 17.3973 | 17.238 | 17.1046 | 16.9488 | 16.7522 | 16.5204 | 16.3403 | 16.1521 | 15.5631 | 14.9561 | 14.3326 | 13.6443 | 13.2205 | 13.1722 | 12.0227 | 11.2689 | 10.7836 | 10.3795 | 9.9481 | 9.5804 | 9.1977 | 8.8113 | 8.4261 | 6.7862 | 4.8893 | 3.6381 | 2.7521 | 2.4987 | 17.8092 | 16.6597 | 15.9059 | 15.4206 | 15.0165 | 14.5851 | 14.2174 | 13.8347 | 13.4483 | 13.0631 | 11.4232 | 9.5263 | 8.2751 | 7.3891 | 7.0225 | 13.1722 | 12.4784 | 11.8291 | 11.3756 | 10.9974 | 10.5621 | 10.1018 | 9.3941 | 8.6804 | 7.9839 | 5.9985 | 4.3812 | 3.4185 | 3.0604 | 3.5585 | 17.8092 | 17.1154 | 16.4661 | 16.0126 | 15.6344 | 15.1991 | 14.7388 | 14.0311 | 13.3174 | 12.6209 | 10.6355 | 9.0182 | 8.0555 | 7.6974 | 8.0737 | 13.1722 | 12.8898 | 12.4422 | 12.2074 | 12.0808 | 11.9056 | 11.6877 | 11.4437 | 11.1547 | 10.8565 | 9.8699 | 8.8879 | 8.2185 | 7.6497 | 7.4013 | 17.8092 | 17.5268 | 17.0792 | 16.8444 | 16.7178 | 16.5426 | 16.3247 | 16.0807 | 15.7917 | 15.4935 | 14.5069 | 13.5249 | 12.8555 | 12.2867 | 12.0474 | 13.1722 | 12.0152 | 11.2396 | 10.7246 | 10.2932 | 9.8428 | 9.3784 | 8.6374 | 7.901 | 7.1848 | 5.1335 | 3.4488 | 2.412 | 1.9919 | 2.4006 | 17.8092 | 16.6522 | 15.8766 | 15.3616 | 14.9302 | 14.4798 | 14.0154 | 13.2744 | 12.538 | 11.8218 | 9.7705 | 8.0858 | 7.049 | 6.6289 | 6.9393 | 347779 | 406066 | SKELMERSDALE | WASHWAY FARM
| Willowbank | 4.8532 | 4.203 | 3.8104 | 3.4086 | 2.9754 | 2.5193 | 2.0519 | 1.5571 | 1.0231 | 0.64439 | -1.0351 | -3.2525 | -4.9148 | -6.6833 | -7.9471 | 8.3532 | 7.703 | 7.3104 | 6.9086 | 6.4754 | 6.0193 | 5.5519 | 5.0571 | 4.5231 | 4.1444 | 2.4649 | 0.24753 | -1.4148 | -3.1833 | -4.5271 | 4.8532 | 4.5086 | 4.4272 | 4.291 | 4.0623 | 3.765 | 3.4099 | 2.9938 | 2.7747 | 2.5494 | 1.8464 | 1.1299 | 0.12039 | -1.2182 | -2.2285 | 8.3532 | 8.0086 | 7.9272 | 7.791 | 7.5623 | 7.265 | 6.9099 | 6.4938 | 6.2747 | 6.0494 | 5.3464 | 4.6299 | 3.6204 | 2.2818 | 1.43 | 4.8532 | 4.0795 | 3.6122 | 3.1392 | 2.6325 | 2.0722 | 1.4978 | 0.90074 | 0.30521 | -0.1394 | -2.0368 | -4.2759 | -5.7836 | -6.9426 | -7.4322 | 8.3532 | 7.5795 | 7.1122 | 6.6392 | 6.1325 | 5.5722 | 4.9978 | 4.4007 | 3.8052 | 3.3606 | 1.4632 | -0.77588 | -2.2836 | -3.4426 | -3.9907 | 4.8532 | 4.3772 | 3.9966 | 3.5581 | 3.0411 | 2.4746 | 1.7889 | 0.79476 | -0.18384 | -0.98618 | -3.2798 | -5.1972 | -6.3728 | -6.9181 | -6.5253 | 8.3532 | 7.8772 | 7.4966 | 7.0581 | 6.5411 | 5.9746 | 5.2889 | 4.2948 | 3.3162 | 2.5138 | 0.22021 | -1.6972 | -2.8728 | -3.4181 | -3.1248 | 4.8532 | 4.3663 | 4.0321 | 3.6812 | 3.3346 | 2.9509 | 2.5283 | 2.075 | 1.5671 | 1.1903 | -0.049848 | -1.2977 | -2.1729 | -2.9618 | -3.4496 | 8.3532 | 7.8663 | 7.5321 | 7.1812 | 6.8346 | 6.4509 | 6.0283 | 5.575 | 5.0671 | 4.6903 | 3.4502 | 2.2023 | 1.3271 | 0.53815 | 0.10605 | 4.8532 | 4.1658 | 3.7018 | 3.2136 | 2.6673 | 2.0906 | 1.4036 | 0.38766 | -0.60286 | -1.4159 | -3.7659 | -5.7679 | -7.3279 | -8.1562 | -7.9425 | 8.3532 | 7.6658 | 7.2018 | 6.7136 | 6.1673 | 5.5906 | 4.9036 | 3.8877 | 2.8971 | 2.0841 | -0.26587 | -2.2679 | -3.8279 | -4.6562 | -4.5001 | 391885 | 406064 | GREENHILL | WHITEGATE
| Willowholme | 9.9589 | 7.4528 | 7.1853 | 7.1176 | 6.9756 | 6.815 | 6.6671 | 6.521 | 6.3188 | 6.1384 | 4.359 | 1.5313 | -0.7472 | -3.0674 | -5.1172 | 14.0959 | 11.5898 | 11.3223 | 11.2546 | 11.1126 | 10.952 | 10.8041 | 10.658 | 10.4558 | 10.2754 | 8.496 | 5.6683 | 3.3898 | 1.0696 | -1.1583 | 9.9589 | 8.8847 | 8.8533 | 8.7599 | 8.6317 | 8.4835 | 8.2716 | 7.9885 | 7.7432 | 7.4952 | 6.6491 | 5.5747 | 4.6184 | 3.7093 | 3.2069 | 14.0959 | 13.0217 | 12.9903 | 12.8969 | 12.7687 | 12.6205 | 12.4086 | 12.1255 | 11.8802 | 11.6322 | 10.7861 | 9.7117 | 8.7554 | 7.8463 | 7.406 | 9.9589 | 7.1108 | 6.8022 | 6.7724 | 6.6683 | 6.5523 | 6.472 | 6.3947 | 6.2878 | 6.1833 | 4.7482 | 2.0313 | -0.15968 | -2.3566 | -4.1703 | 14.0959 | 11.2478 | 10.9392 | 10.9094 | 10.8053 | 10.6893 | 10.609 | 10.5317 | 10.4248 | 10.3203 | 8.8852 | 6.1683 | 3.9773 | 1.7804 | -0.25128 | 9.9589 | 8.1394 | 8.034 | 8.019 | 7.9085 | 7.7646 | 7.4735 | 6.6375 | 5.7587 | 4.8776 | 2.3358 | -0.1424 | -2.1408 | -3.3672 | -2.3732 | 14.0959 | 12.2764 | 12.171 | 12.156 | 12.0455 | 11.9016 | 11.6105 | 10.7745 | 9.8957 | 9.0146 | 6.4728 | 3.9946 | 1.9962 | 0.76982 | 1.5395 | 9.9589 | 8.1655 | 8.0539 | 8.0495 | 8.0285 | 7.9754 | 7.8919 | 7.7862 | 7.5938 | 7.4031 | 6.4911 | 5.3401 | 4.5768 | 3.9598 | 3.8183 | 14.0959 | 12.3025 | 12.1909 | 12.1865 | 12.1655 | 12.1124 | 12.0289 | 11.9232 | 11.7308 | 11.5401 | 10.6281 | 9.4771 | 8.7138 | 8.0968 | 7.9114 | 9.9589 | 6.997 | 6.6319 | 6.5378 | 6.3561 | 6.1686 | 5.8233 | 4.913 | 3.9842 | 3.0504 | 0.32637 | -2.3042 | -4.4732 | -5.902 | -5.1294 | 14.0959 | 11.134 | 10.7689 | 10.6748 | 10.4931 | 10.3056 | 9.9603 | 9.05 | 8.1212 | 7.1874 | 4.4634 | 1.8328 | -0.33622 | -1.765 | -1.1686 | 338653 | 556688 | CARLISLE | HARKER
| Wilmslow | 4.9089 | 4.6714 | 4.393 | 4.0319 | 3.6978 | 3.3554 | 3.0146 | 2.6753 | 2.3059 | 1.9557 | 0.42025 | -1.7093 | -3.3786 | -5.2229 | -6.8431 | 8.4089 | 8.1714 | 7.893 | 7.5319 | 7.1978 | 6.8554 | 6.5146 | 6.1753 | 5.8059 | 5.4557 | 3.9203 | 1.7907 | 0.1214 | -1.7229 | -3.436 | 4.9089 | 4.759 | 4.5566 | 4.3878 | 4.2176 | 4.0022 | 3.7282 | 3.3827 | 3.1588 | 2.9378 | 2.2897 | 1.6389 | 1.013 | 0.29764 | -0.26229 | 8.4089 | 8.259 | 8.0566 | 7.8878 | 7.7176 | 7.5022 | 7.2282 | 6.8827 | 6.6588 | 6.4378 | 5.7897 | 5.1389 | 4.513 | 3.7976 | 3.3316 | 4.9089 | 4.6484 | 4.3656 | 4.0023 | 3.6675 | 3.3248 | 2.9811 | 2.6412 | 2.3036 | 1.99 | 0.57698 | -1.3575 | -2.6717 | -4.1884 | -5.564 | 8.4089 | 8.1484 | 7.8656 | 7.5023 | 7.1675 | 6.8248 | 6.4811 | 6.1412 | 5.8036 | 5.49 | 4.077 | 2.1425 | 0.8283 | -0.68838 | -2.2033 | 4.9089 | 4.872 | 4.6624 | 4.3293 | 4.0014 | 3.6525 | 3.2072 | 2.4663 | 1.6911 | 0.93393 | -1.2235 | -3.107 | -4.483 | -5.3707 | -4.7564 | 8.4089 | 8.372 | 8.1624 | 7.8293 | 7.5014 | 7.1525 | 6.7072 | 5.9663 | 5.1911 | 4.4339 | 2.2765 | 0.393 | -0.98304 | -1.8707 | -1.3991 | 4.9089 | 4.7834 | 4.5483 | 4.225 | 3.9514 | 3.6613 | 3.3561 | 3.045 | 2.683 | 2.3283 | 1.266 | 0.3634 | -0.064218 | -0.47988 | -0.68085 | 8.4089 | 8.2834 | 8.0483 | 7.725 | 7.4514 | 7.1613 | 6.8561 | 6.545 | 6.183 | 5.8283 | 4.766 | 3.8634 | 3.4358 | 3.0201 | 2.8154 | 4.9089 | 4.7732 | 4.5009 | 4.1188 | 3.758 | 3.3955 | 2.9371 | 2.158 | 1.3602 | 0.58259 | -1.8113 | -3.9474 | -5.423 | -6.4457 | -5.9949 | 8.4089 | 8.2732 | 8.0009 | 7.6188 | 7.258 | 6.8955 | 6.4371 | 5.658 | 4.8602 | 4.0826 | 1.6887 | -0.44738 | -1.923 | -2.9457 | -2.6014 | 384710 | 381286 | MOSS NOOK | SOUTH MANCHESTER
| Windermere | 8.6772 | 8.0241 | 7.6602 | 7.3485 | 6.968 | 6.5758 | 6.3582 | 6.1378 | 5.8872 | 5.6667 | 4.2961 | 1.958 | 0.010192 | -1.9827 | -4.0805 | 12.6772 | 12.0241 | 11.6602 | 11.3485 | 10.968 | 10.5758 | 10.3582 | 10.1378 | 9.8872 | 9.6667 | 8.2961 | 5.958 | 4.0102 | 2.0173 | -0.23018 | 8.6772 | 8.3024 | 8.1096 | 7.883 | 7.6312 | 7.3578 | 7.0115 | 6.5997 | 6.363 | 6.1296 | 5.4513 | 4.8098 | 4.2317 | 3.4801 | 2.7743 | 12.6772 | 12.3024 | 12.1096 | 11.883 | 11.6312 | 11.3578 | 11.0115 | 10.5997 | 10.363 | 10.1296 | 9.4513 | 8.8098 | 8.2317 | 7.4801 | 6.8814 | 8.6772 | 7.9464 | 7.569 | 7.2556 | 6.8746 | 6.482 | 6.2619 | 6.041 | 5.8287 | 5.6501 | 4.4133 | 2.2375 | 0.46632 | -1.2386 | -2.6332 | 12.6772 | 11.9464 | 11.569 | 11.2556 | 10.8746 | 10.482 | 10.2619 | 10.041 | 9.8287 | 9.6501 | 8.4133 | 6.2375 | 4.4663 | 2.7614 | 1.1729 | 8.6772 | 8.2989 | 8.0247 | 7.7359 | 7.3979 | 7.0272 | 6.6773 | 5.9133 | 5.1232 | 4.3578 | 2.1714 | 0.091793 | -1.5154 | -2.4355 | -1.6205 | 12.6772 | 12.2989 | 12.0247 | 11.7359 | 11.3979 | 11.0272 | 10.6773 | 9.9133 | 9.1232 | 8.3578 | 6.1714 | 4.0918 | 2.4846 | 1.5645 | 2.1821 | 8.6772 | 8.1843 | 7.8732 | 7.6092 | 7.3432 | 7.0621 | 6.892 | 6.6707 | 6.3839 | 6.0991 | 5.1343 | 4.0431 | 3.2719 | 2.5311 | 2.3256 | 12.6772 | 12.1843 | 11.8732 | 11.6092 | 11.3432 | 11.0621 | 10.892 | 10.6707 | 10.3839 | 10.0991 | 9.1343 | 8.0431 | 7.2719 | 6.5311 | 6.2782 | 8.6772 | 8.0224 | 7.6368 | 7.2643 | 6.8514 | 6.4426 | 6.0617 | 5.2296 | 4.3976 | 3.5944 | 1.3228 | -0.80138 | -2.8351 | -4.1428 | -3.4935 | 12.6772 | 12.0224 | 11.6368 | 11.2643 | 10.8514 | 10.4426 | 10.0617 | 9.2296 | 8.3976 | 7.5944 | 5.3228 | 3.1986 | 1.1649 | -0.14275 | 0.35299 | 341657 | 498418 | KENDAL (PARKSIDE RD) | HUTTON
| Winifred Rd | 4.5741 | 4.1015 | 3.7381 | 3.4165 | 3.0074 | 2.5909 | 2.2038 | 1.8475 | 1.4613 | 1.0929 | -0.97849 | -4.155 | -6.5441 | -8.7783 | -10.3775 | 8.0741 | 7.6015 | 7.2381 | 6.9165 | 6.5074 | 6.0909 | 5.7038 | 5.3475 | 4.9613 | 4.5929 | 2.5215 | -0.65504 | -3.0441 | -5.2783 | -7.0511 | 4.5741 | 4.3538 | 4.1171 | 3.883 | 3.6064 | 3.3309 | 2.9795 | 2.5168 | 2.1917 | 1.8387 | 0.76871 | -0.32474 | -1.3611 | -2.5106 | -3.3623 | 8.0741 | 7.8538 | 7.6171 | 7.383 | 7.1064 | 6.8309 | 6.4795 | 6.0168 | 5.6917 | 5.3387 | 4.2687 | 3.1753 | 2.1389 | 0.98936 | 0.28176 | 4.5741 | 3.9869 | 3.5255 | 3.1176 | 2.6132 | 2.0968 | 1.6163 | 1.1543 | 0.68714 | 0.20156 | -2.1725 | -5.2596 | -7.3562 | -9.0535 | -9.8309 | 8.0741 | 7.4869 | 7.0255 | 6.6176 | 6.1132 | 5.5968 | 5.1163 | 4.6543 | 4.1871 | 3.7016 | 1.3275 | -1.7596 | -3.8562 | -5.5535 | -6.4428 | 4.5741 | 4.2904 | 3.9295 | 3.5692 | 3.0903 | 2.5743 | 1.9154 | 0.74602 | -0.41312 | -1.5433 | -4.6797 | -7.2746 | -8.8267 | -9.4255 | -8.7085 | 8.0741 | 7.7904 | 7.4295 | 7.0692 | 6.5903 | 6.0743 | 5.4154 | 4.246 | 3.0869 | 1.9567 | -1.1797 | -3.7746 | -5.3267 | -5.9255 | -5.3314 | 4.5741 | 4.3012 | 4.0146 | 3.769 | 3.5051 | 3.2282 | 2.9387 | 2.6277 | 2.2345 | 1.8316 | 0.5169 | -0.87691 | -1.9693 | -3.0149 | -3.7085 | 8.0741 | 7.8012 | 7.5146 | 7.269 | 7.0051 | 6.7282 | 6.4387 | 6.1277 | 5.7345 | 5.3316 | 4.0169 | 2.6231 | 1.5307 | 0.48506 | -0.11879 | 4.5741 | 4.124 | 3.6544 | 3.1953 | 2.6258 | 2.0466 | 1.3131 | 0.040339 | -1.1845 | -2.3817 | -5.73 | -8.5132 | -10.2527 | -11.0834 | -10.5508 | 8.0741 | 7.624 | 7.1544 | 6.6953 | 6.1258 | 5.5466 | 4.8131 | 3.5403 | 2.3155 | 1.1183 | -2.23 | -5.0132 | -6.7527 | -7.5834 | -7.1388 | 389971 | 388470 | ADSWOOD | BREDBURY
| Withington | 3.2616 | 2.591 | 2.2146 | 1.906 | 1.4873 | 1.0206 | 0.58406 | 0.21016 | -0.13835 | -0.44946 | -2.3706 | -5.3836 | -7.5583 | -9.3989 | -10.5974 | 6.7616 | 6.091 | 5.7146 | 5.406 | 4.9873 | 4.5206 | 4.0841 | 3.7102 | 3.3616 | 3.0505 | 1.1294 | -1.8836 | -4.0583 | -5.8989 | -7.3773 | 3.2616 | 3.0301 | 2.7874 | 2.5302 | 2.21 | 1.9205 | 1.5636 | 1.1474 | 0.88476 | 0.61436 | -0.16766 | -0.89396 | -1.5542 | -2.2048 | -2.6567 | 6.7616 | 6.5301 | 6.2874 | 6.0302 | 5.71 | 5.4205 | 5.0636 | 4.6474 | 4.3848 | 4.1144 | 3.3323 | 2.606 | 1.9458 | 1.2952 | 0.90997 | 3.2616 | 2.4405 | 1.9621 | 1.5419 | 0.96739 | 0.37092 | -0.18408 | -0.6979 | -1.1623 | -1.6233 | -3.9309 | -6.8975 | -8.76 | -10.0156 | -10.1642 | 6.7616 | 5.9405 | 5.4621 | 5.0419 | 4.4674 | 3.8709 | 3.3159 | 2.8021 | 2.3377 | 1.8767 | -0.43089 | -3.3975 | -5.26 | -6.5156 | -6.9602 | 3.2616 | 2.8922 | 2.5576 | 2.2263 | 1.7 | 1.1058 | 0.38476 | -0.81363 | -1.9749 | -3.0964 | -6.1879 | -8.6444 | -9.99 | -10.2087 | -8.8239 | 6.7616 | 6.3922 | 6.0576 | 5.7263 | 5.2 | 4.6058 | 3.8848 | 2.6864 | 1.5251 | 0.40356 | -2.6879 | -5.1444 | -6.49 | -6.7087 | -5.6269 | 3.2616 | 2.9741 | 2.7245 | 2.5204 | 2.2882 | 2.0354 | 1.7541 | 1.4629 | 1.1319 | 0.80201 | -0.28516 | -1.3773 | -2.1084 | -2.7786 | -3.0697 | 6.7616 | 6.4741 | 6.2245 | 6.0204 | 5.7882 | 5.5354 | 5.2541 | 4.9629 | 4.6319 | 4.302 | 3.2148 | 2.1227 | 1.3916 | 0.72145 | 0.43171 | 3.2616 | 2.5947 | 2.1035 | 1.637 | 0.99427 | 0.33567 | -0.45828 | -1.7735 | -3.0159 | -4.2165 | -7.5271 | -10.1291 | -11.6229 | -12.0263 | -10.9039 | 6.7616 | 6.0947 | 5.6035 | 5.137 | 4.4943 | 3.8357 | 3.0417 | 1.7265 | 0.48413 | -0.71651 | -4.0271 | -6.6291 | -8.1229 | -8.5263 | -7.6454 | 384841 | 392774 | WEST DIDSBURY | SOUTH MANCHESTER
| Withyfold Drive | 18.0185 | 16.6267 | 16.1336 | 15.8849 | 15.5197 | 15.1307 | 14.7605 | 14.3946 | 13.9543 | 13.5515 | 11.2131 | 7.1562 | 4.0262 | 0.74317 | -2.1886 | 25.0185 | 23.6267 | 23.1336 | 22.8849 | 22.5197 | 22.1307 | 21.7605 | 21.3946 | 20.9543 | 20.5515 | 18.2131 | 14.1562 | 11.0262 | 7.7432 | 4.6875 | 18.0185 | 17.4594 | 17.1507 | 16.8896 | 16.5506 | 16.1849 | 15.7205 | 15.1267 | 14.6442 | 14.1438 | 12.6315 | 10.8945 | 9.4619 | 7.8968 | 5.9312 | 25.0185 | 24.4594 | 24.1507 | 23.8896 | 23.5506 | 23.1849 | 22.7205 | 22.1267 | 21.6442 | 21.1438 | 19.6315 | 17.8945 | 16.4619 | 14.8968 | 13.1065 | 18.0185 | 16.4635 | 15.9666 | 15.776 | 15.4823 | 15.1783 | 14.9176 | 14.6708 | 14.0651 | 13.6994 | 11.5346 | 7.2266 | 4.3268 | 1.3266 | -1.334 | 25.0185 | 23.4635 | 22.9666 | 22.776 | 22.4823 | 22.1783 | 21.9176 | 21.6708 | 21.0651 | 20.6994 | 18.5346 | 14.2266 | 11.3268 | 8.3266 | 5.4795 | 18.0185 | 17.248 | 16.9627 | 16.831 | 16.558 | 16.218 | 15.5083 | 14.3986 | 13.0048 | 10.9425 | 7.4746 | 4.0772 | 1.4201 | -0.33671 | 0.46854 | 25.0185 | 24.248 | 23.9627 | 23.831 | 23.558 | 23.218 | 22.5083 | 21.3986 | 20.0048 | 17.9425 | 14.4746 | 11.0772 | 8.4201 | 6.6633 | 7.2728 | 18.0185 | 17.1874 | 16.8687 | 16.7277 | 16.5474 | 16.3111 | 16.0337 | 15.74 | 15.3271 | 14.9199 | 13.5243 | 11.7311 | 10.6011 | 9.4743 | 8.8296 | 25.0185 | 24.1874 | 23.8687 | 23.7277 | 23.5474 | 23.3111 | 23.0337 | 22.74 | 22.3271 | 21.9199 | 20.5243 | 18.7311 | 17.6011 | 16.4743 | 15.8764 | 18.0185 | 16.5661 | 16.0302 | 15.7448 | 15.3293 | 14.9108 | 14.1076 | 12.8592 | 11.3695 | 9.212 | 5.4437 | 1.7869 | -1.1064 | -3.1162 | -2.613 | 25.0185 | 23.5661 | 23.0302 | 22.7448 | 22.3293 | 21.9108 | 21.1076 | 19.8592 | 18.3695 | 16.212 | 12.4437 | 8.7869 | 5.8936 | 3.8838 | 4.2569 | 392132 | 374352 | MACCLESFIELD | MACCLESFIELD
| Woodbine St | 6.3198 | 5.8403 | 5.5728 | 5.3734 | 5.0944 | 4.7932 | 4.5001 | 4.2214 | 3.8877 | 3.5689 | 1.8903 | -0.76561 | -2.8973 | -5.0743 | -7.1395 | 9.8198 | 9.3403 | 9.0728 | 8.8734 | 8.5944 | 8.2932 | 8.0001 | 7.7214 | 7.3877 | 7.0689 | 5.3903 | 2.7344 | 0.60266 | -1.5743 | -3.6631 | 6.3198 | 6.0737 | 5.8722 | 5.6976 | 5.4962 | 5.28 | 4.9986 | 4.6057 | 4.2418 | 3.8718 | 2.7295 | 1.4955 | 0.31124 | -1.0427 | -2.0471 | 9.8198 | 9.5737 | 9.3722 | 9.1976 | 8.9962 | 8.78 | 8.4986 | 8.1057 | 7.7418 | 7.3718 | 6.2295 | 4.9955 | 3.8112 | 2.4573 | 1.6265 | 6.3198 | 5.807 | 5.549 | 5.3849 | 5.1414 | 4.882 | 4.6308 | 4.348 | 4.059 | 3.7851 | 2.4265 | -0.015835 | -2.0085 | -3.9957 | -5.8204 | 9.8198 | 9.307 | 9.049 | 8.8849 | 8.6414 | 8.382 | 8.1308 | 7.848 | 7.559 | 7.2851 | 5.9265 | 3.4842 | 1.4915 | -0.49574 | -2.3895 | 6.3198 | 6.1306 | 5.9622 | 5.8297 | 5.5958 | 5.3267 | 4.9562 | 4.1967 | 3.3851 | 2.5662 | 0.17995 | -2.1776 | -3.9903 | -5.1756 | -4.8828 | 9.8198 | 9.6306 | 9.4622 | 9.3297 | 9.0958 | 8.8267 | 8.4562 | 7.6967 | 6.8851 | 6.0662 | 3.6799 | 1.3224 | -0.49034 | -1.6756 | -1.4596 | 6.3198 | 6.0262 | 5.822 | 5.6842 | 5.5301 | 5.3483 | 5.1485 | 4.9266 | 4.6009 | 4.272 | 3.1685 | 1.927 | 1.0715 | 0.2393 | -0.3594 | 9.8198 | 9.5262 | 9.322 | 9.1842 | 9.0301 | 8.8483 | 8.6485 | 8.4266 | 8.1009 | 7.772 | 6.6685 | 5.427 | 4.5715 | 3.7393 | 3.2136 | 6.3198 | 5.9308 | 5.6675 | 5.4638 | 5.1654 | 4.8529 | 4.4297 | 3.601 | 2.7459 | 1.8826 | -0.66314 | -3.182 | -5.1588 | -6.5346 | -6.451 | 9.8198 | 9.4308 | 9.1675 | 8.9638 | 8.6654 | 8.3529 | 7.9297 | 7.101 | 6.2459 | 5.3826 | 2.8369 | 0.31802 | -1.6588 | -3.0346 | -2.9818 | 390519 | 412388 | CASTLETON | ROCHDALE
| Woodfield Rd | 8.7668 | 8.0527 | 7.678 | 7.3824 | 6.884 | 6.2593 | 5.6414 | 4.8447 | 3.867 | 2.7899 | -1.4407 | -6.4948 | -10.0903 | -13.2324 | -15.5988 | 13.4038 | 12.6897 | 12.315 | 12.0194 | 11.521 | 10.8963 | 10.2784 | 9.4817 | 8.504 | 7.4269 | 3.1963 | -1.8578 | -5.4533 | -8.5954 | -11.0163 | 8.7668 | 8.4764 | 8.2524 | 8.0476 | 7.7917 | 7.4727 | 7.0555 | 6.5275 | 6.0399 | 5.4873 | 3.4039 | 0.79337 | -2.0538 | -5.4168 | -7.6663 | 13.4038 | 13.1134 | 12.8894 | 12.6846 | 12.4287 | 12.1097 | 11.6925 | 11.1645 | 10.6769 | 10.1243 | 8.0409 | 5.4304 | 2.5832 | -0.77983 | -2.7316 | 8.7668 | 7.9612 | 7.5765 | 7.296 | 6.8364 | 6.2714 | 5.7451 | 5.0831 | 4.299 | 3.4083 | -0.6053 | -5.8959 | -9.8726 | -13.1353 | -15.3021 | 13.4038 | 12.5982 | 12.2135 | 11.933 | 11.4734 | 10.9084 | 10.3821 | 9.7201 | 8.936 | 8.0453 | 4.0317 | -1.2589 | -5.2356 | -8.4983 | -10.7606 | 8.7668 | 8.4037 | 8.1397 | 7.8966 | 7.4458 | 6.8289 | 6.0604 | 4.6699 | 3.0987 | 1.4233 | -3.7527 | -8.5708 | -11.8737 | -13.9194 | -13.6173 | 13.4038 | 13.0407 | 12.7767 | 12.5336 | 12.0828 | 11.4659 | 10.6974 | 9.3069 | 7.7357 | 6.0603 | 0.88426 | -3.9338 | -7.2367 | -9.2824 | -9.0906 | 8.7668 | 8.3951 | 8.1223 | 7.9103 | 7.5587 | 7.077 | 6.5952 | 5.9689 | 5.1756 | 4.2755 | 1.0264 | -2.4631 | -4.8821 | -6.5312 | -7.1717 | 13.4038 | 13.0321 | 12.7593 | 12.5473 | 12.1957 | 11.714 | 11.2322 | 10.6059 | 9.8126 | 8.9125 | 5.6634 | 2.1739 | -0.24509 | -1.8942 | -2.4951 | 8.7668 | 8.0762 | 7.6943 | 7.3802 | 6.889 | 6.2975 | 5.5932 | 4.268 | 2.8171 | 1.2563 | -3.8603 | -9.0796 | -12.9591 | -15.4088 | -15.3104 | 13.4038 | 12.7132 | 12.3313 | 12.0172 | 11.526 | 10.9345 | 10.2302 | 8.905 | 7.4541 | 5.8933 | 0.77666 | -4.4426 | -8.3221 | -10.7718 | -10.7417 | 358258 | 418014 | WRIGHTINGTON | PENWORTHAM
| Woodhill Lane | 3.0785 | 2.9729 | 2.298 | 1.468 | 0.58502 | 0.6915 | -0.7911 | -0.89171 | -0.96405 | -1.0198 | -1.7628 | -3.2757 | -4.5188 | -5.8379 | -7.014 | 4.0785 | 3.9729 | 3.298 | 2.468 | 1.585 | 0.6915 | -0.7911 | -0.89171 | -0.96405 | -1.0198 | -1.7628 | -3.2757 | -4.5188 | -5.8379 | -7.1268 | 3.0785 | 2.9382 | 2.6041 | 2.2518 | 1.8605 | 2.4758 | 1.8473 | 1.5689 | 1.4796 | 1.3844 | 1.1086 | 0.83898 | 0.60385 | 0.36045 | 0.18172 | 4.0785 | 3.9382 | 3.6041 | 3.2518 | 2.8605 | 2.4758 | 1.8473 | 1.5689 | 1.4796 | 1.3844 | 1.1086 | 0.83898 | 0.60385 | 0.36045 | 0.20523 | 3.0785 | 2.9776 | 2.3112 | 1.4947 | 0.62551 | 0.74779 | -0.70968 | -0.78612 | -0.82852 | -0.85896 | -1.5191 | -2.9582 | -4.1309 | -5.3619 | -6.4335 | 4.0785 | 3.9776 | 3.3112 | 2.4947 | 1.6255 | 0.74779 | -0.70968 | -0.78612 | -0.82852 | -0.85896 | -1.5191 | -2.9582 | -4.1309 | -5.3619 | -6.5636 | 3.0785 | 3.1386 | 2.5263 | 1.7415 | 0.89443 | 1.0328 | -0.50996 | -1.0095 | -1.5183 | -2.0184 | -3.4444 | -4.8014 | -5.8658 | -6.488 | -5.8987 | 4.0785 | 4.1386 | 3.5263 | 2.7415 | 1.8944 | 1.0328 | -0.50996 | -1.0095 | -1.5183 | -2.0184 | -3.4444 | -4.8014 | -5.8658 | -6.488 | -6.0307 | 3.0785 | 2.9863 | 2.3254 | 1.5231 | 0.69858 | 0.88806 | -0.52797 | -0.60336 | -0.6783 | -0.75037 | -1.0176 | -1.3326 | -1.5429 | -1.7581 | -1.8046 | 4.0785 | 3.9863 | 3.3254 | 2.5231 | 1.6986 | 0.88806 | -0.52797 | -0.60336 | -0.6783 | -0.75037 | -1.0176 | -1.3326 | -1.5429 | -1.7581 | -1.8235 | 3.0785 | 3.1003 | 2.4401 | 1.6018 | 0.70246 | 0.7973 | -0.79746 | -1.3598 | -1.8967 | -2.4258 | -3.9433 | -5.3782 | -6.5302 | -7.2792 | -6.8491 | 4.0785 | 4.1003 | 3.4401 | 2.6018 | 1.7025 | 0.7973 | -0.79746 | -1.3598 | -1.8967 | -2.4258 | -3.9433 | -5.3782 | -6.5302 | -7.2792 | -6.9453 | 343294 | 463785 | LANCASTER | HEYSHAM
| Woodhouse Park | 5.5397 | 5.1248 | 4.9751 | 4.9262 | 4.8388 | 4.7324 | 4.6353 | 4.5646 | 4.4314 | 4.3336 | 3.1859 | 0.84918 | -1.1043 | -2.8633 | -4.9049 | 9.0397 | 8.6248 | 8.4751 | 8.4262 | 8.3388 | 8.2324 | 8.1353 | 8.0646 | 7.9314 | 7.8336 | 6.6859 | 4.3492 | 2.3957 | 0.63673 | -1.5154 | 5.5397 | 5.3783 | 5.2572 | 5.19 | 5.1385 | 5.0791 | 4.9853 | 4.8521 | 4.6903 | 4.5307 | 4.0687 | 3.6202 | 3.2355 | 2.8458 | 2.493 | 9.0397 | 8.8783 | 8.7572 | 8.69 | 8.6385 | 8.5791 | 8.4853 | 8.3521 | 8.1903 | 8.0307 | 7.5687 | 7.1202 | 6.7355 | 6.3458 | 6.0565 | 5.5397 | 5.0773 | 4.928 | 4.9054 | 4.8393 | 4.7561 | 4.6966 | 4.6589 | 4.5765 | 4.5199 | 3.5055 | 1.2716 | -0.58583 | -2.2242 | -4.1215 | 9.0397 | 8.5773 | 8.428 | 8.4054 | 8.3393 | 8.2561 | 8.1966 | 8.1589 | 8.0765 | 8.0199 | 7.0055 | 4.7716 | 2.9142 | 1.2758 | -0.75879 | 5.5397 | 5.4084 | 5.336 | 5.3374 | 5.2789 | 5.1942 | 5.0741 | 4.3619 | 3.6044 | 2.8558 | 0.70456 | -1.406 | -3.1007 | -3.8537 | -3.1849 | 9.0397 | 8.9084 | 8.836 | 8.8374 | 8.7789 | 8.6942 | 8.5741 | 7.8619 | 7.1044 | 6.3558 | 4.2046 | 2.094 | 0.39927 | -0.35368 | 0.17069 | 5.5397 | 5.2929 | 5.1936 | 5.1941 | 5.2168 | 5.224 | 5.2159 | 5.1907 | 5.0805 | 4.9743 | 4.5981 | 4.1774 | 3.7956 | 3.3552 | 3.1654 | 9.0397 | 8.7929 | 8.6936 | 8.6941 | 8.7168 | 8.724 | 8.7159 | 8.6907 | 8.5805 | 8.4743 | 8.0981 | 7.6774 | 7.2956 | 6.8552 | 6.6562 | 5.5397 | 5.1899 | 5.04 | 4.9977 | 4.8991 | 4.7871 | 4.6305 | 3.8663 | 3.0739 | 2.2881 | 0.016304 | -2.1824 | -3.9725 | -4.8495 | -4.3393 | 9.0397 | 8.6899 | 8.54 | 8.4977 | 8.3991 | 8.2871 | 8.1305 | 7.3663 | 6.5739 | 5.7881 | 3.5163 | 1.3176 | -0.47251 | -1.3495 | -0.94828 | 382132 | 386340 | MOSS NOOK | SOUTH MANCHESTER
| Woodley | 9.6401 | 8.98 | 8.4585 | 8.0471 | 7.7256 | 7.3718 | 7.0017 | 6.6198 | 6.1488 | 5.6674 | 3.7143 | 1.3436 | -0.36082 | -1.8061 | -3.0492 | 14.2771 | 13.617 | 13.0955 | 12.6841 | 12.3626 | 12.0088 | 11.6387 | 11.2568 | 10.7858 | 10.3044 | 8.3513 | 5.9806 | 4.2762 | 2.8309 | 1.5268 | 9.6401 | 9.4821 | 9.2495 | 9.0675 | 8.9414 | 8.8102 | 8.6399 | 8.4202 | 8.1112 | 7.7794 | 6.7025 | 5.5189 | 3.9744 | 2.1336 | 0.82524 | 14.2771 | 14.1191 | 13.8865 | 13.7045 | 13.5784 | 13.4472 | 13.2769 | 13.0572 | 12.7482 | 12.4164 | 11.3395 | 10.1559 | 8.6114 | 6.7706 | 5.64 | 9.6401 | 8.8243 | 8.2113 | 7.7164 | 7.3114 | 6.8737 | 6.4182 | 5.9501 | 5.4332 | 4.8985 | 2.6362 | 0.16005 | -1.4932 | -2.9875 | -3.8851 | 14.2771 | 13.4613 | 12.8483 | 12.3534 | 11.9484 | 11.5107 | 11.0552 | 10.5871 | 10.0702 | 9.5355 | 7.2732 | 4.7971 | 3.1438 | 1.6495 | 0.81072 | 9.6401 | 9.1253 | 8.5999 | 8.0297 | 7.6473 | 7.2018 | 6.6461 | 5.827 | 4.9515 | 4.0758 | 1.5098 | -0.63104 | -2.0693 | -2.7401 | -2.4967 | 14.2771 | 13.7623 | 13.2369 | 12.6667 | 12.2843 | 11.8388 | 11.2831 | 10.464 | 9.5885 | 8.7128 | 6.1468 | 4.006 | 2.5677 | 1.8969 | 2.0696 | 9.6401 | 9.3719 | 8.9593 | 8.6196 | 8.4345 | 8.2107 | 7.942 | 7.6352 | 7.2089 | 6.7547 | 5.2376 | 3.7284 | 2.464 | 1.0137 | 0.22992 | 14.2771 | 14.0089 | 13.5963 | 13.2566 | 13.0715 | 12.8477 | 12.579 | 12.2722 | 11.8459 | 11.3917 | 9.8746 | 8.3654 | 7.101 | 5.6507 | 4.971 | 9.6401 | 8.8612 | 8.242 | 7.6196 | 7.1966 | 6.7471 | 6.2016 | 5.373 | 4.4999 | 3.6278 | 1.017 | -1.2389 | -2.6707 | -3.6738 | -3.9539 | 14.2771 | 13.4982 | 12.879 | 12.2566 | 11.8336 | 11.3841 | 10.8386 | 10.01 | 9.1369 | 8.2648 | 5.654 | 3.3981 | 1.9663 | 0.96317 | 0.71438 | 393116 | 392019 | VERNON PARK | BREDBURY
| Woolfold | 12.14 | 11.8777 | 11.6917 | 11.5543 | 11.3698 | 11.1877 | 11.0359 | 10.9005 | 10.697 | 10.5175 | 8.8863 | 5.7719 | 3.093 | 0.12168 | -2.4406 | 16.14 | 15.8777 | 15.6917 | 15.5543 | 15.3698 | 15.1877 | 15.0359 | 14.9005 | 14.697 | 14.5175 | 12.8863 | 9.7719 | 7.093 | 4.1217 | 1.4056 | 12.14 | 12.0208 | 11.8819 | 11.746 | 11.5754 | 11.3838 | 11.1381 | 10.827 | 10.5407 | 10.2521 | 9.3898 | 8.5399 | 7.7057 | 6.7252 | 6.0633 | 16.14 | 16.0208 | 15.8819 | 15.746 | 15.5754 | 15.3838 | 15.1381 | 14.827 | 14.5407 | 14.2521 | 13.3898 | 12.5399 | 11.7057 | 10.7252 | 10.1717 | 12.14 | 11.875 | 11.7119 | 11.6221 | 11.0297 | 10.447 | 9.9136 | 9.4058 | 8.9986 | 8.5961 | 6.914 | 4.0384 | 1.5722 | -1.1415 | -3.4057 | 16.14 | 15.875 | 15.7119 | 15.6221 | 15.0297 | 14.447 | 13.9136 | 13.4058 | 12.9986 | 12.5961 | 10.914 | 8.0384 | 5.5722 | 2.8585 | 0.38524 | 12.14 | 12.1397 | 12.0626 | 11.9973 | 11.4017 | 10.7836 | 10.0079 | 8.635 | 7.3583 | 6.084 | 2.9613 | 0.21434 | -2.0661 | -3.6343 | -2.6819 | 16.14 | 16.1397 | 16.0626 | 15.9973 | 15.4017 | 14.7836 | 14.0079 | 12.635 | 11.3583 | 10.084 | 6.9613 | 4.2143 | 1.9339 | 0.36566 | 1.1071 | 12.14 | 12.0373 | 11.9262 | 11.8618 | 11.794 | 11.6966 | 11.5882 | 11.4861 | 11.2939 | 11.1084 | 10.4483 | 9.5187 | 8.7058 | 7.9499 | 7.5188 | 16.14 | 16.0373 | 15.9262 | 15.8618 | 15.794 | 15.6966 | 15.5882 | 15.4861 | 15.2939 | 15.1084 | 14.4483 | 13.5187 | 12.7058 | 11.9499 | 11.5459 | 12.14 | 11.9941 | 11.8116 | 11.6469 | 10.9622 | 10.2849 | 9.4382 | 7.9617 | 6.6058 | 5.2538 | 1.9033 | -1.043 | -3.5226 | -5.3507 | -4.6957 | 16.14 | 15.9941 | 15.8116 | 15.6469 | 14.9622 | 14.2849 | 13.4382 | 11.9617 | 10.6058 | 9.2538 | 5.9033 | 2.957 | 0.47735 | -1.3507 | -0.84155 | 378874 | 411666 | BURY | KEARSLEY
| Wordsworth St | 10.2981 | 10.0884 | 9.9462 | 9.7871 | 9.4869 | 9.1678 | 8.871 | 8.5985 | 8.3264 | 8.0703 | 6.0328 | 2.5501 | -0.16778 | -2.7407 | -4.4154 | 14.9351 | 14.7254 | 14.5832 | 14.4241 | 14.1239 | 13.8048 | 13.508 | 13.2355 | 12.9634 | 12.7073 | 10.6698 | 7.1871 | 4.4692 | 1.8963 | -0.06914 | 10.2981 | 10.166 | 10.0955 | 10.0061 | 9.8439 | 9.6569 | 9.4002 | 9.0753 | 8.8471 | 8.6028 | 7.8617 | 7.0995 | 6.3524 | 5.4911 | 4.9116 | 14.9351 | 14.803 | 14.7325 | 14.6431 | 14.4809 | 14.2939 | 14.0372 | 13.7123 | 13.4841 | 13.2398 | 12.4987 | 11.7365 | 10.9894 | 10.1281 | 9.6418 | 10.2981 | 9.9828 | 9.7285 | 9.454 | 9.0339 | 8.5897 | 8.1769 | 7.7698 | 7.3554 | 6.9379 | 4.5191 | 1.1644 | -1.096 | -2.9451 | -3.579 | 14.9351 | 14.6198 | 14.3655 | 14.091 | 13.6709 | 13.2267 | 12.8139 | 12.4068 | 11.9924 | 11.5749 | 9.1561 | 5.8014 | 3.541 | 1.6919 | 0.83944 | 10.2981 | 10.37 | 10.2146 | 9.9763 | 9.561 | 9.101 | 8.4419 | 7.0988 | 5.8055 | 4.5702 | 1.1906 | -1.5302 | -3.1487 | -3.5556 | -2.2768 | 14.9351 | 15.007 | 14.8516 | 14.6133 | 14.198 | 13.738 | 13.0789 | 11.7358 | 10.4425 | 9.2072 | 5.8276 | 3.1068 | 1.4883 | 1.0814 | 2.1317 | 10.2981 | 10.1145 | 10.0165 | 9.9394 | 9.8047 | 9.6314 | 9.4116 | 9.1583 | 8.863 | 8.557 | 7.491 | 6.2553 | 5.2793 | 4.3506 | 3.8372 | 14.9351 | 14.7515 | 14.6535 | 14.5764 | 14.4417 | 14.2684 | 14.0486 | 13.7953 | 13.5 | 13.194 | 12.128 | 10.8923 | 9.9163 | 8.9876 | 8.5196 | 10.2981 | 10.306 | 10.0641 | 9.7285 | 9.2239 | 8.7023 | 7.9626 | 6.5131 | 5.1388 | 3.8205 | 0.18332 | -2.7514 | -4.586 | -5.2814 | -4.2861 | 14.9351 | 14.943 | 14.7011 | 14.3655 | 13.8609 | 13.3393 | 12.5996 | 11.1501 | 9.7758 | 8.4575 | 4.8203 | 1.8856 | 0.051019 | -0.64443 | 0.19447 | 370709 | 410873 | BOLTON | KEARSLEY
| Worsley Mesnes | 14.1532 | 12.6218 | 12.261 | 12.1816 | 11.9496 | 11.7035 | 11.4667 | 11.2232 | 10.9311 | 10.6597 | 9.139 | 6.6223 | 4.45 | 2.0189 | -0.21887 | 18.7902 | 17.2588 | 16.898 | 16.8186 | 16.5866 | 16.3405 | 16.1037 | 15.8602 | 15.5681 | 15.2967 | 13.776 | 11.2593 | 9.087 | 6.6559 | 4.3338 | 14.1532 | 13.635 | 13.4935 | 13.4281 | 13.3146 | 13.1746 | 12.9755 | 12.6995 | 12.4346 | 12.162 | 11.3405 | 10.5199 | 9.7475 | 8.9358 | 8.4075 | 18.7902 | 18.272 | 18.1305 | 18.0651 | 17.9516 | 17.8116 | 17.6125 | 17.3365 | 17.0716 | 16.799 | 15.9775 | 15.1569 | 14.3845 | 13.5728 | 13.131 | 14.1532 | 12.396 | 12.0044 | 11.952 | 11.751 | 11.5421 | 11.3605 | 11.1765 | 10.9426 | 10.7222 | 9.3537 | 6.9528 | 4.8893 | 2.576 | 0.4674 | 18.7902 | 17.033 | 16.6414 | 16.589 | 16.388 | 16.1791 | 15.9975 | 15.8135 | 15.5796 | 15.3592 | 13.9907 | 11.5898 | 9.5263 | 7.213 | 4.9971 | 14.1532 | 13.134 | 12.9102 | 12.882 | 12.6805 | 12.4491 | 12.0822 | 11.2297 | 10.3503 | 9.4821 | 7.0342 | 4.6778 | 2.7204 | 1.3582 | 1.8603 | 18.7902 | 17.771 | 17.5472 | 17.519 | 17.3175 | 17.0861 | 16.7192 | 15.8667 | 14.9873 | 14.1191 | 11.6712 | 9.3148 | 7.3574 | 5.9952 | 6.3841 | 14.1532 | 13.2315 | 13.0243 | 13.0096 | 12.9001 | 12.7552 | 12.5772 | 12.3647 | 12.0761 | 11.7902 | 10.9082 | 9.9762 | 9.3168 | 8.6948 | 8.3526 | 18.7902 | 17.8685 | 17.6613 | 17.6466 | 17.5371 | 17.3922 | 17.2142 | 17.0017 | 16.7131 | 16.4272 | 15.5452 | 14.6132 | 13.9538 | 13.3318 | 13.013 | 14.1532 | 12.3757 | 11.9428 | 11.8411 | 11.5729 | 11.2995 | 10.8798 | 9.9536 | 9.0166 | 8.0908 | 5.4678 | 2.9726 | 0.87832 | -0.65145 | -0.34554 | 18.7902 | 17.0127 | 16.5798 | 16.4781 | 16.2099 | 15.9365 | 15.5168 | 14.5906 | 13.6536 | 12.7278 | 10.1048 | 7.6096 | 5.5153 | 3.9855 | 4.2225 | 357435 | 403977 | WIGAN | KIRKBY
| Wrightington | 11.4318 | 8.4623 | 7.7679 | 7.5789 | 7.299 | 6.9777 | 6.6964 | 6.4254 | 6.0676 | 5.7471 | 4.097 | 1.482 | -0.60073 | -2.6529 | -4.4597 | 16.0688 | 13.0993 | 12.4049 | 12.2159 | 11.936 | 11.6147 | 11.3334 | 11.0624 | 10.7046 | 10.3841 | 8.734 | 6.119 | 4.0363 | 1.9841 | 0.083647 | 11.4318 | 10.8643 | 10.5982 | 10.3866 | 10.123 | 9.8352 | 9.4774 | 8.9957 | 8.5449 | 8.0916 | 6.7648 | 5.5107 | 4.3844 | 3.1433 | 2.2699 | 16.0688 | 15.5013 | 15.2352 | 15.0236 | 14.76 | 14.4722 | 14.1144 | 13.6327 | 13.1819 | 12.7286 | 11.4018 | 10.1477 | 9.0214 | 7.7803 | 7.0516 | 11.4318 | 8.0193 | 7.0347 | 6.6603 | 6.231 | 5.7647 | 5.3517 | 5.2045 | 4.9826 | 4.7752 | 3.467 | 1.1674 | -0.64574 | -2.3947 | -3.8746 | 16.0688 | 12.6563 | 11.6717 | 11.2973 | 10.868 | 10.4017 | 9.9887 | 9.8415 | 9.6196 | 9.4122 | 8.104 | 5.8044 | 3.9913 | 2.2423 | 0.6074 | 11.4318 | 9.1941 | 8.4665 | 8.1314 | 7.7027 | 7.256 | 6.681 | 5.9544 | 5.1587 | 4.372 | 2.1218 | -0.077678 | -1.7192 | -2.7026 | -1.98 | 16.0688 | 13.8311 | 13.1035 | 12.7684 | 12.3397 | 11.893 | 11.318 | 10.5914 | 9.7957 | 9.009 | 6.7588 | 4.5593 | 2.9178 | 1.9344 | 2.4907 | 11.4318 | 10.4946 | 10.1959 | 10.0726 | 9.917 | 9.7062 | 9.4592 | 9.1572 | 8.7246 | 8.2941 | 6.8776 | 5.3065 | 4.191 | 2.989 | 2.5143 | 16.0688 | 15.1316 | 14.8329 | 14.7096 | 14.554 | 14.3432 | 14.0962 | 13.7942 | 13.3616 | 12.9311 | 11.5146 | 9.9435 | 8.828 | 7.626 | 7.1631 | 11.4318 | 7.7006 | 6.6174 | 6.1608 | 5.6166 | 5.0486 | 4.3785 | 3.5064 | 2.5951 | 1.6972 | -0.86689 | -3.3201 | -5.1812 | -6.4001 | -5.9307 | 16.0688 | 12.3376 | 11.2544 | 10.7978 | 10.2536 | 9.6856 | 9.0155 | 8.1434 | 7.2321 | 6.3342 | 3.7701 | 1.3169 | -0.54422 | -1.7631 | -1.4045 | 353466 | 413290 | WRIGHTINGTON | PENWORTHAM
| Yealand | 0.6231 | -0.86522 | -1.1782 | -1.2418 | -1.3347 | -1.4489 | -1.6257 | -1.8736 | -2.2926 | -2.8367 | -4.6898 | -6.3757 | -7.4615 | -8.2299 | -8.7132 | 8.6231 | 7.1348 | 6.8218 | 6.7582 | 6.6653 | 6.5511 | 6.3743 | 6.1264 | 5.7074 | 5.1633 | 3.3102 | 1.6243 | 0.53845 | -0.22991 | -0.71203 | 0.6231 | -0.019303 | -0.18393 | -0.24622 | -0.32216 | -0.41055 | -0.52056 | -0.65237 | -0.78949 | -0.94011 | -1.7469 | -2.9755 | -4.2704 | -5.6784 | -6.5918 | 8.6231 | 7.9807 | 7.8161 | 7.7538 | 7.6778 | 7.5895 | 7.4794 | 7.3476 | 7.2105 | 7.0599 | 6.2531 | 5.0245 | 3.7296 | 2.3216 | 1.5239 | 0.6231 | -1.0989 | -1.445 | -1.4913 | -1.5636 | -1.6725 | -1.834 | -2.0382 | -2.2868 | -2.7044 | -4.4759 | -6.3465 | -7.6367 | -8.4992 | -8.9396 | 8.6231 | 6.9011 | 6.555 | 6.5087 | 6.4364 | 6.3275 | 6.166 | 5.9618 | 5.7132 | 5.2956 | 3.5241 | 1.6535 | 0.36327 | -0.49916 | -0.94868 | 0.6231 | -0.56233 | -0.80315 | -0.84253 | -0.91182 | -1.0476 | -1.2642 | -1.6157 | -2.143 | -2.7767 | -4.7563 | -6.3878 | -7.4081 | -7.9834 | -7.9973 | 8.6231 | 7.4377 | 7.1968 | 7.1575 | 7.0882 | 6.9524 | 6.7358 | 6.3843 | 5.857 | 5.2233 | 3.2437 | 1.6122 | 0.59191 | 0.016594 | -0.01231 | 0.6231 | -0.60398 | -0.85885 | -0.89956 | -0.95121 | -1.0267 | -1.1621 | -1.3657 | -1.6351 | -2.0834 | -3.6963 | -5.2475 | -6.2786 | -6.931 | -7.1361 | 8.6231 | 7.396 | 7.1412 | 7.1004 | 7.0488 | 6.9733 | 6.8379 | 6.6343 | 6.3649 | 5.9166 | 4.3037 | 2.7525 | 1.7214 | 1.069 | 0.87661 | 0.6231 | -1.3048 | -1.6966 | -1.7628 | -1.8529 | -1.9561 | -2.127 | -2.4582 | -2.8343 | -3.2893 | -5.247 | -7.1068 | -8.3784 | -9.1106 | -9.1753 | 8.6231 | 6.6952 | 6.3034 | 6.2372 | 6.1471 | 6.0439 | 5.873 | 5.5418 | 5.1657 | 4.7107 | 2.753 | 0.89321 | -0.37842 | -1.1106 | -1.1811 | 351537 | 475934 | KENDAL (PARKSIDE RD) | HUTTON | Firm Capacity marginally exceeded in FY25. HV load transfer to Arnside primary.

## BSP Headroom
Click the scenario name to move directly to the associated results | Best View
Counterfactual
Electric Engagement
Holistic Transition
Hydrogen Evolution
Accelerated Decarbonisation
| BSP | Best View Firm Headroom MVA | [14 empty] | Best View Non Firm Headroom MVA | [14 empty] | Counterfactual Firm Headroom MVA | [14 empty] | Counterfactual Non Firm Headroom MVA | [14 empty] | Electric Engagement Firm Headroom MVA | [15 empty] | Electric Engagement Non Firm Headroom MVA | [14 empty] | Holistic Transition Firm Headroom MVA | [15 empty] | Holistic Transition Non Firm Headroom MVA | [14 empty] | Hydrogen Evolution Firm Headroom MVA | [15 empty] | Hydrogen Evolution Non Firm Headroom MVA | [14 empty] | Accelerated Decarbonisation Firm Headroom MVA | [14 empty] | Accelerated Decarbonisation Non Firm Headroom MVA
|  | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2036 | 2039 | 2042 | 2046 | 2051 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2036 | 2039 | 2042 | 2046 | 2051 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2036 | 2039 | 2042 | 2046 | 2051 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2036 | 2039 | 2042 | 2046 | 2051 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2036 | 2039 | 2042 | 2046 | 2051 |  | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2036 | 2039 | 2042 | 2046 | 2051 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2036 | 2039 | 2042 | 2046 | 2051 |  | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2036 | 2039 | 2042 | 2046 | 2051 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2036 | 2039 | 2042 | 2046 | 2051 |  | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2036 | 2039 | 2042 | 2046 | 2051 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2036 | 2039 | 2042 | 2046 | 2051 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2036 | 2039 | 2042 | 2046 | 2051 | Easting | Northing | GSP | Comments (Based on Best View Headroom)
| Adswood | 67.4473 | 61.6324 | 59.4393 | 57.8297 | 55.5188 | 53.0236 | 51.3419 | 49.6735 | 47.5879 | 45.7481 | 38.2972 | 27.9781 | 20.0403 | 12.397 | 6.9457 | 85.4473 | 79.6324 | 77.4393 | 75.8297 | 73.5188 | 71.0236 | 69.3419 | 67.6735 | 65.5879 | 63.7481 | 56.2972 | 45.9781 | 38.0403 | 30.397 | 24.9457 | 67.4473 | 65.0586 | 64.0806 | 63.0257 | 61.8101 | 60.5294 | 59.0135 | 57.2573 | 55.6912 | 54.0895 | 50.3733 | 46.122 | 42.1652 | 38.1368 | 35.3914 | 85.4473 | 83.0586 | 82.0806 | 81.0257 | 79.8101 | 78.5294 | 77.0135 | 75.2573 | 73.6912 | 72.0895 | 68.3733 | 64.122 | 60.1652 | 56.1368 | 53.3914 | 67.4473 | 60.8028 | 58.2903 | 56.5331 | 54.0553 | 51.4765 | 49.6526 | 47.65 | 45.4687 | 43.396 | 35.2647 | 25.1384 | 17.8698 | 11.7665 | 8.7545 | 0 | 85.4473 | 78.8028 | 76.2903 | 74.5331 | 72.0553 | 69.4765 | 67.6526 | 65.65 | 63.4687 | 61.396 | 53.2647 | 43.1384 | 35.8698 | 29.7665 | 26.7545 | 67.4473 | 63.1305 | 61.2037 | 59.5842 | 57.1422 | 54.4479 | 51.9547 | 47.6181 | 43.1671 | 38.9336 | 28.4017 | 19.8215 | 14.4092 | 12.0922 | 14.3614 | 0 | 85.4473 | 81.1305 | 79.2037 | 77.5842 | 75.1422 | 72.4479 | 69.9547 | 65.6181 | 61.1671 | 56.9336 | 46.4017 | 37.8215 | 32.4092 | 30.0922 | 32.3614 | 67.4473 | 64.2434 | 62.7384 | 61.4187 | 59.5768 | 57.5495 | 56.127 | 54.6472 | 52.6543 | 50.8201 | 45.8189 | 40.8267 | 37.3798 | 33.9434 | 31.9598 | 0 | 85.4473 | 82.2434 | 80.7384 | 79.4187 | 77.5768 | 75.5495 | 74.127 | 72.6472 | 70.6543 | 68.8201 | 63.8189 | 58.8267 | 55.3798 | 51.9434 | 49.9598 | 67.4473 | 60.899 | 58.2516 | 56.2849 | 53.5369 | 50.6102 | 47.9035 | 43.2461 | 38.5752 | 34.1106 | 22.7646 | 13.4026 | 7.2348 | 4.0663 | 6.1119 | 85.4473 | 78.899 | 76.2516 | 74.2849 | 71.5369 | 68.6102 | 65.9035 | 61.2461 | 56.5752 | 52.1106 | 40.7646 | 31.4026 | 25.2348 | 22.0663 | 24.1119 | 389188 | 388310 | BREDBURY
| Agecroft | 15.0099 | 12.5195 | 10.9053 | 9.603 | 7.9901 | 18.2861 | 16.5251 | 14.8372 | 12.8371 | 10.9175 | 2.0354 | -10.5208 | -19.8263 | -28.4177 | -34.6845 | 27.0099 | 24.5195 | 22.9053 | 21.603 | 19.9901 | 18.2861 | 16.5251 | 14.8372 | 12.8371 | 10.9175 | 2.0354 | -10.5208 | -19.8263 | -28.4177 | -34.6845 | 15.0099 | 13.8461 | 12.8466 | 11.9299 | 10.8445 | 21.7682 | 20.3154 | 18.6339 | 17.0951 | 15.4622 | 10.617 | 5.7965 | 1.2963 | -3.4232 | -6.7017 | 27.0099 | 25.8461 | 24.8466 | 23.9299 | 22.8445 | 21.7682 | 20.3154 | 18.6339 | 17.0951 | 15.4622 | 10.617 | 5.7965 | 1.2963 | -3.4232 | -6.7017 | 15.0099 | 12.073 | 10.1575 | 8.6374 | 6.7834 | 16.5288 | 14.2942 | 12.0199 | 9.6181 | 7.4555 | -2.3011 | -14.843 | -23.3626 | -30.1309 | -33.0971 | 0 | 27.0099 | 24.073 | 22.1575 | 20.6374 | 18.7834 | 16.5288 | 14.2942 | 12.0199 | 9.6181 | 7.4555 | -2.3011 | -14.843 | -23.3626 | -30.1309 | -33.0971 | 15.0099 | 13.7614 | 12.3179 | 10.8676 | 9.0661 | 18.7466 | 15.8224 | 10.8087 | 5.7184 | 1.0036 | -11.7389 | -22.1557 | -28.4832 | -31.0069 | -27.6996 | 0 | 27.0099 | 25.7614 | 24.3179 | 22.8676 | 21.0661 | 18.7466 | 15.8224 | 10.8087 | 5.7184 | 1.0036 | -11.7389 | -22.1557 | -28.4832 | -31.0069 | -27.6996 | 15.0099 | 13.2485 | 11.9495 | 10.974 | 9.9252 | 20.7681 | 19.4311 | 18.081 | 16.177 | 14.2334 | 8.2966 | 2.3964 | -1.8414 | -5.573 | -7.5439 | 0 | 27.0099 | 25.2485 | 23.9495 | 22.974 | 21.9252 | 20.7681 | 19.4311 | 18.081 | 16.177 | 14.2334 | 8.2966 | 2.3964 | -1.8414 | -5.573 | -7.5439 | 15.0099 | 12.8506 | 10.9048 | 9.0432 | 6.8772 | 16.3276 | 13.1228 | 7.7291 | 2.3954 | -2.5694 | -16.2124 | -27.5319 | -34.758 | -38.1415 | -35.4805 | 27.0099 | 24.8506 | 22.9048 | 21.0432 | 18.8772 | 16.3276 | 13.1228 | 7.7291 | 2.3954 | -2.5694 | -16.2124 | -27.5319 | -34.758 | -38.1415 | -35.4805 | 380345 | 401831 | KEARSLEY
| Altrincham | 60.8777 | 56.6142 | 55.1285 | 54.41 | 53.3982 | 52.3291 | 51.3206 | 50.3634 | 49.2398 | 48.2083 | 41.2425 | 29.3666 | 19.7814 | 9.792 | 1.4368 | 78.8777 | 74.6142 | 73.1285 | 72.41 | 71.3982 | 70.3291 | 69.3206 | 68.3634 | 67.2398 | 66.2083 | 59.2425 | 47.3666 | 37.7814 | 27.792 | 19.4368 | 60.8777 | 59.4111 | 58.4975 | 57.6941 | 56.6801 | 55.597 | 54.2157 | 52.4661 | 51.2004 | 49.9057 | 45.9752 | 41.9357 | 38.1105 | 33.6953 | 30.4358 | 78.8777 | 77.4111 | 76.4975 | 75.6941 | 74.6801 | 73.597 | 72.2157 | 70.4661 | 69.2004 | 67.9057 | 63.9752 | 59.9357 | 56.1105 | 51.6953 | 48.4358 | 60.8777 | 55.9922 | 54.3523 | 53.6556 | 52.5143 | 51.329 | 49.8659 | 48.4492 | 46.9447 | 45.3277 | 37.8049 | 26.8375 | 18.3281 | 9.9763 | 3.883 | 0 | 78.8777 | 73.9922 | 72.3523 | 71.6556 | 70.5143 | 69.329 | 67.8659 | 66.4492 | 64.9447 | 63.3277 | 55.8049 | 44.8375 | 36.3281 | 27.9763 | 21.883 | 60.8777 | 58.4268 | 57.4332 | 56.9487 | 55.9011 | 54.7074 | 52.5423 | 48.3 | 43.9128 | 39.5573 | 27.7889 | 17.7805 | 10.4677 | 6.1818 | 9.3699 | 0 | 78.8777 | 76.4268 | 75.4332 | 74.9487 | 73.9011 | 72.7074 | 70.5423 | 66.3 | 61.9128 | 57.5573 | 45.7889 | 35.7805 | 28.4677 | 24.1818 | 27.3699 | 60.8777 | 58.7843 | 57.9013 | 57.4748 | 56.9539 | 56.3144 | 55.5935 | 54.8188 | 53.7367 | 52.6617 | 48.9721 | 44.1777 | 40.4779 | 36.9419 | 34.6908 | 0 | 78.8777 | 76.7843 | 75.9013 | 75.4748 | 74.9539 | 74.3144 | 73.5935 | 72.8188 | 71.7367 | 70.6617 | 66.9721 | 62.1777 | 58.4779 | 54.9419 | 52.6908 | 60.8777 | 56.3416 | 54.5982 | 53.6887 | 52.2565 | 50.7939 | 48.2962 | 43.6137 | 38.9519 | 34.3205 | 21.688 | 10.9417 | 2.9033 | -2.3261 | -0.31654 | 78.8777 | 74.3416 | 72.5982 | 71.6887 | 70.2565 | 68.7939 | 66.2962 | 61.6137 | 56.9519 | 52.3205 | 39.688 | 28.9417 | 20.9033 | 15.6739 | 17.6835 | 376380 | 389012 | CARRINGTON
| Atherton | 26.9483 | 21.0293 | 18.8952 | 17.7362 | 15.5628 | 13.2877 | 11.0993 | 9.0015 | 6.5302 | 4.1718 | -9.1077 | -30.3801 | -48.2081 | -65.6457 | -80.2112 | 26.9483 | 21.0293 | 18.8952 | 17.7362 | 15.5628 | 13.2877 | 11.0993 | 9.0015 | 6.5302 | 4.1718 | -9.1077 | -30.3801 | -48.2081 | -65.6457 | -80.2112 | 26.9483 | 24.6617 | 23.4823 | 22.536 | 21.2462 | 19.7711 | 17.8101 | 15.2292 | 13.0261 | 10.7652 | 3.7992 | -3.4432 | -10.4389 | -18.1008 | -23.0175 | 26.9483 | 24.6617 | 23.4823 | 22.536 | 21.2462 | 19.7711 | 17.8101 | 15.2292 | 13.0261 | 10.7652 | 3.7992 | -3.4432 | -10.4389 | -18.1008 | -23.0175 | 26.9483 | 20.1963 | 17.8773 | 16.7893 | 13.8822 | 10.9179 | 8.0654 | 5.3299 | 2.3218 | -0.53669 | -13.8866 | -34.0995 | -50.5528 | -65.8924 | -77.5268 | 0 | 26.9483 | 20.1963 | 17.8773 | 16.7893 | 13.8822 | 10.9179 | 8.0654 | 5.3299 | 2.3218 | -0.53669 | -13.8866 | -34.0995 | -50.5528 | -65.8924 | -77.5268 | 26.9483 | 23.7221 | 22.3315 | 21.5192 | 18.6941 | 15.6084 | 11.3581 | 3.3868 | -4.8566 | -12.8859 | -34.6323 | -53.085 | -66.926 | -75.0097 | -69.4142 | 0 | 26.9483 | 23.7221 | 22.3315 | 21.5192 | 18.6941 | 15.6084 | 11.3581 | 3.3868 | -4.8566 | -12.8859 | -34.6323 | -53.085 | -66.926 | -75.0097 | -69.4142 | 26.9483 | 23.4482 | 22.0724 | 21.4643 | 20.3215 | 18.9257 | 17.2631 | 15.4549 | 13.0316 | 10.5796 | 2.8798 | -6.2438 | -13.5646 | -19.4624 | -22.5717 | 0 | 26.9483 | 23.4482 | 22.0724 | 21.4643 | 20.3215 | 18.9257 | 17.2631 | 15.4549 | 13.0316 | 10.5796 | 2.8798 | -6.2438 | -13.5646 | -19.4624 | -22.5717 | 26.9483 | 20.901 | 18.4276 | 16.9442 | 13.5147 | 10.0393 | 5.3202 | -3.3044 | -12.0101 | -20.5051 | -43.8086 | -63.7547 | -79.0743 | -88.8771 | -85.1693 | 26.9483 | 20.901 | 18.4276 | 16.9442 | 13.5147 | 10.0393 | 5.3202 | -3.3044 | -12.0101 | -20.5051 | -43.8086 | -63.7547 | -79.0743 | -88.8771 | -85.1693 | 366150 | 402088 | KEARSLEY
| Barrow & Sandgate | 66.2962 | 64.5277 | 62.9006 | 46.5647 | 29.8205 | 27.3535 | 22.804 | 21.2399 | 19.7341 | 18.2803 | 10.7614 | -10.0358 | -17.5207 | -23.1824 | -27.5646 | 92.2962 | 90.5277 | 88.9006 | 72.5647 | 55.8205 | 53.3535 | 48.804 | 47.2399 | 45.7341 | 44.2803 | 36.7614 | 15.9642 | 8.4793 | 2.8176 | -1.5646 | 66.2962 | 65.3945 | 64.3224 | 48.3192 | 32.2295 | 31.4745 | 30.4935 | 29.335 | 28.5256 | 27.6986 | 25.2079 | 22.6263 | 20.7011 | 19.0384 | 13.8023 | 92.2962 | 91.3945 | 90.3224 | 74.3192 | 58.2295 | 57.4745 | 56.4935 | 55.335 | 54.5256 | 53.6986 | 51.2079 | 48.6263 | 46.7011 | 45.0384 | 39.8023 | 66.2962 | 64.3619 | 62.7717 | 46.4835 | 29.8806 | 27.593 | 23.199 | 21.8366 | 20.5738 | 19.3633 | 0.11328 | -18.275 | -24.5742 | -29.0038 | -31.6007 | 0 | 92.2962 | 90.3619 | 88.7717 | 72.4835 | 55.8806 | 53.593 | 49.199 | 47.8366 | 46.5738 | 45.3633 | 26.1133 | 7.725 | 1.4258 | -3.0038 | -5.6007 | 66.2962 | 65.8745 | 64.0722 | 48.0249 | 22.7745 | 20.8302 | 16.2158 | 13.0992 | -3.1771 | -5.7578 | -14.5981 | -22.2048 | -27.7906 | -29.7485 | -23.6181 | 0 | 92.2962 | 91.8745 | 90.0722 | 74.0249 | 48.7745 | 46.8302 | 42.2158 | 39.0992 | 22.8229 | 20.2422 | 11.4019 | 3.7952 | -1.7906 | -3.7485 | 2.3819 | 66.2962 | 65.0517 | 63.6102 | 47.4767 | 31.1842 | 29.2761 | 24.9261 | 23.5289 | 22.1314 | 20.6931 | 15.5045 | 0.1855 | -2.458 | -2.9105 | -1.4743 | 0 | 92.2962 | 91.0517 | 89.6102 | 73.4767 | 57.1842 | 55.2761 | 50.9261 | 49.5289 | 48.1314 | 46.6931 | 41.5045 | 26.1855 | 23.542 | 23.0895 | 24.5257 | 66.2962 | 64.9236 | 62.7345 | 46.401 | 20.8848 | 18.9498 | 14.2605 | 10.891 | -5.5718 | -8.336 | -17.7978 | -26.0387 | -32.7372 | -35.6319 | -29.8663 | 92.2962 | 90.9236 | 88.7345 | 72.401 | 46.8848 | 44.9498 | 40.2605 | 36.891 | 20.4282 | 17.664 | 8.2022 | -0.038721 | -6.7372 | -9.6319 | -3.8663 | 319709 | 470489 | HARKER
| Barton | 78.0713 | 63.762 | 50.1322 | 38.7909 | 34.9482 | 32.4443 | 29.9013 | 27.267 | 21.0717 | 13.7408 | -5.2295 | -35.5818 | -45.912 | -56.3427 | -64.4916 | 96.0713 | 81.762 | 68.1322 | 56.7909 | 52.9482 | 50.4443 | 47.9013 | 45.267 | 39.0717 | 31.7408 | 12.7705 | -17.5818 | -27.912 | -38.3427 | -46.4916 | 78.0713 | 74.0888 | 63.9499 | 54.6539 | 53.3351 | 52.4404 | 51.3446 | 49.9991 | 48.4396 | 46.8137 | 40.8496 | 35.035 | 28.8943 | 21.4636 | 16.4987 | 96.0713 | 92.0888 | 81.9499 | 72.6539 | 71.3351 | 70.4404 | 69.3446 | 67.9991 | 66.4396 | 64.8137 | 58.8496 | 53.035 | 46.8943 | 39.4636 | 34.4987 | 78.0713 | 61.3617 | 38.862 | 19.0249 | 14.6663 | 11.6319 | 8.5334 | 4.9726 | -4.3612 | -24.8437 | -115.9895 | -156.1249 | -166.1962 | -174.7357 | -177.6604 | 0 | 96.0713 | 79.3617 | 56.862 | 37.0249 | 32.6663 | 29.6319 | 26.5334 | 22.9726 | 13.6388 | -6.8437 | -97.9895 | -138.1249 | -148.1962 | -156.7357 | -159.6604 | 78.0713 | 66.2812 | 44.951 | 21.4658 | 9.965 | 7.4144 | 3.4187 | -6.3104 | -16.5443 | -34.0345 | -86.9625 | -125.4024 | -134.2136 | -139.9933 | -141.2663 | 0 | 96.0713 | 84.2812 | 62.951 | 39.4658 | 27.965 | 25.4144 | 21.4187 | 11.6896 | 1.4557 | -16.0345 | -68.9625 | -107.4024 | -116.2136 | -121.9933 | -123.2663 | 78.0713 | 70.0136 | 57.8038 | 46.7638 | 43.4166 | 41.3372 | 39.0782 | 36.6728 | 30.6025 | 23.3204 | 6.5448 | -19.085 | -25.5956 | -32.4416 | -37.3476 | 0 | 96.0713 | 88.0136 | 75.8038 | 64.7638 | 61.4166 | 59.3372 | 57.0782 | 54.6728 | 48.6025 | 41.3204 | 24.5448 | -1.085 | -7.5956 | -14.4416 | -19.3476 | 78.0713 | 59.9191 | 37.0591 | -6.9317 | -18.6909 | -41.5162 | -45.5386 | -75.59 | -81.736 | -107.0844 | -136.2184 | -175.8633 | -185.9048 | -192.6222 | -194.6589 | 96.0713 | 77.9191 | 55.0591 | 11.0683 | -0.69095 | -23.5162 | -27.5386 | -57.59 | -63.736 | -89.0844 | -118.2184 | -157.8633 | -167.9048 | -174.6222 | -176.6589 | 376758 | 397174 | CARRINGTON
| Belfield | 39.8326 | 37.4448 | 30.4001 | 23.8462 | 17.1031 | 10.3089 | 3.7059 | -2.8798 | -9.6996 | -16.4768 | -39.6363 | -66.4569 | -79.717 | -87.3612 | -93.941 | 39.8326 | 37.4448 | 30.4001 | 23.8462 | 17.1031 | 10.3089 | 3.7059 | -2.8798 | -9.6996 | -16.4768 | -39.6363 | -66.4569 | -79.717 | -87.3612 | -93.941 | 39.8326 | 38.86 | 38.2514 | 37.8206 | 37.3253 | 36.7873 | 36.0773 | 35.1365 | 34.2359 | 33.3177 | 30.4767 | 27.4709 | 24.4592 | 21.0806 | 18.6029 | 39.8326 | 38.86 | 38.2514 | 37.8206 | 37.3253 | 36.7873 | 36.0773 | 35.1365 | 34.2359 | 33.3177 | 30.4767 | 27.4709 | 24.4592 | 21.0806 | 18.6029 | 39.8326 | 37.171 | 30.1235 | 23.4218 | 16.527 | 9.6002 | 2.9881 | -3.384 | -9.881 | -16.4047 | -38.8498 | -65.1247 | -77.8888 | -84.8515 | -90.5609 | 0 | 39.8326 | 37.171 | 30.1235 | 23.4218 | 16.527 | 9.6002 | 2.9881 | -3.384 | -9.881 | -16.4047 | -38.8498 | -65.1247 | -77.8888 | -84.8515 | -90.5609 | 39.8326 | 38.5653 | 31.8609 | 25.2267 | 18.3309 | 11.3452 | 4.1444 | -4.4414 | -13.1997 | -21.9892 | -48.0812 | -73.8613 | -85.9791 | -89.8538 | -87.3987 | 0 | 39.8326 | 38.5653 | 31.8609 | 25.2267 | 18.3309 | 11.3452 | 4.1444 | -4.4414 | -13.1997 | -21.9892 | -48.0812 | -73.8613 | -85.9791 | -89.8538 | -87.3987 | 39.8326 | 38.4144 | 31.6504 | 25.269 | 18.8659 | 12.3828 | 5.9801 | -0.48525 | -7.2731 | -14.0709 | -34.8627 | -56.0002 | -64.1212 | -66.0512 | -67.0628 | 0 | 39.8326 | 38.4144 | 31.6504 | 25.269 | 18.8659 | 12.3828 | 5.9801 | -0.48525 | -7.2731 | -14.0709 | -34.8627 | -56.0002 | -64.1212 | -66.0512 | -67.0628 | 39.8326 | 37.4103 | 30.3028 | 23.4478 | 16.3512 | 9.2293 | 1.863 | -6.9396 | -15.8336 | -24.7627 | -51.3676 | -77.6911 | -90.3805 | -94.9548 | -93.2637 | 39.8326 | 37.4103 | 30.3028 | 23.4478 | 16.3512 | 9.2293 | 1.863 | -6.9396 | -15.8336 | -24.7627 | -51.3676 | -77.6911 | -90.3805 | -94.9548 | -93.2637 | 391033 | 413945 | ROCHDALE
| Bispham | 39.5033 | 35.6703 | 34.4976 | 33.9052 | 32.9517 | 31.9305 | 30.9528 | 29.9965 | 28.7525 | 23.128 | 14.3877 | -1.6444 | -16.8602 | -31.1345 | -43.7523 | 39.5033 | 35.6703 | 34.4976 | 33.9052 | 32.9517 | 31.9305 | 30.9528 | 29.9965 | 28.7525 | 23.128 | 14.3877 | -1.6444 | -16.8602 | -31.1345 | -43.7523 | 39.5033 | 38.3326 | 37.5896 | 36.8532 | 35.7916 | 34.605 | 33.0626 | 31.147 | 29.6329 | 28.0842 | 23.3336 | 18.371 | 12.6974 | 7.7254 | 4.2257 | 39.5033 | 38.3326 | 37.5896 | 36.8532 | 35.7916 | 34.605 | 33.0626 | 31.147 | 29.6329 | 28.0842 | 23.3336 | 18.371 | 12.6974 | 7.7254 | 4.2257 | 39.5033 | 35.2597 | 34.0659 | 33.6423 | 32.881 | 32.1021 | 31.497 | 31.0408 | 30.3531 | 29.7075 | 21.2539 | 0.9554 | -11.2776 | -24.4086 | -36.1713 | 0 | 39.5033 | 35.2597 | 34.0659 | 33.6423 | 32.881 | 32.1021 | 31.497 | 31.0408 | 30.3531 | 29.7075 | 21.2539 | 0.9554 | -11.2776 | -24.4086 | -36.1713 | 39.5033 | 37.8526 | 37.3234 | 37.0041 | 35.9038 | 34.884 | 33.0724 | 27.4621 | 18.118 | 12.2465 | -2.0869 | -15.9879 | -27.0506 | -34.1822 | -29.7199 | 0 | 39.5033 | 37.8526 | 37.3234 | 37.0041 | 35.9038 | 34.884 | 33.0724 | 27.4621 | 18.118 | 12.2465 | -2.0869 | -15.9879 | -27.0506 | -34.1822 | -29.7199 | 39.5033 | 38.0913 | 37.5931 | 37.442 | 37.1423 | 36.6361 | 36.0043 | 35.3317 | 34.2382 | 28.6503 | 24.5584 | 19.344 | 13.5999 | 9.7343 | 7.6855 | 0 | 39.5033 | 38.0913 | 37.5931 | 37.442 | 37.1423 | 36.6361 | 36.0043 | 35.3317 | 34.2382 | 28.6503 | 24.5584 | 19.344 | 13.5999 | 9.7343 | 7.6855 | 39.5033 | 35.8581 | 34.5166 | 33.6 | 31.9651 | 30.6039 | 28.3861 | 22.2003 | 12.4499 | 6.1773 | -9.4051 | -24.392 | -36.4714 | -44.7263 | -41.3602 | 39.5033 | 35.8581 | 34.5166 | 33.6 | 31.9651 | 30.6039 | 28.3861 | 22.2003 | 12.4499 | 6.1773 | -9.4051 | -24.392 | -36.4714 | -44.7263 | -41.3602 | 332328 | 439711 | PENWORTHAM
| Blackburn | 46.4952 | 41.1861 | 39.0914 | 37.8537 | 36.3301 | 34.7467 | 33.0726 | 31.4985 | 29.7274 | 27.9449 | 20.2888 | 9.8912 | 0.2511 | -9.8972 | -18.4828 | 46.4952 | 41.1861 | 39.0914 | 37.8537 | 36.3301 | 34.7467 | 33.0726 | 31.4985 | 29.7274 | 27.9449 | 20.2888 | 9.8912 | 0.2511 | -9.8972 | -18.4828 | 46.4952 | 44.558 | 43.5889 | 42.9129 | 42.1348 | 41.2425 | 40.1061 | 38.7056 | 37.6182 | 36.4999 | 33.2214 | 30.0286 | 26.9805 | 23.7452 | 21.4634 | 46.4952 | 44.558 | 43.5889 | 42.9129 | 42.1348 | 41.2425 | 40.1061 | 38.7056 | 37.6182 | 36.4999 | 33.2214 | 30.0286 | 26.9805 | 23.7452 | 21.4634 | 46.4952 | 40.4297 | 38.092 | 36.7605 | 35.0828 | 33.2649 | 31.4072 | 29.756 | 28.0587 | 26.3613 | 18.845 | 8.541 | 0.21336 | -8.4854 | -16.0382 | 0 | 46.4952 | 40.4297 | 38.092 | 36.7605 | 35.0828 | 33.2649 | 31.4072 | 29.756 | 28.0587 | 26.3613 | 18.845 | 8.541 | 0.21336 | -8.4854 | -16.0382 | 46.4952 | 42.8148 | 41.0215 | 39.7996 | 38.2513 | 36.4889 | 34.0478 | 30.0122 | 25.5208 | 21.0695 | 8.9588 | -1.412 | -9.788 | -14.9016 | -11.112 | 0 | 46.4952 | 42.8148 | 41.0215 | 39.7996 | 38.2513 | 36.4889 | 34.0478 | 30.0122 | 25.5208 | 21.0695 | 8.9588 | -1.412 | -9.788 | -14.9016 | -11.112 | 46.4952 | 43.0227 | 41.3644 | 40.377 | 39.3713 | 38.2641 | 36.784 | 35.3704 | 33.6879 | 31.9278 | 26.7116 | 21.9827 | 18.653 | 15.8307 | 14.8264 | 0 | 46.4952 | 43.0227 | 41.3644 | 40.377 | 39.3713 | 38.2641 | 36.784 | 35.3704 | 33.6879 | 31.9278 | 26.7116 | 21.9827 | 18.653 | 15.8307 | 14.8264 | 46.4952 | 40.431 | 37.9799 | 36.4466 | 34.6163 | 32.7729 | 30.2666 | 25.7177 | 21.0798 | 16.4841 | 3.8138 | -7.3133 | -16.5011 | -22.5964 | -19.8265 | 46.4952 | 40.431 | 37.9799 | 36.4466 | 34.6163 | 32.7729 | 30.2666 | 25.7177 | 21.0798 | 16.4841 | 3.8138 | -7.3133 | -16.5011 | -22.5964 | -19.8265 | 370584 | 429294 | PENWORTHAM
| Blackpool | 46.7396 | 34.7463 | 24.0066 | 19.9545 | 14.8549 | 2.2646 | -7.1825 | -10.0845 | -13.0749 | -15.2275 | -26.274 | -42.8205 | -56.6367 | -71.5386 | -84.4482 | 47.5796 | 35.5863 | 24.8466 | 20.7945 | 15.6949 | 3.1046 | -6.3425 | -9.2445 | -12.2349 | -14.3875 | -25.434 | -41.9805 | -55.7967 | -70.6986 | -83.6082 | 46.7396 | 42.7147 | 35.5812 | 33.939 | 31.7902 | 27.1101 | 23.0288 | 20.5531 | 19.187 | 18.0264 | 14.365 | 10.4621 | 6.7076 | 2.5957 | -0.57573 | 47.5796 | 43.5547 | 36.4212 | 34.779 | 32.6302 | 27.9501 | 23.8688 | 21.3931 | 20.027 | 18.8664 | 15.205 | 11.3021 | 7.5476 | 3.4357 | 0.26427 | 46.7396 | 33.3826 | -4.8803 | -36.1197 | -41.5243 | -54.3903 | -64.0031 | -67.1419 | -70.2289 | -72.5753 | -82.7209 | -98.5271 | -111.6468 | -125.6248 | -136.9925 | 0 | 47.5796 | 34.2226 | -4.0403 | -35.2797 | -40.6843 | -53.5503 | -63.1631 | -66.3019 | -69.3889 | -71.7353 | -81.8809 | -97.6871 | -110.8068 | -124.7848 | -136.1525 | 46.7396 | 37.8672 | 0.57933 | -30.525 | -35.9008 | -48.8206 | -59.5768 | -67.2467 | -75.15 | -82.3317 | -100.2832 | -115.1516 | -126.9855 | -134.3418 | -128.6289 | 0 | 47.5796 | 38.7072 | 1.4193 | -29.685 | -35.0608 | -47.9806 | -58.7368 | -66.4067 | -74.31 | -81.4917 | -99.4432 | -114.3116 | -126.1455 | -133.5018 | -127.7889 | 46.7396 | 38.4871 | 28.5485 | 24.8131 | 20.3225 | 8.3982 | -0.56842 | -3.2266 | -6.1732 | -8.404 | -14.4356 | -18.8462 | -21.9 | -24.9287 | -26.1195 | 0 | 47.5796 | 39.3271 | 29.3885 | 25.6531 | 21.1625 | 9.2382 | 0.27158 | -2.3866 | -5.3332 | -7.564 | -13.5956 | -18.0062 | -21.06 | -24.0887 | -25.2795 | 46.7396 | 33.0987 | -5.4123 | -37.0249 | -42.8834 | -56.1756 | -67.3768 | -75.5998 | -83.7713 | -91.2333 | -110.129 | -125.8584 | -138.601 | -147.1411 | -142.7929 | 47.5796 | 33.9387 | -4.5723 | -36.1849 | -42.0434 | -55.3356 | -66.5368 | -74.7598 | -82.9313 | -90.3933 | -109.289 | -125.0184 | -137.761 | -146.3011 | -141.9529 | 330835 | 435308 | PENWORTHAM
| Bloom St | 37.0849 | 27.6301 | 24.5951 | 23.4699 | 22.4991 | 21.5405 | 20.9871 | 20.4142 | 19.4949 | 18.6123 | 15.5688 | 11.9628 | 9.323 | 6.756 | 4.67 | 78.8849 | 69.4301 | 66.3951 | 65.2699 | 64.2991 | 63.3405 | 62.7871 | 62.2142 | 61.2949 | 60.4123 | 57.3688 | 53.7628 | 51.123 | 48.556 | 46.47 | 37.0849 | 34.0556 | 32.6293 | 31.8541 | 31.2293 | 30.5822 | 29.8815 | 29.0479 | 28.0218 | 26.9985 | 24.1605 | 21.5413 | 19.4393 | 17.1966 | 15.0619 | 78.8849 | 75.8556 | 74.4293 | 73.6541 | 73.0293 | 72.3822 | 71.6815 | 70.8479 | 69.8218 | 68.7985 | 65.9605 | 63.3413 | 61.2393 | 58.9966 | 56.8619 | 37.0849 | 26.134 | 18.9605 | 13.9652 | 12.9009 | 11.8415 | 11.1698 | 10.4737 | 9.5971 | 8.7729 | 5.8932 | 2.6734 | 0.58041 | -1.1419 | -2.0346 | 0 | 78.8849 | 67.934 | 60.7605 | 55.7652 | 54.7009 | 53.6415 | 52.9698 | 52.2737 | 51.3971 | 50.5729 | 47.6932 | 44.4734 | 42.3804 | 40.6581 | 39.7654 | 37.0849 | 29.2334 | 22.7767 | 17.9022 | 16.9429 | 15.9513 | 15.2195 | 14.1262 | 12.7897 | 11.5084 | 8.0104 | 5.0278 | 3.1864 | 2.214 | 2.8199 | 0 | 78.8849 | 71.0334 | 64.5767 | 59.7022 | 58.7429 | 57.7513 | 57.0195 | 55.9262 | 54.5897 | 53.3084 | 49.8104 | 46.8278 | 44.9864 | 44.014 | 44.6199 | 37.0849 | 31.2816 | 29.0346 | 27.9916 | 27.1455 | 26.2798 | 25.7735 | 25.2311 | 24.3094 | 23.3977 | 20.8348 | 18.4789 | 16.9114 | 15.4362 | 14.5603 | 0 | 78.8849 | 73.0816 | 70.8346 | 69.7916 | 68.9455 | 68.0798 | 67.5735 | 67.0311 | 66.1094 | 65.1977 | 62.6348 | 60.2789 | 58.7114 | 57.2362 | 56.3603 | 37.0849 | 24.8997 | 17.4624 | 12.4556 | 11.3763 | 10.3134 | 9.5203 | 8.3142 | 6.9306 | 5.6087 | 2.0316 | -0.98823 | -2.8771 | -3.9163 | -3.4681 | 78.8849 | 66.6997 | 59.2624 | 54.2556 | 53.1763 | 52.1134 | 51.3203 | 50.1142 | 48.7306 | 47.4087 | 43.8316 | 40.8118 | 38.9229 | 37.8837 | 38.3319 | 384221 | 397717 | SOUTH MANCHESTER
| Bolton | 42.126 | 36.879 | 34.5938 | 33.032 | 30.2658 | 36.3054 | 33.4974 | 30.3034 | 27.4001 | 24.5811 | 7.6856 | -19.284 | -40.8794 | -60.9325 | -76.5059 | 51.126 | 45.879 | 43.5938 | 42.032 | 39.2658 | 36.3054 | 33.4974 | 30.3034 | 27.4001 | 24.5811 | 7.6856 | -19.284 | -40.8794 | -60.9325 | -76.5059 | 42.126 | 39.935 | 38.5013 | 37.158 | 35.3483 | 42.3262 | 39.7382 | 36.5138 | 34.3174 | 31.9888 | 24.3404 | 16.1683 | 7.3166 | -1.0666 | -7.0685 | 51.126 | 48.935 | 47.5013 | 46.158 | 44.3483 | 42.3262 | 39.7382 | 36.5138 | 34.3174 | 31.9888 | 24.3404 | 16.1683 | 7.3166 | -1.0666 | -7.0685 | 42.126 | 35.9604 | 33.2542 | 31.4671 | 28.501 | 33.7715 | 30.9283 | 28.1972 | 25.2995 | 22.3047 | 3.5699 | -22.3335 | -41.2026 | -57.7286 | -68.013 | 0 | 51.126 | 44.9604 | 42.2542 | 40.4671 | 37.501 | 33.7715 | 30.9283 | 28.1972 | 25.2995 | 22.3047 | 3.5699 | -22.3335 | -41.2026 | -57.7286 | -68.013 | 42.126 | 39.641 | 37.9264 | 35.1366 | 31.7131 | 37.5487 | 33.1064 | 24.086 | 14.8657 | 5.7471 | -20.1944 | -43.2489 | -59.1081 | -66.6919 | -58.5318 | 0 | 51.126 | 48.641 | 46.9264 | 44.1366 | 40.7131 | 37.5487 | 33.1064 | 24.086 | 14.8657 | 5.7471 | -20.1944 | -43.2489 | -59.1081 | -66.6919 | -58.5318 | 42.126 | 39.1211 | 37.5861 | 36.6646 | 35.2032 | 42.4297 | 40.3677 | 37.5264 | 34.652 | 31.6517 | 21.402 | 9.0848 | -0.076161 | -7.4268 | -11.0524 | 0 | 51.126 | 48.1211 | 46.5861 | 45.6646 | 44.2032 | 42.4297 | 40.3677 | 37.5264 | 34.652 | 31.6517 | 21.402 | 9.0848 | -0.076161 | -7.4268 | -11.0524 | 42.126 | 37.2259 | 34.4306 | 30.8802 | 26.7625 | 32.1351 | 26.8633 | 16.8059 | 6.8228 | -3.0744 | -31.593 | -57.1711 | -74.765 | -84.4096 | -78.571 | 51.126 | 46.2259 | 43.4306 | 39.8802 | 35.7625 | 32.1351 | 26.8633 | 16.8059 | 6.8228 | -3.0744 | -31.593 | -57.1711 | -74.765 | -84.4096 | -78.571 | 372255 | 410566 | KEARSLEY
| Burnley | 66.5986 | 62.3039 | 60.8983 | 60.21 | 59.2585 | 58.262 | 57.3814 | 56.7682 | 55.9803 | 55.2766 | 49.1638 | 37.6476 | 27.8939 | 17.5952 | 9.2009 | 66.5986 | 62.3039 | 60.8983 | 60.21 | 59.2585 | 58.262 | 57.3814 | 56.7682 | 55.9803 | 55.2766 | 49.1638 | 37.6476 | 27.8939 | 17.5952 | 9.2009 | 66.5986 | 64.7687 | 63.8721 | 63.218 | 62.4512 | 61.5983 | 60.5262 | 59.2395 | 58.2577 | 57.2743 | 54.2831 | 51.15 | 48.2516 | 44.9649 | 42.8722 | 66.5986 | 64.7687 | 63.8721 | 63.218 | 62.4512 | 61.5983 | 60.5262 | 59.2395 | 58.2577 | 57.2743 | 54.2831 | 51.15 | 48.2516 | 44.9649 | 42.8722 | 66.5986 | 61.7538 | 60.3213 | 59.7733 | 58.9617 | 58.1269 | 57.4783 | 57.0539 | 56.3255 | 55.6862 | 50.8064 | 40.0637 | 30.8939 | 21.3407 | 13.8669 | 0 | 66.5986 | 61.7538 | 60.3213 | 59.7733 | 58.9617 | 58.1269 | 57.4783 | 57.0539 | 56.3255 | 55.6862 | 50.8064 | 40.0637 | 30.8939 | 21.3407 | 13.8669 | 66.5986 | 63.8997 | 62.9659 | 62.5482 | 61.7874 | 60.928 | 59.4683 | 55.9083 | 52.2073 | 48.535 | 38.0074 | 27.7757 | 19.4498 | 14.2214 | 18.3025 | 0 | 66.5986 | 63.8997 | 62.9659 | 62.5482 | 61.7874 | 60.928 | 59.4683 | 55.9083 | 52.2073 | 48.535 | 38.0074 | 27.7757 | 19.4498 | 14.2214 | 18.3025 | 66.5986 | 63.6869 | 62.6359 | 62.1787 | 61.6938 | 61.1191 | 60.4727 | 59.9619 | 59.1535 | 58.3502 | 55.512 | 52.3222 | 49.7008 | 47.1016 | 46.149 | 0 | 66.5986 | 63.6869 | 62.6359 | 62.1787 | 61.6938 | 61.1191 | 60.4727 | 59.9619 | 59.1535 | 58.3502 | 55.512 | 52.3222 | 49.7008 | 47.1016 | 46.149 | 66.5986 | 61.8222 | 60.2921 | 59.5717 | 58.5326 | 57.4798 | 55.7877 | 51.9118 | 48.0114 | 44.1315 | 32.9081 | 21.9429 | 12.853 | 6.5838 | 9.4473 | 66.5986 | 61.8222 | 60.2921 | 59.5717 | 58.5326 | 57.4798 | 55.7877 | 51.9118 | 48.0114 | 44.1315 | 32.9081 | 21.9429 | 12.853 | 6.5838 | 9.4473 | 385569 | 434469 | ROCHDALE
| Bury | 46.1752 | 41.2365 | 39.0176 | 37.7246 | 35.7804 | 33.6134 | 31.671 | 29.6294 | 27.388 | 25.1877 | 12.1385 | -8.4568 | -24.7879 | -42.0707 | -57.0549 | 46.1752 | 41.2365 | 39.0176 | 37.7246 | 35.7804 | 33.6134 | 31.671 | 29.6294 | 27.388 | 25.1877 | 12.1385 | -8.4568 | -24.7879 | -42.0707 | -57.0549 | 46.1752 | 44.5563 | 43.4744 | 42.6255 | 41.5903 | 40.1044 | 38.2598 | 35.9713 | 33.9774 | 31.888 | 25.2854 | 18.3005 | 11.5957 | 4.3004 | -1.0166 | 46.1752 | 44.5563 | 43.4744 | 42.6255 | 41.5903 | 40.1044 | 38.2598 | 35.9713 | 33.9774 | 31.888 | 25.2854 | 18.3005 | 11.5957 | 4.3004 | -1.0166 | 46.1752 | 40.5519 | 35.2132 | 30.9343 | 28.6806 | 26.2234 | 23.9354 | 21.7032 | 19.5322 | 17.4499 | 6.982 | -11.7272 | -27.1184 | -43.1288 | -56.5723 | 0 | 46.1752 | 40.5519 | 35.2132 | 30.9343 | 28.6806 | 26.2234 | 23.9354 | 21.7032 | 19.5322 | 17.4499 | 6.982 | -11.7272 | -27.1184 | -43.1288 | -56.5723 | 46.1752 | 43.2772 | 38.7317 | 34.8017 | 32.7087 | 30.1954 | 27.0335 | 21.2707 | 14.5806 | 7.8278 | -11.5702 | -30.0775 | -44.168 | -53.7915 | -49.9059 | 0 | 46.1752 | 43.2772 | 38.7317 | 34.8017 | 32.7087 | 30.1954 | 27.0335 | 21.2707 | 14.5806 | 7.8278 | -11.5702 | -30.0775 | -44.168 | -53.7915 | -49.9059 | 46.1752 | 43.7339 | 42.2445 | 41.3693 | 40.1332 | 38.603 | 36.9833 | 35.1916 | 33.0605 | 30.8853 | 23.1854 | 14.4221 | 7.9074 | 2.1138 | -1.0163 | 0 | 46.1752 | 43.7339 | 42.2445 | 41.3693 | 40.1332 | 38.603 | 36.9833 | 35.1916 | 33.0605 | 30.8853 | 23.1854 | 14.4221 | 7.9074 | 2.1138 | -1.0163 | 46.1752 | 40.9691 | 35.6115 | 31.1207 | 28.6012 | 25.959 | 22.3918 | 15.3358 | 8.3212 | 1.2409 | -19.2361 | -39.1049 | -54.5757 | -65.7482 | -63.4879 | 46.1752 | 40.9691 | 35.6115 | 31.1207 | 28.6012 | 25.959 | 22.3918 | 15.3358 | 8.3212 | 1.2409 | -19.2361 | -39.1049 | -54.5757 | -65.7482 | -63.4879 | 380272 | 411184 | KEARSLEY
| Buxton | 12.5387 | 11.9194 | 11.04 | 10.5869 | 10.2711 | 9.942 | 9.6747 | 6.7768 | 0.32223 | -0.27977 | -8.7159 | -13.143 | -17.1071 | -19.5641 | -20.6455 | 12.5387 | 11.9194 | 11.04 | 10.5869 | 10.2711 | 9.942 | 9.6747 | 6.7768 | 0.32223 | -0.27977 | -8.7159 | -13.143 | -17.1071 | -19.5641 | -20.6455 | 12.5387 | 12.2158 | 11.3832 | 10.9028 | 10.6266 | 10.4081 | 10.125 | 7.0759 | 6.265 | 5.4468 | 2.7314 | 0.18636 | -2.1866 | -14.9391 | -16.5215 | 12.5387 | 12.2158 | 11.3832 | 10.9028 | 10.6266 | 10.4081 | 10.125 | 7.0759 | 6.265 | 5.4468 | 2.7314 | 0.18636 | -2.1866 | -14.9391 | -16.5215 | 12.5387 | 11.8515 | -26.7895 | -64.914 | -65.2757 | -65.6577 | -65.937 | -68.4201 | -73.4021 | -73.6331 | -80.3846 | -86.5171 | -89.3672 | -90.0875 | -88.735 | 0 | 12.5387 | 11.8515 | -26.7895 | -64.914 | -65.2757 | -65.6577 | -65.937 | -68.4201 | -73.4021 | -73.6331 | -80.3846 | -86.5171 | -89.3672 | -90.0875 | -88.735 | 12.5387 | 12.3594 | -26.1411 | -64.2253 | -64.6639 | -65.0507 | -65.568 | -68.7848 | -74.4441 | -79.1611 | -84.2953 | -86.9014 | -88.2064 | -87.4961 | -83.8227 | 0 | 12.5387 | 12.3594 | -26.1411 | -64.2253 | -64.6639 | -65.0507 | -65.568 | -68.7848 | -74.4441 | -79.1611 | -84.2953 | -86.9014 | -88.2064 | -87.4961 | -83.8227 | 12.5387 | 12.1856 | 11.3979 | 11.0307 | 10.8901 | 10.7561 | 10.6461 | 7.8442 | 1.4288 | 0.83529 | -6.5175 | -8.5646 | -10.6341 | -11.2968 | -10.854 | 0 | 12.5387 | 12.1856 | 11.3979 | 11.0307 | 10.8901 | 10.7561 | 10.6461 | 7.8442 | 1.4288 | 0.83529 | -6.5175 | -8.5646 | -10.6341 | -11.2968 | -10.854 | 12.5387 | 12.0939 | -26.5527 | -64.7574 | -65.3059 | -65.768 | -66.3716 | -69.6943 | -75.3925 | -80.1525 | -85.5177 | -88.435 | -90.0582 | -89.6685 | -86.3084 | 12.5387 | 12.0939 | -26.5527 | -64.7574 | -65.3059 | -65.768 | -66.3716 | -69.6943 | -75.3925 | -80.1525 | -85.5177 | -88.435 | -90.0582 | -89.6685 | -86.3084 | 407769 | 375476 | STALYBRIDGE
| Carlisle | 36.9232 | 24.3328 | 19.5619 | 16.658 | 12.9682 | 8.994 | 4.6125 | -1.3418 | -5.6826 | -10.115 | -32.7675 | -64.0641 | -89.6782 | -108.2518 | -123.948 | 58.1232 | 45.5328 | 40.7619 | 37.858 | 34.1682 | 30.194 | 25.8125 | 19.8582 | 15.5174 | 11.085 | -11.5675 | -42.8641 | -68.4782 | -87.0518 | -102.748 | 36.9232 | 32.5881 | 29.0125 | 25.7773 | 22.2736 | 18.6936 | 14.5088 | 9.5737 | 5.4345 | 1.2176 | -11.8587 | -26.2444 | -41.821 | -54.8985 | -61.3649 | 58.1232 | 53.7881 | 50.2125 | 46.9773 | 43.4736 | 39.8936 | 35.7088 | 30.7737 | 26.6345 | 22.4176 | 9.3413 | -5.0444 | -20.621 | -33.6985 | -40.1649 | 36.9232 | 22.6535 | 17.146 | 13.9924 | 10.0566 | 5.9153 | 1.5972 | -6.022 | -9.8285 | -13.7659 | -38.7527 | -70.6105 | -97.0522 | -115.536 | -128.8799 | 0 | 58.1232 | 43.8535 | 38.346 | 35.1924 | 31.2566 | 27.1153 | 22.7972 | 15.178 | 11.3715 | 7.4341 | -17.5527 | -49.4105 | -75.8522 | -94.336 | -107.6799 | 36.9232 | 28.5402 | 24.2522 | 20.485 | 12.4877 | 2.933 | -3.5597 | -13.6934 | -23.354 | -33.2951 | -63.7469 | -92.5667 | -115.8356 | -125.7461 | -117.1016 | 0 | 58.1232 | 49.7402 | 45.4522 | 41.685 | 33.6877 | 24.133 | 17.6403 | 7.5066 | -2.154 | -12.0951 | -42.5469 | -71.3667 | -94.6356 | -104.5461 | -95.9016 | 36.9232 | 30.2332 | 26.6584 | 24.1694 | 21.5588 | 18.7995 | 15.3167 | 9.8974 | 5.7548 | 1.4909 | -15.2258 | -33.1673 | -46.641 | -52.5828 | -54.0383 | 0 | 58.1232 | 51.4332 | 47.8584 | 45.3694 | 42.7588 | 39.9995 | 36.5167 | 31.0974 | 26.9548 | 22.6909 | 5.9742 | -11.9673 | -25.441 | -31.3828 | -32.8383 | 36.9232 | 22.4311 | 16.5401 | 12.0821 | 3.4565 | -6.517 | -13.483 | -24.2133 | -34.1131 | -44.2987 | -76.1663 | -106.8783 | -132.0671 | -143.9079 | -137.0727 | 58.1232 | 43.6311 | 37.7401 | 33.2821 | 24.6565 | 14.683 | 7.717 | -3.0133 | -12.9131 | -23.0987 | -54.9663 | -85.6783 | -110.8671 | -122.7079 | -115.8727 | 338655 | 556583 | HARKER
| Carlisle North | 9.6115 | 4.7571 | 3.7399 | 3.5488 | 3.3641 | 3.1063 | 2.7458 | 2.2518 | 1.5785 | 0.82501 | -1.5468 | -3.8698 | -5.4611 | -6.488 | -6.9697 | 30.1115 | 25.2571 | 24.2399 | 24.0488 | 23.8641 | 23.6063 | 23.2458 | 22.7518 | 22.0785 | 21.325 | 18.9532 | 16.6302 | 15.0389 | 14.012 | 13.5303 | 9.6115 | 7.7787 | 7.263 | 7.0461 | 6.8409 | 6.5798 | 6.2565 | 5.8611 | 5.5292 | 5.15 | 3.7266 | 1.9713 | 0.16779 | -1.725 | -2.8956 | 30.1115 | 28.2787 | 27.763 | 27.5461 | 27.3409 | 27.0798 | 26.7565 | 26.3611 | 26.0292 | 25.65 | 24.2266 | 22.4713 | 20.6678 | 18.775 | 17.6044 | 9.6115 | 3.9637 | 2.8137 | 2.6342 | 2.4758 | 2.2636 | 1.9747 | 1.5831 | 1.081 | 0.49847 | -1.6317 | -4.0004 | -5.7751 | -6.7671 | -6.9557 | 0 | 30.1115 | 24.4637 | 23.3137 | 23.1342 | 22.9758 | 22.7636 | 22.4747 | 22.0831 | 21.581 | 20.9985 | 18.8683 | 16.4996 | 14.7249 | 13.7329 | 13.5443 | 9.6115 | 5.6085 | 4.7911 | 4.6647 | 4.5438 | 4.331 | 4.0066 | 3.55 | 2.9185 | 2.1997 | -0.7424 | -3.105 | -4.4721 | -5.0228 | -4.5767 | 0 | 30.1115 | 26.1085 | 25.2911 | 25.1647 | 25.0438 | 24.831 | 24.5066 | 24.05 | 23.4185 | 22.6997 | 19.7576 | 17.395 | 16.0279 | 15.4772 | 15.9233 | 9.6115 | 6.1419 | 5.3911 | 5.2469 | 5.1213 | 4.9187 | 4.6268 | 4.249 | 3.7225 | 3.1194 | 0.99898 | -0.96976 | -2.435 | -3.2556 | -3.2826 | 0 | 30.1115 | 26.6419 | 25.8911 | 25.7469 | 25.6213 | 25.4187 | 25.1268 | 24.749 | 24.2225 | 23.6194 | 21.499 | 19.5302 | 18.065 | 17.2444 | 17.2174 | 9.6115 | 3.181 | 1.3765 | 0.67783 | 0.000146 | -0.73075 | -1.5453 | -2.484 | -3.5331 | -4.6628 | -7.8832 | -10.5913 | -12.3365 | -13.1146 | -12.7294 | 30.1115 | 23.681 | 21.8765 | 21.1778 | 20.5001 | 19.7693 | 18.9547 | 18.016 | 16.9669 | 15.8372 | 12.6168 | 9.9087 | 8.1635 | 7.3854 | 7.7706 | 338547 | 560280 | HARKER
| Carrington BSP | 32.4336 | 31.924 | 31.6607 | 23.9197 | 16.1422 | 15.8902 | 14.426 | 14.0208 | 13.4987 | 12.9398 | 5.9619 | -1.2373 | -6.5235 | -10.5591 | -14.3461 | 53.4336 | 52.924 | 52.6607 | 44.9197 | 37.1422 | 36.8902 | 35.426 | 35.0208 | 34.4987 | 33.9398 | 26.9619 | 19.7627 | 14.4765 | 10.4409 | 6.6539 | 32.4336 | 32.2427 | 32.0326 | 24.2823 | 16.5206 | 16.2946 | 16.0094 | 15.6042 | 15.2547 | 14.878 | 13.5828 | 11.0356 | 8.1202 | 0.42616 | -15.4916 | 53.4336 | 53.2427 | 53.0326 | 45.2823 | 37.5206 | 37.2946 | 37.0094 | 36.6042 | 36.2547 | 35.878 | 34.5828 | 32.0356 | 29.1202 | 21.4262 | 5.5084 | 32.4336 | 31.8495 | 31.5723 | 23.8302 | 15.9777 | 15.6626 | 14.164 | 13.7222 | 13.0435 | 12.1232 | 4.5239 | -9.3131 | -14.6191 | -19.9111 | -23.3722 | 0 | 53.4336 | 52.8495 | 52.5723 | 44.8302 | 36.9777 | 36.6626 | 35.164 | 34.7222 | 34.0435 | 33.1232 | 25.5239 | 11.6869 | 6.3809 | 1.0889 | -2.3722 | 32.4336 | 32.1833 | 28.9182 | 21.4345 | 13.8125 | 13.6725 | 12.2672 | 10.679 | 8.581 | -0.76631 | -8.2893 | -13.8356 | -18.5913 | -22.0726 | -20.8777 | 0 | 53.4336 | 53.1833 | 49.9182 | 42.4345 | 34.8125 | 34.6725 | 33.2672 | 31.679 | 29.581 | 20.2337 | 12.7107 | 7.1644 | 2.4087 | -1.0726 | 0.12233 | 32.4336 | 32.2042 | 32.0317 | 24.3551 | 16.6699 | 16.4938 | 15.091 | 14.7698 | 14.3416 | 13.8705 | 9.228 | 4.6461 | 1.7093 | 0.49095 | 0.12564 | 0 | 53.4336 | 53.2042 | 53.0317 | 45.3551 | 37.6699 | 37.4938 | 36.091 | 35.7698 | 35.3416 | 34.8705 | 30.228 | 25.6461 | 22.7093 | 21.491 | 21.1256 | 32.4336 | 31.9333 | 28.5661 | 21.0179 | 13.3463 | 13.2003 | 11.5297 | 9.6388 | 7.5683 | -1.7601 | -9.486 | -15.526 | -20.8013 | -24.735 | -23.8811 | 53.4336 | 52.9333 | 49.5661 | 42.0179 | 34.3463 | 34.2003 | 32.5297 | 30.6388 | 28.5683 | 19.2399 | 11.514 | 5.474 | 0.19871 | -3.735 | -2.8811 | 373110 | 393020 | CARRINGTON
| Castleton | 45.287 | 39.2071 | 36.0227 | 32.7435 | 29.2051 | 25.5501 | 21.3512 | 20.061 | 18.4742 | 16.8994 | 9.0197 | -2.8032 | -12.7417 | -22.6494 | -33.7635 | 45.287 | 39.2071 | 36.0227 | 32.7435 | 29.2051 | 25.5501 | 21.3512 | 20.061 | 18.4742 | 16.8994 | 9.0197 | -2.8032 | -12.7417 | -22.6494 | -33.7635 | 45.287 | 43.4109 | 42.4014 | 41.7196 | 41.0284 | 40.2806 | 39.3103 | 37.9809 | 36.5976 | 35.1783 | 30.6918 | 25.7745 | 20.4939 | 14.3652 | 9.1897 | 45.287 | 43.4109 | 42.4014 | 41.7196 | 41.0284 | 40.2806 | 39.3103 | 37.9809 | 36.5976 | 35.1783 | 30.6918 | 25.7745 | 20.4939 | 14.3652 | 9.1897 | 45.287 | 38.2998 | 34.9351 | 31.1932 | 27.2266 | 23.1584 | 18.4653 | 17.2502 | 15.9085 | 14.5887 | 6.815 | -4.6285 | -13.6721 | -22.4202 | -30.7917 | 0 | 45.287 | 38.2998 | 34.9351 | 31.1932 | 27.2266 | 23.1584 | 18.4653 | 17.2502 | 15.9085 | 14.5887 | 6.815 | -4.6285 | -13.6721 | -22.4202 | -30.7917 | 45.287 | 40.8474 | 38.1184 | 33.9286 | 29.4824 | 24.941 | 20.2042 | 16.6464 | 12.7957 | 8.9553 | -2.3639 | -13.128 | -22.3204 | -28.876 | -26.4362 | 0 | 45.287 | 40.8474 | 38.1184 | 33.9286 | 29.4824 | 24.941 | 20.2042 | 16.6464 | 12.7957 | 8.9553 | -2.3639 | -13.128 | -22.3204 | -28.876 | -26.4362 | 45.287 | 42.2479 | 39.7898 | 36.7682 | 33.7413 | 30.5647 | 26.7119 | 25.6632 | 24.1683 | 22.615 | 17.3857 | 11.7619 | 7.4217 | 4.0273 | 2.1178 | 0 | 45.287 | 42.2479 | 39.7898 | 36.7682 | 33.7413 | 30.5647 | 26.7119 | 25.6632 | 24.1683 | 22.615 | 17.3857 | 11.7619 | 7.4217 | 4.0273 | 2.1178 | 45.287 | 38.0113 | 34.5231 | 30.0929 | 25.4451 | 20.8346 | 16.0736 | 12.3981 | 8.5133 | 4.6444 | -6.8974 | -18.0779 | -28.5503 | -36.6688 | -35.6738 | 45.287 | 38.0113 | 34.5231 | 30.0929 | 25.4451 | 20.8346 | 16.0736 | 12.3981 | 8.5133 | 4.6444 | -6.8974 | -18.0779 | -28.5503 | -36.6688 | -35.6738 | 388461 | 411290 | ROCHDALE
| Chadderton | 34.2862 | 26.0303 | 23.375 | 21.9179 | 20.0181 | 17.6088 | 14.8637 | 12.1292 | 9.0299 | 6.0469 | -8.1734 | -28.4738 | -44.1508 | -58.8714 | -70.8757 | 34.2862 | 26.0303 | 23.375 | 21.9179 | 20.0181 | 17.6088 | 14.8637 | 12.1292 | 9.0299 | 6.0469 | -8.1734 | -28.4738 | -44.1508 | -58.8714 | -70.8757 | 34.2862 | 31.8984 | 30.7937 | 29.8539 | 28.8426 | 27.7701 | 26.3897 | 23.856 | 21.222 | 18.4824 | 10.0472 | 1.5148 | -6.5831 | -15.1422 | -21.0448 | 34.2862 | 31.8984 | 30.7937 | 29.8539 | 28.8426 | 27.7701 | 26.3897 | 23.856 | 21.222 | 18.4824 | 10.0472 | 1.5148 | -6.5831 | -15.1422 | -21.0448 | 34.2862 | 24.6142 | 16.5173 | 9.8115 | 7.4889 | 5.1016 | 2.7075 | -0.18006 | -3.355 | -6.6129 | -21.5475 | -41.8264 | -56.7265 | -69.7812 | -78.7803 | 0 | 34.2862 | 24.6142 | 16.5173 | 9.8115 | 7.4889 | 5.1016 | 2.7075 | -0.18006 | -3.355 | -6.6129 | -21.5475 | -41.8264 | -56.7265 | -69.7812 | -78.7803 | 34.2862 | 28.2312 | 21.065 | 14.5965 | 12.4098 | 9.9873 | 6.7162 | 0.066174 | -7.0101 | -14.0708 | -34.201 | -52.3712 | -64.9611 | -72.0939 | -69.1732 | 0 | 34.2862 | 28.2312 | 21.065 | 14.5965 | 12.4098 | 9.9873 | 6.7162 | 0.066174 | -7.0101 | -14.0708 | -34.201 | -52.3712 | -64.9611 | -72.0939 | -69.1732 | 34.2862 | 30.4495 | 28.8933 | 27.8955 | 26.8602 | 25.68 | 23.8541 | 21.6013 | 18.742 | 15.8249 | 6.0315 | -4.3191 | -11.5968 | -18.2383 | -22.3519 | 0 | 34.2862 | 30.4495 | 28.8933 | 27.8955 | 26.8602 | 25.68 | 23.8541 | 21.6013 | 18.742 | 15.8249 | 6.0315 | -4.3191 | -11.5968 | -18.2383 | -22.3519 | 34.2862 | 24.5735 | 16.342 | 9.4417 | 6.8833 | 4.231 | -0.15751 | -7.57 | -15.0467 | -22.5028 | -43.9334 | -63.2224 | -76.9245 | -85.199 | -83.6322 | 34.2862 | 24.5735 | 16.342 | 9.4417 | 6.8833 | 4.231 | -0.15751 | -7.57 | -15.0467 | -22.5028 | -43.9334 | -63.2224 | -76.9245 | -85.199 | -83.6322 | 389137 | 403821 | WHITEGATE
| Droylsden | 51.9604 | 46.979 | 45.2044 | 43.9424 | 41.9041 | 40.0691 | 38.292 | 36.5986 | 34.6393 | 32.9172 | 22.6239 | 6.3099 | -6.2735 | -18.2781 | -27.6956 | 51.9604 | 46.979 | 45.2044 | 43.9424 | 41.9041 | 40.0691 | 38.292 | 36.5986 | 34.6393 | 32.9172 | 22.6239 | 6.3099 | -6.2735 | -18.2781 | -27.6956 | 51.9604 | 50.4815 | 49.6572 | 48.99 | 48.1074 | 47.1287 | 45.8014 | 44.0494 | 42.4972 | 40.8912 | 35.9455 | 30.7841 | 25.7882 | 20.3295 | 16.384 | 51.9604 | 50.4815 | 49.6572 | 48.99 | 48.1074 | 47.1287 | 45.8014 | 44.0494 | 42.4972 | 40.8912 | 35.9455 | 30.7841 | 25.7882 | 20.3295 | 16.384 | 51.9604 | 46.0635 | 43.8899 | 42.4059 | 40.1455 | 38.0781 | 36.1461 | 34.2663 | 32.2102 | 30.2622 | 19.4016 | 3.6538 | -7.5394 | -17.0554 | -22.6161 | 0 | 51.9604 | 46.0635 | 43.8899 | 42.4059 | 40.1455 | 38.0781 | 36.1461 | 34.2663 | 32.2102 | 30.2622 | 19.4016 | 3.6538 | -7.5394 | -17.0554 | -22.6161 | 51.9604 | 48.9141 | 47.4387 | 46.0881 | 43.8312 | 41.6372 | 38.6633 | 32.993 | 27.2183 | 21.6925 | 6.023 | -7.6965 | -16.7087 | -20.7605 | -16.138 | 0 | 51.9604 | 48.9141 | 47.4387 | 46.0881 | 43.8312 | 41.6372 | 38.6633 | 32.993 | 27.2183 | 21.6925 | 6.023 | -7.6965 | -16.7087 | -20.7605 | -16.138 | 51.9604 | 49.6195 | 48.5645 | 47.705 | 46.4293 | 45.2818 | 43.9618 | 42.4953 | 40.545 | 38.7076 | 32.3687 | 25.5341 | 20.9541 | 16.7098 | 14.1702 | 0 | 51.9604 | 49.6195 | 48.5645 | 47.705 | 46.4293 | 45.2818 | 43.9618 | 42.4953 | 40.545 | 38.7076 | 32.3687 | 25.5341 | 20.9541 | 16.7098 | 14.1702 | 51.9604 | 46.6061 | 44.3089 | 42.4935 | 39.8172 | 37.353 | 34.0488 | 27.9277 | 21.8368 | 15.9907 | -0.74907 | -15.4639 | -25.4605 | -30.646 | -27.3081 | 51.9604 | 46.6061 | 44.3089 | 42.4935 | 39.8172 | 37.353 | 34.0488 | 27.9277 | 21.8368 | 15.9907 | -0.74907 | -15.4639 | -25.4605 | -30.646 | -27.3081 | 390140 | 398146 | STALYBRIDGE
| Egremont | 32.2485 | 30.8569 | 30.3742 | 30.0074 | 29.3494 | 28.6571 | 28.113 | 27.7206 | 27.1111 | 26.6182 | 22.1204 | 13.6529 | 6.6991 | 0.011063 | -5.3761 | 32.2485 | 30.8569 | 30.3742 | 30.0074 | 29.3494 | 28.6571 | 28.113 | 27.7206 | 27.1111 | 26.6182 | 22.1204 | 13.6529 | 6.6991 | 0.011063 | -5.3761 | 32.2485 | 31.6761 | 31.3503 | 30.9351 | 30.3924 | 29.7822 | 28.9755 | 27.9619 | 27.1401 | 26.3229 | 23.907 | 21.6243 | 19.5894 | 17.5491 | 16.4114 | 32.2485 | 31.6761 | 31.3503 | 30.9351 | 30.3924 | 29.7822 | 28.9755 | 27.9619 | 27.1401 | 26.3229 | 23.907 | 21.6243 | 19.5894 | 17.5491 | 16.4114 | 32.2485 | 30.7867 | 21.1372 | 11.7016 | 11.2119 | 10.7155 | 10.4439 | 10.348 | 10.1294 | 9.9416 | 6.3248 | -1.3918 | -7.6831 | -13.5759 | -18.0424 | 0 | 32.2485 | 30.7867 | 21.1372 | 11.7016 | 11.2119 | 10.7155 | 10.4439 | 10.348 | 10.1294 | 9.9416 | 6.3248 | -1.3918 | -7.6831 | -13.5759 | -18.0424 | 32.2485 | 31.9923 | 22.6782 | 13.2955 | 12.8428 | 12.2875 | 11.3566 | 8.8394 | 6.1354 | 3.4556 | -4.1471 | -11.3475 | -16.8686 | -19.3997 | -14.8905 | 0 | 32.2485 | 31.9923 | 22.6782 | 13.2955 | 12.8428 | 12.2875 | 11.3566 | 8.8394 | 6.1354 | 3.4556 | -4.1471 | -11.3475 | -16.8686 | -19.3997 | -14.8905 | 32.2485 | 31.723 | 31.5181 | 31.4031 | 31.2695 | 31.0639 | 30.7766 | 30.4434 | 29.764 | 29.1003 | 26.6222 | 23.6719 | 21.7392 | 20.1699 | 20.4743 | 0 | 32.2485 | 31.723 | 31.5181 | 31.4031 | 31.2695 | 31.0639 | 30.7766 | 30.4434 | 29.764 | 29.1003 | 26.6222 | 23.6719 | 21.7392 | 20.1699 | 20.4743 | 32.2485 | 31.2785 | 21.3768 | 11.4495 | 10.487 | 9.5387 | 8.1805 | 5.177 | 2.0936 | -0.96702 | -9.3373 | -17.1953 | -23.3511 | -26.6366 | -22.9579 | 32.2485 | 31.2785 | 21.3768 | 11.4495 | 10.487 | 9.5387 | 8.1805 | 5.177 | 2.0936 | -0.96702 | -9.3373 | -17.1953 | -23.3511 | -26.6366 | -22.9579 | 301070 | 513074 | HARKER
| Frederick Rd | 21.7635 | -1.8046 | -17.3998 | -30.6594 | -38.8674 | 21.8656 | 13.3573 | 5.8311 | -2.0818 | -7.0503 | -24.7692 | -43.6407 | -56.537 | -69.422 | -81.1781 | 63.7635 | 40.1954 | 24.6002 | 11.3406 | 3.1326 | 84.8656 | 76.3573 | 68.8311 | 60.9182 | 55.9497 | 38.2308 | 19.3593 | 6.463 | -6.422 | -18.1781 | 21.7635 | 13.5885 | 10.3614 | 7.9284 | 5.5594 | 71.9583 | 69.0597 | 65.4164 | 62.0328 | 58.595 | 48.3093 | 37.7621 | 28.2933 | 17.6519 | 8.0383 | 63.7635 | 55.5885 | 52.3614 | 49.9284 | 47.5594 | 134.9583 | 132.0597 | 128.4164 | 125.0328 | 121.595 | 111.3093 | 100.7621 | 91.2933 | 80.6519 | 71.0383 | 21.7635 | -5.5651 | -22.1893 | -35.719 | -44.226 | 16.2034 | 4.947 | -5.9335 | -16.936 | -22.714 | -40.2827 | -58.8709 | -71.0367 | -82.3543 | -91.4634 | 0 | 63.7635 | 36.4349 | 19.8107 | 6.281 | -2.226 | 79.2034 | 67.947 | 57.0665 | 46.064 | 40.286 | 22.7173 | 4.1291 | -8.0367 | -19.3543 | -28.4634 | 21.7635 | 2.3234 | -12.4842 | -25.7403 | -33.7235 | 26.8269 | 15.0792 | 1.8746 | -11.6208 | -19.807 | -40.5615 | -57.7291 | -68.153 | -75.4723 | -77.6078 | 0 | 63.7635 | 44.3234 | 29.5158 | 16.2597 | 8.2765 | 89.8269 | 78.0792 | 64.8746 | 51.3792 | 43.193 | 22.4385 | 5.2709 | -5.153 | -12.4723 | -14.6078 | 21.7635 | 8.0305 | -5.4304 | -18.2646 | -25.8069 | 35.5139 | 27.4962 | 20.206 | 12.2261 | 7.0039 | -8.4031 | -21.1569 | -28.9497 | -36.8789 | -43.4495 | 0 | 63.7635 | 50.0305 | 36.5696 | 23.7354 | 16.1931 | 98.5139 | 90.4962 | 83.206 | 75.2261 | 70.0039 | 54.5969 | 41.8431 | 34.0503 | 26.1211 | 19.5505 | 21.7635 | -8.1293 | -25.3348 | -38.9879 | -47.6649 | 12.6302 | 0.63794 | -12.9263 | -27.0671 | -35.891 | -59.1261 | -78.5575 | -91.254 | -101.4224 | -107.0748 | 63.7635 | 33.8707 | 16.6652 | 3.0121 | -5.6649 | 75.6302 | 63.6379 | 50.0737 | 35.9329 | 27.109 | 3.8739 | -15.5575 | -28.254 | -38.4224 | -44.0748 | 381795 | 399250 | KEARSLEY
| Golborne | 51.0817 | 47.2062 | 45.586 | 44.5145 | 43.0651 | 41.4898 | 39.9106 | 38.4668 | 36.3728 | 33.9528 | 22.3255 | 6.3215 | -6.0932 | -18.3725 | -29.0275 | 69.0817 | 65.2062 | 63.586 | 62.5145 | 61.0651 | 59.4898 | 57.9106 | 56.4668 | 54.3728 | 51.9528 | 40.3255 | 24.3215 | 11.9068 | -0.37254 | -11.0275 | 51.0817 | 49.7187 | 48.7404 | 48.018 | 47.1584 | 46.1623 | 44.8059 | 42.9505 | 40.9259 | 38.7261 | 31.6251 | 23.5284 | 15.7467 | 7.5391 | 2.2968 | 69.0817 | 67.7187 | 66.7404 | 66.018 | 65.1584 | 64.1623 | 62.8059 | 60.9505 | 58.9259 | 56.7261 | 49.6251 | 41.5284 | 33.7467 | 25.5391 | 20.2968 | 51.0817 | 46.8114 | 45.2288 | 44.4257 | 42.8255 | 41.1615 | 39.6453 | 38.3392 | 36.5984 | 34.9628 | 24.9416 | 9.6171 | -2.2904 | -13.2691 | -22.3177 | 0 | 69.0817 | 64.8114 | 63.2288 | 62.4257 | 60.8255 | 59.1615 | 57.6453 | 56.3392 | 54.5984 | 52.9628 | 42.9416 | 27.6171 | 15.7096 | 4.7309 | -4.3177 | 51.0817 | 49.166 | 48.2067 | 47.5656 | 45.983 | 44.1648 | 41.6365 | 36.8021 | 31.4733 | 26.242 | 11.299 | -2.8029 | -13.5042 | -20.0743 | -16.4402 | 0 | 69.0817 | 67.166 | 66.2067 | 65.5656 | 63.983 | 62.1648 | 59.6365 | 54.8021 | 49.4733 | 44.242 | 29.299 | 15.1971 | 4.4958 | -2.0743 | 1.5598 | 51.0817 | 49.124 | 48.0885 | 47.4175 | 46.6974 | 45.7431 | 44.5723 | 43.4199 | 41.4577 | 39.2928 | 31.1827 | 22.5422 | 16.6997 | 12.0523 | 10.0244 | 0 | 69.0817 | 67.124 | 66.0885 | 65.4175 | 64.6974 | 63.7431 | 62.5723 | 61.4199 | 59.4577 | 57.2928 | 49.1827 | 40.5422 | 34.6997 | 30.0523 | 28.0244 | 51.0817 | 47.2642 | 45.5667 | 44.472 | 42.499 | 40.467 | 37.7039 | 32.536 | 27.0222 | 21.5981 | 5.6728 | -9.7657 | -21.8172 | -29.6765 | -27.2358 | 69.0817 | 65.2642 | 63.5667 | 62.472 | 60.499 | 58.467 | 55.7039 | 50.536 | 45.0222 | 39.5981 | 23.6728 | 8.2343 | -3.8172 | -11.6765 | -9.2358 | 360607 | 397690 | BOLD
| Greenhill | 33.3465 | 29.3862 | 26.2317 | 23.795 | 21.0229 | 18.1389 | 15.3156 | 12.5803 | 9.8552 | 7.8763 | -2.5073 | -18.285 | -30.6262 | -42.1067 | -50.6392 | 33.3465 | 29.3862 | 26.2317 | 23.795 | 21.0229 | 18.1389 | 15.3156 | 12.5803 | 9.8552 | 7.8763 | -2.5073 | -18.285 | -30.6262 | -42.1067 | -50.6392 | 33.3465 | 31.575 | 30.1784 | 29.007 | 27.7285 | 26.3475 | 24.6375 | 22.4561 | 20.6157 | 18.781 | 12.8576 | 6.2054 | -0.29176 | -7.5253 | -13.1835 | 33.3465 | 31.575 | 30.1784 | 29.007 | 27.7285 | 26.3475 | 24.6375 | 22.4561 | 20.6157 | 18.781 | 12.8576 | 6.2054 | -0.29176 | -7.5253 | -13.1835 | 33.3465 | 28.547 | 24.9185 | 22.0559 | 18.7013 | 15.2256 | 11.784 | 8.4255 | 5.1666 | 2.615 | -9.0035 | -24.7175 | -35.6999 | -44.6661 | -49.0267 | 0 | 33.3465 | 28.547 | 24.9185 | 22.0559 | 18.7013 | 15.2256 | 11.784 | 8.4255 | 5.1666 | 2.615 | -9.0035 | -24.7175 | -35.6999 | -44.6661 | -49.0267 | 33.3465 | 30.7219 | 27.6505 | 24.9317 | 21.6197 | 18.1135 | 13.8329 | 7.1931 | 0.72546 | -4.8167 | -20.034 | -33.489 | -41.9995 | -45.8235 | -42.8174 | 0 | 33.3465 | 30.7219 | 27.6505 | 24.9317 | 21.6197 | 18.1135 | 13.8329 | 7.1931 | 0.72546 | -4.8167 | -20.034 | -33.489 | -41.9995 | -45.8235 | -42.8174 | 33.3465 | 30.8245 | 28.0971 | 25.9887 | 23.915 | 21.7123 | 19.3693 | 16.8553 | 14.0937 | 11.9617 | 4.9542 | -2.5353 | -8.2372 | -13.8565 | -18.137 | 0 | 33.3465 | 30.8245 | 28.0971 | 25.9887 | 23.915 | 21.7123 | 19.3693 | 16.8553 | 14.0937 | 11.9617 | 4.9542 | -2.5353 | -8.2372 | -13.8565 | -18.137 | 33.3465 | 29.2493 | 25.5911 | 22.4939 | 18.8348 | 15.0883 | 10.5706 | 3.5585 | -3.111 | -8.8535 | -24.9821 | -39.422 | -48.9751 | -54.0401 | -52.4122 | 33.3465 | 29.2493 | 25.5911 | 22.4939 | 18.8348 | 15.0883 | 10.5706 | 3.5585 | -3.111 | -8.8535 | -24.9821 | -39.422 | -48.9751 | -54.0401 | -52.4122 | 393262 | 404755 | WHITEGATE
| Hartshead-Heyrod | 32.6619 | 29.6642 | 28.0639 | 27.0047 | 25.3277 | 23.5338 | 21.8577 | 20.301 | 18.3642 | 16.55 | 4.3852 | -15.88 | -32.1239 | -48.2193 | -61.066 | 94.6619 | 91.6642 | 90.0639 | 89.0047 | 87.3277 | 85.5338 | 83.8577 | 82.301 | 80.3642 | 78.55 | 66.3852 | 46.12 | 29.8761 | 13.7807 | 0.93401 | 32.6619 | 31.3123 | 30.2959 | 29.349 | 28.1033 | 26.7111 | 24.8821 | 22.5774 | 20.6464 | 18.6522 | 12.4472 | 6.0007 | -0.14157 | -6.9647 | -11.7143 | 94.6619 | 93.3123 | 92.2959 | 91.349 | 90.1033 | 88.7111 | 86.8821 | 84.5774 | 82.6464 | 80.6522 | 74.4472 | 68.0007 | 61.8584 | 55.0353 | 50.2857 | 32.6619 | 28.9277 | 26.6639 | 25.0806 | 22.8066 | 20.7215 | 18.8704 | 17.1291 | 15.149 | 13.1806 | 1.0688 | -18.1911 | -32.7313 | -46.0038 | -54.6877 | 0 | 94.6619 | 90.9277 | 88.6639 | 87.0806 | 84.8066 | 82.7215 | 80.8704 | 79.1291 | 77.149 | 75.1806 | 63.0688 | 43.8089 | 29.2687 | 15.9962 | 7.3123 | 32.6619 | 31.3677 | 29.7942 | 28.4598 | 26.2563 | 24.0679 | 20.8843 | 14.0996 | 7.0896 | 0.22441 | -18.8929 | -35.957 | -48.0912 | -54.245 | -47.8274 | 0 | 94.6619 | 93.3677 | 91.7942 | 90.4598 | 88.2563 | 86.0679 | 82.8843 | 76.0996 | 69.0896 | 62.2244 | 43.1071 | 26.043 | 13.9088 | 7.755 | 14.1726 | 32.6619 | 30.7939 | 29.6761 | 29.1406 | 28.4535 | 27.5463 | 26.4258 | 25.1535 | 23.2614 | 21.3345 | 14.5605 | 6.6927 | 0.51874 | -4.9889 | -7.8041 | 0 | 94.6619 | 92.7939 | 91.6761 | 91.1406 | 90.4535 | 89.5463 | 88.4258 | 87.1535 | 85.2614 | 83.3345 | 76.5605 | 68.6927 | 62.5187 | 57.0111 | 54.1959 | 32.6619 | 30.0959 | 27.7876 | 25.8272 | 23.0574 | 20.4954 | 16.8609 | 9.458 | 2.0328 | -5.2561 | -25.8011 | -44.2233 | -57.7208 | -65.5006 | -60.9133 | 94.6619 | 92.0959 | 89.7876 | 87.8272 | 85.0574 | 82.4954 | 78.8609 | 71.458 | 64.0328 | 56.7439 | 36.1989 | 17.7767 | 4.2792 | -3.5006 | 1.0867 | 397322 | 399942 | STALYBRIDGE
| Hazel Grove | 52.2018 | 49.6775 | 46.9511 | 44.8216 | 43.9314 | 43.1869 | 42.4941 | 41.6711 | 40.5173 | 39.4722 | 31.4673 | 15.2304 | 2.8369 | -10.2243 | -22.0288 | 70.2018 | 67.6775 | 64.9511 | 62.8216 | 61.9314 | 61.1869 | 60.4941 | 59.6711 | 58.5173 | 57.4722 | 49.4673 | 33.2304 | 20.8369 | 7.7757 | -4.0288 | 52.2018 | 51.2862 | 50.6878 | 50.0616 | 49.1475 | 48.0979 | 46.7399 | 44.9145 | 43.4077 | 41.8663 | 37.1838 | 32.4828 | 27.5309 | 22.4916 | 17.9351 | 70.2018 | 69.2862 | 68.6878 | 68.0616 | 67.1475 | 66.0979 | 64.7399 | 62.9145 | 61.4077 | 59.8663 | 55.1838 | 50.4828 | 45.5309 | 40.4916 | 35.9351 | 52.2018 | 49.4949 | 46.9026 | 45.0758 | 44.44 | 43.9879 | 43.613 | 43.1669 | 42.4648 | 41.7337 | 30.2943 | 16.8431 | 5.5062 | -6.7848 | -17.505 | 0 | 70.2018 | 67.4949 | 64.9026 | 63.0758 | 62.44 | 61.9879 | 61.613 | 61.1669 | 60.4648 | 59.7337 | 48.2943 | 34.8431 | 23.5062 | 11.2152 | 0.49499 | 52.2018 | 51.597 | 51.1746 | 46.3278 | 41.5285 | 41.1971 | 40.0254 | 36.2259 | 31.9061 | 27.5389 | 14.3518 | 1.558 | -8.9095 | -15.8533 | -12.0725 | 0 | 70.2018 | 69.597 | 69.1746 | 64.3278 | 59.5285 | 59.1971 | 58.0254 | 54.2259 | 49.9061 | 45.5389 | 32.3518 | 19.558 | 9.0905 | 2.1467 | 5.9275 | 52.2018 | 51.0234 | 48.7925 | 47.0401 | 46.7002 | 46.3551 | 45.9042 | 45.2985 | 44.2744 | 43.2732 | 39.4928 | 32.7413 | 28.8157 | 25.608 | 23.4918 | 0 | 70.2018 | 69.0234 | 66.7925 | 65.0401 | 64.7002 | 64.3551 | 63.9042 | 63.2985 | 62.2744 | 61.2732 | 57.4928 | 50.7413 | 46.8157 | 43.608 | 41.4918 | 52.2018 | 50.3422 | 49.2687 | 43.9055 | 38.6485 | 38.0271 | 36.481 | 32.1971 | 27.5143 | 22.7861 | 8.4832 | -5.264 | -16.6593 | -24.7156 | -22.1766 | 70.2018 | 68.3422 | 67.2687 | 61.9055 | 56.6485 | 56.0271 | 54.481 | 50.1971 | 45.5143 | 40.7861 | 26.4832 | 12.736 | 1.3407 | -6.7156 | -4.1766 | 391313 | 386877 | BREDBURY
| Huncoat | 57.4481 | 51.8774 | 48.9542 | 47.0831 | 45.2663 | 43.3587 | 41.787 | 40.1615 | 38.8156 | 37.5072 | 27.0158 | 8.8804 | -5.8085 | -21.1105 | -33.0666 | 71.2481 | 65.6774 | 62.7542 | 60.8831 | 59.0663 | 57.1587 | 55.587 | 53.9615 | 52.6156 | 51.3072 | 40.8158 | 22.6804 | 7.9915 | -7.3105 | -19.2666 | 57.4481 | 55.5877 | 54.4009 | 53.4465 | 52.5211 | 51.4639 | 50.2362 | 48.7168 | 47.5424 | 46.3369 | 41.3938 | 35.535 | 29.9221 | 24.2165 | 20.5344 | 71.2481 | 69.3877 | 68.2009 | 67.2465 | 66.3211 | 65.2639 | 64.0362 | 62.5168 | 61.3424 | 60.1369 | 55.1938 | 49.335 | 43.7221 | 38.0165 | 34.3344 | 57.4481 | 50.7933 | 47.5615 | 45.5245 | 43.5406 | 41.4609 | 39.7025 | 37.818 | 36.4533 | 35.1235 | 26.3967 | 9.86 | -4.0046 | -17.1 | -26.4176 | 0 | 71.2481 | 64.5933 | 61.3615 | 59.3245 | 57.3406 | 55.2609 | 53.5025 | 51.618 | 50.2533 | 48.9235 | 40.1967 | 23.66 | 9.7954 | -3.3 | -12.6176 | 57.4481 | 53.608 | 51.11 | 49.2137 | 47.3999 | 45.363 | 42.7146 | 37.3238 | 32.2987 | 26.748 | 9.2784 | -7.0884 | -19.5685 | -26.7392 | -20.3294 | 0 | 71.2481 | 67.408 | 64.91 | 63.0137 | 61.1999 | 59.163 | 56.5146 | 51.1238 | 46.0987 | 40.548 | 23.0784 | 6.7116 | -5.7685 | -12.9392 | -6.5294 | 57.4481 | 54.369 | 52.3203 | 50.758 | 49.5532 | 48.1701 | 46.8577 | 45.3755 | 44.0579 | 42.6901 | 38.0327 | 31.1254 | 25.8841 | 21.7007 | 20.1317 | 0 | 71.2481 | 68.169 | 66.1203 | 64.558 | 63.3532 | 61.9701 | 60.6577 | 59.1755 | 57.8579 | 56.4901 | 51.8327 | 44.9254 | 39.6841 | 35.5007 | 33.9317 | 57.4481 | 50.6189 | 47.2963 | 45.0527 | 42.9328 | 40.7525 | 38.0013 | 32.3631 | 27.1619 | 20.8725 | 2.1062 | -15.6679 | -29.5504 | -38.3945 | -33.7514 | 71.2481 | 64.4189 | 61.0963 | 58.8527 | 56.7328 | 54.5525 | 51.8013 | 46.1631 | 40.9619 | 34.6725 | 15.9062 | -1.8679 | -15.7504 | -24.5945 | -19.9514 | 377997 | 431083 | PADIHAM
| Hyde | 45.7804 | 41.745 | 40.0609 | 39.0385 | 37.0638 | 34.9904 | 33.0954 | 31.3387 | 29.1995 | 27.1742 | 15.3324 | -3.7778 | -19.9935 | -35.7571 | -49.2401 | 45.7804 | 41.745 | 40.0609 | 39.0385 | 37.0638 | 34.9904 | 33.0954 | 31.3387 | 29.1995 | 27.1742 | 15.3324 | -3.7778 | -19.9935 | -35.7571 | -49.2401 | 45.7804 | 44.0656 | 42.9688 | 42.0589 | 40.4638 | 38.7846 | 36.7611 | 34.2444 | 31.9678 | 29.6684 | 22.4343 | 15.0003 | 7.889 | 1.2928 | -2.96 | 45.7804 | 44.0656 | 42.9688 | 42.0589 | 40.4638 | 38.7846 | 36.7611 | 34.2444 | 31.9678 | 29.6684 | 22.4343 | 15.0003 | 7.889 | 1.2928 | -2.96 | 45.7804 | 41.3272 | 39.5156 | 37.9781 | 35.2401 | 32.4769 | 30.003 | 28.3634 | 26.4825 | 24.6041 | 13.8197 | -3.817 | -18.9826 | -33.4231 | -45.3299 | 0 | 45.7804 | 41.3272 | 39.5156 | 37.9781 | 35.2401 | 32.4769 | 30.003 | 28.3634 | 26.4825 | 24.6041 | 13.8197 | -3.817 | -18.9826 | -33.4231 | -45.3299 | 45.7804 | 43.4928 | 42.2983 | 40.9351 | 38.2487 | 35.3984 | 31.7122 | 25.5716 | 19.1013 | 12.6331 | -5.1878 | -22.4397 | -36.518 | -45.0139 | -40.4149 | 0 | 45.7804 | 43.4928 | 42.2983 | 40.9351 | 38.2487 | 35.3984 | 31.7122 | 25.5716 | 19.1013 | 12.6331 | -5.1878 | -22.4397 | -36.518 | -45.0139 | -40.4149 | 45.7804 | 43.342 | 42.1744 | 41.5633 | 40.4015 | 39.116 | 37.7469 | 36.2786 | 34.1689 | 32.0508 | 24.5514 | 15.9877 | 9.6766 | 4.9026 | 2.78 | 0 | 45.7804 | 43.342 | 42.1744 | 41.5633 | 40.4015 | 39.116 | 37.7469 | 36.2786 | 34.1689 | 32.0508 | 24.5514 | 15.9877 | 9.6766 | 4.9026 | 2.78 | 45.7804 | 41.5582 | 39.5923 | 37.6455 | 34.4437 | 31.2522 | 27.2169 | 20.5602 | 13.716 | 6.8793 | -12.1049 | -30.4769 | -45.6899 | -55.5769 | -52.54 | 45.7804 | 41.5582 | 39.5923 | 37.6455 | 34.4437 | 31.2522 | 27.2169 | 20.5602 | 13.716 | 6.8793 | -12.1049 | -30.4769 | -45.6899 | -55.5769 | -52.54 | 395522 | 395647 | STALYBRIDGE
| Kendal (Parkside Rd) | 24.393 | 17.3214 | 14.8427 | 13.3721 | 8.5512 | 6.3478 | 1.8798 | 0.11081 | -2.1471 | -4.4776 | -16.7075 | -40.032 | -56.4076 | -75.1099 | -88.6331 | 36.393 | 29.3214 | 26.8427 | 25.3721 | 20.5512 | 18.3478 | 13.8798 | 12.1108 | 9.8529 | 7.5224 | -4.7075 | -28.032 | -44.4076 | -63.1099 | -76.6331 | 24.393 | 20.7796 | 18.81 | 16.9754 | 14.8222 | 12.5794 | 9.8026 | 6.4061 | 4.1903 | 1.9644 | -4.8555 | -12.0011 | -18.5973 | -29.5449 | -35.3685 | 36.393 | 32.7796 | 30.81 | 28.9754 | 26.8222 | 24.5794 | 21.8026 | 18.4061 | 16.1903 | 13.9644 | 7.1445 | -0.0010926 | -6.5973 | -17.5449 | -23.3685 | 24.393 | 16.5293 | 14.0423 | 12.8631 | 8.4485 | 6.6031 | 2.7782 | 1.5831 | -0.13027 | -1.4866 | -25.016 | -42.822 | -57.3469 | -70.3168 | -81.4849 | 0 | 36.393 | 28.5293 | 26.0423 | 24.8631 | 20.4485 | 18.6031 | 14.7782 | 13.5831 | 11.8697 | 10.5134 | -13.016 | -30.822 | -45.3469 | -58.3168 | -69.4849 | 24.393 | 20.1347 | 18.5314 | 10.0633 | 6.3068 | 4.5275 | 2.0239 | -3.612 | -10.4902 | -17.118 | -36.4709 | -53.5547 | -66.4277 | -73.2627 | -66.512 | 0 | 36.393 | 32.1347 | 30.5314 | 22.0633 | 18.3068 | 16.5275 | 14.0239 | 8.388 | 1.5098 | -5.118 | -24.4709 | -41.5547 | -54.4277 | -61.2627 | -54.512 | 24.393 | 19.3681 | 17.4113 | 16.2765 | 12.3297 | 11.0621 | 7.1565 | 5.6068 | 3.306 | 0.74047 | -7.2948 | -19.6565 | -25.9354 | -34.0914 | -35.5518 | 0 | 36.393 | 31.3681 | 29.4113 | 28.2765 | 24.3297 | 23.0621 | 19.1565 | 17.6068 | 15.306 | 12.7405 | 4.7052 | -7.6565 | -13.9354 | -22.0914 | -23.5518 | 24.393 | 16.7996 | 14.0793 | 4.9143 | 0.50549 | -1.7477 | -4.7913 | -11.1296 | -18.3443 | -25.3173 | -45.9692 | -64.4304 | -78.6704 | -87.001 | -81.7901 | 36.393 | 28.7996 | 26.0793 | 16.9143 | 12.5055 | 10.2523 | 7.2087 | 0.87036 | -6.3443 | -13.3173 | -33.9692 | -52.4304 | -66.6704 | -75.001 | -69.7901 | 351915 | 491858 | HUTTON
| Lancaster | 22.9917 | 15.0245 | 8.1318 | 4.2949 | -0.29264 | -5.0966 | -10.4328 | -16.2747 | -20.3696 | -23.0741 | -38.9511 | -105.8158 | -123.1728 | -143.2502 | -157.6164 | 22.9917 | 15.0245 | 8.1318 | 4.2949 | -0.29264 | -5.0966 | -10.4328 | -16.2747 | -20.3696 | -23.0741 | -38.9511 | -105.8158 | -123.1728 | -143.2502 | -157.6164 | 22.9917 | 18.9588 | 16.7984 | 14.7125 | 12.2608 | 9.7771 | 6.5685 | 3.064 | 0.079666 | -2.6747 | -11.2624 | -21.4344 | -30.168 | -40.0858 | -48.4897 | 22.9917 | 18.9588 | 16.7984 | 14.7125 | 12.2608 | 9.7771 | 6.5685 | 3.064 | 0.079666 | -2.6747 | -11.2624 | -21.4344 | -30.168 | -40.0858 | -48.4897 | 22.9917 | 14.1542 | 7.3241 | 3.8266 | -0.40291 | -4.7713 | -10.608 | -15.6688 | -18.6912 | -20.5837 | -36.8157 | -101.5876 | -118.0556 | -136.1244 | -148.4253 | 0 | 22.9917 | 14.1542 | 7.3241 | 3.8266 | -0.40291 | -4.7713 | -10.608 | -15.6688 | -18.6912 | -20.5837 | -36.8157 | -101.5876 | -118.0556 | -136.1244 | -148.4253 | 22.9917 | 18.2941 | 14.0316 | 7.0131 | -0.017809 | -5.4175 | -11.4329 | -19.9504 | -29.2388 | -37.4356 | -103.1058 | -124.2333 | -138.7437 | -148.2584 | -137.9159 | 0 | 22.9917 | 18.2941 | 14.0316 | 7.0131 | -0.017809 | -5.4175 | -11.4329 | -19.9504 | -29.2388 | -37.4356 | -103.1058 | -124.2333 | -138.7437 | -148.2584 | -137.9159 | 22.9917 | 17.107 | 10.823 | 7.4882 | 3.9214 | 0.19455 | -4.3633 | -9.7876 | -13.7629 | -16.5421 | -26.4033 | -78.6852 | -83.0422 | -88.8131 | -87.6118 | 0 | 22.9917 | 17.107 | 10.823 | 7.4882 | 3.9214 | 0.19455 | -4.3633 | -9.7876 | -13.7629 | -16.5421 | -26.4033 | -78.6852 | -83.0422 | -88.8131 | -87.6118 | 22.9917 | 14.7096 | 7.2151 | -2.5544 | -12.2594 | -20.1032 | -28.6143 | -39.7628 | -52.4248 | -64.0211 | -138.362 | -161.278 | -177.6436 | -189.161 | -180.8159 | 22.9917 | 14.7096 | 7.2151 | -2.5544 | -12.2594 | -20.1032 | -28.6143 | -39.7628 | -52.4248 | -64.0211 | -138.362 | -161.278 | -177.6436 | -189.161 | -180.8159 | 348644 | 463628 | HEYSHAM | Firm Capacity marginally exceeded in FY28. Review in ED2 and potential reinforcement in ED3.
| Leyland | 33.0873 | 20.5687 | 14.6273 | 10.8345 | 6.6559 | 2.821 | 0.85411 | -1.2252 | -4.147 | -7.0726 | -22.6542 | -42.1332 | -57.2578 | -72.0218 | -84.2029 | 48.0513 | 35.5327 | 29.5913 | 25.7985 | 21.6199 | 17.785 | 15.8181 | 13.7388 | 10.817 | 7.8914 | -7.6902 | -27.1692 | -42.2938 | -57.0578 | -69.2389 | 33.0873 | 28.0315 | 25.2872 | 23.3773 | 21.3043 | 19.2428 | 17.256 | 14.6875 | 11.959 | 9.1248 | 0.12519 | -9.4628 | -18.6206 | -28.3799 | -38.4584 | 48.0513 | 42.9955 | 40.2512 | 38.3413 | 36.2683 | 34.2068 | 32.22 | 29.6515 | 26.923 | 24.0888 | 15.0892 | 5.5012 | -3.6566 | -13.4159 | -23.4944 | 33.0873 | 18.8266 | 10.4614 | 3.6068 | -3.6247 | -9.312 | -10.7005 | -12.1034 | -14.0595 | -16.2307 | -30.3959 | -50.5418 | -64.6609 | -77.7969 | -87.4539 | 0 | 48.0513 | 33.7906 | 25.4254 | 18.5708 | 11.3393 | 5.652 | 4.2635 | 2.8606 | 0.90453 | -1.2667 | -15.4319 | -35.5778 | -49.6969 | -62.8329 | -72.4899 | 33.0873 | 24.0868 | 16.8883 | 10.2466 | 3.0536 | -2.8327 | -5.4205 | -13.2763 | -23.0255 | -29.1089 | -47.2322 | -64.15 | -76.5024 | -83.8345 | -78.9804 | 0 | 48.0513 | 39.0508 | 31.8523 | 25.2106 | 18.0176 | 12.1313 | 9.5435 | 1.6877 | -8.0615 | -14.1449 | -32.2682 | -49.186 | -61.5384 | -68.8705 | -64.0164 | 33.0873 | 24.1799 | 19.1412 | 15.8641 | 12.5602 | 9.456 | 7.9903 | 6.342 | 3.7076 | 0.95641 | -10.1924 | -19.9847 | -26.5016 | -31.742 | -33.8484 | 0 | 48.0513 | 39.1439 | 34.1052 | 30.8281 | 27.5242 | 24.42 | 22.9543 | 21.306 | 18.6716 | 15.9204 | 4.7716 | -5.0207 | -11.5376 | -16.778 | -18.8844 | 33.0873 | 18.0047 | 9.2768 | 2.0404 | -7.5057 | -14.562 | -18.3388 | -27.5291 | -37.8348 | -44.1721 | -63.5735 | -82.212 | -96.2561 | -105.2103 | -101.8133 | 48.0513 | 32.9687 | 24.2408 | 17.0044 | 7.4583 | 0.40204 | -3.3748 | -12.5651 | -22.8708 | -29.2081 | -48.6095 | -67.248 | -81.2921 | -90.2463 | -86.8493 | 354121 | 423373 | PENWORTHAM
| Longsight | 33.5719 | 21.3221 | 10.39 | 0.70063 | -9.2253 | -15.4827 | -19.9762 | -25.8487 | -27.2713 | -28.633 | -37.5924 | -48.7337 | -56.9298 | -64.4274 | -69.4774 | 51.5719 | 39.3221 | 28.39 | 18.7006 | 8.7747 | 2.5173 | -1.9762 | -7.8487 | -9.2713 | -10.633 | -19.5924 | -30.7337 | -38.9298 | -46.4274 | -51.4774 | 33.5719 | 27.7724 | 18.9429 | 9.7313 | 0.52945 | -4.8819 | -8.9585 | -13.3996 | -14.7714 | -16.1686 | -20.3294 | -24.6197 | -28.4943 | -32.6873 | -36.1957 | 51.5719 | 45.7724 | 36.9429 | 27.7313 | 18.5294 | 13.1181 | 9.0415 | 4.6004 | 3.2286 | 1.8314 | -2.3294 | -6.6197 | -10.4943 | -14.6873 | -18.1957 | 33.5719 | 19.6599 | 8.0393 | -2.0247 | -12.4445 | -19.2242 | -24.2006 | -30.5159 | -32.2506 | -34.0008 | -44.1576 | -56.3238 | -63.2534 | -68.4965 | -69.8334 | 0 | 51.5719 | 37.6599 | 26.0393 | 15.9753 | 5.5555 | -1.2242 | -6.2006 | -12.5159 | -14.2506 | -16.0008 | -26.1576 | -38.3238 | -45.2534 | -50.4965 | -51.8334 | 33.5719 | 23.5006 | 12.7439 | 2.8175 | -7.5379 | -14.2934 | -19.8777 | -30.7287 | -36.4066 | -40.2721 | -51.1366 | -60.1562 | -65.304 | -66.8873 | -62.841 | 0 | 51.5719 | 41.5006 | 30.7439 | 20.8175 | 10.4621 | 3.7066 | -1.8777 | -12.7287 | -18.4066 | -22.2721 | -33.1366 | -42.1562 | -47.304 | -48.8873 | -44.841 | 33.5719 | 25.5939 | 15.6112 | 6.131 | -3.3781 | -9.1127 | -13.2365 | -18.9481 | -20.3922 | -21.9022 | -28.4507 | -33.4278 | -36.6759 | -39.7499 | -41.1926 | 0 | 51.5719 | 43.5939 | 33.6112 | 24.131 | 14.6219 | 8.8873 | 4.7635 | -0.94811 | -2.3922 | -3.9022 | -10.4507 | -15.4278 | -18.6759 | -21.7499 | -23.1926 | 33.5719 | 19.0949 | 7.2314 | -2.9786 | -13.5975 | -20.5481 | -26.3654 | -37.5266 | -43.3234 | -47.4137 | -58.9128 | -68.5123 | -74.2742 | -76.6402 | -73.5559 | 51.5719 | 37.0949 | 25.2314 | 15.0214 | 4.4025 | -2.5481 | -8.3654 | -19.5266 | -25.3234 | -29.4137 | -40.9128 | -50.5123 | -56.2742 | -58.6402 | -55.5559 | 385592 | 396016 | BREDBURY | Firm Capacity exceeded in FY28. Review in ED2 and potential reinforcement in ED3.
| Lower Darwen | 12.317 | 6.0422 | 3.8585 | 2.4929 | 0.868 | 24.1614 | 22.5429 | 20.9173 | 18.4734 | 16.4894 | 3.4448 | -13.349 | -26.9084 | -39.3838 | -48.383 | 62.317 | 56.0422 | 53.8585 | 52.4929 | 50.868 | 49.1614 | 47.5429 | 45.9173 | 43.4734 | 41.4894 | 28.4448 | 11.651 | -1.9084 | -14.3838 | -23.383 | 12.317 | 9.9234 | 9.059 | 8.3702 | 7.5022 | 31.5229 | 30.1961 | 28.4613 | 26.5563 | 25.02 | 20.2489 | 14.6986 | 9.9802 | 4.9229 | 1.7284 | 62.317 | 59.9234 | 59.059 | 58.3702 | 57.5022 | 56.5229 | 55.1961 | 53.4613 | 51.5563 | 50.02 | 45.2489 | 39.6986 | 34.9802 | 29.9229 | 26.7284 | 12.317 | 5.0256 | 2.4463 | 0.90018 | -0.92553 | 22.1841 | 20.4752 | 18.763 | 16.4155 | 14.3697 | 0.5414 | -16.6988 | -28.2659 | -38.4913 | -44.1258 | 0 | 62.317 | 55.0256 | 52.4463 | 50.9002 | 49.0745 | 47.1841 | 45.4752 | 43.763 | 41.4155 | 39.3697 | 25.5414 | 8.3012 | -3.2659 | -13.4913 | -19.1258 | 12.317 | 8.0675 | 6.0691 | 4.7111 | 2.956 | 26.0148 | 22.6414 | 14.3557 | 8.3345 | 1.2837 | -16.1483 | -29.9787 | -39.6142 | -44.1105 | -37.689 | 0 | 62.317 | 58.0675 | 56.0691 | 54.7111 | 52.956 | 51.0148 | 47.6414 | 39.3557 | 33.3345 | 26.2837 | 8.8517 | -4.9787 | -14.6142 | -19.1105 | -12.689 | 12.317 | 8.0651 | 6.4052 | 5.3889 | 4.4761 | 28.4074 | 27.147 | 25.6977 | 23.2822 | 21.2231 | 12.5412 | 6.0405 | 1.3934 | -1.9239 | -3.3238 | 0 | 62.317 | 58.0651 | 56.4052 | 55.3889 | 54.4761 | 53.4074 | 52.147 | 50.6977 | 48.2822 | 46.2231 | 37.5412 | 31.0405 | 26.3934 | 23.0761 | 21.6762 | 12.317 | 5.2666 | 2.4305 | 0.62546 | -1.5308 | 21.2667 | 17.5866 | 8.8886 | 2.6283 | -4.6717 | -23.0998 | -38.1287 | -49.0625 | -54.9993 | -50.1078 | 62.317 | 55.2666 | 52.4305 | 50.6255 | 48.4692 | 46.2667 | 42.5866 | 33.8886 | 27.6283 | 20.3283 | 1.9002 | -13.1287 | -24.0625 | -29.9993 | -25.1078 | 369695 | 424981 | ROCHDALE
| Lytham | 19.9546 | 17.8133 | 16.9517 | 16.2985 | 15.495 | 14.6683 | 13.8967 | 13.2075 | 12.5868 | 12.0622 | 7.9391 | 0.35495 | -5.7751 | -12.3945 | -18.2773 | 19.9546 | 17.8133 | 16.9517 | 16.2985 | 15.495 | 14.6683 | 13.8967 | 13.2075 | 12.5868 | 12.0622 | 7.9391 | 0.35495 | -5.7751 | -12.3945 | -18.2773 | 19.9546 | 18.8486 | 18.0765 | 17.415 | 16.6513 | 15.9553 | 15.0869 | 13.9993 | 13.1875 | 12.3809 | 10.012 | 7.673 | 5.5695 | 3.2791 | 1.5843 | 19.9546 | 18.8486 | 18.0765 | 17.415 | 16.6513 | 15.9553 | 15.0869 | 13.9993 | 13.1875 | 12.3809 | 10.012 | 7.673 | 5.5695 | 3.2791 | 1.5843 | 19.9546 | 17.6068 | 16.761 | 16.219 | 15.5203 | 14.8117 | 14.2189 | 13.7085 | 13.3602 | 13.0475 | 9.5926 | 2.5884 | -2.9989 | -8.9065 | -13.9644 | 0 | 19.9546 | 17.6068 | 16.761 | 16.219 | 15.5203 | 14.8117 | 14.2189 | 13.7085 | 13.3602 | 13.0475 | 9.5926 | 2.5884 | -2.9989 | -8.9065 | -13.9644 | 19.9546 | 18.9325 | 18.4263 | 18.0086 | 17.3656 | 16.6581 | 15.6152 | 13.2036 | 10.8256 | 8.4419 | 1.5775 | -5.0712 | -10.1774 | -13.3497 | -10.8138 | 0 | 19.9546 | 18.9325 | 18.4263 | 18.0086 | 17.3656 | 16.6581 | 15.6152 | 13.2036 | 10.8256 | 8.4419 | 1.5775 | -5.0712 | -10.1774 | -13.3497 | -10.8138 | 19.9546 | 18.513 | 17.8586 | 17.3642 | 16.8306 | 16.3113 | 15.8087 | 15.294 | 14.7222 | 14.1812 | 12.3435 | 10.2339 | 8.879 | 7.5491 | 6.8918 | 0 | 19.9546 | 18.513 | 17.8586 | 17.3642 | 16.8306 | 16.3113 | 15.8087 | 15.294 | 14.7222 | 14.1812 | 12.3435 | 10.2339 | 8.879 | 7.5491 | 6.8918 | 19.9546 | 17.954 | 17.0819 | 16.413 | 15.5371 | 14.66 | 13.4047 | 10.7233 | 8.1809 | 5.6299 | -1.7564 | -8.8417 | -14.4357 | -18.1967 | -16.3175 | 19.9546 | 17.954 | 17.0819 | 16.413 | 15.5371 | 14.66 | 13.4047 | 10.7233 | 8.1809 | 5.6299 | -1.7564 | -8.8417 | -14.4357 | -18.1967 | -16.3175 | 335361 | 429316 | PENWORTHAM
| Moss Nook | 44.7437 | 40.3349 | 38.2915 | 36.4366 | 34.2584 | 31.9839 | 27.2328 | 25.1743 | 23.0605 | 20.5176 | 10.1281 | -6.3578 | -18.4792 | -30.9832 | -42.8255 | 69.9437 | 65.5349 | 63.4915 | 61.6366 | 59.4584 | 57.1839 | 52.4328 | 50.3743 | 48.2605 | 45.7176 | 35.3281 | 18.8422 | 6.7208 | -5.7832 | -17.6255 | 44.7437 | 43.0868 | 42.0375 | 41.1408 | 40.0017 | 38.8004 | 37.2235 | 35.1504 | 33.5268 | 31.3028 | 26.3766 | 21.2752 | 16.205 | 10.5792 | 6.5288 | 69.9437 | 68.2868 | 67.2375 | 66.3408 | 65.2017 | 64.0004 | 62.4235 | 60.3504 | 58.7268 | 56.5028 | 51.5766 | 46.4752 | 41.405 | 35.7792 | 31.7288 | 44.7437 | 39.8324 | 37.795 | 36.1896 | 32.541 | 30.544 | 26.2287 | 24.5584 | 22.6962 | 20.4248 | 11.2752 | -3.5334 | -14.7865 | -26.2066 | -36.7513 | 0 | 69.9437 | 65.0324 | 62.995 | 61.3896 | 57.741 | 55.744 | 51.4287 | 49.7584 | 47.8962 | 45.6248 | 36.4752 | 21.6666 | 10.4135 | -1.0066 | -11.5513 | 44.7437 | 42.6233 | 41.305 | 39.8634 | 37.9394 | 35.2132 | 29.9819 | 24.8842 | 19.3687 | 12.9041 | -2.8698 | -17.0763 | -27.3343 | -33.6534 | -30.2927 | 0 | 69.9437 | 67.8233 | 66.505 | 65.0634 | 63.1394 | 60.4132 | 55.1819 | 50.0842 | 44.5687 | 38.1041 | 22.3302 | 8.1237 | -2.1343 | -8.4534 | -5.0927 | 44.7437 | 42.4863 | 41.161 | 39.7227 | 38.3342 | 36.8026 | 32.6211 | 30.906 | 28.869 | 26.2711 | 19.7403 | 12.6975 | 8.9836 | 4.8473 | 2.479 | 0 | 69.9437 | 67.6863 | 66.361 | 64.9227 | 63.5342 | 62.0026 | 57.8211 | 56.106 | 54.069 | 51.4711 | 44.9403 | 37.8975 | 34.1836 | 30.0473 | 27.679 | 44.7437 | 40.3496 | 38.1919 | 36.2583 | 33.8618 | 30.813 | 25.1899 | 19.5739 | 13.7452 | 6.9632 | -9.883 | -24.9959 | -36.1207 | -43.4601 | -41.2617 | 69.9437 | 65.5496 | 63.3919 | 61.4583 | 59.0618 | 56.013 | 50.3899 | 44.7739 | 38.9452 | 32.1632 | 15.317 | 0.20408 | -10.9207 | -18.2601 | -16.0617 | 384073 | 385068 | MACCLESFIELD
| Moss Nook Primary | 17.6034 | 15.7544 | 15.1231 | 14.934 | 14.7444 | 14.5125 | 14.3144 | 14.1411 | 13.8813 | 13.6449 | 12.1764 | 9.654 | 7.5639 | 5.3549 | 3.3093 | 23.6034 | 21.7544 | 21.1231 | 20.934 | 20.7444 | 20.5125 | 20.3144 | 20.1411 | 19.8813 | 19.6449 | 18.1764 | 15.654 | 13.5639 | 11.3549 | 9.3093 | 17.6034 | 17.1588 | 16.9417 | 16.7365 | 16.5157 | 16.2454 | 15.8384 | 15.3863 | 15.0596 | 14.7309 | 13.7934 | 12.9841 | 12.3311 | 11.4563 | 10.846 | 23.6034 | 23.1588 | 22.9417 | 22.7365 | 22.5157 | 22.2454 | 21.8384 | 21.3863 | 21.0596 | 20.7309 | 19.7934 | 18.9841 | 18.3311 | 17.4563 | 16.846 | 17.6034 | 15.4161 | 14.716 | 14.5233 | 14.3331 | 14.1438 | 13.9638 | 13.7781 | 13.5841 | 13.4137 | 12.4739 | 10.2791 | 8.4351 | 6.5355 | 4.8581 | 0 | 23.6034 | 21.4161 | 20.716 | 20.5233 | 20.3331 | 20.1438 | 19.9638 | 19.7781 | 19.5841 | 19.4137 | 18.4739 | 16.2791 | 14.4351 | 12.5355 | 10.8581 | 17.6034 | 16.1677 | 15.6771 | 15.538 | 15.393 | 15.2163 | 14.9679 | 14.2652 | 13.4782 | 12.6801 | 10.3897 | 8.1967 | 6.4689 | 5.402 | 6.0861 | 0 | 23.6034 | 22.1677 | 21.6771 | 21.538 | 21.393 | 21.2163 | 20.9679 | 20.2652 | 19.4782 | 18.6801 | 16.3897 | 14.1967 | 12.4689 | 11.402 | 12.0861 | 17.6034 | 16.7388 | 16.4302 | 16.3023 | 16.2007 | 16.0669 | 15.9122 | 15.7508 | 15.5311 | 15.3154 | 14.5083 | 13.4432 | 12.7207 | 12.0986 | 11.8428 | 0 | 23.6034 | 22.7388 | 22.4302 | 22.3023 | 22.2007 | 22.0669 | 21.9122 | 21.7508 | 21.5311 | 21.3154 | 20.5083 | 19.4432 | 18.7207 | 18.0986 | 17.8428 | 17.6034 | 15.115 | 14.3451 | 14.1296 | 13.8419 | 13.5651 | 13.1877 | 12.38 | 11.524 | 10.6603 | 8.1875 | 5.8404 | 3.9751 | 2.7594 | 3.2794 | 23.6034 | 21.115 | 20.3451 | 20.1296 | 19.8419 | 19.5651 | 19.1877 | 18.38 | 17.524 | 16.6603 | 14.1875 | 11.8404 | 9.9751 | 8.7594 | 9.2794 | 384084 | 385010 | SOUTH MANCHESTER
| Nelson | 12.36 | 8.9185 | 7.542 | 6.7433 | 5.6465 | 13.7475 | 12.9076 | 12.0292 | 11.0252 | 10.101 | 3.2444 | -11.6667 | -24.6457 | -38.2783 | -49.3404 | 33.7728 | 30.3313 | 28.9548 | 28.1561 | 27.0593 | 25.7475 | 24.9076 | 24.0292 | 23.0252 | 22.101 | 15.2444 | 0.33329 | -12.6457 | -26.2783 | -37.3404 | 12.36 | 11.1865 | 10.3611 | 9.6931 | 8.9399 | 17.456 | 16.4029 | 14.7658 | 13.5998 | 12.422 | 8.8191 | 5.1459 | 1.7213 | -2.0117 | -4.6144 | 33.7728 | 32.5993 | 31.7739 | 31.1059 | 30.3527 | 29.456 | 28.4029 | 26.7658 | 25.5998 | 24.422 | 20.8191 | 17.1459 | 13.7213 | 9.9883 | 7.3856 | 12.36 | 8.4173 | 6.9561 | 6.1568 | 5.066 | 13.158 | 12.317 | 11.4551 | 10.6086 | 9.86 | 3.489 | -8.2482 | -20.5102 | -33.2257 | -43.1804 | 0 | 33.7728 | 29.8301 | 28.3689 | 27.5696 | 26.4788 | 25.158 | 24.317 | 23.4551 | 22.6086 | 21.86 | 15.489 | 3.7518 | -8.5102 | -21.2257 | -31.1804 | 12.36 | 10.3722 | 9.4427 | 8.8534 | 7.9373 | 16.1185 | 14.5206 | 10.4783 | 6.3296 | 2.0121 | -12.405 | -26.0902 | -37.1321 | -43.9202 | -38.0264 | 0 | 33.7728 | 31.785 | 30.8555 | 30.2662 | 29.3501 | 28.1185 | 26.5206 | 22.4783 | 18.3296 | 14.0121 | -0.40503 | -14.0902 | -25.1321 | -31.9202 | -26.0264 | 12.36 | 10.7291 | 9.7948 | 9.2525 | 8.6841 | 17.2558 | 16.6379 | 15.859 | 14.8222 | 13.7765 | 10.1899 | 6.2319 | 3.5528 | 1.1674 | 0.63259 | 0 | 33.7728 | 32.1419 | 31.2076 | 30.6653 | 30.0969 | 29.2558 | 28.6379 | 27.859 | 26.8222 | 25.7765 | 22.1899 | 18.2319 | 15.5528 | 13.1674 | 12.6326 | 12.36 | 8.6833 | 7.2039 | 6.2766 | 5.0575 | 13.0823 | 11.3591 | 7.046 | 2.5332 | -2.7688 | -18.1299 | -32.759 | -44.8412 | -53.0393 | -48.7643 | 33.7728 | 30.0961 | 28.6167 | 27.6894 | 26.4703 | 25.0823 | 23.3591 | 19.046 | 14.5332 | 9.2312 | -6.1299 | -20.759 | -32.8412 | -41.0393 | -36.7643 | 385989 | 438643 | PADIHAM
| New Mills | 24.4959 | 23.6554 | 23.1722 | 22.8722 | 22.4095 | 21.9253 | 21.3437 | 20.9472 | 20.3575 | 19.8103 | 16.1467 | 9.8511 | 4.649 | -0.67989 | -5.12 | 24.4959 | 23.6554 | 23.1722 | 22.8722 | 22.4095 | 21.9253 | 21.3437 | 20.9472 | 20.3575 | 19.8103 | 16.1467 | 9.8511 | 4.649 | -0.67989 | -5.12 | 24.4959 | 24.0404 | 23.5981 | 23.2136 | 22.765 | 22.2818 | 21.6558 | 20.8511 | 20.1368 | 19.4136 | 17.0878 | 14.876 | 12.7886 | 10.3659 | 8.6946 | 24.4959 | 24.0404 | 23.5981 | 23.2136 | 22.765 | 22.2818 | 21.6558 | 20.8511 | 20.1368 | 19.4136 | 17.0878 | 14.876 | 12.7886 | 10.3659 | 8.6946 | 24.4959 | 23.615 | 23.1679 | 22.9698 | 22.4335 | 22.0754 | 21.8327 | 21.6222 | 21.3004 | 20.9641 | 14.7073 | 8.811 | 4.0096 | -0.75117 | -4.4944 | 0 | 24.4959 | 23.615 | 23.1679 | 22.9698 | 22.4335 | 22.0754 | 21.8327 | 21.6222 | 21.3004 | 20.9641 | 14.7073 | 8.811 | 4.0096 | -0.75117 | -4.4944 | 24.4959 | 24.36 | 23.9302 | 23.7933 | 23.4739 | 19.3108 | 18.8311 | 17.1866 | 15.3318 | 13.4536 | 7.7381 | 2.1898 | -2.1243 | -4.6868 | -2.482 | 0 | 24.4959 | 24.36 | 23.9302 | 23.7933 | 23.4739 | 19.3108 | 18.8311 | 17.1866 | 15.3318 | 13.4536 | 7.7381 | 2.1898 | -2.1243 | -4.6868 | -2.482 | 24.4959 | 24.0023 | 23.654 | 23.4768 | 23.2827 | 23.0424 | 22.5735 | 22.1908 | 21.5467 | 20.8982 | 18.6711 | 16.1713 | 14.1515 | 12.4239 | 11.7974 | 0 | 24.4959 | 24.0023 | 23.654 | 23.4768 | 23.2827 | 23.0424 | 22.5735 | 22.1908 | 21.5467 | 20.8982 | 18.6711 | 16.1713 | 14.1515 | 12.4239 | 11.7974 | 24.4959 | 23.9406 | 23.2755 | 22.9401 | 22.439 | 18.1496 | 17.5188 | 15.6701 | 13.6851 | 11.6751 | 5.5092 | -0.49288 | -5.2693 | -8.3952 | -6.8006 | 24.4959 | 23.9406 | 23.2755 | 22.9401 | 22.439 | 18.1496 | 17.5188 | 15.6701 | 13.6851 | 11.6751 | 5.5092 | -0.49288 | -5.2693 | -8.3952 | -6.8006 | 401141 | 383916 | STALYBRIDGE
| Orrell | 24.8262 | 20.2232 | 17.9014 | 16.4225 | 14.7232 | 24.9021 | 23.3806 | 22.1262 | 15.9957 | 14.4849 | 3.0231 | -7.9623 | -17.6805 | -26.2995 | -32.8089 | 51.5262 | 46.9232 | 44.6014 | 43.1225 | 41.4232 | 39.6021 | 38.0806 | 36.8262 | 30.6957 | 29.1849 | 17.7231 | 6.7377 | -2.9805 | -11.5995 | -18.1089 | 24.8262 | 23.4491 | 22.5883 | 21.9639 | 21.222 | 32.3308 | 31.2416 | 29.9553 | 28.4769 | 26.9189 | 22.1075 | 17.276 | 11.9379 | 7.2448 | 4.397 | 51.5262 | 50.1491 | 49.2883 | 48.6639 | 47.922 | 47.0308 | 45.9416 | 44.6553 | 43.1769 | 41.6189 | 36.8075 | 31.976 | 26.6379 | 21.9448 | 19.097 | 24.8262 | 19.6428 | 17.2731 | 15.9654 | 14.3808 | 24.7098 | 23.4203 | 22.4788 | 16.9064 | 15.8088 | 4.4234 | -5.996 | -14.4377 | -22.4358 | -28.0251 |  | 51.5262 | 46.3428 | 43.9731 | 42.6654 | 41.0808 | 39.4098 | 38.1203 | 37.1788 | 31.6064 | 30.5088 | 19.1234 | 8.704 | 0.26227 | -7.7358 | -13.3251 | 24.8262 | 21.6436 | 19.901 | 18.7889 | 17.3135 | 27.5076 | 25.4878 | 12.3353 | 9.2077 | 5.9426 | -4.1723 | -14.0376 | -21.6943 | -26.3961 | -23.003 |  | 51.5262 | 48.3436 | 46.601 | 45.4889 | 44.0135 | 42.2076 | 40.1878 | 27.0353 | 23.9077 | 20.6426 | 10.5277 | 0.66244 | -6.9943 | -11.6961 | -8.303 | 24.8262 | 22.523 | 20.9116 | 19.8777 | 18.8456 | 29.506 | 28.2579 | 27.2467 | 21.2971 | 19.88 | 10.9298 | 5.6208 | 1.1847 | -1.8058 | -2.1482 |  | 51.5262 | 49.223 | 47.6116 | 46.5777 | 45.5456 | 44.206 | 42.9579 | 41.9467 | 35.9971 | 34.58 | 25.6298 | 20.3208 | 15.8847 | 12.8942 | 12.5518 | 24.8262 | 19.3459 | 16.8001 | 15.251 | 13.4205 | 23.5014 | 21.3978 | 8 | 4.6809 | 1.2293 | -9.6958 | -20.5851 | -29.0664 | -34.5304 | -31.8999 | 51.5262 | 46.0459 | 43.5001 | 41.951 | 40.1205 | 38.2014 | 36.0978 | 22.7 | 19.3809 | 15.9293 | 5.0042 | -5.8851 | -14.3664 | -19.8304 | -17.1999 | 352784 | 404565 | KIRKBY
| Padiham | 34.1904 | 30.1388 | 27.054 | 25.8821 | 24.6316 | 23.366 | 19.1423 | 18.0852 | 16.2274 | 10.0732 | 0.74859 | -14.4733 | -32.6299 | -41.0797 | -47.7851 | 65.6904 | 61.6388 | 58.554 | 57.3821 | 56.1316 | 54.866 | 50.6423 | 49.5852 | 47.7274 | 41.5732 | 32.2486 | 17.0267 | -1.1299 | -9.5797 | -16.2851 | 34.1904 | 32.3711 | 31.1787 | 30.2117 | 29.1978 | 28.136 | 26.764 | 25.0152 | 23.2154 | 21.3946 | 14.1236 | 8.5558 | 3.2372 | -10.5416 | -15.1624 | 65.6904 | 63.8711 | 62.6787 | 61.7117 | 60.6978 | 59.636 | 58.264 | 56.5152 | 54.7154 | 52.8946 | 45.6236 | 40.0558 | 34.7372 | 20.9584 | 16.3376 | 34.1904 | 29.5609 | 26.3864 | 25.1728 | 23.8976 | 22.6165 | 21.4085 | 20.2112 | 19.09 | 18.0752 | 0.48567 | -13.9074 | -22.328 | -29.5169 | -34.572 |  | 65.6904 | 61.0609 | 57.8864 | 56.6728 | 55.3976 | 54.1165 | 52.9085 | 51.7112 | 50.59 | 49.5752 | 31.9857 | 17.5926 | 9.172 | 1.9831 | -3.072 | 34.1904 | 31.2709 | 28.5355 | 27.4229 | 23.0191 | 21.5988 | 18.2469 | 15.2952 | 11.8023 | -0.87672 | -16.19 | -25.3599 | -32.2467 | -36.0848 | -32.0834 |  | 65.6904 | 62.7709 | 60.0355 | 58.9229 | 54.5191 | 53.0988 | 49.7469 | 46.7952 | 43.3023 | 30.6233 | 15.31 | 6.1401 | -0.74673 | -4.5848 | -0.5834 | 34.1904 | 31.1495 | 28.3428 | 27.3784 | 26.5456 | 25.6558 | 21.7248 | 20.8931 | 19.2608 | 13.0678 | 6.1365 | -3.4158 | -16.5789 | -19.4619 | -20.1546 |  | 65.6904 | 62.6495 | 59.8428 | 58.8784 | 58.0456 | 57.1558 | 53.2248 | 52.3931 | 50.7608 | 44.5678 | 37.6365 | 28.0842 | 14.9211 | 12.0381 | 11.3454 | 34.1904 | 29.4396 | 26.195 | 24.8335 | 20.2193 | 18.7256 | 15.3351 | 12.2339 | 8.28 | -5.1061 | -21.7795 | -31.9059 | -39.728 | -44.5557 | -41.5408 | 65.6904 | 60.9396 | 57.695 | 56.3335 | 51.7193 | 50.2256 | 46.8351 | 43.7339 | 39.78 | 26.3939 | 9.7205 | -0.40593 | -8.228 | -13.0557 | -10.0408 | 378571 | 433224 | PADIHAM
| Peel | 15.0919 | 11.9344 | 7.4205 | 3.3453 | -0.9645 | -5.3395 | -6.362 | -7.2033 | -8.1097 | -8.958 | -12.8386 | -18.8699 | -24.0153 | -29.0829 | -33.6998 | 15.0919 | 11.9344 | 7.4205 | 3.3453 | -0.9645 | -5.3395 | -6.362 | -7.2033 | -8.1097 | -8.958 | -12.8386 | -18.8699 | -24.0153 | -29.0829 | -33.6998 | 15.0919 | 13.8241 | 13.0125 | 12.4488 | 11.8783 | 11.2963 | 10.5538 | 9.5255 | 8.4962 | 7.4744 | 4.4046 | 1.0902 | -1.9226 | -5.2643 | -9.0671 | 15.0919 | 13.8241 | 13.0125 | 12.4488 | 11.8783 | 11.2963 | 10.5538 | 9.5255 | 8.4962 | 7.4744 | 4.4046 | 1.0902 | -1.9226 | -5.2643 | -9.0671 | 15.0919 | 11.5204 | 6.9692 | 2.8666 | -1.3666 | -5.5767 | -6.4944 | -7.1966 | -7.8925 | -8.5146 | -13.056 | -18.437 | -22.9158 | -27.0031 | -30.4862 |  | 15.0919 | 11.5204 | 6.9692 | 2.8666 | -1.3666 | -5.5767 | -6.4944 | -7.1966 | -7.8925 | -8.5146 | -13.056 | -18.437 | -22.9158 | -27.0031 | -30.4862 | 15.0919 | 12.9174 | 8.6169 | 4.6673 | 0.4752 | -5.321 | -6.4799 | -8.8349 | -10.7478 | -12.605 | -17.9015 | -22.988 | -26.7411 | -29.0073 | -27.5721 |  | 15.0919 | 12.9174 | 8.6169 | 4.6673 | 0.4752 | -5.321 | -6.4799 | -8.8349 | -10.7478 | -12.605 | -17.9015 | -22.988 | -26.7411 | -29.0073 | -27.5721 | 15.0919 | 13.0186 | 8.7566 | 4.8088 | 0.74359 | -3.4069 | -4.2723 | -5.0599 | -6.0452 | -7.0217 | -9.914 | -13.0214 | -15.4354 | -17.3999 | -18.3981 |  | 15.0919 | 13.0186 | 8.7566 | 4.8088 | 0.74359 | -3.4069 | -4.2723 | -5.0599 | -6.0452 | -7.0217 | -9.914 | -13.0214 | -15.4354 | -17.3999 | -18.3981 | 15.0919 | 11.5005 | 6.7981 | 2.6471 | -1.729 | -7.652 | -8.9413 | -11.502 | -13.5462 | -15.5277 | -21.1843 | -26.6256 | -30.7116 | -33.3857 | -32.5051 | 15.0919 | 11.5005 | 6.7981 | 2.6471 | -1.729 | -7.652 | -8.9413 | -11.502 | -13.5462 | -15.5277 | -21.1843 | -26.6256 | -30.7116 | -33.3857 | -32.5051 | 335644 | 432080 | PENWORTHAM | Firm Capacity exceeded in FY28. Review in ED2 and potential reinforcement in ED3.
| Penrith & Shap | 37.5585 | 30.9902 | 28.9392 | 27.5985 | 25.2697 | 22.8259 | 20.1918 | 17.2424 | 13.1036 | 8.3083 | -16.3554 | -35.8817 | -54.8234 | -65.6115 | -74.2557 | 37.5585 | 30.9902 | 28.9392 | 27.5985 | 25.2697 | 22.8259 | 20.1918 | 17.2424 | 13.1036 | 8.3083 | -16.3554 | -35.8817 | -54.8234 | -65.6115 | -74.2557 | 37.5585 | 35.2286 | 33.8165 | 32.2717 | 30.3411 | 28.5913 | 26.3146 | 21.0437 | 19.7188 | 18.2408 | 12.3045 | 2.3545 | -9.06 | -26.4247 | -44.4912 | 37.5585 | 35.2286 | 33.8165 | 32.2717 | 30.3411 | 28.5913 | 26.3146 | 21.0437 | 19.7188 | 18.2408 | 12.3045 | 2.3545 | -9.06 | -26.4247 | -44.4912 | 37.5585 | 30.1791 | 28.0698 | 26.9652 | 24.9125 | 22.846 | 20.7768 | 17.9183 | 14.2733 | 10.233 | -15.0837 | -41.5047 | -57.9268 | -69.2875 | -77.0653 |  | 37.5585 | 30.1791 | 28.0698 | 26.9652 | 24.9125 | 22.846 | 20.7768 | 17.9183 | 14.2733 | 10.233 | -15.0837 | -41.5047 | -57.9268 | -69.2875 | -77.0653 | 37.5585 | 33.1401 | 31.6138 | 30.059 | 26.5244 | 23.7717 | 20.7831 | 14.6036 | -3.4507 | -10.031 | -32.4197 | -51.0055 | -63.1012 | -69.8208 | -68.0612 |  | 37.5585 | 33.1401 | 31.6138 | 30.059 | 26.5244 | 23.7717 | 20.7831 | 14.6036 | -3.4507 | -10.031 | -32.4197 | -51.0055 | -63.1012 | -69.8208 | -68.0612 | 37.5585 | 34.5208 | 33.1287 | 31.9236 | 30.2697 | 28.8447 | 27.1565 | 25.0172 | 21.8688 | 17.8332 | -3.6561 | -19.041 | -34.5367 | -43.0455 | -47.0024 |  | 37.5585 | 34.5208 | 33.1287 | 31.9236 | 30.2697 | 28.8447 | 27.1565 | 25.0172 | 21.8688 | 17.8332 | -3.6561 | -19.041 | -34.5367 | -43.0455 | -47.0024 | 37.5585 | 30.0916 | 27.6383 | 25.6907 | 21.818 | 18.8774 | 15.7305 | 9.3652 | -8.1627 | -13.7227 | -35.2107 | -55.7208 | -69.9541 | -78.1106 | -77.0686 | 37.5585 | 30.0916 | 27.6383 | 25.6907 | 21.818 | 18.8774 | 15.7305 | 9.3652 | -8.1627 | -13.7227 | -35.2107 | -55.7208 | -69.9541 | -78.1106 | -77.0686 | 349996 | 530398 | HUTTON
| Preston East | 25.2591 | 18.6958 | 15.4123 | 4.6817 | -9.2992 | -14.1871 | -18.0019 | -22.3154 | -26.7568 | -31.1505 | -41.101 | -52.2483 | -61.1679 | -69.5592 | -77.0113 | 25.2591 | 18.6958 | 15.4123 | 4.6817 | -9.2992 | -14.1871 | -18.0019 | -22.3154 | -26.7568 | -31.1505 | -41.101 | -52.2483 | -61.1679 | -69.5592 | -77.0113 | 25.2591 | 23.8767 | 22.9055 | 14.8989 | 2.8601 | 1.6858 | 0.50125 | -1.0087 | -2.1041 | -3.223 | -6.7683 | -10.5026 | -14.2949 | -18.7254 | -21.8031 | 25.2591 | 23.8767 | 22.9055 | 14.8989 | 2.8601 | 1.6858 | 0.50125 | -1.0087 | -2.1041 | -3.223 | -6.7683 | -10.5026 | -14.2949 | -18.7254 | -21.8031 | 25.2591 | 17.6698 | 13.0684 | 0.77416 | -14.7834 | -20.755 | -24.5732 | -28.8719 | -33.1871 | -37.44 | -47.0538 | -56.4412 | -64.7845 | -72.3442 | -78.586 |  | 25.2591 | 17.6698 | 13.0684 | 0.77416 | -14.7834 | -20.755 | -24.5732 | -28.8719 | -33.1871 | -37.44 | -47.0538 | -56.4412 | -64.7845 | -72.3442 | -78.586 | 25.2591 | 20.454 | 16.4984 | 4.4124 | -12.4219 | -18.3139 | -22.5453 | -28.6573 | -34.9888 | -41.7171 | -54.9594 | -64.9791 | -72.4258 | -76.3522 | -73.354 |  | 25.2591 | 20.454 | 16.4984 | 4.4124 | -12.4219 | -18.3139 | -22.5453 | -28.6573 | -34.9888 | -41.7171 | -54.9594 | -64.9791 | -72.4258 | -76.3522 | -73.354 | 25.2591 | 23.2557 | 20.8171 | 10.7313 | -3.3697 | -7.826 | -11.3611 | -15.508 | -19.906 | -24.3323 | -32.3423 | -37.253 | -40.5487 | -43.0085 | -43.8917 |  | 25.2591 | 23.2557 | 20.8171 | 10.7313 | -3.3697 | -7.826 | -11.3611 | -15.508 | -19.906 | -24.3323 | -32.3423 | -37.253 | -40.5487 | -43.0085 | -43.8917 | 25.2591 | 17.3241 | 12.6099 | 0.060236 | -17.4395 | -23.6474 | -28.1615 | -34.8507 | -41.94 | -48.7671 | -62.4705 | -73.1966 | -81.3833 | -86.1149 | -83.9365 | 25.2591 | 17.3241 | 12.6099 | 0.060236 | -17.4395 | -23.6474 | -28.1615 | -34.8507 | -41.94 | -48.7671 | -62.4705 | -73.1966 | -81.3833 | -86.1149 | -83.9365 | 356774 | 432942 | PENWORTHAM | Firm Capacity exceeded in FY28. Review in ED2 and if required transfer a primary onto Ribble BSP.
| Radcliffe | 8.1587 | 5.7967 | 5.0662 | 4.5604 | 3.8725 | 3.1537 | 2.4605 | 1.7798 | 0.91209 | 0.074841 | -5.1618 | -11.9383 | -17.0303 | -21.7413 | -25.0074 | 15.1587 | 12.7967 | 12.0662 | 11.5604 | 10.8725 | 10.1537 | 9.4605 | 8.7798 | 7.9121 | 7.0748 | 1.8382 | -4.9383 | -10.0303 | -14.7413 | -18.0074 | 8.1587 | 7.2466 | 6.9752 | 6.6375 | 6.171 | 5.6377 | 4.9506 | 4.1019 | 3.3275 | 2.4783 | -0.486 | -3.1915 | -5.8378 | -8.8358 | -10.668 | 15.1587 | 14.2466 | 13.9752 | 13.6375 | 13.171 | 12.6377 | 11.9506 | 11.1019 | 10.3275 | 9.4783 | 6.514 | 3.8085 | 1.1622 | -1.8358 | -3.668 | 8.1587 | 5.3567 | 4.4064 | 3.7577 | 2.9195 | 2.0492 | 1.2356 | 0.42175 | -0.51982 | -1.5467 | -7.6376 | -14.4891 | -19.1614 | -22.9058 | -24.5812 |  | 15.1587 | 12.3567 | 11.4064 | 10.7577 | 9.9195 | 9.0492 | 8.2356 | 7.4217 | 6.4802 | 5.4533 | -0.63757 | -7.4891 | -12.1614 | -15.9058 | -17.5812 | 8.1587 | 6.6498 | 6.0433 | 5.0637 | 3.8432 | 2.9752 | 1.7856 | -0.47789 | -2.8051 | -5.0755 | -11.4858 | -16.862 | -20.3048 | -22.1824 | -21.1243 |  | 15.1587 | 13.6498 | 13.0433 | 12.0637 | 10.8432 | 9.9752 | 8.7856 | 6.5221 | 4.1949 | 1.9245 | -4.4858 | -9.862 | -13.3048 | -15.1824 | -14.1243 | 8.1587 | 6.7173 | 6.2859 | 5.9778 | 5.6014 | 5.1153 | 4.5428 | 3.9317 | 3.0972 | 2.2248 | -1.4189 | -5.0613 | -7.6507 | -10.0399 | -11.5517 |  | 15.1587 | 13.7173 | 13.2859 | 12.9778 | 12.6014 | 12.1153 | 11.5428 | 10.9317 | 10.0972 | 9.2248 | 5.5811 | 1.9387 | -0.65067 | -3.0399 | -4.5517 | 8.1587 | 5.6002 | 4.5851 | 3.3502 | 1.9038 | 0.89427 | -0.46906 | -2.9812 | -5.4971 | -7.9546 | -14.9746 | -20.8984 | -24.7136 | -26.9125 | -26.3361 | 15.1587 | 12.6002 | 11.5851 | 10.3502 | 8.9038 | 7.8943 | 6.5309 | 4.0188 | 1.5029 | -0.95461 | -7.9746 | -13.8984 | -17.7136 | -19.9125 | -19.3361 | 377524 | 406160 | KEARSLEY
| Red Bank | 45.2487 | 33.3638 | 28.1291 | 23.3545 | 21.2718 | 18.9335 | 17.3467 | 15.8105 | 14.013 | 12.441 | 5.8496 | -3.6587 | -10.9562 | -18.0773 | -24.368 | 63.2487 | 51.3638 | 46.1291 | 41.3545 | 39.2718 | 36.9335 | 35.3467 | 33.8105 | 32.013 | 30.441 | 23.8496 | 14.3413 | 7.0438 | -0.077289 | -6.368 | 45.2487 | 41.6161 | 38.7122 | 34.1387 | 32.8959 | 31.5752 | 30.2129 | 28.5725 | 27.138 | 25.6889 | 21.548 | 17.561 | 13.6466 | 9.3181 | 5.5377 | 63.2487 | 59.6161 | 56.7122 | 52.1387 | 50.8959 | 49.5752 | 48.2129 | 46.5725 | 45.138 | 43.6889 | 39.548 | 35.561 | 31.6466 | 27.3181 | 23.5377 | 45.2487 | 31.5707 | 22.7636 | 15.1629 | 12.4883 | 9.891 | 8.1149 | 6.3448 | 4.6712 | 3.0818 | -3.5052 | -12.5963 | -19.0996 | -24.9192 | -29.1853 |  | 63.2487 | 49.5707 | 40.7636 | 33.1629 | 30.4883 | 27.891 | 26.1149 | 24.3448 | 22.6712 | 21.0818 | 14.4948 | 5.4037 | -1.0996 | -6.9192 | -11.1853 | 45.2487 | 35.8881 | 28.0783 | 20.457 | 18.0396 | 15.4758 | 13.3042 | 9.8084 | 6.2896 | 2.8871 | -6.2353 | -14.4322 | -19.9438 | -22.949 | -21.6465 |  | 63.2487 | 53.8881 | 46.0783 | 38.457 | 36.0396 | 33.4758 | 31.3042 | 27.8084 | 24.2896 | 20.8871 | 11.7647 | 3.5678 | -1.9438 | -4.949 | -3.6465 | 45.2487 | 38.9033 | 34.8867 | 30.1863 | 28.4956 | 26.7907 | 25.5155 | 24.1193 | 22.3042 | 20.6355 | 15.8744 | 11.023 | 7.7194 | 4.4508 | 2.2352 |  | 63.2487 | 56.9033 | 52.8867 | 48.1863 | 46.4956 | 44.7907 | 43.5155 | 42.1193 | 40.3042 | 38.6355 | 33.8744 | 29.023 | 25.7194 | 22.4508 | 20.2352 | 45.2487 | 30.5478 | 21.4143 | 13.7407 | 10.7658 | 7.9829 | 5.5361 | 1.7096 | -1.9763 | -5.5529 | -15.2493 | -23.8638 | -29.7843 | -33.2716 | -32.5829 | 63.2487 | 48.5478 | 39.4143 | 31.7407 | 28.7658 | 25.9829 | 23.5361 | 19.7096 | 16.0237 | 12.4471 | 2.7507 | -5.8638 | -11.7843 | -15.2716 | -14.5829 | 384542 | 399276 | WHITEGATE
| Ribble | 108.7368 | 94.3823 | 85.6398 | 79.2424 | 74.9708 | 70.7364 | 66.8853 | 63.6034 | 59.5632 | 56.2289 | 38.5276 | 10.9237 | -11.37 | -34.3879 | -53.8207 | 144.7368 | 130.3823 | 121.6398 | 115.2424 | 110.9708 | 106.7364 | 102.8853 | 99.6034 | 95.5632 | 92.2289 | 74.5276 | 46.9237 | 24.63 | 1.6121 | -17.8207 | 108.7368 | 102.9881 | 100.8067 | 99.1196 | 97.079 | 94.9159 | 92.1001 | 88.5377 | 85.568 | 82.4047 | 72.6069 | 62.4013 | 52.0679 | 41.4924 | 34.8725 | 144.7368 | 138.9881 | 136.8067 | 135.1196 | 133.079 | 130.9159 | 128.1001 | 124.5377 | 121.568 | 118.4047 | 108.6069 | 98.4013 | 88.0679 | 77.4924 | 70.8725 | 108.7368 | 92.4124 | 80.6818 | 70.4503 | 62.3594 | 55.7976 | 52.6599 | 50.1751 | 47.1915 | 44.6954 | 29.2304 | 3.347 | -17.3506 | -38.0922 | -54.5325 |  | 144.7368 | 128.4124 | 116.6818 | 106.4503 | 98.3594 | 91.7976 | 88.6599 | 86.1751 | 83.1915 | 80.6954 | 65.2304 | 39.347 | 18.6494 | -2.0922 | -18.5325 | 108.7368 | 99.0809 | 88.8643 | 78.9245 | 70.9353 | 64.1327 | 59.0988 | 49.846 | 39.9442 | 30.5171 | 4.0312 | -20.1457 | -38.6155 | -49.7815 | -41.4604 |  | 144.7368 | 135.0809 | 124.8643 | 114.9245 | 106.9353 | 100.1327 | 95.0988 | 85.846 | 75.9442 | 66.5171 | 40.0312 | 15.8543 | -2.6155 | -13.7815 | -5.4604 | 108.7368 | 99.0955 | 91.6133 | 85.9178 | 82.8429 | 79.6222 | 76.4104 | 73.5658 | 69.7018 | 66.3488 | 55.7748 | 45.0994 | 37.1406 | 30.4273 | 27.8145 |  | 144.7368 | 135.0955 | 127.6133 | 121.9178 | 118.8429 | 115.6222 | 112.4104 | 109.5658 | 105.7018 | 102.3488 | 91.7748 | 81.0994 | 73.1406 | 66.4273 | 63.8145 | 108.7368 | 91.9918 | 79.838 | 68.9758 | 60.1238 | 52.8156 | 47.2066 | 37.1338 | 26.7126 | 16.7595 | -11.6406 | -37.8214 | -58.27 | -71.6029 | -65.5215 | 144.7368 | 127.9918 | 115.838 | 104.9758 | 96.1238 | 88.8156 | 83.2066 | 73.1338 | 62.7126 | 52.7595 | 24.3594 | -1.8214 | -22.27 | -35.6029 | -29.5215 | 351794 | 429241 | PENWORTHAM
| Risley | 4.7888 | 2.9481 | 2.6206 | 2.463 | 2.2567 | 2.0359 | 1.8198 | 1.5844 | 1.2695 | 0.96195 | -0.63924 | -3.1236 | -5.1691 | -7.5539 | -9.685 | 15.4888 | 13.6481 | 13.3206 | 13.163 | 12.9567 | 12.7359 | 12.5198 | 12.2844 | 11.9695 | 11.662 | 10.0608 | 7.5764 | 5.5309 | 3.1461 | 1.015 | 4.7888 | 4.0389 | 3.9408 | 3.798 | 3.6517 | 3.4766 | 3.259 | 3.0038 | 2.7368 | 2.4627 | 1.609 | 0.67504 | -0.12191 | -1.1846 | -1.9313 | 15.4888 | 14.7389 | 14.6408 | 14.498 | 14.3517 | 14.1766 | 13.959 | 13.7038 | 13.4368 | 13.1627 | 12.309 | 11.375 | 10.5781 | 9.5154 | 8.7687 | 4.7888 | 2.689 | 2.3099 | 2.1534 | 1.9518 | 1.739 | 1.5342 | 1.3162 | 1.0638 | 0.8222 | -0.61431 | -2.96 | -4.8016 | -6.5457 | -8.0673 |  | 15.4888 | 13.389 | 13.0099 | 12.8534 | 12.6518 | 12.439 | 12.2342 | 12.0162 | 11.7638 | 11.5222 | 10.0857 | 7.74 | 5.8984 | 4.1543 | 2.6327 | 4.7888 | 3.3839 | 3.191 | 3.093 | 2.8737 | 2.6708 | 2.3348 | 1.5987 | 0.79917 | 0.0055272 | -2.3131 | -4.4926 | -6.3106 | -7.539 | -6.8252 |  | 15.4888 | 14.0839 | 13.891 | 13.793 | 13.5737 | 13.3708 | 13.0348 | 12.2987 | 11.4992 | 10.7055 | 8.3869 | 6.2074 | 4.3894 | 3.161 | 3.8748 | 4.7888 | 3.6066 | 3.4523 | 3.3732 | 3.3052 | 3.1916 | 3.0265 | 2.8208 | 2.5185 | 2.2045 | 1.1495 | -0.0010547 | -0.75819 | -1.3794 | -1.4793 |  | 15.4888 | 14.3066 | 14.1523 | 14.0732 | 14.0052 | 13.8916 | 13.7265 | 13.5208 | 13.2185 | 12.9045 | 11.8495 | 10.6989 | 9.9418 | 9.3206 | 9.2207 | 4.7888 | 2.5593 | 2.1388 | 1.9615 | 1.6756 | 1.4494 | 1.101 | 0.32082 | -0.50075 | -1.3132 | -3.6993 | -6.1041 | -8.3747 | -9.7939 | -9.2421 | 15.4888 | 13.2593 | 12.8388 | 12.6615 | 12.3756 | 12.1494 | 11.801 | 11.0208 | 10.1992 | 9.3868 | 7.0007 | 4.5959 | 2.3253 | 0.90613 | 1.4579 | 365181 | 392989 | BOLD
| Rochdale Central | 49.181 | 48.3191 | 47.7963 | 47.2269 | 46.5942 | 45.9331 | 45.2573 | 44.5377 | 43.8159 | 43.1195 | 37.4564 | 29.0108 | 22.4816 | 15.3861 | 9.1611 | 61.181 | 60.3191 | 59.7963 | 59.2269 | 58.5942 | 57.9331 | 57.2573 | 56.5377 | 55.8159 | 55.1195 | 49.4564 | 41.0108 | 34.4816 | 27.3861 | 21.1611 | 49.181 | 48.5872 | 47.9909 | 47.3762 | 46.6402 | 45.7586 | 44.7023 | 43.3598 | 42.8436 | 42.3177 | 39.9256 | 37.1199 | 34.67 | 32.338 | 30.8745 | 61.181 | 60.5872 | 59.9909 | 59.3762 | 58.6402 | 57.7586 | 56.7023 | 55.3598 | 54.8436 | 54.3177 | 51.9256 | 49.1199 | 46.67 | 44.338 | 42.8745 | 49.181 | 48.2436 | 47.7307 | 47.1003 | 46.4222 | 45.7298 | 45.0349 | 44.2993 | 43.5249 | 42.7848 | 37.9733 | 29.6694 | 23.123 | 16.5814 | 11.3317 |  | 61.181 | 60.2436 | 59.7307 | 59.1003 | 58.4222 | 57.7298 | 57.0349 | 56.2993 | 55.5249 | 54.7848 | 49.9733 | 41.6694 | 35.123 | 28.5814 | 23.3317 | 49.181 | 48.8813 | 48.6458 | 48.2185 | 47.7003 | 47.0972 | 46.3065 | 44.0333 | 40.966 | 37.9117 | 29.3085 | 21.4459 | 15.4458 | 11.4999 | 13.4896 |  | 61.181 | 60.8813 | 60.6458 | 60.2185 | 59.7003 | 59.0972 | 58.3065 | 56.0333 | 52.966 | 49.9117 | 41.3085 | 33.4459 | 27.4458 | 23.4999 | 25.4896 | 49.181 | 48.6678 | 48.3042 | 47.8817 | 47.4417 | 46.8999 | 46.2669 | 45.592 | 44.8993 | 44.1971 | 41.6643 | 37.5622 | 34.9086 | 31.4675 | 29.5696 |  | 61.181 | 60.6678 | 60.3042 | 59.8817 | 59.4417 | 58.8999 | 58.2669 | 57.592 | 56.8993 | 56.1971 | 53.6643 | 49.5622 | 46.9086 | 43.4675 | 41.5696 | 49.181 | 48.4382 | 47.9158 | 47.2272 | 46.4661 | 45.6932 | 44.7357 | 42.2087 | 38.9971 | 35.7934 | 26.6422 | 18.1843 | 11.5766 | 6.9106 | 8.1365 | 61.181 | 60.4382 | 59.9158 | 59.2272 | 58.4661 | 57.6932 | 56.7357 | 54.2087 | 50.9971 | 47.7934 | 38.6422 | 30.1843 | 23.5766 | 18.9106 | 20.1365 | 389111 | 413393 | ROCHDALE
| Rossendale | 59.6374 | 58.3583 | 56.834 | 55.7655 | 54.6825 | 53.5733 | 49.2611 | 48.231 | 46.7498 | 45.285 | 37.261 | 25.014 | 14.3436 | 2.1025 | -7.6445 | 70.4374 | 69.1583 | 67.634 | 66.5655 | 65.4825 | 64.3733 | 60.0611 | 59.031 | 57.5498 | 56.085 | 48.061 | 35.814 | 25.1436 | 12.9025 | 3.1555 | 59.6374 | 58.7765 | 57.6991 | 56.9813 | 56.2885 | 55.2767 | 53.9842 | 52.3548 | 50.9955 | 49.6051 | 45.3156 | 40.8606 | 36.6961 | 32.216 | 26.8809 | 70.4374 | 69.5765 | 68.4991 | 67.7813 | 67.0885 | 66.0767 | 64.7842 | 63.1548 | 61.7955 | 60.4051 | 56.1156 | 51.6606 | 47.4961 | 43.016 | 37.6809 | 59.6374 | 58.1615 | 56.3903 | 55.0769 | 53.7567 | 52.4139 | 48.03 | 46.7837 | 45.2788 | 43.7969 | 30.7571 | 18.8707 | 9.9664 | 1.3015 | -6.0985 |  | 70.4374 | 68.9615 | 67.1903 | 65.8769 | 64.5567 | 63.2139 | 58.83 | 57.5837 | 56.0788 | 54.5969 | 41.5571 | 29.6707 | 20.7664 | 12.1015 | 4.7015 | 59.6374 | 59.2419 | 57.8412 | 56.7346 | 52.4164 | 51.2853 | 49.4171 | 45.4443 | 40.9515 | 36.7301 | 23.9522 | 12.2975 | 2.7945 | -2.6564 | 1.8999 |  | 70.4374 | 70.0419 | 68.6412 | 67.5346 | 63.2164 | 62.0853 | 60.2171 | 56.2443 | 51.7515 | 47.5301 | 34.7522 | 23.0975 | 13.5945 | 8.1436 | 12.6999 | 59.6374 | 58.6346 | 57.3033 | 56.5099 | 55.9315 | 55.2489 | 51.1745 | 50.3257 | 48.9312 | 47.4834 | 42.5263 | 37.333 | 33.8705 | 30.8506 | 29.6412 |  | 70.4374 | 69.4346 | 68.1033 | 67.3099 | 66.7315 | 66.0489 | 61.9745 | 61.1257 | 59.7312 | 58.2834 | 53.3263 | 48.133 | 44.6705 | 41.6506 | 40.4412 | 59.6374 | 58.7928 | 57.0769 | 55.6714 | 51.0977 | 49.8653 | 47.9408 | 43.7885 | 39.213 | 34.917 | 20.9181 | 7.2932 | -3.2116 | -9.865 | -6.6271 | 70.4374 | 69.5928 | 67.8769 | 66.4714 | 61.8977 | 60.6653 | 58.7408 | 54.5885 | 50.013 | 45.717 | 31.7181 | 18.0932 | 7.5884 | 0.93504 | 4.1729 | 380261 | 422010 | PADIHAM
| Royton | 33.9934 | 31.2596 | 29.9637 | 29.1611 | 28.1876 | 75.5859 | 74.6365 | 73.7006 | 72.4732 | 71.2485 | 64.7861 | 55.2143 | 47.7461 | 40.5469 | 34.9066 | 100.4062 | 97.6724 | 96.3765 | 95.5739 | 94.6004 | 93.5859 | 92.6365 | 91.7006 | 90.4732 | 89.2485 | 82.7861 | 73.2143 | 65.7461 | 58.5469 | 52.9066 | 33.9934 | 33.229 | 32.5369 | 31.9916 | 31.4138 | 79.2146 | 78.4586 | 77.4919 | 76.4454 | 75.3465 | 71.8878 | 68.2479 | 64.6302 | 60.641 | 57.7323 | 100.4062 | 99.6418 | 98.9497 | 98.4044 | 97.8266 | 97.2146 | 96.4586 | 95.4919 | 94.4454 | 93.3465 | 89.8878 | 86.2479 | 82.6302 | 78.641 | 75.7323 | 33.9934 | 30.8026 | 29.3274 | 28.2385 | 26.7893 | 73.719 | 72.341 | 70.9886 | 69.4717 | 67.9931 | 60.7036 | 51.2963 | 44.5767 | 38.7868 | 35.3408 |  | 100.4062 | 97.2154 | 95.7402 | 94.6513 | 93.2021 | 91.719 | 90.341 | 88.9886 | 87.4717 | 85.9931 | 78.7036 | 69.2963 | 62.5767 | 56.7868 | 53.3408 | 33.9934 | 31.9583 | 30.8019 | 29.7558 | 28.2869 | 75.1046 | 73.0865 | 69.5619 | 65.8968 | 62.3495 | 52.1666 | 43.8142 | 38.2528 | 35.4434 | 37.9236 |  | 100.4062 | 98.3711 | 97.2147 | 96.1686 | 94.6997 | 93.1046 | 91.0865 | 87.5619 | 83.8968 | 80.3495 | 70.1666 | 61.8142 | 56.2528 | 53.4434 | 55.9236 | 33.9934 | 32.812 | 31.9413 | 31.3637 | 30.8062 | 78.5667 | 77.8657 | 77.1031 | 75.9604 | 74.764 | 70.7183 | 66.5355 | 63.6534 | 61.1506 | 59.7336 |  | 100.4062 | 99.2248 | 98.3541 | 97.7765 | 97.219 | 96.5667 | 95.8657 | 95.1031 | 93.9604 | 92.764 | 88.7183 | 84.5355 | 81.6534 | 79.1506 | 77.7336 | 33.9934 | 30.7202 | 29.1269 | 27.8411 | 26.1645 | 72.8647 | 70.7226 | 67.0049 | 63.219 | 59.5497 | 48.8524 | 39.8455 | 33.6252 | 30.1222 | 31.8998 | 100.4062 | 97.133 | 95.5397 | 94.2539 | 92.5773 | 90.8647 | 88.7226 | 85.0049 | 81.219 | 77.5497 | 66.8524 | 57.8455 | 51.6252 | 48.1222 | 49.8998 | 392426 | 407533 | WHITEGATE
| Sale | 28.7689 | 26.5499 | 25.4637 | 24.6059 | 23.3234 | 21.944 | 20.5276 | 19.2198 | 17.7547 | 16.1592 | 8.5656 | -2.4877 | -10.817 | -18.3652 | -24.3216 | 28.7689 | 26.5499 | 25.4637 | 24.6059 | 23.3234 | 21.944 | 20.5276 | 19.2198 | 17.7547 | 16.1592 | 8.5656 | -2.4877 | -10.817 | -18.3652 | -24.3216 | 28.7689 | 27.8382 | 27.202 | 26.55 | 25.653 | 24.7222 | 23.5126 | 22.0559 | 20.889 | 19.6692 | 15.4161 | 11.122 | 7.1824 | 3.1705 | 0.47613 | 28.7689 | 27.8382 | 27.202 | 26.55 | 25.653 | 24.7222 | 23.5126 | 22.0559 | 20.889 | 19.6692 | 15.4161 | 11.122 | 7.1824 | 3.1705 | 0.47613 | 28.7689 | 26.1454 | 24.8434 | 23.8546 | 22.3896 | 20.8436 | 19.1465 | 17.5394 | 15.8594 | 13.9449 | 5.4797 | -5.4378 | -13.3688 | -20.0408 | -23.6004 |  | 28.7689 | 26.1454 | 24.8434 | 23.8546 | 22.3896 | 20.8436 | 19.1465 | 17.5394 | 15.8594 | 13.9449 | 5.4797 | -5.4378 | -13.3688 | -20.0408 | -23.6004 | 28.7689 | 27.8806 | 27.0561 | 26.2313 | 24.8007 | 23.1643 | 20.7733 | 16.6159 | 12.3732 | 8.1521 | -3.2757 | -12.6188 | -18.6007 | -21.0638 | -18.3727 |  | 28.7689 | 27.8806 | 27.0561 | 26.2313 | 24.8007 | 23.1643 | 20.7733 | 16.6159 | 12.3732 | 8.1521 | -3.2757 | -12.6188 | -18.6007 | -21.0638 | -18.3727 | 28.7689 | 27.4829 | 26.7728 | 26.2906 | 25.6628 | 24.8936 | 23.9471 | 22.9282 | 21.6389 | 20.1739 | 15.2844 | 10.2215 | 6.5493 | 2.9838 | 0.91796 |  | 28.7689 | 27.4829 | 26.7728 | 26.2906 | 25.6628 | 24.8936 | 23.9471 | 22.9282 | 21.6389 | 20.1739 | 15.2844 | 10.2215 | 6.5493 | 2.9838 | 0.91796 | 28.7689 | 26.8815 | 25.5383 | 24.3035 | 22.513 | 20.6568 | 17.9936 | 13.4545 | 8.9219 | 4.4294 | -7.9034 | -18.0716 | -24.8362 | -28.152 | -26.1799 | 28.7689 | 26.8815 | 25.5383 | 24.3035 | 22.513 | 20.6568 | 17.9936 | 13.4545 | 8.9219 | 4.4294 | -7.9034 | -18.0716 | -24.8362 | -28.152 | -26.1799 | 378726 | 392892 | CARRINGTON
| Skelmersdale | 28.4116 | 24.9894 | 22.8234 | 21.3333 | 20.1094 | 18.9177 | 17.7216 | 16.4962 | 14.9052 | 13.318 | 5.4628 | -5.2134 | -12.9975 | -19.5068 | -23.768 | 28.4116 | 24.9894 | 22.8234 | 21.3333 | 20.1094 | 18.9177 | 17.7216 | 16.4962 | 14.9052 | 13.318 | 5.4628 | -5.2134 | -12.9975 | -19.5068 | -23.768 | 28.4116 | 27.2245 | 26.3045 | 25.6371 | 24.8989 | 24.1352 | 23.0977 | 21.749 | 20.5531 | 19.297 | 15.2799 | 10.9652 | 6.7387 | 2.2504 | -0.794 | 28.4116 | 27.2245 | 26.3045 | 25.6371 | 24.8989 | 24.1352 | 23.0977 | 21.749 | 20.5531 | 19.297 | 15.2799 | 10.9652 | 6.7387 | 2.2504 | -0.794 | 28.4116 | 24.3303 | 21.7779 | 20.0542 | 18.5739 | 17.1448 | 15.869 | 14.5671 | 13.067 | 11.4252 | 3.284 | -7.0514 | -14.1502 | -19.2328 | -21.0186 |  | 28.4116 | 24.3303 | 21.7779 | 20.0542 | 18.5739 | 17.1448 | 15.869 | 14.5671 | 13.067 | 11.4252 | 3.284 | -7.0514 | -14.1502 | -19.2328 | -21.0186 | 28.4116 | 26.2777 | 24.1978 | 22.5439 | 21.069 | 19.5515 | 17.6282 | 14.08 | 10.3255 | 6.5397 | -4.1477 | -12.9244 | -18.0837 | -19.3182 | -16.0058 |  | 28.4116 | 26.2777 | 24.1978 | 22.5439 | 21.069 | 19.5515 | 17.6282 | 14.08 | 10.3255 | 6.5397 | -4.1477 | -12.9244 | -18.0837 | -19.3182 | -16.0058 | 28.4116 | 26.4527 | 24.6889 | 23.4856 | 22.8475 | 22.2181 | 21.4208 | 20.4312 | 18.9503 | 17.3938 | 11.956 | 6.4921 | 2.684 | -0.88442 | -2.1968 |  | 28.4116 | 26.4527 | 24.6889 | 23.4856 | 22.8475 | 22.2181 | 21.4208 | 20.4312 | 18.9503 | 17.3938 | 11.956 | 6.4921 | 2.684 | -0.88442 | -2.1968 | 28.4116 | 24.6664 | 22.016 | 20.0239 | 18.253 | 16.5615 | 14.4464 | 10.6464 | 6.7914 | 2.8982 | -8.4254 | -18.069 | -24.1754 | -26.2184 | -23.1236 | 28.4116 | 24.6664 | 22.016 | 20.0239 | 18.253 | 16.5615 | 14.4464 | 10.6464 | 6.7914 | 2.8982 | -8.4254 | -18.069 | -24.1754 | -26.2184 | -23.1236 | 347172 | 407455 | WASHWAY FARM
| Spadeadam 132/11kV* | 27.3166 | 27.351 | 27.2809 | 27.2673 | 27.3017 | 27.3435 | 27.3915 | 27.4439 | 27.417 | 27.3958 | 27.3664 | 27.3786 | 27.4405 | 27.5918 | 27.8688 | 34.3166 | 34.351 | 34.2809 | 34.2673 | 34.3017 | 34.3435 | 34.3915 | 34.4439 | 34.417 | 34.3958 | 34.3664 | 34.3786 | 34.4405 | 34.5918 | 34.8688 | 27.3166 | 27.3508 | 27.2838 | 27.2727 | 27.3062 | 27.3421 | 27.3819 | 27.4261 | 27.3614 | 27.2999 | 27.1439 | 27.0274 | 26.9489 | 26.904 | 26.9348 | 34.3166 | 34.3508 | 34.2838 | 34.2727 | 34.3062 | 34.3421 | 34.3819 | 34.4261 | 34.3614 | 34.2999 | 34.1439 | 34.0274 | 33.9489 | 33.904 | 33.9348 | 27.3166 | 27.3487 | 27.2778 | 27.2613 | 27.2947 | 27.3357 | 27.3823 | 27.4336 | 27.4401 | 27.4579 | 27.5488 | 27.686 | 27.8761 | 28.202 | 28.6988 |  | 34.3166 | 34.3487 | 34.2778 | 34.2613 | 34.2947 | 34.3357 | 34.3823 | 34.4336 | 34.4401 | 34.4579 | 34.5488 | 34.686 | 34.8761 | 35.202 | 35.6988 | 27.3166 | 27.3557 | 27.293 | 27.2856 | 27.3273 | 27.3723 | 27.422 | 27.4799 | 27.4906 | 27.512 | 27.6105 | 27.7485 | 27.9388 | 28.2631 | 28.7632 |  | 34.3166 | 34.3557 | 34.293 | 34.2856 | 34.3273 | 34.3723 | 34.422 | 34.4799 | 34.4906 | 34.512 | 34.6105 | 34.7485 | 34.9388 | 35.2631 | 35.7632 | 27.3166 | 27.3524 | 27.2867 | 27.2794 | 27.3198 | 27.363 | 27.4098 | 27.4643 | 27.44 | 27.4205 | 27.3917 | 27.3989 | 27.4554 | 27.5985 | 27.8733 |  | 34.3166 | 34.3524 | 34.2867 | 34.2794 | 34.3198 | 34.363 | 34.4098 | 34.4643 | 34.44 | 34.4205 | 34.3917 | 34.3989 | 34.4554 | 34.5985 | 34.8733 | 27.3166 | 27.3501 | 27.2794 | 27.2628 | 27.2961 | 27.3373 | 27.3839 | 27.4348 | 27.4408 | 27.4581 | 27.5485 | 27.6864 | 27.8776 | 28.2051 | 28.7052 | 34.3166 | 34.3501 | 34.2794 | 34.2628 | 34.2961 | 34.3373 | 34.3839 | 34.4348 | 34.4408 | 34.4581 | 34.5485 | 34.6864 | 34.8776 | 35.2051 | 35.7052 | 361282 | 570359 | HARKER
| Stainburn & Siddick | 40.0081 | 38.0788 | 36.167 | 34.9138 | 33.7231 | 32.5179 | 31.4665 | 30.5761 | 28.3179 | 21.6448 | 7.0554 | -1.9755 | -14.4008 | -26.9479 | -38.021 | 84.1081 | 82.1788 | 80.267 | 79.0138 | 77.8231 | 76.6179 | 75.5665 | 74.6761 | 72.4179 | 65.7448 | 51.1554 | 42.1245 | 29.6992 | 17.1521 | 6.079 | 40.0081 | 38.8617 | 37.3163 | 36.1519 | 35.0446 | 33.7697 | 32.2198 | 30.3892 | 28.5201 | 26.5916 | 19.5829 | 13.1834 | 6.2201 | -0.92016 | -4.1641 | 84.1081 | 82.9617 | 81.4163 | 80.2519 | 79.1446 | 77.8697 | 76.3198 | 74.4892 | 72.6201 | 70.6916 | 63.6829 | 57.2834 | 50.3201 | 43.1798 | 39.9359 | 40.0081 | 38.0688 | 36.2851 | 35.3684 | 34.4764 | 33.5651 | 32.4748 | 30.5097 | 27.3621 | 21.0417 | 3.6353 | -7.0999 | -13.0054 | -23.3403 | -31.7999 |  | 84.1081 | 82.1688 | 80.3851 | 79.4684 | 78.5764 | 77.6651 | 76.5748 | 74.6097 | 71.4621 | 65.1417 | 47.7353 | 37.0001 | 31.0946 | 20.7597 | 12.3001 | 40.0081 | 39.3266 | 38.0307 | 33.5363 | 31.7022 | 30.028 | 28.8806 | 26.5532 | 20.8023 | 15.5418 | -1.1148 | -16.0174 | -27.2748 | -32.7953 | -24.6731 |  | 84.1081 | 83.4266 | 82.1307 | 77.6363 | 75.8022 | 74.128 | 72.9806 | 70.6532 | 64.9023 | 59.6418 | 42.9852 | 28.0826 | 16.8252 | 11.3047 | 19.4269 | 40.0081 | 38.8614 | 37.2939 | 36.3994 | 35.7749 | 34.9946 | 34.0888 | 33.1839 | 31.3613 | 26.3237 | 12.2718 | 2.7586 | -3.6093 | -8.7785 | -9.1078 |  | 84.1081 | 82.9614 | 81.3939 | 80.4994 | 79.8749 | 79.0946 | 78.1888 | 77.2839 | 75.4613 | 70.4237 | 56.3718 | 46.8586 | 40.4907 | 35.3215 | 34.9922 | 40.0081 | 38.3437 | 36.4444 | 31.3919 | 29.0504 | 27.0421 | 25.8077 | 22.9745 | 17.5988 | 12.7984 | -4.1816 | -19.5819 | -31.4786 | -37.9474 | -31.1484 | 84.1081 | 82.4437 | 80.5444 | 75.4919 | 73.1504 | 71.1421 | 69.9077 | 67.0745 | 61.6988 | 56.8984 | 39.9184 | 24.5181 | 12.6214 | 6.1526 | 12.9516 | 302535 | 529330 | HARKER
| Stretford | 41.616 | 34.8151 | 29.8185 | 26.6861 | 23.5483 | 20.2839 | 17.2148 | 14.5917 | 11.5707 | 8.502 | -7.3447 | -22.1489 | -35.5848 | -44.3296 | -50.5421 | 73.116 | 66.3151 | 61.3185 | 58.1861 | 55.0483 | 51.7839 | 48.7148 | 46.0917 | 43.0707 | 40.002 | 24.1553 | 9.3511 | -4.0848 | -12.8296 | -19.0421 | 41.616 | 39.6377 | 38.3465 | 37.3068 | 36.1861 | 35.0154 | 33.6595 | 32.1901 | 30.7102 | 29.1321 | 23.9073 | 17.0892 | 7.1019 | 0.63782 | -9.2116 | 73.116 | 71.1377 | 69.8465 | 68.8068 | 67.6861 | 66.5154 | 65.1595 | 63.6901 | 62.2102 | 60.6321 | 55.4073 | 48.5892 | 38.6019 | 32.1378 | 22.2884 | 41.616 | 33.6118 | 24.1054 | 16.4909 | 12.5998 | 8.7373 | 4.46 | 0.67204 | -3.3869 | -7.4898 | -29.9487 | -48.3628 | -57.4 | -64.383 | -68.1536 |  | 73.116 | 65.1118 | 55.6054 | 47.9909 | 44.0998 | 40.2373 | 35.96 | 32.172 | 28.1131 | 24.0102 | 1.5513 | -16.8628 | -25.9 | -32.883 | -36.6536 | 41.616 | 36.2408 | 27.4226 | 19.8472 | 15.9689 | 11.6336 | 5.0637 | -7.5623 | -22.8023 | -28.5501 | -43.1807 | -54.1494 | -61.8394 | -65.5685 | -62.6965 |  | 73.116 | 67.7408 | 58.9226 | 51.3472 | 47.4689 | 43.1336 | 36.5637 | 23.9377 | 8.6977 | 2.9499 | -11.6807 | -22.6494 | -30.3394 | -34.0685 | -31.1965 | 41.616 | 38.312 | 34.0573 | 31.151 | 28.4206 | 25.563 | 22.8263 | 20.4587 | 17.5936 | 14.6165 | 1.2919 | -8.04 | -16.8936 | -20.872 | -22.2831 |  | 73.116 | 69.812 | 65.5573 | 62.651 | 59.9206 | 57.063 | 54.3263 | 51.9587 | 49.0936 | 46.1165 | 32.7919 | 23.46 | 14.6064 | 10.628 | 9.2169 | 41.616 | 33.0972 | 23.4324 | 15.8421 | 11.7504 | 7.3085 | 0.66291 | -12.108 | -27.3734 | -33.1467 | -48.1479 | -59.8996 | -68.4064 | -73.1933 | -71.0252 | 73.116 | 64.5972 | 54.9324 | 47.3421 | 43.2504 | 38.8085 | 32.1629 | 19.392 | 4.1266 | -1.6467 | -16.6479 | -28.3996 | -36.9064 | -41.6933 | -39.5252 | 380069 | 395104 | SOUTH MANCHESTER
| Stuart St | 109.1944 | 83.6598 | 73.299 | 67.3474 | 60.8935 | 54.3359 | 48.4846 | 44.0383 | 40.3704 | 36.5561 | 23.4668 | 7.2375 | -5.2833 | -20.5328 | -30.7376 | 166.1944 | 140.6598 | 130.299 | 124.3474 | 117.8935 | 111.3359 | 105.4846 | 101.0383 | 97.3704 | 93.5561 | 80.4668 | 64.2375 | 51.7167 | 36.4672 | 26.2624 | 109.1944 | 99.542 | 94.0732 | 89.6296 | 85.1927 | 80.6466 | 75.8563 | 72.5407 | 69.4319 | 66.2612 | 56.8979 | 47.5042 | 38.8095 | 28.3089 | 21.1119 | 166.1944 | 156.542 | 151.0732 | 146.6296 | 142.1927 | 137.6466 | 132.8563 | 129.5407 | 126.4319 | 123.2612 | 113.8979 | 104.5042 | 95.8095 | 85.3089 | 78.1119 | 109.1944 | 79.7612 | 67.8713 | 61.0754 | 53.7654 | 46.3301 | 39.6232 | 35.2633 | 30.8406 | 26.4256 | 10.9151 | -5.9877 | -19.4088 | -33.8142 | -41.5325 |  | 166.1944 | 136.7612 | 124.8713 | 118.0754 | 110.7654 | 103.3301 | 96.6232 | 92.2633 | 87.8406 | 83.4256 | 67.9151 | 51.0123 | 37.5912 | 23.1858 | 15.4675 | 109.1944 | 87.8855 | 77.8096 | 71.2566 | 64.132 | 56.792 | 49.6579 | 43.3899 | 36.9858 | 30.6755 | 12.8102 | -3.6521 | -17.2781 | -27.7073 | -28.8448 |  | 166.1944 | 144.8855 | 134.8096 | 128.2566 | 121.132 | 113.792 | 106.6579 | 100.3899 | 93.9858 | 87.6755 | 69.8102 | 53.3479 | 39.7219 | 29.2927 | 28.1552 | 109.1944 | 93.9507 | 86.3507 | 80.8681 | 75.0812 | 69.0049 | 63.4518 | 59.1198 | 55.406 | 51.4566 | 40.2252 | 28.8265 | 20.3574 | 10.7353 | 6.3878 |  | 166.1944 | 150.9507 | 143.3507 | 137.8681 | 132.0812 | 126.0049 | 120.4518 | 116.1198 | 112.406 | 108.4566 | 97.2252 | 85.8265 | 77.3574 | 67.7353 | 63.3878 | 109.1944 | 76.9427 | 64.4111 | 57.551 | 50.1535 | 42.6721 | 35.4265 | 28.9348 | 22.4458 | 16.0591 | -2.0729 | -19.556 | -34.0587 | -45.3355 | -47.3863 | 166.1944 | 133.9427 | 121.4111 | 114.551 | 107.1535 | 99.6721 | 92.4265 | 85.9348 | 79.4458 | 73.0591 | 54.9271 | 37.444 | 22.9413 | 11.6645 | 9.6137 | 387247 | 398875 | STALYBRIDGE
| Thornton | 26.5548 | 24.8264 | 23.9994 | 23.3303 | 22.3003 | 21.2194 | 20.255 | 19.3351 | 18.298 | 17.3487 | 11.5041 | 1.6469 | -7.6707 | -15.8482 | -23.5131 | 38.5548 | 36.8264 | 35.9994 | 35.3303 | 34.3003 | 33.2194 | 32.255 | 31.3351 | 30.298 | 29.3487 | 23.5041 | 13.6469 | 4.3293 | -3.8482 | -11.5131 | 26.5548 | 25.5316 | 24.8288 | 24.1045 | 23.1915 | 22.2477 | 21.0213 | 18.9238 | 17.7632 | 16.5845 | 13.0615 | 9.2416 | 5.6337 | 0.13093 | -2.8077 | 38.5548 | 37.5316 | 36.8288 | 36.1045 | 35.1915 | 34.2477 | 33.0213 | 30.9238 | 29.7632 | 28.5845 | 25.0615 | 21.2416 | 17.6337 | 12.1309 | 9.1923 | 26.5548 | 24.7426 | 23.8805 | 23.2761 | 22.3057 | 21.3078 | 20.5043 | 10.936 | 10.3208 | 9.705 | 3.3259 | -7.1273 | -14.4114 | -21.8201 | -28.5713 |  | 38.5548 | 36.7426 | 35.8805 | 35.2761 | 34.3057 | 33.3078 | 32.5043 | 22.936 | 22.3208 | 21.705 | 15.3259 | 4.8727 | -2.4114 | -9.8201 | -16.5713 | 26.5548 | 25.9895 | 25.4714 | 24.9492 | 24.0404 | 23.0403 | 21.6714 | 18.7625 | 14.2869 | 5.1351 | -5.0386 | -13.6594 | -20.2614 | -24.4589 | -22.5018 |  | 38.5548 | 37.9895 | 37.4714 | 36.9492 | 36.0404 | 35.0403 | 33.6714 | 30.7625 | 26.2869 | 17.1351 | 6.9614 | -1.6594 | -8.2614 | -12.4589 | -10.5018 | 26.5548 | 25.415 | 24.7824 | 24.31 | 23.7247 | 23.0884 | 22.3872 | 21.525 | 20.3701 | 19.2151 | 15.2202 | 10.6504 | 6.1488 | 3.1579 | 1.5838 |  | 38.5548 | 37.415 | 36.7824 | 36.31 | 35.7247 | 35.0884 | 34.3872 | 33.525 | 32.3701 | 31.2151 | 27.2202 | 22.6504 | 18.1488 | 15.1579 | 13.5838 | 26.5548 | 25.2592 | 24.3589 | 23.5057 | 22.2882 | 21.0643 | 19.4271 | 16.1649 | 10.8516 | 0.86101 | -11.8649 | -22.9433 | -31.9783 | -39.3274 | -41.2224 | 38.5548 | 37.2592 | 36.3589 | 35.5057 | 34.2882 | 33.0643 | 31.4271 | 28.1649 | 22.8516 | 12.861 | 0.13511 | -10.9433 | -19.9783 | -27.3274 | -29.2224 | 334559 | 443368 | STANAH
| Ulverston | 37.8293 | 36.2213 | 35.3845 | 34.7967 | 33.7009 | 32.5647 | 31.71 | 30.9607 | 30.0555 | 29.2745 | 21.7153 | 9.0033 | -0.432 | -13.3952 | -21.6048 | 37.8293 | 36.2213 | 35.3845 | 34.7967 | 33.7009 | 32.5647 | 31.71 | 30.9607 | 30.0555 | 29.2745 | 21.7153 | 9.0033 | -0.432 | -13.3952 | -21.6048 | 37.8293 | 36.9898 | 36.3036 | 35.6223 | 34.7848 | 33.9435 | 32.8596 | 30.4993 | 29.8486 | 29.2023 | 26.8196 | 23.3008 | 20.7376 | 13.435 | 9.9395 | 37.8293 | 36.9898 | 36.3036 | 35.6223 | 34.7848 | 33.9435 | 32.8596 | 30.4993 | 29.8486 | 29.2023 | 26.8196 | 23.3008 | 20.7376 | 13.435 | 9.9395 | 37.8293 | 36.1154 | 35.3291 | 34.8903 | 33.9431 | 32.9802 | 32.378 | 31.8966 | 31.2323 | 30.7494 | 19.6835 | 8.1123 | -0.54703 | -9.1129 | -16.2242 |  | 37.8293 | 36.1154 | 35.3291 | 34.8903 | 33.9431 | 32.9802 | 32.378 | 31.8966 | 31.2323 | 30.7494 | 19.6835 | 8.1123 | -0.54703 | -9.1129 | -16.2242 | 37.8293 | 37.4962 | 37.0468 | 36.508 | 35.5996 | 33.7871 | 30.903 | 23.9166 | 20.0538 | 15.6654 | 4.7017 | -4.9582 | -12.7012 | -17.1297 | -13.0149 |  | 37.8293 | 37.4962 | 37.0468 | 36.508 | 35.5996 | 33.7871 | 30.903 | 23.9166 | 20.0538 | 15.6654 | 4.7017 | -4.9582 | -12.7012 | -17.1297 | -13.0149 | 37.8293 | 37.011 | 36.388 | 35.9597 | 35.3558 | 34.7496 | 34.1682 | 33.4673 | 32.4552 | 31.4563 | 26.482 | 20.7915 | 17.8682 | 11.5989 | 10.5066 |  | 37.8293 | 37.011 | 36.388 | 35.9597 | 35.3558 | 34.7496 | 34.1682 | 33.4673 | 32.4552 | 31.4563 | 26.482 | 20.7915 | 17.8682 | 11.5989 | 10.5066 | 37.8293 | 36.7048 | 35.85 | 34.9599 | 33.72 | 31.6625 | 28.4824 | 21.1047 | 16.9898 | 12.3483 | 0.60771 | -9.7137 | -18.1232 | -23.4095 | -20.2753 | 37.8293 | 36.7048 | 35.85 | 34.9599 | 33.72 | 31.6625 | 28.4824 | 21.1047 | 16.9898 | 12.3483 | 0.60771 | -9.7137 | -18.1232 | -23.4095 | -20.2753 | 327495 | 477808 | HARKER
| Vernon Park | 16.2219 | 9.5984 | 6.3861 | 3.5423 | 0.38394 | -5.4425 | -8.5609 | -11.7433 | -16.727 | -19.7507 | -37.8314 | -56.949 | -71.1642 | -86.5474 | -97.3739 | 16.2219 | 9.5984 | 6.3861 | 3.5423 | 0.38394 | -5.4425 | -8.5609 | -11.7433 | -16.727 | -19.7507 | -37.8314 | -56.949 | -71.1642 | -86.5474 | -97.3739 | 16.2219 | 12.2834 | 10.0054 | 7.8495 | 5.498 | 3.0594 | 0.24646 | -2.9399 | -5.6062 | -8.3134 | -15.6347 | -23.9656 | -31.4067 | -40.7876 | -46.0805 | 16.2219 | 12.2834 | 10.0054 | 7.8495 | 5.498 | 3.0594 | 0.24646 | -2.9399 | -5.6062 | -8.3134 | -15.6347 | -23.9656 | -31.4067 | -40.7876 | -46.0805 | 16.2219 | 8.7771 | 5.192 | 2.0633 | -1.3937 | -7.5289 | -13.021 | -16.6968 | -21.9392 | -25.2009 | -42.548 | -60.868 | -74.6823 | -87.293 | -96.084 |  | 16.2219 | 8.7771 | 5.192 | 2.0633 | -1.3937 | -7.5289 | -13.021 | -16.6968 | -21.9392 | -25.2009 | -42.548 | -60.868 | -74.6823 | -87.293 | -96.084 | 16.2219 | 11.2768 | 8.4528 | 1.0201 | -1.9119 | -7.7161 | -11.888 | -21.3774 | -30.265 | -36.6991 | -53.5201 | -70.3725 | -82.1832 | -89.4346 | -86.4826 |  | 16.2219 | 11.2768 | 8.4528 | 1.0201 | -1.9119 | -7.7161 | -11.888 | -21.3774 | -30.265 | -36.6991 | -53.5201 | -70.3725 | -82.1832 | -89.4346 | -86.4826 | 16.2219 | 11.4624 | 8.8452 | 6.4617 | 4.0058 | -1.2161 | -3.9305 | -6.8148 | -11.6834 | -14.7146 | -27.2909 | -37.1758 | -43.6603 | -51.1203 | -54.3325 |  | 16.2219 | 11.4624 | 8.8452 | 6.4617 | 4.0058 | -1.2161 | -3.9305 | -6.8148 | -11.6834 | -14.7146 | -27.2909 | -37.1758 | -43.6603 | -51.1203 | -54.3325 | 16.2219 | 9.3729 | 5.8015 | -2.135 | -5.4754 | -11.4526 | -15.7385 | -25.5503 | -34.6274 | -41.1562 | -61.0918 | -79.0814 | -92.0353 | -100.452 | -98.8484 | 16.2219 | 9.3729 | 5.8015 | -2.135 | -5.4754 | -11.4526 | -15.7385 | -25.5503 | -34.6274 | -41.1562 | -61.0918 | -79.0814 | -92.0353 | -100.452 | -98.8484 | 391131 | 390929 | BREDBURY
| West Didsbury | 16.8449 | 11.232 | 8.1036 | 5.5333 | 2.1392 | -1.4632 | -5.1416 | -8.6246 | -12.0827 | -15.1044 | -28.7167 | -48.2559 | -62.3633 | -74.6105 | -83.0917 | 53.3449 | 47.732 | 44.6036 | 42.0333 | 38.6392 | 35.0368 | 31.3584 | 27.8754 | 24.4173 | 21.3956 | 7.7833 | -11.7559 | -25.8633 | -38.1105 | -46.5917 | 16.8449 | 14.7618 | 13.0378 | 11.2085 | 8.8781 | 6.581 | 3.7125 | 0.33534 | -2.2075 | -4.9714 | -12.6909 | -19.7481 | -25.8411 | -31.6264 | -35.2036 | 53.3449 | 51.2618 | 49.5378 | 47.7085 | 45.3781 | 43.081 | 40.2125 | 36.8353 | 34.2925 | 31.5286 | 23.8091 | 16.7519 | 10.6589 | 4.8736 | 1.2964 | 16.8449 | 10.0467 | 6.1596 | 2.9405 | -1.2127 | -5.5408 | -9.4861 | -13.3335 | -17.0471 | -20.7627 | -36.4134 | -56.0675 | -68.9406 | -78.6642 | -82.3594 |  | 53.3449 | 46.5467 | 42.6596 | 39.4405 | 35.2873 | 30.9592 | 27.0139 | 23.1665 | 19.4529 | 15.7373 | 0.08665 | -19.5675 | -32.4406 | -42.1642 | -45.8594 | 16.8449 | 13.4159 | 10.5678 | 7.8815 | 4.1769 | -0.17239 | -5.1511 | -12.9717 | -20.6842 | -28.2292 | -48.5212 | -65.327 | -75.2897 | -78.8946 | -72.5899 |  | 53.3449 | 49.9159 | 47.0678 | 44.3815 | 40.6769 | 36.3276 | 31.3489 | 23.5283 | 15.8158 | 8.2708 | -12.0212 | -28.827 | -38.7897 | -42.3946 | -36.0899 | 16.8449 | 13.8385 | 11.6211 | 9.7907 | 7.7037 | 5.3394 | 2.5244 | -0.40594 | -3.6737 | -6.7306 | -15.6357 | -24.4124 | -30.2897 | -35.6074 | -38.231 |  | 53.3449 | 50.3385 | 48.1211 | 46.2907 | 44.2037 | 41.8394 | 39.0244 | 36.0941 | 32.8263 | 29.7694 | 20.8643 | 12.0876 | 6.2103 | 0.89255 | -1.731 | 16.8449 | 11.0415 | 7.0592 | 3.524 | -1.0298 | -5.7358 | -11.1129 | -19.6402 | -27.8786 | -35.9507 | -57.8269 | -75.7737 | -86.8682 | -91.7874 | -87.2213 | 53.3449 | 47.5415 | 43.5592 | 40.024 | 35.4702 | 30.7642 | 25.3871 | 16.8598 | 8.6214 | 0.54927 | -21.3269 | -39.2737 | -50.3682 | -55.2874 | -50.7213 | 382900 | 393269 | SOUTH MANCHESTER
| Westhoughton | 52.4555 | 46.7101 | 44.2376 | 39.6527 | 34.6925 | 32.4193 | 30.1274 | 27.7102 | 24.7887 | 21.8161 | 8.9909 | -5.814 | -16.731 | -27.193 | -35.3699 | 52.4555 | 46.7101 | 44.2376 | 39.6527 | 34.6925 | 32.4193 | 30.1274 | 27.7102 | 24.7887 | 21.8161 | 8.9909 | -5.814 | -16.731 | -27.193 | -35.3699 | 52.4555 | 50.434 | 49.9047 | 46.4833 | 42.8717 | 41.9484 | 40.6984 | 39.0166 | 37.2543 | 35.3712 | 28.7823 | 21.7166 | 14.9906 | 8.0004 | 3.538 | 52.4555 | 50.434 | 49.9047 | 46.4833 | 42.8717 | 41.9484 | 40.6984 | 39.0166 | 37.2543 | 35.3712 | 28.7823 | 21.7166 | 14.9906 | 8.0004 | 3.538 | 52.4555 | 45.8854 | 42.9835 | 38.0976 | 32.8457 | 30.4435 | 28.3758 | 26.2333 | 23.7184 | 21.0214 | 8.7097 | -6.1005 | -16.5987 | -25.5648 | -31.2156 |  | 52.4555 | 45.8854 | 42.9835 | 38.0976 | 32.8457 | 30.4435 | 28.3758 | 26.2333 | 23.7184 | 21.0214 | 8.7097 | -6.1005 | -16.5987 | -25.5648 | -31.2156 | 52.4555 | 48.6261 | 46.4283 | 41.7111 | 36.4927 | 33.9531 | 30.9885 | 25.7979 | 20.2588 | 14.6012 | -1.9356 | -14.8064 | -23.3831 | -28.0993 | -24.7327 |  | 52.4555 | 48.6261 | 46.4283 | 41.7111 | 36.4927 | 33.9531 | 30.9885 | 25.7979 | 20.2588 | 14.6012 | -1.9356 | -14.8064 | -23.3831 | -28.0993 | -24.7327 | 52.4555 | 49.3222 | 47.6709 | 43.4652 | 39.1473 | 37.4005 | 35.4395 | 33.2906 | 30.5523 | 27.6815 | 18.1656 | 9.4044 | 3.5787 | -1.0459 | -3.1554 |  | 52.4555 | 49.3222 | 47.6709 | 43.4652 | 39.1473 | 37.4005 | 35.4395 | 33.2906 | 30.5523 | 27.6815 | 18.1656 | 9.4044 | 3.5787 | -1.0459 | -3.1554 | 52.4555 | 45.9189 | 42.8399 | 37.6957 | 32.1147 | 29.388 | 26.2215 | 20.7262 | 15.011 | 9.1682 | -8.3019 | -22.4308 | -32.2543 | -38.178 | -35.9214 | 52.4555 | 45.9189 | 42.8399 | 37.6957 | 32.1147 | 29.388 | 26.2215 | 20.7262 | 15.011 | 9.1682 | -8.3019 | -22.4308 | -32.2543 | -38.178 | -35.9214 | 365831 | 407025 | KEARSLEY
| Wigan | 18.2167 | 12.9383 | 11.324 | 10.3407 | 8.8927 | 35.3597 | 33.9128 | 32.5421 | 30.9277 | 29.3739 | 20.4081 | 6.772 | -5.3059 | -18.0252 | -29.2143 | 57.2167 | 51.9383 | 50.324 | 49.3407 | 47.8927 | 46.3597 | 44.9128 | 43.5421 | 41.9277 | 40.3739 | 31.4081 | 17.772 | 5.6941 | -7.0252 | -18.2143 | 18.2167 | 16.452 | 15.4927 | 14.7718 | 13.8705 | 40.8398 | 39.4971 | 37.7855 | 36.4256 | 35.0142 | 30.7113 | 26.2346 | 21.945 | 17.2393 | 13.9798 | 57.2167 | 55.452 | 54.4927 | 53.7718 | 52.8705 | 51.8398 | 50.4971 | 48.7855 | 47.4256 | 46.0142 | 41.7113 | 37.2346 | 32.945 | 28.2393 | 24.9798 | 18.2167 | 12.2679 | 1.6446 | -8.1112 | -9.6608 | 16.7401 | 15.2738 | 13.887 | 12.5505 | 11.2991 | 4.1514 | -9.3972 | -20.7308 | -32.3592 | -42.2617 |  | 57.2167 | 51.2679 | 40.6446 | 30.8888 | 29.3392 | 27.7401 | 26.2738 | 24.887 | 23.5505 | 22.2991 | 15.1514 | 1.6028 | -9.7308 | -21.3592 | -31.2617 | 18.2167 | 15.0224 | 5.098 | -4.5159 | -6.0122 | 20.3206 | 17.8905 | 12.8239 | 7.6602 | 2.5722 | -10.7716 | -23.5478 | -33.8782 | -40.3854 | -36.3455 |  | 57.2167 | 54.0224 | 44.098 | 34.4841 | 32.9878 | 31.3206 | 28.8905 | 23.8239 | 18.6602 | 13.5722 | 0.2284 | -12.5478 | -22.8782 | -29.3854 | -25.3455 | 18.2167 | 15.6177 | 14.7108 | 14.0855 | 13.3317 | 40.4258 | 39.3751 | 38.2109 | 36.6368 | 35.019 | 28.6548 | 21.6362 | 16.7438 | 12.7827 | 11.142 |  | 57.2167 | 54.6177 | 53.7108 | 53.0855 | 52.3317 | 51.4258 | 50.3751 | 49.2109 | 47.6368 | 46.019 | 39.6548 | 32.6362 | 27.7438 | 23.7827 | 22.142 | 18.2167 | 12.4419 | 1.6735 | -8.3627 | -10.2438 | 15.8351 | 13.1049 | 7.6292 | 2.2118 | -3.1362 | -17.3863 | -31.0461 | -42.2813 | -49.8663 | -47.0161 | 57.2167 | 51.4419 | 40.6735 | 30.6373 | 28.7562 | 26.8351 | 24.1049 | 18.6292 | 13.2118 | 7.8638 | -6.3863 | -20.0461 | -31.2813 | -38.8663 | -36.0161 | 358343 | 404626 | KIRKBY
| Wrightington | 9.179 | -1.2551 | -7.5674 | -9.1576 | -11.5035 | -13.9872 | -16.1561 | -18.4602 | -21.4136 | -24.2971 | -38.9671 | -61.0097 | -78.3967 | -95.9248 | -111.1189 | 9.179 | -1.2551 | -7.5674 | -9.1576 | -11.5035 | -13.9872 | -16.1561 | -18.4602 | -21.4136 | -24.2971 | -38.9671 | -61.0097 | -78.3967 | -95.9248 | -111.1189 | 9.179 | 6.9008 | 5.4585 | 4.111 | 2.3745 | 0.47086 | -2.0234 | -5.3681 | -8.3176 | -11.3449 | -20.8262 | -30.8849 | -40.6301 | -51.7422 | -58.8856 | 9.179 | 6.9008 | 5.4585 | 4.111 | 2.3745 | 0.47086 | -2.0234 | -5.3681 | -8.3176 | -11.3449 | -20.8262 | -30.8849 | -40.6301 | -51.7422 | -58.8856 | 9.179 | -1.9812 | -8.4771 | -9.9399 | -12.2392 | -14.585 | -16.4106 | -18.0271 | -20.143 | -22.3364 | -35.0237 | -55.8412 | -72.2592 | -88.3565 | -101.6401 |  | 9.179 | -1.9812 | -8.4771 | -9.9399 | -12.2392 | -14.585 | -16.4106 | -18.0271 | -20.143 | -22.3364 | -35.0237 | -55.8412 | -72.2592 | -88.3565 | -101.6401 | 9.179 | 1.746 | -3.7936 | -5.0258 | -7.2288 | -9.7232 | -12.9019 | -19.3088 | -26.2904 | -33.3714 | -53.794 | -73.2547 | -87.8551 | -97.144 | -92.6958 |  | 9.179 | 1.746 | -3.7936 | -5.0258 | -7.2288 | -9.7232 | -12.9019 | -19.3088 | -26.2904 | -33.3714 | -53.794 | -73.2547 | -87.8551 | -97.144 | -92.6958 | 9.179 | 2.2858 | -3.1204 | -4.1916 | -5.607 | -7.2939 | -9.0005 | -11.0616 | -14.0052 | -17.0349 | -27.4629 | -38.8496 | -47.511 | -55.2427 | -58.723 |  | 9.179 | 2.2858 | -3.1204 | -4.1916 | -5.607 | -7.2939 | -9.0005 | -11.0616 | -14.0052 | -17.0349 | -27.4629 | -38.8496 | -47.511 | -55.2427 | -58.723 | 9.179 | -1.4803 | -8.1791 | -10.1689 | -13.0389 | -15.9361 | -19.5703 | -26.6257 | -34.0036 | -41.485 | -63.519 | -84.8559 | -101.2772 | -112.4015 | -109.7101 | 9.179 | -1.4803 | -8.1791 | -10.1689 | -13.0389 | -15.9361 | -19.5703 | -26.6257 | -34.0036 | -41.485 | -63.519 | -84.8559 | -101.2772 | -112.4015 | -109.7101 | 354460 | 413610 | PENWORTHAM | Firm Capacity exceeded in FY25. Transfer Standish primary to Wigan BSP. There is a RIIO-ED2 project to reinforce Wigan BSP.

## Gen Primary Headroom
Click the scenario name to move directly to the associated results | Best View
| Counterfactual |  |  |  | 1
Electric Engagement
Holistic Transition
Hydrogen Evolution
Accelerated Decarbonisation
[5 empty] | Best View | [59 empty] | Counterfactual | [59 empty] | Electric Engagement | [59 empty] | Holistic Transition | [59 empty] | Hydrogen Evolution | [59 empty] | Accelerated Decarbonisation
Primary Substation Headroom |  |  |  |  | 2024 |  |  |  | 2025 |  |  |  | 2026 |  |  |  | 2027 |  |  |  | 2028 |  |  |  | 2029 |  |  |  | 2030 |  |  |  | 2031 |  |  |  | 2032 |  |  |  | 2033 |  |  |  | 2036 |  |  |  | 2039 |  |  |  | 2042 |  |  |  | 2046 |  |  |  | 2051 |  |  |  | 2024 |  |  |  | 2025 |  |  |  | 2026 |  |  |  | 2027 |  |  |  | 2028 |  |  |  | 2029 |  |  |  | 2030 |  |  |  | 2031 |  |  |  | 2032 |  |  |  | 2033 |  |  |  | 2036 |  |  |  | 2039 |  |  |  | 2042 |  |  |  | 2046 |  |  |  | 2051 |  |  |  | 2024 |  |  |  | 2025 |  |  |  | 2026 |  |  |  | 2027 |  |  |  | 2028 |  |  |  | 2029 |  |  |  | 2030 |  |  |  | 2031 |  |  |  | 2032 |  |  |  | 2033 |  |  |  | 2036 |  |  |  | 2039 |  |  |  | 2042 |  |  |  | 2046 |  |  |  | 2051 |  |  |  | 2024 |  |  |  | 2025 |  |  |  | 2026 |  |  |  | 2027 |  |  |  | 2028 |  |  |  | 2029 |  |  |  | 2030 |  |  |  | 2031 |  |  |  | 2032 |  |  |  | 2033 |  |  |  | 2036 |  |  |  | 2039 |  |  |  | 2042 |  |  |  | 2046 |  |  |  | 2051 |  |  |  | 2024 |  |  |  | 2025 |  |  |  | 2026 |  |  |  | 2027 |  |  |  | 2028 |  |  |  | 2029 |  |  |  | 2030 |  |  |  | 2031 |  |  |  | 2032 |  |  |  | 2033 |  |  |  | 2036 |  |  |  | 2039 |  |  |  | 2042 |  |  |  | 2046 |  |  |  | 2051 |  |  |  | 2024 |  |  |  | 2025 |  |  |  | 2026 |  |  |  | 2027 |  |  |  | 2028 |  |  |  | 2029 |  |  |  | 2030 |  |  |  | 2031 |  |  |  | 2032 |  |  |  | 2033 |  |  |  | 2036 |  |  |  | 2039 |  |  |  | 2042 |  |  |  | 2046 |  |  |  | 2051
Primary Substation | BSP Group | GSP Group | Primary Substation Location |  | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW) | Generation Headroom - N-0 -(MW) |  |  | Battery Headroom (MW)
|  |  | Easting | Northing | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Inverter Based | Synchronous - LV | Synchronous - HV |  | Comments (Based on Best View Headroom)
ALBION ST | LOWER DARWEN | ROCHDALE | 367434 | 426087 | 30.2977 | 14.717 | 10.7359 | 15.1415 | 30.389 | 14.5442 | 10.6098 | 14.1281 | 30.5197 | 14.4397 | 10.5336 | 13.7874 | 30.6801 | 14.344 | 10.4637 | 13.6018 | 30.8751 | 14.2572 | 10.4004 | 13.3127 | 31.0955 | 14.0941 | 10.2815 | 13.0224 | 31.3467 | 13.9724 | 10.1927 | 12.7648 | 31.6524 | 13.8603 | 10.1109 | 12.5242 | 31.8331 | 13.7567 | 10.0353 | 12.1538 | 31.9675 | 13.5848 | 9.9099 | 11.7853 | 32.4032 | 13.1259 | 9.5752 | 9.7896 | 33.385 | 12.6335 | 9.216 | 6.2616 | 34.0543 | 12.585 | 9.1806 | 3.6845 | 34.337 | 13.75 | 10.0304 | 1.6712 | 34.5075 | 14.6929 | 10.7182 | 0.4483 | 30.2616 | 14.717 | 10.7359 | 15.1415 | 30.3306 | 14.6239 | 10.6679 | 14.6911 | 30.3968 | 14.5275 | 10.5976 | 14.5259 | 30.4747 | 14.4001 | 10.5047 | 14.4258 | 30.5829 | 14.3161 | 10.4434 | 14.2787 | 30.721 | 14.2138 | 10.3687 | 14.1078 | 30.8877 | 13.7821 | 10.0538 | 13.8716 | 31.0785 | 13.6942 | 9.9897 | 13.5584 | 31.1922 | 13.6233 | 9.938 | 13.3046 | 31.3121 | 13.5742 | 9.9022 | 13.0394 | 31.6793 | 13.4084 | 9.7812 | 12.052 | 32.5533 | 13.3655 | 9.7499 | 10.5714 | 32.8653 | 13.6426 | 9.9521 | 9.7361 | 33.236 | 14.8453 | 10.8294 | 8.8037 | 33.3924 | 15.7321 | 11.4763 | 8.3222 | 30.3107 | 14.717 | 10.7359 | 15.1415 | 30.4257 | 14.5021 | 10.5791 | 13.9201 | 30.5912 | 14.362 | 10.4769 | 13.4778 | 30.797 | 14.2509 | 10.3958 | 13.218 | 31.0457 | 14.1009 | 10.2864 | 12.8501 | 31.3279 | 13.8938 | 10.1353 | 12.478 | 31.6508 | 13.7741 | 10.048 | 12.1341 | 31.9263 | 13.6258 | 9.9398 | 11.7571 | 32.0995 | 13.4067 | 9.78 | 11.2858 | 32.2671 | 13.2263 | 9.6484 | 10.8016 | 33.4497 | 12.5591 | 9.1617 | 7.8755 | 34.3232 | 11.9889 | 8.7457 | 4.6265 | 34.6786 | 11.9548 | 8.7209 | 2.734 | 34.9289 | 13.1822 | 9.6162 | 1.3555 | 35.027 | 14.2231 | 10.3755 | 1.0232 | 30.3107 | 14.717 | 10.7359 | 15.1415 | 30.3311 | 14.6041 | 10.6535 | 14.4897 | 30.5492 | 14.51 | 10.5849 | 14.0498 | 30.6641 | 14.4213 | 10.5201 | 13.8304 | 30.8283 | 14.2797 | 10.4169 | 13.4767 | 31.0688 | 14.1113 | 10.294 | 13.0994 | 31.4931 | 13.9791 | 10.1976 | 12.4353 | 32.3715 | 13.6874 | 9.9847 | 10.7874 | 32.541 | 13.5431 | 9.8795 | 9.6979 | 32.9288 | 13.2655 | 9.677 | 8.4157 | 33.4365 | 13.7013 | 9.9949 | 5.4839 | 33.9277 | 13.0765 | 9.5391 | 3.1117 | 34.2616 | 12.8341 | 9.3623 | 1.6924 | 34.5127 | 14.5157 | 10.589 | 1.2596 | 34.52 | 14.4329 | 10.5286 | 2.3791 | 30.2977 | 14.717 | 10.7359 | 15.1415 | 30.3769 | 14.579 | 10.6352 | 14.2979 | 30.4694 | 14.4919 | 10.5717 | 14.0201 | 30.5697 | 14.4122 | 10.5135 | 13.9026 | 30.6992 | 14.3545 | 10.4714 | 13.7567 | 30.8942 | 14.239 | 10.3872 | 13.5837 | 31.1474 | 14.1045 | 10.289 | 13.3803 | 31.4254 | 13.9692 | 10.1903 | 13.1592 | 31.638 | 13.9071 | 10.145 | 12.8512 | 31.8079 | 13.752 | 10.0319 | 12.4655 | 32.2023 | 13.4117 | 9.7837 | 11.2357 | 33.1265 | 13.2338 | 9.6539 | 9.4616 | 33.7588 | 13.4266 | 9.7945 | 8.3051 | 34.0227 | 14.8341 | 10.8213 | 7.5877 | 34.1682 | 15.9397 | 11.6278 | 7.2205 | 30.2977 | 14.717 | 10.7359 | 15.1415 | 30.3518 | 14.5167 | 10.5897 | 14.024 | 30.6203 | 14.3906 | 10.4977 | 13.4359 | 30.7972 | 14.2935 | 10.4269 | 13.1298 | 31.0127 | 14.1351 | 10.3113 | 12.6961 | 31.2533 | 13.9525 | 10.1782 | 12.2616 | 31.6606 | 13.8087 | 10.0732 | 11.5026 | 32.5556 | 13.4962 | 9.8453 | 9.745 | 32.7363 | 13.3376 | 9.7296 | 8.5577 | 33.134 | 13.0379 | 9.511 | 7.1817 | 33.6502 | 13.4306 | 9.7974 | 3.997 | 34.1129 | 12.7693 | 9.3151 | 1.3858 | 34.4286 | 12.4901 | 9.1113 | -0.22525 | 34.6574 | 14.1334 | 10.3101 | -0.8761 | 34.7028 | 14.0192 | 10.2268 | -0.02861
ALDERLEY & CHELFORD | MOSS NOOK | SOUTH MANCHESTER | 385044 | 379026 | 20.4951 | 3.3744 | 2.4252 | 15.876 | 18.7685 | 3.0901 | 2.2209 | 15.169 | 18.8824 | 3.1088 | 2.2344 | 14.6972 | 17.6887 | 2.9123 | 2.0931 | 14.3739 | 16.5484 | 2.7246 | 1.9582 | 14.0104 | 18.2615 | 3.0066 | 2.1609 | 13.6523 | 15.9688 | 2.6291 | 1.8896 | 10.3785 | 14.7956 | 2.436 | 1.7508 | 10.0949 | 13.6619 | 2.2493 | 1.6166 | 9.667 | 11.5345 | 1.8991 | 1.3649 | 8.6069 | 7.6929 | 1.2666 | 0.91031 | 6.5743 | 3.5511 | 0.58467 | 0.42021 | 2.6745 | 2.9075 | 0.47869 | 0.34405 | 0.048816 | 11.0352 | 1.8169 | 1.3058 | -2.7115 | 20.83 | 3.4295 | 2.4648 | -5.0822 | 20.4951 | 3.3744 | 2.4252 | 15.876 | 18.769 | 3.0902 | 2.221 | 15.5606 | 16.2552 | 2.6763 | 1.9235 | 15.2209 | 16.3297 | 2.6886 | 1.9323 | 14.9066 | 14.8132 | 2.4389 | 1.7529 | 14.5407 | 14.3351 | 2.3602 | 1.6963 | 14.1496 | 11.0828 | 1.8247 | 1.3115 | 11.0828 | 10.6511 | 1.7536 | 1.2604 | 10.6511 | 10.1438 | 1.6701 | 1.2003 | 10.1438 | 8.8939 | 1.4643 | 1.0524 | 8.8939 | 7.5061 | 1.2358 | 0.88821 | 7.5061 | 6.2521 | 1.0294 | 0.73983 | 6.2521 | 8.0187 | 1.3202 | 0.94887 | 6.5712 | 19.9973 | 3.2924 | 2.3663 | 4.9542 | 27.6128 | 4.5462 | 3.2675 | 3.7716 | 20.4951 | 3.3744 | 2.4252 | 15.876 | 18.8032 | 3.0958 | 2.225 | 15.1292 | 18.8343 | 3.1009 | 2.2287 | 14.6818 | 17.9104 | 2.9488 | 2.1194 | 14.4309 | 15.0154 | 2.4722 | 1.7768 | 12.183 | 16.3988 | 2.6999 | 1.9405 | 11.9251 | 13.1863 | 2.171 | 1.5604 | 8.8238 | 12.0477 | 1.9836 | 1.4256 | 8.6535 | 10.5473 | 1.7365 | 1.2481 | 8.4128 | 7.9147 | 1.3031 | 0.93656 | 7.2016 | 3.2903 | 0.54173 | 0.38935 | 3.2903 | 2.6844 | 0.44197 | 0.31765 | 2.17 | 2.6844 | 0.44197 | 0.31765 | 0.16014 | 9.7086 | 1.5984 | 1.1488 | -1.6191 | 18.1215 | 2.9836 | 2.1444 | -3.4743 | 20.4951 | 3.3744 | 2.4252 | 15.876 | 19.6952 | 3.2427 | 2.3306 | 15.6382 | 20.5595 | 3.385 | 2.4328 | 15.3612 | 20.352 | 3.3508 | 2.4083 | 15.1805 | 18.2629 | 3.0068 | 2.1611 | 14.9213 | 18.0051 | 2.9644 | 2.1306 | 13.9298 | 14.4577 | 2.3804 | 1.7108 | 10.6187 | 13.3618 | 2.1999 | 1.5811 | 9.7795 | 12.4068 | 2.0427 | 1.4681 | 8.8316 | 10.3457 | 1.7033 | 1.2242 | 6.6604 | 12.9779 | 2.1367 | 1.5357 | 3.2407 | 8.1239 | 1.3375 | 0.96131 | 0.50931 | 5.0989 | 0.8395 | 0.60336 | -1.5725 | 21.0526 | 3.4662 | 2.4912 | -2.8965 | 20.0884 | 3.3074 | 2.3771 | -2.0586 | 20.4951 | 3.3744 | 2.4252 | 15.876 | 19.1588 | 3.1544 | 2.2671 | 15.5142 | 19.4419 | 3.201 | 2.3006 | 15.1826 | 18.3616 | 3.0231 | 2.1728 | 14.9667 | 17.3662 | 2.8592 | 2.055 | 14.7521 | 19.2377 | 3.1673 | 2.2764 | 14.4914 | 17.0659 | 2.8098 | 2.0194 | 11.2622 | 16.1927 | 2.666 | 1.9161 | 11.0248 | 14.7513 | 2.4287 | 1.7456 | 10.613 | 12.7863 | 2.1052 | 1.513 | 9.5435 | 9.791 | 1.612 | 1.1586 | 8.2497 | 7.6283 | 1.2559 | 0.90267 | 6.1407 | 8.3008 | 1.3667 | 0.98225 | 4.6405 | 18.9008 | 3.1119 | 2.2366 | 3.2801 | 30.2926 | 4.9875 | 3.5846 | 2.5501 | 20.4951 | 3.3744 | 2.4252 | 15.876 | 19.2683 | 3.1724 | 2.2801 | 15.2825 | 19.8386 | 3.2663 | 2.3475 | 14.8082 | 19.4798 | 3.2072 | 2.3051 | 14.4653 | 17.1852 | 2.8294 | 2.0336 | 14.0657 | 16.8382 | 2.7723 | 1.9925 | 12.9913 | 13.1637 | 2.1673 | 1.5577 | 9.5806 | 11.8608 | 1.9528 | 1.4035 | 8.5886 | 10.7527 | 1.7703 | 1.2724 | 7.5285 | 8.6458 | 1.4235 | 1.0231 | 5.2487 | 10.9153 | 1.7971 | 1.2916 | 1.5196 | 5.6379 | 0.92824 | 0.66715 | -1.4466 | 2.8312 | 0.46613 | 0.33502 | -3.744 | 18.0582 | 2.9731 | 2.1369 | -5.3149 | 16.8606 | 2.776 | 1.9951 | -4.7639
ALSTON | PENRITH & SHAP | HARKER / HUTTON | 372125 | 546499 | 2.9 | 2.9 | 2.9 | 0.392 | 2.9366 | 2.9366 | 2.9366 | 0.34421 | 2.9681 | 2.9681 | 2.9681 | 0.2896 | 3.0065 | 3.0065 | 3.0065 | 0.24614 | 3.0582 | 3.0582 | 3.0582 | 0.19791 | 3.0909 | 3.0909 | 3.0909 | 0.14772 | 3.127 | 3.127 | 3.127 | 0.10266 | 3.1688 | 3.1688 | 3.1688 | 0.056672 | 3.2047 | 3.2047 | 3.2047 | 0.010619 | 3.2395 | 3.2395 | 3.2395 | -0.029692 | 3.3583 | 3.3583 | 3.3583 | -0.24891 | 3.4881 | 3.4881 | 3.4881 | -0.59988 | 3.583 | 3.583 | 3.583 | -0.88137 | 3.6574 | 3.6574 | 3.6574 | -1.217 | 3.6995 | 3.6995 | 3.6995 | -1.5354 | 2.903 | 2.903 | 2.903 | 0.392 | 2.9426 | 2.9426 | 2.9426 | 0.34131 | 2.9787 | 2.9787 | 2.9787 | 0.27257 | 3.0218 | 3.0218 | 3.0218 | 0.20808 | 3.046 | 3.046 | 3.046 | 0.1408 | 3.0739 | 3.0739 | 3.0739 | 0.067329 | 3.1067 | 3.1067 | 3.1067 | -0.030417 | 3.1448 | 3.1448 | 3.1448 | -0.24094 | 3.1649 | 3.1649 | 3.1649 | -0.28111 | 3.1865 | 3.1865 | 3.1865 | -0.32087 | 3.2593 | 3.2593 | 3.2593 | -0.43377 | 3.3342 | 3.3342 | 3.3342 | -0.52822 | 3.3999 | 3.3999 | 3.3999 | -0.59964 | 3.4648 | 3.4648 | 3.4648 | -0.65756 | 3.5096 | 3.5096 | 3.5096 | -0.74062 | 2.8984 | 2.8984 | 2.8984 | 0.392 | 2.9333 | 2.9333 | 2.9333 | 0.34052 | 2.9617 | 2.9617 | 2.9617 | 0.28529 | 2.9956 | 2.9956 | 2.9956 | 0.24158 | 3.0513 | 3.0513 | 3.0513 | 0.19331 | 3.0922 | 3.0922 | 3.0922 | 0.14313 | 3.1289 | 3.1289 | 3.1289 | 0.097967 | 3.1718 | 3.1718 | 3.1718 | 0.051992 | 3.2071 | 3.2071 | 3.2071 | 0.0151 | 3.2415 | 3.2415 | 3.2415 | -0.015359 | 3.3661 | 3.3661 | 3.3661 | -0.2033 | 3.5068 | 3.5068 | 3.5068 | -0.51902 | 3.6105 | 3.6105 | 3.6105 | -0.76289 | 3.6916 | 3.6916 | 3.6916 | -1.0605 | 3.7312 | 3.7312 | 3.7312 | -1.315 | 2.8984 | 2.8984 | 2.8984 | 0.392 | 2.9194 | 2.9194 | 2.9194 | 0.36691 | 2.9422 | 2.9422 | 2.9422 | 0.32892 | 2.9869 | 2.9869 | 2.9869 | 0.29375 | 3.0363 | 3.0363 | 3.0363 | 0.25971 | 3.0669 | 3.0669 | 3.0669 | 0.21997 | 3.1054 | 3.1054 | 3.1054 | 0.16358 | 3.1566 | 3.1566 | 3.1566 | 0.049976 | 3.2046 | 3.2046 | 3.2046 | -0.0709 | 3.2517 | 3.2517 | 3.2517 | -0.18698 | 3.3909 | 3.3909 | 3.3909 | -0.51438 | 3.5142 | 3.5142 | 3.5142 | -0.91443 | 3.5839 | 3.5839 | 3.5839 | -1.2354 | 3.6277 | 3.6277 | 3.6277 | -1.3989 | 3.6227 | 3.6227 | 3.6227 | -1.2005 | 2.9 | 2.9 | 2.9 | 0.392 | 2.9328 | 2.9328 | 2.9328 | 0.35084 | 2.9613 | 2.9613 | 2.9613 | 0.30161 | 2.9946 | 2.9946 | 2.9946 | 0.26586 | 3.0347 | 3.0347 | 3.0347 | 0.2354 | 3.061 | 3.061 | 3.061 | 0.20284 | 3.0914 | 3.0914 | 3.0914 | 0.16668 | 3.1257 | 3.1257 | 3.1257 | 0.12555 | 3.1554 | 3.1554 | 3.1554 | 0.079662 | 3.1862 | 3.1862 | 3.1862 | 0.03499 | 3.2901 | 3.2901 | 3.2901 | -0.11452 | 3.398 | 3.398 | 3.398 | -0.28106 | 3.4746 | 3.4746 | 3.4746 | -0.38888 | 3.5378 | 3.5378 | 3.5378 | -0.48036 | 3.5657 | 3.5657 | 3.5657 | -0.48844 | 2.9 | 2.9 | 2.9 | 0.392 | 2.9304 | 2.9304 | 2.9304 | 0.34232 | 2.9663 | 2.9663 | 2.9663 | 0.28391 | 3.0264 | 3.0264 | 3.0264 | 0.22742 | 3.056 | 3.056 | 3.056 | 0.17292 | 3.0873 | 3.0873 | 3.0873 | 0.11861 | 3.1248 | 3.1248 | 3.1248 | 0.048154 | 3.1782 | 3.1782 | 3.1782 | -0.086587 | 3.226 | 3.226 | 3.226 | -0.21539 | 3.2734 | 3.2734 | 3.2734 | -0.33868 | 3.4165 | 3.4165 | 3.4165 | -0.68223 | 3.5484 | 3.5484 | 3.5484 | -1.0614 | 3.6366 | 3.6366 | 3.6366 | -1.3941 | 3.6826 | 3.6826 | 3.6826 | -1.5751 | 3.6827 | 3.6827 | 3.6827 | -1.404
AMBLESIDE | KENDAL (PARKSIDE RD) | HARKER / HUTTON | 337602 | 503506 | 28.0223 | 25.3503 | 18.2198 | 17.6559 | 28.0936 | 25.1966 | 18.1093 | 17.0102 | 28.1626 | 25.1022 | 18.0414 | 16.7772 | 28.2448 | 25.0144 | 17.9783 | 16.6578 | 28.3438 | 24.894 | 17.8918 | 16.4858 | 28.4565 | 24.7756 | 17.8067 | 16.3107 | 28.5853 | 24.6629 | 17.7257 | 16.1672 | 28.7374 | 24.5647 | 17.6551 | 16.0353 | 28.8352 | 24.4626 | 17.5817 | 15.8797 | 28.9311 | 24.3651 | 17.5117 | 15.7424 | 29.2318 | 23.9544 | 17.2165 | 14.7086 | 29.5267 | 23.4535 | 16.8565 | 12.8404 | 29.7327 | 22.9732 | 16.5113 | 11.2714 | 29.8925 | 22.4704 | 16.1499 | 9.6551 | 29.9858 | 21.9459 | 15.773 | 8.2231 | 28.0053 | 25.3503 | 18.2198 | 17.6559 | 28.1017 | 25.2615 | 18.1559 | 17.2787 | 28.2062 | 25.1861 | 18.1017 | 17.041 | 28.3399 | 25.0925 | 18.0345 | 16.8455 | 28.5111 | 24.981 | 17.9543 | 16.6318 | 28.7097 | 24.8656 | 17.8714 | 16.4136 | 28.937 | 24.7329 | 17.7761 | 16.1491 | 29.1597 | 24.5981 | 17.6791 | 15.8279 | 29.223 | 24.495 | 17.6051 | 15.6427 | 29.29 | 24.3898 | 17.5295 | 15.4578 | 29.4936 | 24.0849 | 17.3103 | 14.9151 | 29.6851 | 23.7989 | 17.1047 | 14.3823 | 29.8536 | 23.5443 | 16.9218 | 13.8996 | 30.0156 | 23.317 | 16.7584 | 13.335 | 30.1232 | 23.0588 | 16.5728 | 12.864 | 28.0305 | 25.3503 | 18.2198 | 17.6559 | 28.0985 | 25.167 | 18.088 | 16.9373 | 28.1707 | 25.0366 | 17.9943 | 16.7014 | 28.259 | 24.9177 | 17.9089 | 16.6054 | 28.3648 | 24.7746 | 17.806 | 16.4532 | 28.4853 | 24.6397 | 17.709 | 16.3001 | 28.6238 | 24.5109 | 17.6165 | 16.1896 | 28.7877 | 24.3932 | 17.5319 | 16.0918 | 28.8916 | 24.2759 | 17.4476 | 16.0035 | 28.9924 | 24.1612 | 17.3651 | 15.9153 | 29.3216 | 23.679 | 17.0186 | 15.0334 | 29.6547 | 23.1089 | 16.6088 | 13.3132 | 29.8907 | 22.5562 | 16.2116 | 11.8921 | 30.0716 | 21.9557 | 15.78 | 10.4738 | 30.1706 | 20.8844 | 15.01 | 9.293 | 28.0305 | 25.3503 | 18.2198 | 17.6559 | 28.0463 | 25.2269 | 18.1311 | 17.2378 | 28.0751 | 25.1454 | 18.0725 | 17.0765 | 28.1157 | 25.0191 | 17.9817 | 16.9828 | 28.1735 | 24.8844 | 17.8849 | 16.8484 | 28.2571 | 24.692 | 17.7466 | 16.71 | 28.3635 | 24.4279 | 17.5568 | 16.488 | 28.4913 | 24.0799 | 17.3067 | 15.911 | 28.5975 | 23.6875 | 17.0247 | 15.3058 | 28.702 | 23.4305 | 16.8399 | 14.6971 | 29.0205 | 22.597 | 16.2409 | 12.9651 | 29.3292 | 21.8993 | 15.7395 | 11.3235 | 29.5412 | 21.0443 | 15.125 | 10.0355 | 29.6908 | 19.8382 | 14.2581 | 9.2859 | 29.7156 | 19.5381 | 14.0424 | 9.9253 | 28.0223 | 25.3503 | 18.2198 | 17.6559 | 28.0871 | 25.2231 | 18.1284 | 17.1275 | 28.143 | 25.1367 | 18.0662 | 16.9236 | 28.2051 | 25.0557 | 18.008 | 16.8255 | 28.2806 | 24.953 | 17.9342 | 16.7289 | 28.38 | 24.8529 | 17.8623 | 16.6385 | 28.503 | 24.7492 | 17.7877 | 16.5391 | 28.6401 | 24.652 | 17.7179 | 16.4113 | 28.7239 | 24.5458 | 17.6416 | 16.2335 | 28.8098 | 24.4405 | 17.5659 | 16.0561 | 29.092 | 24.1075 | 17.3266 | 15.4342 | 29.3795 | 23.8184 | 17.1188 | 14.7149 | 29.5856 | 23.5227 | 16.9063 | 14.2237 | 29.7535 | 23.1891 | 16.6665 | 13.7389 | 29.8291 | 22.8943 | 16.4546 | 13.5807 | 28.0223 | 25.3503 | 18.2198 | 17.6559 | 28.0712 | 25.1682 | 18.0889 | 16.9432 | 28.136 | 25.0658 | 18.0153 | 16.6856 | 28.2176 | 24.9261 | 17.9149 | 16.5328 | 28.3146 | 24.7787 | 17.809 | 16.3409 | 28.423 | 24.5776 | 17.6644 | 16.156 | 28.5497 | 24.305 | 17.4685 | 15.8801 | 28.7109 | 23.9428 | 17.2082 | 15.2359 | 28.8177 | 23.5891 | 16.954 | 14.6014 | 28.9227 | 23.2803 | 16.732 | 13.9626 | 29.2426 | 22.4584 | 16.1413 | 12.1339 | 29.541 | 21.696 | 15.5933 | 10.4085 | 29.7501 | 20.9262 | 15.0401 | 9.0345 | 29.8933 | 19.7102 | 14.1661 | 8.1734 | 29.926 | 19.2785 | 13.8558 | 8.6844
ANCOATS NORTH T11 & T12 | RED BANK | WHITEGATE | 385022 | 398830 | 30.654 | 6.838 | 4.9882 | 9.9387 | 30.8203 | 5.7316 | 4.1812 | 4.8759 | 31.008 | 5.585 | 4.0742 | 3.4408 | 31.2198 | 5.3951 | 3.9356 | 2.9991 | 31.4462 | 5.2762 | 3.8489 | 2.5726 | 31.4423 | 5.1002 | 3.7206 | 2.1252 | 30.4545 | 4.94 | 3.6037 | 1.6791 | 29.5747 | 4.7973 | 3.4996 | 1.2061 | 28.567 | 4.6338 | 3.3803 | 0.63503 | 27.5543 | 4.4696 | 3.2605 | 0.063265 | 24.4217 | 3.9614 | 2.8898 | -1.7725 | 21.3947 | 3.4704 | 2.5316 | -3.7413 | 19.0164 | 3.0846 | 2.2502 | -5.1177 | 16.9883 | 2.7557 | 2.0102 | -6.5885 | 14.8387 | 2.407 | 1.7559 | -8.0453 | 30.654 | 6.838 | 4.9882 | 9.9387 | 30.811 | 6.55 | 4.7781 | 8.5944 | 30.9677 | 6.2455 | 4.556 | 7.9887 | 31.1541 | 6.214 | 4.533 | 7.6233 | 31.3691 | 6.1087 | 4.4562 | 7.2773 | 31.6163 | 5.9775 | 4.3605 | 6.914 | 31.8913 | 5.6378 | 4.1127 | 6.5012 | 32.205 | 5.4948 | 4.0084 | 5.9726 | 32.434 | 5.3472 | 3.9007 | 5.4338 | 32.0602 | 5.2005 | 3.7937 | 4.88 | 29.5136 | 4.7874 | 3.4923 | 3.2831 | 27.7329 | 4.4985 | 3.2816 | 1.6915 | 25.9301 | 4.2061 | 3.0683 | 0.29134 | 24.551 | 3.9824 | 2.9051 | -1.2424 | 22.9713 | 3.7262 | 2.7182 | -2.5904 | 30.654 | 6.838 | 4.9882 | 9.9387 | 30.8322 | 5.6529 | 4.1237 | 4.0499 | 31.031 | 5.3483 | 3.9015 | 2.2516 | 31.2568 | 5.1037 | 3.7231 | 1.6147 | 30.2901 | 4.9134 | 3.5842 | 0.97561 | 28.8803 | 4.6847 | 3.4174 | 0.30782 | 27.6785 | 4.4897 | 3.2752 | -0.34715 | 26.408 | 4.2836 | 3.1249 | -1.0471 | 25.2566 | 4.0969 | 2.9886 | -1.6292 | 24.1167 | 3.912 | 2.8537 | -2.2534 | 20.3117 | 3.2948 | 2.4035 | -4.3172 | 16.6079 | 2.694 | 1.9652 | -6.532 | 13.7283 | 2.2269 | 1.6245 | -8.0716 | 11.185 | 1.8143 | 1.3235 | -9.5726 | 9.3307 | 1.5135 | 1.1041 | -11.0089 | 30.654 | 6.838 | 4.9882 | 9.9387 | 30.7469 | 5.9553 | 4.3443 | 5.7785 | 30.8882 | 5.7762 | 4.2136 | 4.3676 | 31.0552 | 5.5458 | 4.0456 | 3.7853 | 31.2474 | 5.3827 | 3.9266 | 3.1872 | 31.4816 | 5.1899 | 3.786 | 2.5397 | 30.6322 | 4.9688 | 3.6247 | 1.8701 | 28.9939 | 4.7031 | 3.4308 | 1.0666 | 27.64 | 4.4835 | 3.2706 | 0.36488 | 26.0262 | 4.2217 | 3.0797 | -0.37517 | 21.2025 | 3.4392 | 2.5089 | -2.5383 | 18.027 | 2.9242 | 2.1331 | -4.5913 | 15.5158 | 2.5168 | 1.836 | -5.9921 | 14.5056 | 2.353 | 1.7164 | -7.238 | 12.184 | 1.9764 | 1.4417 | -8.2909 | 30.654 | 6.838 | 4.9882 | 9.9387 | 30.8088 | 6.2572 | 4.5646 | 7.5053 | 30.9678 | 6.1571 | 4.4915 | 6.6252 | 31.1381 | 5.9916 | 4.3708 | 6.2247 | 31.3216 | 5.8776 | 4.2876 | 5.8596 | 31.5448 | 5.7275 | 4.1781 | 5.4636 | 31.793 | 5.5711 | 4.064 | 5.0637 | 32.0583 | 5.4412 | 3.9693 | 4.6315 | 32.3166 | 5.2842 | 3.8547 | 4.0743 | 31.5623 | 5.1197 | 3.7348 | 3.5067 | 28.7016 | 4.6557 | 3.3963 | 1.8128 | 26.2764 | 4.2623 | 3.1093 | 0.14484 | 24.3234 | 3.9455 | 2.8782 | -1.0069 | 22.7648 | 3.6927 | 2.6938 | -2.1575 | 21.1454 | 3.43 | 2.5021 | -3.2452 | 30.654 | 6.838 | 4.9882 | 9.9387 | 30.7816 | 5.5407 | 4.0419 | 3.3661 | 30.972 | 5.2334 | 3.8177 | 1.4175 | 30.7769 | 4.9923 | 3.6418 | 0.77325 | 29.6511 | 4.8097 | 3.5086 | 0.11985 | 28.3914 | 4.6054 | 3.3596 | -0.55879 | 26.9603 | 4.3732 | 3.1902 | -1.2682 | 25.2395 | 4.0941 | 2.9866 | -2.1211 | 23.8665 | 3.8714 | 2.8241 | -2.846 | 22.2206 | 3.6044 | 2.6294 | -3.6118 | 17.118 | 2.7767 | 2.0256 | -5.8815 | 13.8955 | 2.254 | 1.6443 | -8.0143 | 11.2941 | 1.832 | 1.3364 | -9.4727 | 10.1895 | 1.6528 | 1.2057 | -10.8017 | 7.6653 | 1.2434 | 0.90704 | -12.01
ANCOATS NORTH T14 | RED BANK | WHITEGATE | 385032 | 398840 | 20.6563 | 20.6563 | 15.7382 | 7.9347 | 20.7058 | 20.7058 | 15.5145 | 6.3552 | 20.7808 | 20.7808 | 15.3946 | 5.6965 | 20.8542 | 20.8542 | 15.335 | 5.3667 | 20.9267 | 20.9203 | 15.261 | 5.0613 | 21.0087 | 20.8108 | 15.1812 | 4.7531 | 21.1024 | 20.7027 | 15.1023 | 4.4484 | 21.214 | 20.6032 | 15.0298 | 4.1318 | 21.3193 | 20.4988 | 14.9536 | 3.7741 | 21.4299 | 20.3961 | 14.8787 | 3.4208 | 21.7565 | 20.1406 | 14.6923 | 2.7421 | 22.032 | 19.9135 | 14.5266 | 1.941 | 22.2076 | 19.7092 | 14.3776 | 1.3344 | 22.3399 | 19.4261 | 14.1711 | 0.71938 | 22.4256 | 19.2203 | 14.021 | 0.17562 | 20.6549 | 20.6549 | 15.7382 | 7.9347 | 20.7359 | 20.7359 | 15.6694 | 7.49 | 20.8462 | 20.8462 | 15.6033 | 7.1798 | 20.9633 | 20.9633 | 15.5161 | 6.9459 | 21.0905 | 21.0905 | 15.4459 | 6.7254 | 21.2395 | 21.0974 | 15.3902 | 6.4804 | 21.4117 | 20.9298 | 15.268 | 6.2062 | 21.5932 | 20.816 | 15.185 | 5.8873 | 21.6755 | 20.735 | 15.1259 | 5.6667 | 21.7618 | 20.6605 | 15.0715 | 5.4448 | 22.0249 | 20.4164 | 14.8934 | 4.8179 | 22.2975 | 20.1951 | 14.732 | 4.2208 | 22.5486 | 20.002 | 14.5912 | 3.7216 | 22.8183 | 19.8414 | 14.474 | 3.1642 | 23.0356 | 19.6396 | 14.3268 | 2.6303 | 20.6569 | 20.6569 | 15.7382 | 7.9347 | 20.7081 | 20.7081 | 15.4715 | 6.1105 | 20.7842 | 20.7842 | 15.3424 | 5.4012 | 20.8595 | 20.8595 | 15.2502 | 5.0684 | 20.9325 | 20.789 | 15.1653 | 4.7615 | 21.0139 | 20.6576 | 15.0694 | 4.4525 | 21.106 | 20.5453 | 14.9875 | 4.1482 | 21.2139 | 20.4302 | 14.9036 | 3.8342 | 21.3069 | 20.3152 | 14.8197 | 3.5104 | 21.4036 | 20.199 | 14.7349 | 3.1944 | 21.7102 | 19.9003 | 14.517 | 2.623 | 21.9916 | 19.6246 | 14.3158 | 1.9343 | 22.1726 | 19.3831 | 14.1397 | 1.4486 | 22.2892 | 19.1055 | 13.9372 | 1.0132 | 22.3345 | 18.8654 | 13.7621 | 0.71181 | 20.6569 | 20.6569 | 15.7382 | 7.9347 | 20.6768 | 20.6768 | 15.5481 | 6.6565 | 20.7265 | 20.7265 | 15.4649 | 6.0869 | 20.7739 | 20.7739 | 15.3831 | 5.7923 | 20.8203 | 20.8203 | 15.3066 | 5.522 | 20.8801 | 20.8655 | 15.2211 | 5.2432 | 20.952 | 20.7452 | 15.1333 | 4.9424 | 21.036 | 20.6114 | 15.0357 | 4.5591 | 21.1319 | 20.4803 | 14.9401 | 4.1291 | 21.2319 | 20.3351 | 14.8341 | 3.7045 | 21.53 | 20.0408 | 14.6195 | 2.9639 | 21.7815 | 19.7678 | 14.4203 | 2.3035 | 21.9311 | 19.5206 | 14.24 | 1.8521 | 22.0255 | 19.2776 | 14.0628 | 1.5796 | 22.055 | 19.1084 | 13.9393 | 1.6868 | 20.6563 | 20.6563 | 15.7382 | 7.9347 | 20.704 | 20.704 | 15.6346 | 7.2596 | 20.7733 | 20.7733 | 15.5304 | 6.7934 | 20.838 | 20.838 | 15.482 | 6.4796 | 20.9012 | 20.9012 | 15.4112 | 6.199 | 20.9776 | 20.9776 | 15.3395 | 5.9097 | 21.0667 | 20.9233 | 15.2632 | 5.6134 | 21.1671 | 20.8238 | 15.1907 | 5.3028 | 21.2587 | 20.7181 | 15.1136 | 4.9474 | 21.3559 | 20.6148 | 15.0382 | 4.5924 | 21.6638 | 20.3841 | 14.8699 | 4.0181 | 21.9533 | 20.2107 | 14.7434 | 3.4778 | 22.1508 | 20.0573 | 14.6315 | 3.1134 | 22.3022 | 19.8341 | 14.4687 | 2.7754 | 22.3944 | 19.6983 | 14.3696 | 2.5788 | 20.6563 | 20.6563 | 15.7382 | 7.9347 | 20.6959 | 20.6959 | 15.4442 | 5.9022 | 20.7689 | 20.7689 | 15.3386 | 5.1484 | 20.8415 | 20.8415 | 15.2478 | 4.8129 | 20.9119 | 20.7873 | 15.1641 | 4.503 | 20.9898 | 20.6634 | 15.0736 | 4.1932 | 21.0772 | 20.5377 | 14.982 | 3.8627 | 21.181 | 20.3947 | 14.8776 | 3.4394 | 21.2708 | 20.2618 | 14.7807 | 3.0044 | 21.3647 | 20.1165 | 14.6747 | 2.5759 | 21.6602 | 19.8112 | 14.452 | 1.8235 | 21.931 | 19.5281 | 14.2455 | 1.1477 | 22.1037 | 19.2728 | 14.0592 | 0.67845 | 22.2102 | 19.0255 | 13.8788 | 0.38998 | 22.2471 | 18.851 | 13.7515 | 0.47057
ANNIE PIT | STAINBURN & SIDDICK | HARKER / HUTTON | 300011 | 527810 | 22.9079 | 9.1669 | 6.5885 | 10.7295 | 23.0289 | 8.9973 | 6.4666 | 9.9575 | 23.1325 | 8.806 | 6.329 | 9.2358 | 23.2257 | 8.6063 | 6.1855 | 8.6401 | 23.3515 | 8.3582 | 6.0072 | 7.9787 | 23.4983 | 8.1841 | 5.8821 | 7.3082 | 23.6637 | 8.0249 | 5.7676 | 6.6844 | 23.8556 | 7.9077 | 5.6834 | 6.4038 | 24.0266 | 7.7805 | 5.592 | 6.085 | 24.2026 | 7.7029 | 5.5362 | 5.7891 | 24.8847 | 7.3943 | 5.3144 | 4.0964 | 25.6456 | 7.1696 | 5.153 | 0.36582 | 26.0537 | 8.4302 | 6.059 | -2.8397 | 26.3705 | 9.8583 | 7.0854 | -6.0042 | 26.5745 | 9.4525 | 6.7937 | -8.7459 | 22.892 | 9.1669 | 6.5885 | 10.7295 | 22.9749 | 9.0948 | 6.5366 | 10.4447 | 23.0593 | 8.9977 | 6.4668 | 10.1828 | 23.1643 | 8.8802 | 6.3824 | 9.9744 | 23.3012 | 8.7588 | 6.2951 | 9.7788 | 23.4255 | 8.6227 | 6.1973 | 9.5691 | 23.5718 | 8.4246 | 6.0549 | 9.3107 | 23.7474 | 8.2622 | 5.9382 | 8.9869 | 23.8321 | 8.1367 | 5.848 | 8.7414 | 23.9248 | 8.0433 | 5.7809 | 8.4989 | 24.2511 | 7.7514 | 5.5711 | 7.7915 | 24.6225 | 7.4709 | 5.3695 | 7.1137 | 24.9898 | 8.4541 | 6.0761 | 6.5074 | 25.3721 | 10.0707 | 7.238 | 5.8615 | 25.6182 | 10.1683 | 7.3082 | 5.4112 | 22.9146 | 9.1669 | 6.5885 | 10.7295 | 23.0419 | 8.9457 | 6.4294 | 9.8515 | 23.1415 | 8.6669 | 6.2291 | 9.1118 | 23.2407 | 8.3712 | 6.0166 | 8.5147 | 23.3713 | 8.0936 | 5.817 | 7.8541 | 23.5218 | 7.9006 | 5.6783 | 7.1856 | 23.69 | 7.69 | 5.5269 | 6.5642 | 23.8834 | 7.5053 | 5.3942 | 6.2889 | 24.0474 | 7.3261 | 5.2654 | 6.0264 | 24.2139 | 7.1935 | 5.1701 | 5.7915 | 24.9081 | 6.1478 | 4.4186 | 4.2738 | 25.7261 | 6.2322 | 4.4792 | 0.90921 | 26.1931 | 7.1764 | 5.1578 | -2.0865 | 26.5455 | 8.1729 | 5.874 | -4.954 | 26.7526 | 7.8283 | 5.6264 | -7.3104 | 22.9146 | 9.1669 | 6.5885 | 10.7295 | 22.98 | 9.0024 | 6.4702 | 10.1885 | 23.0615 | 8.797 | 6.3226 | 9.5534 | 23.1253 | 8.5161 | 6.1207 | 8.996 | 23.2246 | 8.3198 | 5.9796 | 8.3683 | 23.3622 | 8.1344 | 5.8464 | 7.7083 | 23.5506 | 7.8502 | 5.6421 | 6.8913 | 23.84 | 7.9146 | 5.6884 | 5.7989 | 24.0942 | 7.7008 | 5.5347 | 4.4392 | 24.3068 | 7.8755 | 5.6603 | 3.0693 | 24.9597 | 11.6386 | 8.3649 | -0.62202 | 25.5515 | 10.4558 | 7.5148 | -4.0295 | 25.9546 | 9.4025 | 6.7578 | -6.7701 | 26.2144 | 8.3852 | 6.0266 | -8.193 | 26.2187 | 8.0464 | 5.7831 | -6.4752 | 22.9079 | 9.1669 | 6.5885 | 10.7295 | 23.0072 | 9.0667 | 6.5164 | 10.3676 | 23.1077 | 8.8957 | 6.3935 | 9.7437 | 23.1694 | 8.715 | 6.2636 | 9.2235 | 23.2464 | 8.5045 | 6.1123 | 8.7384 | 23.3526 | 8.3524 | 6.0031 | 8.2435 | 23.4881 | 8.2211 | 5.9086 | 7.7331 | 23.6466 | 8.1133 | 5.8312 | 7.4963 | 23.791 | 7.9908 | 5.7431 | 7.1702 | 23.9462 | 7.9099 | 5.685 | 6.8412 | 24.4792 | 7.7421 | 5.5644 | 5.9969 | 25.0125 | 7.9538 | 5.7166 | 5.1154 | 25.3822 | 9.7299 | 6.9931 | 4.554 | 25.6584 | 11.6797 | 8.3944 | 4.1326 | 25.7632 | 11.7688 | 8.4585 | 4.2523 | 22.9079 | 9.1669 | 6.5885 | 10.7295 | 22.9938 | 8.9394 | 6.4249 | 9.8296 | 23.1062 | 8.7135 | 6.2625 | 9.073 | 23.2025 | 8.4148 | 6.0479 | 8.4382 | 23.329 | 8.2122 | 5.9023 | 7.7396 | 23.4726 | 7.9864 | 5.74 | 7.0383 | 23.6579 | 7.6974 | 5.5323 | 6.1854 | 23.9559 | 7.7908 | 5.5994 | 5.0144 | 24.2337 | 7.4435 | 5.3498 | 3.5721 | 24.5143 | 7.6998 | 5.534 | 2.1674 | 25.1806 | 11.4213 | 8.2087 | -1.6442 | 25.7974 | 10.2133 | 7.3405 | -5.2008 | 26.2368 | 9.1148 | 6.551 | -8.1277 | 26.5154 | 8.0354 | 5.7752 | -9.8172 | 26.5388 | 7.6491 | 5.4976 | -8.4239
ANSDELL | LYTHAM | PENWORTHAM WEST / STANAH | 334416 | 428229 | 20.5024 | 10.4663 | 7.635 | 10.7663 | 20.5591 | 10.1599 | 7.4115 | 9.929 | 20.6433 | 9.8999 | 7.2218 | 9.6345 | 20.7495 | 9.6969 | 7.0737 | 9.4668 | 20.8743 | 9.4224 | 6.8735 | 9.2627 | 21.0133 | 9.1284 | 6.659 | 9.0608 | 21.1691 | 8.9073 | 6.4977 | 8.8812 | 21.3574 | 8.8475 | 6.4542 | 8.722 | 21.4975 | 8.7317 | 6.3697 | 8.5195 | 21.6287 | 8.6621 | 6.3189 | 8.3463 | 22.0319 | 8.3584 | 6.0973 | 7.186 | 22.4559 | 7.9151 | 5.774 | 5.1454 | 22.7673 | 7.554 | 5.5106 | 3.5012 | 23.045 | 7.2951 | 5.3217 | 1.7743 | 23.2397 | 6.946 | 5.067 | 0.24596 | 20.4507 | 10.4663 | 7.635 | 10.7663 | 20.5192 | 10.3027 | 7.5157 | 10.496 | 20.58 | 10.0779 | 7.3517 | 10.325 | 20.6453 | 9.8861 | 7.2118 | 10.1691 | 20.7342 | 9.6876 | 7.067 | 9.9765 | 20.8435 | 9.5133 | 6.9398 | 9.7935 | 20.9725 | 9.3304 | 6.8064 | 9.5737 | 21.1185 | 9.2383 | 6.7392 | 9.3037 | 21.1945 | 9.1547 | 6.6782 | 9.0443 | 21.2729 | 9.0731 | 6.6187 | 8.7837 | 21.5083 | 8.848 | 6.4545 | 8.0316 | 21.7272 | 8.6901 | 6.3393 | 7.345 | 21.915 | 8.5175 | 6.2134 | 6.7498 | 22.1004 | 8.4595 | 6.1711 | 6.1475 | 22.239 | 8.3921 | 6.1219 | 5.7514 | 20.51 | 10.4663 | 7.635 | 10.7663 | 20.573 | 10.1172 | 7.3804 | 9.8296 | 20.6677 | 9.8424 | 7.1799 | 9.5381 | 20.7894 | 9.6164 | 7.015 | 9.4088 | 20.9335 | 9.3541 | 6.8237 | 9.246 | 21.0953 | 9.0365 | 6.592 | 9.0943 | 21.2789 | 8.8784 | 6.4766 | 8.9849 | 21.5014 | 8.7821 | 6.4064 | 8.9046 | 21.6627 | 8.6824 | 6.3337 | 8.7919 | 21.8135 | 8.6189 | 6.2874 | 8.6881 | 22.273 | 8.2524 | 6.02 | 7.6973 | 22.7483 | 7.8267 | 5.7094 | 5.795 | 23.0961 | 7.4387 | 5.4264 | 4.3041 | 23.4029 | 7.1456 | 5.2126 | 2.7834 | 23.6153 | 6.8355 | 4.9864 | 1.4802 | 20.51 | 10.4663 | 7.635 | 10.7663 | 20.514 | 10.2026 | 7.4426 | 10.2264 | 20.5561 | 9.9616 | 7.2669 | 10.0437 | 20.6162 | 9.7358 | 7.1021 | 9.9519 | 20.7042 | 9.4984 | 6.9289 | 9.8023 | 20.8399 | 9.2243 | 6.729 | 9.6315 | 21.0074 | 9.0219 | 6.5813 | 9.3789 | 21.2 | 8.8666 | 6.4681 | 8.7788 | 21.3484 | 8.6585 | 6.3162 | 8.1336 | 21.4918 | 8.4773 | 6.184 | 7.4919 | 21.9262 | 8.1409 | 5.9387 | 5.6442 | 22.3888 | 7.7056 | 5.6211 | 3.8665 | 22.7267 | 7.3357 | 5.3513 | 2.4882 | 23.0099 | 7.1283 | 5.2 | 1.6304 | 23.1125 | 7.0769 | 5.1625 | 2.3117 | 20.5024 | 10.4663 | 7.635 | 10.7663 | 20.5503 | 10.2506 | 7.4777 | 10.3698 | 20.607 | 10.01 | 7.3022 | 10.1926 | 20.6719 | 9.8182 | 7.1622 | 10.0913 | 20.7553 | 9.5622 | 6.9755 | 9.9819 | 20.8801 | 9.2804 | 6.7699 | 9.8607 | 21.0385 | 9.0729 | 6.6186 | 9.7445 | 21.2087 | 9.0256 | 6.584 | 9.6346 | 21.3319 | 8.9085 | 6.4986 | 9.4558 | 21.4526 | 8.8446 | 6.452 | 9.2853 | 21.828 | 8.6531 | 6.3123 | 8.7291 | 22.2244 | 8.4322 | 6.1512 | 8.016 | 22.5193 | 8.3129 | 6.0642 | 7.4692 | 22.7908 | 8.283 | 6.0423 | 6.9874 | 22.9528 | 8.1704 | 5.9602 | 6.6059 | 20.5024 | 10.4663 | 7.635 | 10.7663 | 20.5325 | 10.1135 | 7.3776 | 9.8143 | 20.6131 | 9.8508 | 7.186 | 9.4909 | 20.719 | 9.6101 | 7.0104 | 9.3107 | 20.8448 | 9.3574 | 6.8261 | 9.0831 | 20.9837 | 9.0813 | 6.6247 | 8.8547 | 21.1442 | 8.8516 | 6.4571 | 8.5406 | 21.3554 | 8.6911 | 6.34 | 7.8567 | 21.5179 | 8.4687 | 6.1778 | 7.1389 | 21.672 | 8.2855 | 6.0442 | 6.4269 | 22.1093 | 7.9047 | 5.7663 | 4.3852 | 22.5217 | 7.441 | 5.4281 | 2.4567 | 22.8209 | 7.0433 | 5.138 | 0.94525 | 23.057 | 6.8093 | 4.9673 | -0.080044 | 23.1513 | 6.6951 | 4.884 | 0.40228
ARDWICK | STUART ST | STALYBRIDGE | 384753 | 397415 | 26.3822 | 11.99 | 8.7466 | 4.3111 | 26.4677 | 11.5529 | 8.4276 | 2.5398 | 26.6039 | 11.172 | 8.1498 | 1.3247 | 26.7288 | 11.0115 | 8.0327 | 0.43287 | 26.8576 | 10.8003 | 7.8787 | -0.44051 | 26.9968 | 10.5625 | 7.7052 | -1.3184 | 27.1481 | 10.378 | 7.5706 | -1.9054 | 27.3188 | 10.2728 | 7.4939 | -2.1183 | 27.5009 | 10.1536 | 7.4069 | -2.4239 | 27.6842 | 10.0223 | 7.3111 | -2.7167 | 28.3007 | 9.6581 | 7.0455 | -3.8621 | 28.9485 | 9.2586 | 6.754 | -5.467 | 29.3832 | 8.9444 | 6.5248 | -6.6562 | 29.5 | 8.6415 | 6.3039 | -7.6936 | 29.5092 | 8.3566 | 6.096 | -8.4104 | 26.3712 | 11.99 | 8.7466 | 4.3111 | 26.4249 | 11.8569 | 8.6494 | 3.8931 | 26.5197 | 11.7304 | 8.5572 | 3.5851 | 26.6025 | 11.6034 | 8.4645 | 3.4024 | 26.6851 | 11.481 | 8.3752 | 3.2548 | 26.7792 | 11.3768 | 8.2992 | 3.1025 | 26.8942 | 11.1698 | 8.1482 | 2.9132 | 27.0405 | 11.0763 | 8.08 | 2.6562 | 27.1678 | 10.9671 | 8.0004 | 2.3464 | 27.2969 | 10.8452 | 7.9114 | 2.0338 | 27.6908 | 10.5204 | 7.6745 | 1.1443 | 28.0974 | 10.3114 | 7.5221 | 0.20358 | 28.4749 | 10.1375 | 7.3952 | -0.64997 | 28.8754 | 9.981 | 7.281 | -1.5603 | 29.1631 | 9.7811 | 7.1352 | -2.2149 | 26.3875 | 11.99 | 8.7466 | 4.3111 | 26.5036 | 11.4737 | 8.3699 | 2.2785 | 26.6696 | 11.1121 | 8.1061 | 0.97485 | 26.8321 | 10.8626 | 7.9241 | 0.026484 | 27.0007 | 10.6514 | 7.77 | -0.9047 | 27.186 | 10.384 | 7.575 | -1.8446 | 27.3905 | 10.1581 | 7.4102 | -2.4997 | 27.6178 | 10.0032 | 7.2972 | -2.7863 | 27.8358 | 9.8682 | 7.1987 | -3.1162 | 28.0527 | 9.7452 | 7.109 | -3.4303 | 28.8069 | 9.2964 | 6.7816 | -4.7031 | 29.2382 | 8.8477 | 6.4543 | -6.1876 | 29.3868 | 8.5159 | 6.2122 | -7.0987 | 29.4286 | 8.2209 | 5.9971 | -7.7666 | 29.3211 | 7.938 | 5.7907 | -7.9307 | 26.3875 | 11.99 | 8.7466 | 4.3111 | 26.4386 | 11.6096 | 8.469 | 2.8401 | 26.5715 | 11.3281 | 8.2637 | 1.6754 | 26.7023 | 11.1518 | 8.1351 | 0.76524 | 26.8418 | 10.9526 | 7.9898 | -0.13652 | 27.0118 | 10.704 | 7.8084 | -1.0603 | 27.2182 | 10.4624 | 7.6322 | -1.7607 | 27.4818 | 10.2972 | 7.5116 | -2.2637 | 27.7493 | 10.1069 | 7.3728 | -2.8172 | 28.0137 | 9.92 | 7.2365 | -3.3419 | 28.6317 | 9.3932 | 6.8522 | -4.8943 | 29.0154 | 8.9313 | 6.5153 | -6.2313 | 29.1322 | 8.5748 | 6.2552 | -6.958 | 29.1362 | 8.3798 | 6.1129 | -7.2454 | 28.9895 | 8.2786 | 6.0391 | -6.8686 | 26.3822 | 11.99 | 8.7466 | 4.3111 | 26.4605 | 11.7214 | 8.5506 | 3.2124 | 26.5833 | 11.268 | 8.2199 | 2.1494 | 26.685 | 11.216 | 8.1819 | 1.2925 | 26.7821 | 11.0083 | 8.0304 | 0.48181 | 26.9011 | 10.7868 | 7.8688 | -0.33893 | 27.0408 | 10.6169 | 7.7449 | -0.88606 | 27.1949 | 10.5199 | 7.6741 | -1.0789 | 27.3674 | 10.3958 | 7.5836 | -1.3922 | 27.5463 | 10.2687 | 7.4909 | -1.7052 | 28.1072 | 9.9481 | 7.257 | -2.6386 | 28.6451 | 9.6905 | 7.0691 | -3.5289 | 29.005 | 9.5078 | 6.9358 | -4.0787 | 29.3048 | 9.3024 | 6.786 | -4.5859 | 29.3965 | 9.0873 | 6.629 | -4.8171 | 26.3822 | 11.99 | 8.7466 | 4.3111 | 26.4516 | 11.4392 | 8.3447 | 2.1931 | 26.6104 | 11.1628 | 8.1431 | 0.86149 | 26.7665 | 10.9616 | 7.9963 | -0.095842 | 26.9285 | 10.7327 | 7.8294 | -1.0396 | 27.1034 | 10.479 | 7.6443 | -1.9859 | 27.3075 | 10.238 | 7.4685 | -2.7053 | 27.5806 | 10.0608 | 7.3392 | -3.2452 | 27.8474 | 9.8667 | 7.1976 | -3.8156 | 28.11 | 9.6772 | 7.0594 | -4.3556 | 28.8129 | 9.1395 | 6.6672 | -5.9878 | 29.1529 | 8.6602 | 6.3175 | -7.4525 | 29.2913 | 8.2558 | 6.0225 | -8.2519 | 29.3049 | 8.0819 | 5.8956 | -8.5104 | 29.1714 | 7.982 | 5.8228 | -8.1072
ARNSIDE | KENDAL (PARKSIDE RD) | HARKER / HUTTON | 346495 | 478180 | 18.2334 | 18.2334 | 18.2334 | 13.9244 | 18.2475 | 18.2475 | 18.2475 | 13.8906 | 18.2667 | 18.2667 | 18.2667 | 13.8424 | 18.2896 | 18.2896 | 18.2896 | 13.8006 | 18.3226 | 18.3226 | 18.3226 | 13.7286 | 18.3598 | 18.3598 | 18.3598 | 13.6557 | 18.3991 | 18.3991 | 18.3991 | 13.6014 | 18.4444 | 18.4444 | 18.4444 | 13.5547 | 18.4825 | 18.4825 | 18.4825 | 13.4898 | 18.519 | 18.519 | 18.519 | 13.4289 | 18.6905 | 18.6905 | 18.6905 | 12.9339 | 18.9361 | 18.9361 | 18.6552 | 12.1005 | 19.1093 | 19.1093 | 18.4759 | 11.3638 | 19.2342 | 19.2342 | 18.1827 | 10.633 | 19.2811 | 19.2811 | 17.5942 | 9.9987 | 18.2266 | 18.2266 | 18.2266 | 13.9244 | 18.2468 | 18.2468 | 18.2468 | 13.8823 | 18.2669 | 18.2669 | 18.2669 | 13.821 | 18.2897 | 18.2897 | 18.2897 | 13.7593 | 18.3181 | 18.3181 | 18.3181 | 13.6882 | 18.35 | 18.35 | 18.35 | 13.6209 | 18.3885 | 18.3885 | 18.3885 | 13.5392 | 18.4333 | 18.4333 | 18.4333 | 13.4448 | 18.4557 | 18.4557 | 18.4557 | 13.3651 | 18.479 | 18.479 | 18.479 | 13.2851 | 18.5525 | 18.5525 | 18.5525 | 13.0523 | 18.6263 | 18.6263 | 18.6263 | 12.8407 | 18.6978 | 18.6978 | 18.6978 | 12.6196 | 18.7796 | 18.7796 | 18.7693 | 12.3613 | 18.8448 | 18.8448 | 18.5934 | 12.1584 | 18.2343 | 18.2343 | 18.2343 | 13.9244 | 18.2496 | 18.2496 | 18.2496 | 13.8968 | 18.2702 | 18.2702 | 18.2702 | 13.8561 | 18.2954 | 18.2954 | 18.2954 | 13.8281 | 18.3309 | 18.3309 | 18.3309 | 13.7697 | 18.3708 | 18.3708 | 18.3708 | 13.7129 | 18.4133 | 18.4133 | 18.4133 | 13.6805 | 18.4624 | 18.4624 | 18.4624 | 13.6588 | 18.5015 | 18.5015 | 18.5015 | 13.6132 | 18.538 | 18.538 | 18.538 | 13.5555 | 18.7081 | 18.7081 | 18.7081 | 13.1232 | 18.9537 | 18.9537 | 18.5089 | 12.3457 | 19.1517 | 19.1517 | 18.1321 | 11.7052 | 19.2783 | 19.2783 | 17.5254 | 11.0987 | 19.3146 | 19.3146 | 17.0541 | 10.5573 | 18.2343 | 18.2343 | 18.2343 | 13.9244 | 18.2317 | 18.2317 | 18.2317 | 13.9515 | 18.242 | 18.242 | 18.242 | 13.9283 | 18.2593 | 18.2593 | 18.2593 | 13.8923 | 18.2851 | 18.2851 | 18.2851 | 13.8359 | 18.32 | 18.32 | 18.32 | 13.7758 | 18.3707 | 18.3707 | 18.3707 | 13.6763 | 18.4603 | 18.4603 | 18.4603 | 13.4048 | 18.546 | 18.546 | 18.364 | 13.1193 | 18.6207 | 18.6207 | 18.0445 | 12.8357 | 18.8423 | 18.8423 | 17.6401 | 12.0278 | 19.0298 | 19.0298 | 17.3386 | 11.2733 | 19.1266 | 19.1266 | 17.0555 | 10.6762 | 19.1867 | 19.1867 | 16.8246 | 10.3485 | 19.1694 | 19.1694 | 16.7651 | 10.7314 | 18.2334 | 18.2334 | 18.2334 | 13.9244 | 18.2456 | 18.2456 | 18.2456 | 13.8963 | 18.2604 | 18.2604 | 18.2604 | 13.856 | 18.2762 | 18.2762 | 18.2762 | 13.8268 | 18.2963 | 18.2963 | 18.2963 | 13.7959 | 18.3228 | 18.3228 | 18.3228 | 13.7683 | 18.3586 | 18.3586 | 18.3586 | 13.7336 | 18.4066 | 18.4066 | 18.4066 | 13.6755 | 18.451 | 18.451 | 18.451 | 13.5843 | 18.4972 | 18.4972 | 18.4972 | 13.4918 | 18.6498 | 18.6498 | 18.6498 | 13.1267 | 18.7996 | 18.7996 | 18.7838 | 12.6999 | 18.9069 | 18.9069 | 18.6048 | 12.3899 | 18.9992 | 18.9992 | 18.2826 | 12.1116 | 19.0402 | 19.0402 | 17.3894 | 12.0537 | 18.2334 | 18.2334 | 18.2334 | 13.9244 | 18.2376 | 18.2376 | 18.2376 | 13.9315 | 18.2568 | 18.2568 | 18.2568 | 13.8822 | 18.2848 | 18.2848 | 18.2848 | 13.8167 | 18.3201 | 18.3201 | 18.3201 | 13.7331 | 18.3581 | 18.3581 | 18.3581 | 13.6542 | 18.4098 | 18.4098 | 18.4098 | 13.5331 | 18.5053 | 18.5053 | 18.5053 | 13.2302 | 18.5936 | 18.5936 | 18.2563 | 12.9229 | 18.6759 | 18.6759 | 18.053 | 12.6178 | 18.9002 | 18.9002 | 17.4973 | 11.7443 | 19.0817 | 19.0817 | 17.2634 | 10.9291 | 19.1761 | 19.1761 | 16.9931 | 10.2721 | 19.2308 | 19.2308 | 16.7275 | 9.8705 | 19.2151 | 19.2151 | 16.6694 | 10.1719
ASHTON (GOLBORNE) | ORRELL | WASHWAY FARM / KIRKBY | 357056 | 400663 | 22.806 | 9.9608 | 7.2663 | 13.4232 | 23.3303 | 9.4163 | 6.8691 | 10.3274 | 23.8597 | 7.4308 | 5.4207 | 8.9839 | 24.2541 | 5.4703 | 3.9905 | 8.1793 | 20.4557 | 3.3181 | 2.4205 | 7.2888 | 7.9299 | 1.2863 | 0.93834 | 6.3463 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | -1.1468 | 2.6914 | 0.43658 | 0.31848 | -6.4885 | 2.6914 | 0.43658 | 0.31848 | -10.5759 | 16.3255 | 2.6482 | 1.9318 | -14.2764 | 18.8258 | 3.0537 | 2.2276 | -16.9682 | 22.742 | 9.9608 | 7.2663 | 13.4232 | 23.0283 | 9.7848 | 7.1379 | 12.3893 | 23.2452 | 7.9903 | 5.8288 | 11.906 | 23.538 | 6.2053 | 4.5266 | 11.5789 | 23.9306 | 4.394 | 3.2054 | 11.1919 | 15.8693 | 2.5742 | 1.8778 | 10.721 | 3.5605 | 0.57754 | 0.42131 | 3.5605 | 2.5761 | 0.41787 | 0.30483 | 2.5761 | 1.5016 | 0.24357 | 0.17768 | 1.5016 | 0.28447 | 0.046143 | 0.033661 | 0.28447 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.5592 | 2.6914 | 0.43658 | 0.31848 | -0.26435 | 10.3817 | 1.684 | 1.2285 | -3.4037 | 12.8014 | 2.0765 | 1.5148 | -5.3416 | 22.835 | 9.9608 | 7.2663 | 13.4232 | 23.3035 | 9.3358 | 6.8103 | 9.9313 | 23.8253 | 7.2762 | 5.3079 | 8.548 | 24.2117 | 5.3044 | 3.8695 | 7.8336 | 19.0879 | 3.0962 | 2.2587 | 6.9832 | 7.0871 | 1.1496 | 0.83861 | 6.1074 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | -0.44681 | 2.6914 | 0.43658 | 0.31848 | -7.0628 | 2.6914 | 0.43658 | 0.31848 | -12.0785 | 10.8412 | 1.7585 | 1.2828 | -16.3264 | 13.0261 | 2.113 | 1.5414 | -19.0495 | 22.8357 | 9.9608 | 7.2663 | 13.4232 | 23.279 | 9.5476 | 6.9648 | 10.9839 | 23.6987 | 9.2139 | 6.7214 | 9.8999 | 24.1228 | 8.7018 | 6.3478 | 9.2036 | 24.5229 | 8.4863 | 6.1906 | 8.3735 | 25.0683 | 8.1205 | 5.9238 | 7.4019 | 25.7793 | 7.5306 | 5.4935 | 6.4985 | 26.7438 | 6.9496 | 5.0697 | 4.9991 | 27.4802 | 6.3818 | 4.6554 | 3.3443 | 27.8811 | 5.8518 | 4.2688 | 1.6245 | 29.1125 | 5.5084 | 4.0183 | -3.586 | 26.9471 | 4.3711 | 3.1886 | -8.4902 | 20.6693 | 3.3528 | 2.4458 | -12.7842 | 15.5667 | 2.5251 | 1.842 | -15.8087 | 14.0693 | 2.2822 | 1.6648 | -16.0008 | 22.8053 | 9.9608 | 7.2663 | 13.4232 | 23.2126 | 9.6528 | 7.0416 | 11.5881 | 23.5798 | 7.7511 | 5.6543 | 10.6171 | 23.989 | 5.8327 | 4.2549 | 10.0158 | 23.0765 | 3.7432 | 2.7306 | 9.4055 | 10.8235 | 1.7557 | 1.2807 | 8.6692 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | -0.75503 | 8.2247 | 1.3341 | 0.97322 | -4.0726 | 26.3866 | 4.2802 | 3.1223 | -6.6326 | 30.9759 | 5.0246 | 3.6654 | -7.7751 | 22.8053 | 9.9608 | 7.2663 | 13.4232 | 23.2227 | 9.2737 | 6.765 | 9.5257 | 23.6907 | 8.8429 | 6.4508 | 8.0222 | 24.1689 | 8.3108 | 6.0626 | 7.1731 | 24.5736 | 8.0567 | 5.8773 | 6.2318 | 25.0464 | 7.6894 | 5.6093 | 5.2589 | 25.6452 | 7.1061 | 5.1838 | 4.3848 | 26.4618 | 6.5208 | 4.7569 | 2.856 | 27.2668 | 5.9545 | 4.3437 | 1.1929 | 28.1537 | 5.4096 | 3.9462 | -0.54858 | 29.7859 | 5.0255 | 3.666 | -5.938 | 23.4437 | 3.8028 | 2.7741 | -11.4018 | 16.972 | 2.753 | 2.0083 | -15.6068 | 12.2418 | 1.9857 | 1.4486 | -18.4015 | 11.4322 | 1.8544 | 1.3528 | -17.8926
ASHTON (RIBBLE) | RIBBLE | PENWORTHAM EAST / ROCHDALE | 350275 | 430526 | 4.9684 | 4.9684 | 4.9684 | 3.321 | 5.0352 | 5.0352 | 5.0352 | 2.4479 | 5.1164 | 5.1164 | 5.1164 | 2.1934 | 5.2225 | 5.2225 | 5.2225 | 1.6212 | 5.3419 | 5.3419 | 5.3419 | 1.001 | 5.4446 | 5.4446 | 5.4446 | 0.38074 | 5.5604 | 5.5604 | 5.5604 | -0.22231 | 5.7026 | 5.7026 | 5.7026 | -0.35701 | 5.8242 | 5.8242 | 5.8242 | -0.53714 | 5.9298 | 5.9298 | 5.9298 | -0.69783 | 6.2716 | 6.2716 | 6.2716 | -1.6212 | 6.6313 | 6.6313 | 6.6313 | -3.1667 | 6.8903 | 6.8903 | 6.8903 | -4.441 | 7.1134 | 7.1134 | 7.1134 | -5.6531 | 7.274 | 7.274 | 7.274 | -6.782 | 4.9445 | 4.9445 | 4.9445 | 3.321 | 4.9869 | 4.9869 | 4.9869 | 2.9582 | 5.0281 | 5.0281 | 5.0281 | 2.8218 | 5.0722 | 5.0722 | 5.0722 | 2.7323 | 5.1358 | 5.1358 | 5.1358 | 2.6147 | 5.2177 | 5.2177 | 5.2177 | 2.4806 | 5.3155 | 5.3155 | 5.3155 | 2.3074 | 5.4256 | 5.4256 | 5.4256 | 2.0864 | 5.5145 | 5.5145 | 5.5145 | 1.8615 | 5.6076 | 5.6076 | 5.6076 | 1.6362 | 5.8453 | 5.8453 | 5.8453 | 0.9776 | 6.0721 | 6.0721 | 6.0721 | 0.28777 | 6.275 | 6.275 | 6.275 | -0.39386 | 6.4772 | 6.4772 | 6.4772 | -1.0632 | 6.6087 | 6.6087 | 6.6087 | -1.4575 | 4.9784 | 4.9784 | 4.9784 | 3.321 | 5.0491 | 5.0491 | 5.0491 | 2.331 | 5.1415 | 5.1415 | 5.1415 | 2.0721 | 5.2636 | 5.2636 | 5.2636 | 1.5314 | 5.3774 | 5.3774 | 5.3774 | 0.94493 | 5.49 | 5.49 | 5.49 | 0.36432 | 5.6205 | 5.6205 | 5.6205 | -0.18505 | 5.7662 | 5.7662 | 5.7662 | -0.25894 | 5.878 | 5.878 | 5.878 | -0.36824 | 5.9857 | 5.9857 | 5.9857 | -0.47043 | 6.3413 | 6.3413 | 6.3413 | -1.2267 | 6.7221 | 6.7221 | 6.7221 | -2.7393 | 6.9959 | 6.9959 | 6.9959 | -3.9174 | 7.2223 | 7.2223 | 7.2223 | -5.0149 | 7.3716 | 7.3716 | 7.3716 | -5.9415 | 4.9784 | 4.9784 | 4.9784 | 3.321 | 4.9963 | 4.9963 | 4.9963 | 2.7423 | 5.042 | 5.042 | 5.042 | 2.5838 | 5.1075 | 5.1075 | 5.1075 | 2.0651 | 5.2054 | 5.2054 | 5.2054 | 1.4847 | 5.3205 | 5.3205 | 5.3205 | 0.88416 | 5.4452 | 5.4452 | 5.4452 | 0.23093 | 5.5918 | 5.5918 | 5.5918 | -0.19601 | 5.7183 | 5.7183 | 5.7183 | -0.66444 | 5.8439 | 5.8439 | 5.8439 | -1.1322 | 6.2272 | 6.2272 | 6.2272 | -2.482 | 6.5915 | 6.5915 | 6.5915 | -3.7972 | 6.846 | 6.846 | 6.846 | -4.8127 | 7.0322 | 7.0322 | 7.0322 | -5.3992 | 7.0649 | 7.0649 | 7.0649 | -5.0055 | 4.9684 | 4.9684 | 4.9684 | 3.321 | 5.0253 | 5.0253 | 5.0253 | 2.6757 | 5.08 | 5.08 | 5.08 | 2.4918 | 5.1434 | 5.1434 | 5.1434 | 1.9782 | 5.2271 | 5.2271 | 5.2271 | 1.4572 | 5.3431 | 5.3431 | 5.3431 | 0.91279 | 5.4582 | 5.4582 | 5.4582 | 0.35302 | 5.5849 | 5.5849 | 5.5849 | 0.24538 | 5.6928 | 5.6928 | 5.6928 | 0.071652 | 5.8014 | 5.8014 | 5.8014 | -0.096341 | 6.1174 | 6.1174 | 6.1174 | -0.6579 | 6.4376 | 6.4376 | 6.4376 | -1.4311 | 6.6658 | 6.6658 | 6.6658 | -2.0281 | 6.8586 | 6.8586 | 6.8586 | -2.5366 | 6.9507 | 6.9507 | 6.9507 | -2.7534 | 4.9684 | 4.9684 | 4.9684 | 3.321 | 5.0095 | 5.0095 | 5.0095 | 2.2999 | 5.0872 | 5.0872 | 5.0872 | 2.0096 | 5.1927 | 5.1927 | 5.1927 | 1.4198 | 5.3142 | 5.3142 | 5.3142 | 0.77627 | 5.4146 | 5.4146 | 5.4146 | 0.13768 | 5.5314 | 5.5314 | 5.5314 | -0.55995 | 5.6872 | 5.6872 | 5.6872 | -1.0558 | 5.8218 | 5.8218 | 5.8218 | -1.5803 | 5.9533 | 5.9533 | 5.9533 | -2.1022 | 6.3422 | 6.3422 | 6.3422 | -3.6076 | 6.6974 | 6.6974 | 6.6974 | -5.0472 | 6.9464 | 6.9464 | 6.9464 | -6.1719 | 7.1171 | 7.1171 | 7.1171 | -6.8721 | 7.1502 | 7.1502 | 7.1502 | -6.5687
ASHTON ON MERSEY | SALE | CARRINGTON | 377188 | 392252 | 28.6266 | 9.359 | 6.8273 | 15.269 | 28.739 | 9.1275 | 6.6584 | 14.7493 | 28.9051 | 9.1221 | 6.6544 | 14.4553 | 29.1204 | 9.1178 | 6.6513 | 14.2196 | 29.3775 | 9.0485 | 6.6008 | 13.9131 | 29.6493 | 8.9578 | 6.5346 | 13.599 | 29.8235 | 8.8574 | 6.4613 | 13.3055 | 30.0228 | 8.7896 | 6.4119 | 13.0404 | 30.1824 | 8.6882 | 6.3379 | 12.7398 | 30.3341 | 8.5963 | 6.2709 | 12.4651 | 30.9192 | 8.1365 | 5.9355 | 10.6737 | 31.6469 | 7.5672 | 5.5202 | 8.0567 | 32.1816 | 7.1254 | 5.1979 | 6.0928 | 32.6255 | 6.7258 | 4.9064 | 4.2946 | 32.9239 | 6.3768 | 4.6518 | 3.027 | 28.5823 | 9.359 | 6.8273 | 15.269 | 28.657 | 9.2982 | 6.7829 | 15.073 | 28.7368 | 9.2431 | 6.7427 | 14.916 | 28.8475 | 9.1805 | 6.6971 | 14.7533 | 29.0024 | 9.0884 | 6.6299 | 14.5362 | 29.1887 | 8.9649 | 6.5398 | 14.31 | 29.3379 | 8.7889 | 6.4114 | 14.0303 | 29.5084 | 8.6624 | 6.3191 | 13.6983 | 29.648 | 8.5542 | 6.2402 | 13.4047 | 29.7953 | 8.4381 | 6.1555 | 13.1005 | 30.1046 | 8.1183 | 5.9222 | 12.1966 | 30.3836 | 8.0711 | 5.8878 | 11.3284 | 30.6454 | 7.9762 | 5.8185 | 10.4764 | 30.9251 | 7.8566 | 5.7313 | 9.5728 | 31.1439 | 7.7095 | 5.6239 | 8.9349 | 28.6455 | 9.359 | 6.8273 | 15.269 | 28.7809 | 9.0625 | 6.611 | 14.6367 | 28.9808 | 9.1222 | 6.6545 | 14.2711 | 29.2423 | 9.0761 | 6.6209 | 13.9826 | 29.5555 | 8.9468 | 6.5266 | 13.5605 | 29.8265 | 8.8281 | 6.44 | 13.1309 | 30.0515 | 8.6848 | 6.3355 | 12.7343 | 30.3086 | 8.5831 | 6.2612 | 12.3602 | 30.5132 | 8.4355 | 6.1536 | 11.9541 | 30.711 | 8.2935 | 6.05 | 11.4449 | 31.2978 | 7.684 | 5.6054 | 9.2263 | 31.9506 | 7.0838 | 5.1676 | 6.495 | 32.3906 | 6.5901 | 4.8074 | 4.6048 | 32.7219 | 6.1804 | 4.5085 | 3.0332 | 32.832 | 5.927 | 4.3236 | 2.5157 | 28.6455 | 9.359 | 6.8273 | 15.269 | 28.6661 | 9.1629 | 6.6842 | 15.0153 | 28.7628 | 9.3131 | 6.7938 | 14.7653 | 28.902 | 9.2706 | 6.7628 | 14.5211 | 29.1031 | 9.1559 | 6.6791 | 14.1106 | 29.4068 | 9.0158 | 6.5769 | 13.6562 | 29.7778 | 8.7943 | 6.4153 | 13.0955 | 30.1155 | 8.4783 | 6.1848 | 12.1439 | 30.3863 | 8.1796 | 5.9669 | 11.183 | 30.6458 | 7.8528 | 5.7285 | 10.2502 | 31.3832 | 7.1326 | 5.2031 | 7.6504 | 31.9514 | 6.5509 | 4.7788 | 5.4259 | 32.3073 | 6.1476 | 4.4846 | 3.9125 | 32.4834 | 5.8817 | 4.2906 | 3.0969 | 32.3527 | 5.7829 | 4.2186 | 3.7139 | 28.6266 | 9.359 | 6.8273 | 15.269 | 28.7212 | 9.1803 | 6.6969 | 14.9781 | 28.8325 | 9.1765 | 6.6941 | 14.7821 | 28.965 | 9.1935 | 6.7066 | 14.638 | 29.1378 | 9.1538 | 6.6776 | 14.4707 | 29.3986 | 9.0976 | 6.6365 | 14.2694 | 29.6481 | 9.0165 | 6.5774 | 14.0551 | 29.8216 | 8.952 | 6.5304 | 13.8427 | 29.965 | 8.8589 | 6.4624 | 13.559 | 30.1088 | 8.7635 | 6.3928 | 13.2763 | 30.5719 | 8.4325 | 6.1514 | 12.1776 | 31.0589 | 8.1327 | 5.9327 | 10.9235 | 31.4099 | 7.8973 | 5.761 | 10.0275 | 31.7016 | 7.6813 | 5.6034 | 9.1584 | 31.8673 | 7.4709 | 5.4499 | 8.5869 | 28.6266 | 9.359 | 6.8273 | 15.269 | 28.6955 | 9.1232 | 6.6552 | 14.777 | 28.8638 | 9.2396 | 6.7401 | 14.3928 | 29.0883 | 9.1704 | 6.6897 | 14.0369 | 29.3578 | 9.0183 | 6.5787 | 13.5286 | 29.6583 | 8.8816 | 6.479 | 13.0139 | 29.9279 | 8.6446 | 6.3061 | 12.3792 | 30.2599 | 8.3083 | 6.0608 | 11.3179 | 30.5458 | 7.9959 | 5.8329 | 10.2706 | 30.821 | 7.6574 | 5.586 | 9.2528 | 31.5656 | 6.9011 | 5.0343 | 6.4058 | 32.1177 | 6.2875 | 4.5866 | 4.0084 | 32.4655 | 5.8405 | 4.2606 | 2.3694 | 32.6292 | 5.5502 | 4.0488 | 1.4221 | 32.5131 | 5.4337 | 3.9638 | 1.851
ASHTON UNDER LYNE T11 & T12 | HARTSHEAD-HEYROD | STALYBRIDGE | 393275 | 399319 | 31.5859 | 6.6751 | 4.8694 | 11.2276 | 31.7256 | 6.5556 | 4.7822 | 10.5647 | 31.8612 | 6.4424 | 4.6996 | 10.1607 | 31.9942 | 6.2807 | 4.5817 | 9.84 | 32.1634 | 5.9643 | 4.3509 | 9.447 | 32.3571 | 5.9849 | 4.3659 | 9.0326 | 32.5749 | 5.8588 | 4.2739 | 8.6227 | 32.8239 | 5.7005 | 4.1584 | 8.2047 | 33.0528 | 5.5494 | 4.0482 | 7.7545 | 33.1061 | 5.3701 | 3.9174 | 7.3224 | 29.2165 | 4.7392 | 3.4572 | 5.2551 | 24.5501 | 3.9823 | 2.905 | 1.9422 | 20.402 | 3.3094 | 2.4142 | -0.63303 | 16.2137 | 2.63 | 1.9186 | -3.071 | 12.5811 | 2.0408 | 1.4887 | -4.7466 | 31.5686 | 6.6751 | 4.8694 | 11.2276 | 31.726 | 6.6253 | 4.8331 | 10.9617 | 31.8452 | 6.5437 | 4.7736 | 10.7259 | 31.9734 | 6.4181 | 4.6819 | 10.4886 | 32.1322 | 6.2724 | 4.5756 | 10.2045 | 32.3224 | 6.1204 | 4.4648 | 9.8754 | 32.5547 | 5.85 | 4.2675 | 9.3623 | 32.8304 | 5.6465 | 4.119 | 8.6598 | 32.9695 | 5.5117 | 4.0207 | 8.4115 | 33.1187 | 5.3831 | 3.9269 | 8.0776 | 30.554 | 4.9562 | 3.6155 | 6.9397 | 27.9464 | 4.5332 | 3.3069 | 5.7419 | 24.6492 | 3.9983 | 2.9167 | 4.471 | 23.7295 | 3.8492 | 2.8079 | 3.0904 | 21.736 | 3.5258 | 2.572 | 2.1577 | 31.5894 | 6.6751 | 4.8694 | 11.2276 | 31.733 | 6.5126 | 4.7509 | 10.3821 | 31.884 | 6.329 | 4.6169 | 9.8392 | 32.0327 | 6.0901 | 4.4427 | 9.3776 | 32.2167 | 5.8935 | 4.2992 | 8.836 | 32.424 | 5.7426 | 4.1892 | 8.2623 | 32.6558 | 5.5318 | 4.0354 | 7.6778 | 32.8426 | 5.3274 | 3.8863 | 7.0726 | 31.4318 | 5.0986 | 3.7193 | 6.469 | 29.9463 | 4.8576 | 3.5435 | 5.8751 | 24.7823 | 4.0199 | 2.9325 | 3.335 | 19.5439 | 3.1702 | 2.3126 | 0.3129 | 15.2299 | 2.4704 | 1.8021 | -1.9697 | 10.4255 | 1.6911 | 1.2336 | -3.9401 | 7.1927 | 1.1667 | 0.85111 | -4.8289 | 31.5895 | 6.6751 | 4.8694 | 11.2276 | 31.6316 | 6.5879 | 4.8058 | 10.7814 | 31.7204 | 6.4833 | 4.7295 | 10.3815 | 31.8263 | 6.2131 | 4.5324 | 10.0091 | 31.9705 | 6.1709 | 4.5016 | 9.5361 | 32.1707 | 6.0234 | 4.394 | 8.987 | 32.4253 | 5.7788 | 4.2155 | 8.2731 | 32.7316 | 5.4163 | 3.9511 | 7.1298 | 31.4258 | 5.0976 | 3.7186 | 5.9972 | 29.5822 | 4.7985 | 3.5005 | 4.9098 | 23.7761 | 3.8567 | 2.8134 | 1.8015 | 18.5465 | 3.0084 | 2.1946 | -0.9151 | 14.6036 | 2.3688 | 1.728 | -2.679 | 10.7864 | 1.7497 | 1.2764 | -3.6616 | 9.5513 | 1.5493 | 1.1302 | -3.2015 | 31.5857 | 6.6751 | 4.8694 | 11.2276 | 31.7034 | 6.6083 | 4.8206 | 10.8109 | 31.8112 | 6.5093 | 4.7484 | 10.5065 | 31.9011 | 6.3695 | 4.6465 | 10.2818 | 32.008 | 6.1149 | 4.4607 | 10.0427 | 32.1512 | 6.1306 | 4.4722 | 9.7475 | 32.3332 | 6.0233 | 4.3939 | 9.3946 | 32.5436 | 5.8731 | 4.2844 | 9.0081 | 32.7436 | 5.7222 | 4.1742 | 8.5571 | 32.9555 | 5.5475 | 4.0469 | 8.0986 | 31.0429 | 5.0355 | 3.6733 | 6.6242 | 28.4717 | 4.6184 | 3.369 | 5.1306 | 25.8526 | 4.1935 | 3.0591 | 3.7693 | 23.0369 | 3.7368 | 2.7259 | 2.494 | 20.479 | 3.3219 | 2.4233 | 1.7344 | 31.5857 | 6.6751 | 4.8694 | 11.2276 | 31.6577 | 6.5394 | 4.7704 | 10.5133 | 31.7933 | 6.4065 | 4.6734 | 9.9773 | 31.9382 | 6.1073 | 4.4552 | 9.4945 | 32.1197 | 6.0396 | 4.4058 | 8.9249 | 32.3195 | 5.8804 | 4.2897 | 8.3335 | 32.5738 | 5.6305 | 4.1074 | 7.5879 | 32.388 | 5.2537 | 3.8325 | 6.3619 | 30.2404 | 4.9053 | 3.5783 | 5.1718 | 28.3896 | 4.6051 | 3.3593 | 4.0319 | 22.2788 | 3.6138 | 2.6362 | 0.65575 | 16.62 | 2.6959 | 1.9666 | -2.4402 | 12.316 | 1.9978 | 1.4574 | -4.4505 | 7.9356 | 1.2872 | 0.93901 | -5.6045 | 6.6485 | 1.0784 | 0.78671 | -5.4415
ASHTON UNDER LYNE T13 | HARTSHEAD-HEYROD | STALYBRIDGE | 393285 | 399329 | 19.2288 | 19.2288 | 15.8204 | 11.5913 | 19.2553 | 19.2553 | 15.7588 | 11.3456 | 19.2868 | 19.2868 | 15.7284 | 11.2497 | 19.3261 | 19.3261 | 15.698 | 11.2132 | 19.3806 | 19.3806 | 15.6697 | 11.1618 | 19.4425 | 19.4425 | 15.6342 | 11.1063 | 19.511 | 19.511 | 15.5982 | 11.0562 | 19.5787 | 19.5787 | 15.5622 | 11.0073 | 19.6118 | 19.6118 | 15.5264 | 10.9322 | 19.6412 | 19.6412 | 15.49 | 10.8653 | 19.7967 | 19.7967 | 15.3652 | 10.3521 | 19.9451 | 19.9451 | 15.1982 | 9.4198 | 20.0572 | 20.0572 | 15.0537 | 8.6353 | 20.1599 | 20.1599 | 14.8674 | 7.7835 | 20.2296 | 20.1817 | 14.7223 | 6.9321 | 19.2237 | 19.2237 | 15.8204 | 11.5913 | 19.2491 | 19.2491 | 15.7995 | 11.5332 | 19.2733 | 19.2733 | 15.7708 | 11.4685 | 19.3024 | 19.3024 | 15.7416 | 11.4221 | 19.3421 | 19.3421 | 15.7227 | 11.3751 | 19.3897 | 19.3897 | 15.694 | 11.3218 | 19.4485 | 19.4485 | 15.6506 | 11.2504 | 19.504 | 19.504 | 15.6193 | 11.1616 | 19.5301 | 19.5301 | 15.5908 | 11.0742 | 19.5565 | 19.5565 | 15.5614 | 10.9872 | 19.6384 | 19.6384 | 15.4762 | 10.7287 | 19.7248 | 19.7248 | 15.4049 | 10.4734 | 19.8113 | 19.8113 | 15.3206 | 10.2511 | 19.9113 | 19.9113 | 15.2687 | 10.0194 | 19.9899 | 19.9899 | 15.1855 | 9.8418 | 19.231 | 19.231 | 15.8204 | 11.5913 | 19.2611 | 19.2611 | 15.7432 | 11.3085 | 19.2971 | 19.2971 | 15.7117 | 11.2053 | 19.3434 | 19.3434 | 15.6511 | 11.1678 | 19.4063 | 19.4063 | 15.6329 | 11.1159 | 19.4782 | 19.4782 | 15.5898 | 11.06 | 19.5558 | 19.5558 | 15.5479 | 11.0085 | 19.6029 | 19.6029 | 15.5051 | 10.9592 | 19.639 | 19.639 | 15.4688 | 10.9016 | 19.6694 | 19.6694 | 15.4311 | 10.8541 | 19.8576 | 19.8576 | 15.2637 | 10.4018 | 20.0128 | 20.0128 | 15.1087 | 9.5415 | 20.127 | 20.127 | 14.9478 | 8.8349 | 20.2264 | 20.2264 | 14.784 | 8.0893 | 20.286 | 20.0579 | 14.632 | 7.3816 | 19.231 | 19.231 | 15.8204 | 11.5913 | 19.2212 | 19.2212 | 15.7704 | 11.4642 | 19.2339 | 19.2339 | 15.7528 | 11.4071 | 19.2553 | 19.2553 | 15.7213 | 11.3928 | 19.2954 | 19.2954 | 15.6845 | 11.3585 | 19.3552 | 19.3552 | 15.632 | 11.3111 | 19.4424 | 19.4424 | 15.5799 | 11.2041 | 19.5091 | 19.5091 | 15.4998 | 10.9114 | 19.5587 | 19.5587 | 15.4287 | 10.6008 | 19.6058 | 19.6058 | 15.3527 | 10.301 | 19.7475 | 19.7475 | 15.1705 | 9.4473 | 19.8947 | 19.8947 | 15.0006 | 8.5525 | 20.0018 | 20.0018 | 14.8383 | 7.793 | 20.0803 | 20.0803 | 14.704 | 7.3288 | 20.0764 | 20.0764 | 14.6925 | 7.7794 | 19.2288 | 19.2288 | 15.8204 | 11.5913 | 19.2519 | 19.2519 | 15.7875 | 11.5272 | 19.2734 | 19.2734 | 15.7615 | 11.4794 | 19.2959 | 19.2959 | 15.7354 | 11.4654 | 19.3278 | 19.3278 | 15.7136 | 11.4562 | 19.3756 | 19.3756 | 15.6849 | 11.4375 | 19.4396 | 19.4396 | 15.6507 | 11.4048 | 19.4962 | 19.4962 | 15.6141 | 11.3607 | 19.5367 | 19.5367 | 15.5808 | 11.2796 | 19.5795 | 19.5795 | 15.5436 | 11.1979 | 19.7318 | 19.7318 | 15.4505 | 10.9226 | 19.8568 | 19.8568 | 15.3618 | 10.6255 | 19.9466 | 19.9466 | 15.2999 | 10.4186 | 20.0278 | 20.0278 | 15.1872 | 10.2317 | 20.067 | 20.067 | 15.1678 | 10.2151 | 19.2288 | 19.2288 | 15.8204 | 11.5913 | 19.2287 | 19.2287 | 15.7486 | 11.3419 | 19.2567 | 19.2567 | 15.728 | 11.2393 | 19.2968 | 19.2968 | 15.6909 | 11.1973 | 19.353 | 19.353 | 15.6503 | 11.1382 | 19.4157 | 19.4157 | 15.5974 | 11.0781 | 19.5016 | 19.5016 | 15.5441 | 10.9609 | 19.5854 | 19.5854 | 15.4549 | 10.6454 | 19.6392 | 19.6392 | 15.3862 | 10.3211 | 19.6895 | 19.6895 | 15.3112 | 10.0086 | 19.8324 | 19.8324 | 15.1146 | 9.1246 | 19.9668 | 19.9668 | 14.9481 | 8.2532 | 20.0648 | 20.0648 | 14.7759 | 7.4172 | 20.1334 | 20.05 | 14.6262 | 6.8318 | 20.1319 | 20.0208 | 14.6049 | 7.178
ASHWOOD DALE | BUXTON | STALYBRIDGE | 406537 | 373050 | 31.3147 | 10.8223 | 7.8947 | 13.1501 | 31.4162 | 10.5704 | 7.711 | 12.6484 | 31.54 | 10.2704 | 7.4921 | 12.3763 | 31.6694 | 9.9086 | 7.2282 | 12.1556 | 31.7925 | 9.889 | 7.2139 | 11.8298 | 31.9276 | 9.8201 | 7.1636 | 11.4801 | 32.0488 | 9.6921 | 7.0703 | 11.1418 | 32.1909 | 9.5733 | 6.9836 | 10.8424 | 32.3107 | 9.4802 | 6.9157 | 10.5587 | 32.4293 | 9.3916 | 6.8511 | 10.295 | 32.8235 | 8.9404 | 6.5219 | 8.522 | 33.2286 | 8.4062 | 6.1322 | 5.6123 | 33.5106 | 8.015 | 5.8468 | 3.4179 | 33.7488 | 8.5076 | 6.2062 | 1.3289 | 33.8985 | 8.1393 | 5.9375 | -0.24017 | 31.2963 | 10.8223 | 7.8947 | 13.1501 | 31.3623 | 10.6285 | 7.7534 | 12.865 | 31.4339 | 10.4849 | 7.6486 | 12.6333 | 31.513 | 10.2618 | 7.4858 | 12.4083 | 31.6151 | 9.936 | 7.2481 | 12.1361 | 31.7153 | 9.6829 | 7.0636 | 11.8786 | 31.8365 | 9.6985 | 7.0749 | 11.5432 | 31.9886 | 9.5473 | 6.9646 | 11.1093 | 32.0861 | 9.4336 | 6.8817 | 10.8708 | 32.1897 | 9.3047 | 6.7876 | 10.6236 | 32.5169 | 8.9437 | 6.5243 | 9.8775 | 32.8661 | 8.5318 | 6.2238 | 9.0766 | 33.2139 | 8.5523 | 6.2388 | 8.285 | 33.5327 | 8.9294 | 6.5139 | 7.3817 | 33.7102 | 9.117 | 6.6507 | 6.6557 | 31.3221 | 10.8223 | 7.8947 | 13.1501 | 31.4616 | 10.5366 | 7.6863 | 12.5298 | 31.6118 | 10.1717 | 7.4201 | 12.1617 | 31.7478 | 9.69 | 7.0687 | 11.8521 | 31.9043 | 9.7993 | 7.1484 | 11.4288 | 32.0608 | 9.6457 | 7.0364 | 10.9759 | 32.2189 | 9.4819 | 6.9169 | 10.5428 | 32.4008 | 9.3364 | 6.8108 | 10.1279 | 32.546 | 9.1857 | 6.7008 | 9.7486 | 32.69 | 9.0551 | 6.6055 | 9.3636 | 33.1825 | 8.5095 | 6.2075 | 7.2582 | 33.6729 | 7.9083 | 5.769 | 4.3476 | 34.0082 | 7.455 | 5.4383 | 2.3768 | 34.2808 | 7.9494 | 5.799 | 0.78802 | 34.4297 | 7.7767 | 5.673 | 0.097925 | 31.3221 | 10.8223 | 7.8947 | 13.1501 | 31.3551 | 10.6041 | 7.7356 | 12.9359 | 31.4474 | 10.2472 | 7.4752 | 12.666 | 31.5178 | 9.9283 | 7.2426 | 12.3823 | 31.6118 | 9.9902 | 7.2877 | 11.9689 | 31.7443 | 9.816 | 7.1606 | 11.5251 | 31.9137 | 9.5264 | 6.9493 | 10.9393 | 32.1044 | 9.1141 | 6.6486 | 9.855 | 32.2625 | 8.7738 | 6.4003 | 8.7956 | 32.4213 | 8.7044 | 6.3497 | 7.7679 | 32.9082 | 9.0623 | 6.6108 | 4.8672 | 33.3501 | 8.4576 | 6.1697 | 2.4212 | 33.6377 | 7.9936 | 5.8312 | 0.95995 | 33.8461 | 7.6967 | 5.6146 | 0.4253 | 33.9108 | 7.6413 | 5.5742 | 1.2194 | 31.3147 | 10.8223 | 7.8947 | 13.1501 | 31.4068 | 10.6065 | 7.7373 | 12.8185 | 31.513 | 10.3091 | 7.5204 | 12.5962 | 31.6142 | 9.9673 | 7.271 | 12.4228 | 31.7131 | 9.9599 | 7.2656 | 12.2133 | 31.8396 | 9.9263 | 7.2411 | 12.0066 | 31.9677 | 9.8168 | 7.1612 | 11.7848 | 32.0955 | 9.7028 | 7.0781 | 11.5357 | 32.2022 | 9.6102 | 7.0105 | 11.2445 | 32.3113 | 9.5133 | 6.9398 | 10.9496 | 32.662 | 9.1948 | 6.7075 | 9.946 | 33.0094 | 8.9623 | 6.5379 | 8.8654 | 33.2573 | 8.7901 | 6.4122 | 8.1157 | 33.4731 | 9.5506 | 6.967 | 7.3323 | 33.601 | 9.3888 | 6.849 | 6.7589 | 31.3147 | 10.8223 | 7.8947 | 13.1501 | 31.3697 | 10.5735 | 7.7132 | 12.7691 | 31.5239 | 10.201 | 7.4415 | 12.4113 | 31.6473 | 9.8645 | 7.196 | 12.0557 | 31.7909 | 9.9129 | 7.2313 | 11.5718 | 31.9485 | 9.7292 | 7.0973 | 11.0687 | 32.0964 | 9.4276 | 6.8773 | 10.4072 | 32.2903 | 9.0071 | 6.5705 | 9.2378 | 32.4509 | 8.6512 | 6.3109 | 8.1405 | 32.6107 | 8.5677 | 6.25 | 7.0716 | 33.0989 | 8.8949 | 6.4887 | 4.035 | 33.5373 | 8.2616 | 6.0267 | 1.4742 | 33.8299 | 7.7687 | 5.6671 | -0.12083 | 34.0397 | 7.4614 | 5.443 | -0.82834 | 34.1272 | 7.3576 | 5.3672 | -0.25088
ASKAM & DALTON | ULVERSTON | HARKER / HUTTON | 321558 | 477806 | 8.7904 | 8.7904 | 7.0675 | 8.7904 | 8.9289 | 8.9289 | 7.0024 | 8.9289 | 9.0488 | 9.0488 | 6.6053 | 9.0488 | 9.2023 | 8.634 | 6.2054 | 9.2023 | 9.4283 | 8.0249 | 5.7677 | 9.4283 | 9.6657 | 7.3982 | 5.3173 | 9.6657 | 9.8901 | 6.8039 | 4.8901 | 9.5349 | 10.134 | 6.5694 | 4.7215 | 9.3639 | 10.3393 | 6.3715 | 4.5793 | 9.142 | 10.5288 | 6.2339 | 4.4805 | 8.9442 | 11.6046 | 5.3757 | 3.8636 | 7.1361 | 12.7903 | 4.1811 | 3.005 | 3.0758 | 13.1664 | 2.908 | 2.09 | -0.36009 | 11.1801 | 1.8407 | 1.323 | -3.7687 | 2.2279 | 0.36681 | 0.26363 | -6.4932 | 8.7922 | 8.7922 | 7.0675 | 8.7922 | 8.9415 | 8.9415 | 7.0128 | 8.9415 | 9.0619 | 9.0619 | 6.9295 | 9.0619 | 9.2229 | 9.2229 | 6.8343 | 9.2229 | 9.4393 | 9.3449 | 6.7164 | 9.4393 | 9.6883 | 9.1679 | 6.5891 | 9.3746 | 9.9829 | 8.942 | 6.4268 | 9.0264 | 10.3172 | 8.7529 | 6.2909 | 8.6214 | 10.4796 | 8.6094 | 6.1877 | 8.3801 | 10.6454 | 8.4638 | 6.0831 | 8.1412 | 11.1355 | 8.0433 | 5.7809 | 7.4673 | 11.5893 | 7.6411 | 5.4918 | 6.8753 | 11.9686 | 7.2529 | 5.2128 | 6.1765 | 12.3577 | 6.9107 | 4.9668 | 5.3409 | 12.7072 | 6.3591 | 4.5704 | 4.6433 | 8.7897 | 8.7897 | 7.0675 | 8.7897 | 8.93 | 8.93 | 6.9829 | 8.93 | 9.0494 | 9.0494 | 6.5445 | 9.0494 | 9.2035 | 8.4919 | 6.1033 | 9.2035 | 9.428 | 7.7674 | 5.5826 | 9.428 | 9.6629 | 7.1747 | 5.1566 | 9.6629 | 9.8852 | 6.5132 | 4.6812 | 9.532 | 10.1252 | 6.0389 | 4.3402 | 9.3654 | 10.3297 | 6.0336 | 4.3365 | 9.2014 | 10.5143 | 5.8176 | 4.1812 | 9.066 | 11.6227 | 4.9147 | 3.5323 | 8.1282 | 13.0059 | 3.2562 | 2.3403 | 4.4085 | 13.1195 | 2.16 | 1.5524 | 1.2874 | 3.9627 | 0.65244 | 0.46892 | -1.7369 | 2.6844 | 0.44197 | 0.31765 | -4.0176 | 8.7897 | 8.7897 | 7.0675 | 8.7897 | 8.8054 | 8.8054 | 7.008 | 8.8054 | 8.8519 | 8.8519 | 6.6091 | 8.8519 | 9.022 | 8.544 | 6.1407 | 9.022 | 9.1868 | 7.9193 | 5.6918 | 9.1868 | 9.3935 | 7.2249 | 5.1927 | 9.3935 | 9.6993 | 5.2627 | 3.7824 | 9.6993 | 10.3104 | 4.7758 | 3.4324 | 8.7174 | 10.911 | 3.7729 | 2.7117 | 7.3731 | 11.4596 | 2.8057 | 2.0165 | 6.0363 | 9.5707 | 1.5757 | 1.1325 | 2.2555 | 3.1622 | 0.52063 | 0.37418 | -1.2568 | 2.6844 | 0.44197 | 0.31765 | -4.0468 | 2.6844 | 0.44197 | 0.31765 | -5.5076 | 2.6844 | 0.44197 | 0.31765 | -3.3804 | 8.7904 | 8.7904 | 7.0675 | 8.7904 | 8.9101 | 8.9101 | 7.0151 | 8.9101 | 8.994 | 8.994 | 6.6274 | 8.994 | 9.0908 | 8.6817 | 6.2397 | 9.0908 | 9.2198 | 8.1004 | 5.8219 | 9.2198 | 9.3859 | 7.4845 | 5.3792 | 9.3859 | 9.596 | 6.9021 | 4.9607 | 9.596 | 9.8472 | 6.6675 | 4.7921 | 9.7028 | 10.0731 | 6.4651 | 4.6466 | 9.4615 | 10.3023 | 6.323 | 4.5445 | 9.2243 | 11.0671 | 5.6884 | 4.0884 | 8.4723 | 11.9108 | 5.0628 | 3.6387 | 7.32 | 12.532 | 4.1185 | 2.96 | 6.4653 | 13.0453 | 3.7944 | 2.7271 | 5.703 | 13.0815 | 3.1832 | 2.2878 | 5.7094 | 8.7904 | 8.7904 | 7.0675 | 8.7904 | 8.8573 | 8.8573 | 6.9911 | 8.8573 | 8.9761 | 8.9761 | 6.5754 | 8.9761 | 9.2302 | 8.4596 | 6.0801 | 9.2302 | 9.4699 | 7.8252 | 5.6242 | 9.4699 | 9.7131 | 7.118 | 5.1159 | 9.6564 | 10.0493 | 5.2117 | 3.7458 | 9.3745 | 10.7267 | 4.588 | 3.2975 | 7.955 | 11.3703 | 3.581 | 2.5738 | 6.5158 | 11.9468 | 2.6006 | 1.8691 | 5.0854 | 7.7561 | 1.277 | 0.9178 | 1.0265 | 1.0054 | 0.16552 | 0.11897 | -2.7412 | 2.6844 | 0.44197 | 0.31765 | -5.7953 | 2.6844 | 0.44197 | 0.31765 | -7.6093 | 2.6844 | 0.44197 | 0.31765 | -5.882
ASKERTON CASTLE | - | HARKER / HUTTON | 354779 | 568913 | 3.2 | 3.2 | 3.2 | 1.6266 | 3.2092 | 3.2092 | 3.2092 | 1.6089 | 3.2205 | 3.2205 | 3.2205 | 1.5707 | 3.2348 | 3.2348 | 3.2348 | 1.5312 | 3.2517 | 3.2517 | 3.2517 | 1.4893 | 3.2696 | 3.2696 | 3.2696 | 1.4367 | 3.2891 | 3.2891 | 3.2891 | 1.3777 | 3.3116 | 3.3116 | 3.3116 | 1.3056 | 3.3291 | 3.3291 | 3.3291 | 1.2394 | 3.3454 | 3.3454 | 3.3454 | 1.1776 | 3.3952 | 3.3952 | 3.3952 | 0.99478 | 3.4461 | 3.4461 | 3.4461 | 0.81723 | 3.4816 | 3.4816 | 3.4816 | 0.69875 | 3.5092 | 3.5092 | 3.5092 | 0.62308 | 3.5268 | 3.5268 | 3.5268 | 0.59469 | 3.1955 | 3.1955 | 3.1955 | 1.6266 | 3.2097 | 3.2097 | 3.2097 | 1.619 | 3.2233 | 3.2233 | 3.2233 | 1.5979 | 3.2393 | 3.2393 | 3.2393 | 1.5804 | 3.2609 | 3.2609 | 3.2609 | 1.5591 | 3.2875 | 3.2875 | 3.2875 | 1.4861 | 3.3187 | 3.3187 | 3.3187 | 1.4009 | 3.3539 | 3.3539 | 3.3539 | 1.3051 | 3.3677 | 3.3677 | 3.3677 | 1.2541 | 3.3819 | 3.3819 | 3.3819 | 1.2024 | 3.4234 | 3.4234 | 3.4234 | 1.0555 | 3.4593 | 3.4593 | 3.4593 | 0.93528 | 3.4876 | 3.4876 | 3.4876 | 0.84538 | 3.5118 | 3.5118 | 3.5118 | 0.77654 | 3.525 | 3.525 | 3.525 | 0.75294 | 3.2 | 3.2 | 3.2 | 1.6266 | 3.2093 | 3.2093 | 3.2093 | 1.6052 | 3.2207 | 3.2207 | 3.2207 | 1.562 | 3.2352 | 3.2352 | 3.2352 | 1.515 | 3.2521 | 3.2521 | 3.2521 | 1.4641 | 3.2701 | 3.2701 | 3.2701 | 1.3997 | 3.2895 | 3.2895 | 3.2895 | 1.3264 | 3.312 | 3.312 | 3.312 | 1.2361 | 3.3299 | 3.3299 | 3.3299 | 1.1623 | 3.3461 | 3.3461 | 3.3461 | 1.0934 | 3.3956 | 3.3956 | 3.3956 | 0.89074 | 3.4459 | 3.4459 | 3.4459 | 0.69578 | 3.481 | 3.481 | 3.481 | 0.56952 | 3.5079 | 3.5079 | 3.5079 | 0.49614 | 3.5248 | 3.5248 | 3.5248 | 0.48173 | 3.2 | 3.2 | 3.2 | 1.6266 | 3.1992 | 3.1992 | 3.1992 | 1.6195 | 3.2025 | 3.2025 | 3.2025 | 1.5926 | 3.2086 | 3.2086 | 3.2086 | 1.5662 | 3.2179 | 3.2179 | 3.2179 | 1.5354 | 3.2319 | 3.2319 | 3.2319 | 1.4797 | 3.2485 | 3.2485 | 3.2485 | 1.4113 | 3.2665 | 3.2665 | 3.2665 | 1.3346 | 3.283 | 3.283 | 3.283 | 1.2701 | 3.2986 | 3.2986 | 3.2986 | 1.208 | 3.3457 | 3.3457 | 3.3457 | 1.0231 | 3.3947 | 3.3947 | 3.3947 | 0.83392 | 3.4284 | 3.4284 | 3.4284 | 0.71346 | 3.4525 | 3.4525 | 3.4525 | 0.64472 | 3.4577 | 3.4577 | 3.4577 | 0.6663 | 3.2 | 3.2 | 3.2 | 1.6266 | 3.2078 | 3.2078 | 3.2078 | 1.6127 | 3.2153 | 3.2153 | 3.2153 | 1.5836 | 3.2242 | 3.2242 | 3.2242 | 1.5585 | 3.2356 | 3.2356 | 3.2356 | 1.5329 | 3.2519 | 3.2519 | 3.2519 | 1.491 | 3.272 | 3.272 | 3.272 | 1.4336 | 3.2928 | 3.2928 | 3.2928 | 1.3711 | 3.3082 | 3.3082 | 3.3082 | 1.3132 | 3.3233 | 3.3233 | 3.3233 | 1.2564 | 3.371 | 3.371 | 3.371 | 1.0795 | 3.4213 | 3.4213 | 3.4213 | 0.89642 | 3.4568 | 3.4568 | 3.4568 | 0.77139 | 3.487 | 3.487 | 3.487 | 0.67469 | 3.501 | 3.501 | 3.501 | 0.6463 | 3.2 | 3.2 | 3.2 | 1.6266 | 3.2048 | 3.2048 | 3.2048 | 1.6102 | 3.2157 | 3.2157 | 3.2157 | 1.5718 | 3.2307 | 3.2307 | 3.2307 | 1.5316 | 3.2479 | 3.2479 | 3.2479 | 1.4862 | 3.2659 | 3.2659 | 3.2659 | 1.4327 | 3.286 | 3.286 | 3.286 | 1.3715 | 3.3112 | 3.3112 | 3.3112 | 1.2925 | 3.3318 | 3.3318 | 3.3318 | 1.2233 | 3.351 | 3.351 | 3.351 | 1.1581 | 3.4052 | 3.4052 | 3.4052 | 0.977 | 3.455 | 3.455 | 3.455 | 0.81765 | 3.4887 | 3.4887 | 3.4887 | 0.70664 | 3.511 | 3.511 | 3.511 | 0.65373 | 3.5173 | 3.5173 | 3.5173 | 0.69188
ASPATRIA | STAINBURN & SIDDICK | HARKER / HUTTON | 314417 | 542840 | 13.1607 | 13.1607 | 12.9538 | 7.5882 | 13.2443 | 13.2443 | 12.8847 | 7.3175 | 13.3442 | 13.3442 | 12.409 | 7.2314 | 13.4692 | 13.4692 | 11.9343 | 7.1825 | 13.6104 | 13.6104 | 11.4367 | 7.0623 | 13.7808 | 13.7808 | 10.9374 | 6.9269 | 13.9849 | 13.9849 | 10.4437 | 6.8073 | 14.2377 | 14.2377 | 10.3808 | 6.692 | 14.4429 | 14.3563 | 10.3181 | 6.5602 | 14.6494 | 14.3021 | 10.2792 | 6.4473 | 15.2902 | 14.0131 | 10.0715 | 5.5488 | 15.7645 | 13.653 | 9.8126 | 3.8562 | 16.0451 | 13.5145 | 9.7132 | 2.2563 | 16.2966 | 16.2966 | 11.82 | 0.69501 | 16.4808 | 16.4808 | 11.9056 | -0.74121 | 13.1447 | 13.1447 | 12.9538 | 7.5882 | 13.2247 | 13.2247 | 12.9155 | 7.4533 | 13.3031 | 13.3031 | 12.4544 | 7.3416 | 13.4057 | 13.4057 | 11.9813 | 7.2206 | 13.5437 | 13.5437 | 11.4935 | 7.067 | 13.7155 | 13.7155 | 11.0035 | 6.9112 | 13.9037 | 13.9037 | 10.5063 | 6.713 | 14.1216 | 14.1216 | 10.4178 | 6.4054 | 14.2123 | 14.2123 | 10.3631 | 6.2822 | 14.3116 | 14.3116 | 10.3098 | 6.1598 | 14.6622 | 14.1172 | 10.1463 | 5.7206 | 15.0497 | 13.8845 | 9.9791 | 5.2568 | 15.4104 | 13.7256 | 9.8649 | 4.8142 | 15.7731 | 15.6636 | 11.2577 | 4.2711 | 16.0164 | 16.0164 | 12.6559 | 3.7794 | 13.1676 | 13.1676 | 12.9538 | 7.5882 | 13.2542 | 13.2542 | 12.8647 | 7.301 | 13.3636 | 13.3636 | 12.3515 | 7.2234 | 13.4941 | 13.4941 | 11.8414 | 7.1978 | 13.6484 | 13.6484 | 11.3206 | 7.1027 | 13.8337 | 13.8337 | 10.8056 | 6.9976 | 14.0548 | 14.0548 | 10.2964 | 6.9222 | 14.3284 | 14.2032 | 10.2081 | 6.8028 | 14.5417 | 14.0823 | 10.1213 | 6.6899 | 14.7571 | 13.9931 | 10.0571 | 6.5923 | 15.354 | 13.6097 | 9.7816 | 5.9068 | 15.7307 | 13.1329 | 9.4389 | 4.398 | 16.0081 | 12.852 | 9.237 | 2.8877 | 16.2458 | 15.6151 | 11.2229 | 1.4337 | 16.4114 | 15.6293 | 11.2331 | 0.13952 | 13.1677 | 13.1677 | 12.9538 | 7.5882 | 13.1883 | 13.1883 | 12.9011 | 7.528 | 13.2413 | 13.2413 | 12.8344 | 7.5028 | 13.3247 | 13.3247 | 12.7438 | 7.4628 | 13.4344 | 13.4344 | 12.6459 | 7.3719 | 13.5905 | 13.5905 | 12.549 | 7.2681 | 13.7935 | 13.7935 | 12.4136 | 7.0891 | 14.0377 | 14.0377 | 12.2407 | 6.6128 | 14.2498 | 14.2498 | 12.0868 | 6.1015 | 14.4668 | 14.4668 | 11.9472 | 5.5901 | 15.138 | 15.138 | 11.7578 | 3.8646 | 15.5896 | 15.5896 | 11.2627 | 2.1566 | 15.8365 | 15.1875 | 10.9156 | 0.84187 | 15.9965 | 15.8483 | 11.3905 | 0.11018 | 15.9754 | 15.3099 | 11.0035 | 0.72263 | 13.1606 | 13.1606 | 12.9538 | 7.5882 | 13.2317 | 13.2317 | 12.9105 | 7.4898 | 13.3022 | 13.3022 | 12.4418 | 7.4415 | 13.3902 | 13.3902 | 11.9719 | 7.4106 | 13.4973 | 13.4973 | 11.4872 | 7.36 | 13.6415 | 13.6415 | 11.0022 | 7.3095 | 13.8311 | 13.8311 | 10.5165 | 7.2404 | 14.0497 | 14.0497 | 10.4553 | 7.1353 | 14.2209 | 14.2209 | 10.3901 | 6.9869 | 14.4002 | 14.3942 | 10.3454 | 6.8373 | 15.0019 | 14.1698 | 10.1841 | 6.2471 | 15.5262 | 14.0108 | 10.0699 | 5.5251 | 15.7319 | 14.0943 | 10.1299 | 5.0282 | 15.9074 | 15.9074 | 12.3772 | 4.4554 | 15.9762 | 15.9762 | 12.6391 | 4.1821 | 13.1606 | 13.1606 | 12.9538 | 7.5882 | 13.2048 | 13.2048 | 12.879 | 7.4042 | 13.2971 | 13.2971 | 12.8004 | 7.3143 | 13.4242 | 13.4242 | 12.6996 | 7.218 | 13.5605 | 13.5605 | 12.5923 | 7.0735 | 13.7217 | 13.7217 | 12.4885 | 6.9287 | 13.9167 | 13.9167 | 12.346 | 6.7011 | 14.1718 | 14.1718 | 12.163 | 6.1634 | 14.3786 | 14.3786 | 12.0039 | 5.6186 | 14.5899 | 14.5899 | 11.861 | 5.0729 | 15.2552 | 15.2552 | 11.6512 | 3.2302 | 15.8812 | 15.4848 | 11.1292 | 1.391 | 16.1431 | 14.9569 | 10.7498 | -0.04931 | 16.3088 | 15.6128 | 11.2212 | -0.92942 | 16.2983 | 15.2023 | 10.9262 | -0.47513
ATHERTON TOWN CENTRE | ATHERTON | KEARSLEY | 367546 | 403338 | 33.127 | 5.4541 | 3.92 | 20.4386 | 32.435 | 5.3402 | 3.8381 | 19.2883 | 31.5439 | 5.1935 | 3.7326 | 18.9584 | 30.1703 | 4.9673 | 3.5701 | 18.7975 | 27.9356 | 4.5994 | 3.3057 | 18.1959 | 25.9564 | 4.2735 | 3.0715 | 17.5479 | 24.4596 | 4.0271 | 2.8943 | 16.928 | 23.1136 | 3.8055 | 2.7351 | 16.3478 | 21.6356 | 3.5621 | 2.5602 | 15.6234 | 20.0466 | 3.3005 | 2.3722 | 14.814 | 13.2424 | 2.1803 | 1.567 | 10.4485 | 4.4487 | 0.73244 | 0.52642 | 3.7433 | 2.6844 | 0.44197 | 0.31765 | -1.7266 | 2.6844 | 0.44197 | 0.31765 | -7.3796 | 2.6844 | 0.44197 | 0.31765 | -12.5625 | 33.127 | 5.4541 | 3.92 | 20.4386 | 33.2618 | 5.4763 | 3.9359 | 19.9048 | 32.711 | 5.3856 | 3.8708 | 19.6643 | 31.8694 | 5.247 | 3.7712 | 19.4522 | 30.2714 | 4.9839 | 3.5821 | 19.1133 | 28.6442 | 4.7161 | 3.3895 | 18.7135 | 25.987 | 4.2786 | 3.0751 | 18.1577 | 24.4426 | 4.0243 | 2.8923 | 17.4179 | 23.1248 | 3.8073 | 2.7364 | 16.8706 | 21.8525 | 3.5978 | 2.5858 | 16.3084 | 17.8071 | 2.9318 | 2.1071 | 14.1447 | 13.5543 | 2.2316 | 1.6039 | 11.8369 | 11.2115 | 1.8459 | 1.3267 | 9.6739 | 8.0755 | 1.3296 | 0.95558 | 7.4411 | 4.8996 | 0.80668 | 0.57978 | 4.8996 | 33.127 | 5.4541 | 3.92 | 20.4386 | 32.1771 | 5.2977 | 3.8076 | 19.1732 | 30.6911 | 5.0531 | 3.6317 | 18.8645 | 29.25 | 4.8158 | 3.4612 | 18.7861 | 25.6604 | 4.2248 | 3.0364 | 17.7954 | 23.8225 | 3.9222 | 2.819 | 16.7777 | 21.7243 | 3.5767 | 2.5707 | 15.7809 | 19.7366 | 3.2495 | 2.3355 | 14.8359 | 17.7346 | 2.9199 | 2.0986 | 13.8576 | 15.739 | 2.5913 | 1.8624 | 12.9164 | 7.8955 | 1.2999 | 0.93429 | 7.8955 | 2.6844 | 0.44197 | 0.31765 | 2.0342 | 2.6844 | 0.44197 | 0.31765 | -3.2912 | 2.6844 | 0.44197 | 0.31765 | -8.5727 | 2.6844 | 0.44197 | 0.31765 | -13.0133 | 33.127 | 5.4541 | 3.92 | 20.4386 | 33.3299 | 5.4875 | 3.944 | 20.174 | 32.7372 | 5.3899 | 3.8738 | 20.1181 | 31.1431 | 5.1275 | 3.6852 | 20.119 | 28.4766 | 4.6885 | 3.3697 | 19.142 | 26.161 | 4.3072 | 3.0957 | 18.0889 | 23.2881 | 3.8342 | 2.7557 | 16.638 | 18.9974 | 3.1278 | 2.248 | 13.9178 | 14.8708 | 2.4484 | 1.7597 | 11.1189 | 10.925 | 1.7987 | 1.2928 | 8.4783 | 0.78337 | 0.12898 | 0.092697 | 0.78337 | 2.6844 | 0.44197 | 0.31765 | -4.2772 | 2.6844 | 0.44197 | 0.31765 | -9.1573 | 2.6844 | 0.44197 | 0.31765 | -12.2575 | 2.6844 | 0.44197 | 0.31765 | -10.458 | 33.127 | 5.4541 | 3.92 | 20.4386 | 32.9767 | 5.4294 | 3.9022 | 19.7224 | 32.3613 | 5.328 | 3.8294 | 19.5539 | 31.1412 | 5.1272 | 3.685 | 19.5574 | 29.5162 | 4.8596 | 3.4927 | 19.2934 | 27.7867 | 4.5749 | 3.288 | 18.9519 | 26.5112 | 4.3649 | 3.1371 | 18.5297 | 25.3438 | 4.1727 | 2.999 | 18.0573 | 23.998 | 3.9511 | 2.8397 | 17.4395 | 22.5002 | 3.7045 | 2.6625 | 16.7042 | 17.7406 | 2.9209 | 2.0993 | 14.1376 | 13.4738 | 2.2184 | 1.5944 | 11.4236 | 9.6401 | 1.5872 | 1.1407 | 9.5387 | 5.5487 | 0.91355 | 0.65659 | 5.5487 | 3.3656 | 0.55412 | 0.39825 | 3.3656 | 33.127 | 5.4541 | 3.92 | 20.4386 | 32.634 | 5.3729 | 3.8616 | 19.5884 | 31.6566 | 5.212 | 3.746 | 19.2678 | 29.7963 | 4.9057 | 3.5258 | 19.0772 | 26.937 | 4.435 | 3.1875 | 17.9256 | 24.4303 | 4.0223 | 2.8909 | 16.7528 | 21.3942 | 3.5224 | 2.5316 | 15.1526 | 16.86 | 2.7759 | 1.9951 | 12.2395 | 12.617 | 2.0773 | 1.493 | 9.3135 | 8.4984 | 1.3992 | 1.0056 | 6.5428 | 2.6844 | 0.44197 | 0.31765 | -0.76975 | 2.6844 | 0.44197 | 0.31765 | -7.3114 | 2.6844 | 0.44197 | 0.31765 | -12.6914 | 2.6844 | 0.44197 | 0.31765 | -16.3672 | 2.6844 | 0.44197 | 0.31765 | -15.1849
ATHLETIC ST | BURNLEY | ROCHDALE | 385381 | 432208 | 22.2618 | 13.8499 | 10.1033 | 10.0085 | 22.3742 | 13.5783 | 9.9052 | 8.4905 | 22.5386 | 13.4659 | 9.8232 | 8.187 | 22.7586 | 13.3349 | 9.7277 | 8.1331 | 22.9038 | 13.1263 | 9.5755 | 7.9825 | 23.0476 | 13.1482 | 9.5914 | 7.8032 | 23.2142 | 13.0415 | 9.5136 | 7.5433 | 23.4172 | 12.9037 | 9.4131 | 7.2909 | 23.5841 | 12.7892 | 9.3295 | 6.9889 | 23.7448 | 12.7565 | 9.3057 | 6.7187 | 24.2473 | 12.409 | 9.0522 | 5.0223 | 24.7163 | 11.9188 | 8.6946 | 2.18 | 25.055 | 11.5639 | 8.4357 | -0.1573 | 25.3411 | 11.8293 | 8.6293 | -2.4676 | 25.5259 | 11.3393 | 8.2718 | -4.3309 | 22.2252 | 13.8499 | 10.1033 | 10.0085 | 22.3027 | 13.7373 | 10.0212 | 9.4309 | 22.3785 | 13.6751 | 9.9758 | 9.2626 | 22.4829 | 13.6122 | 9.9299 | 9.1728 | 22.633 | 13.5376 | 9.8755 | 9.0384 | 22.8265 | 13.4629 | 9.821 | 8.8855 | 22.9556 | 13.1552 | 9.5965 | 8.6797 | 23.0848 | 13.0641 | 9.5301 | 8.4235 | 23.1718 | 12.9943 | 9.4791 | 8.0979 | 23.2629 | 12.9334 | 9.4347 | 7.7677 | 23.555 | 12.7316 | 9.2875 | 6.7946 | 23.852 | 12.57 | 9.1697 | 5.9081 | 24.1269 | 12.4162 | 9.0575 | 5.1261 | 24.4064 | 12.5562 | 9.1596 | 4.3777 | 24.6027 | 12.9004 | 9.4107 | 3.9353 | 22.2786 | 13.8499 | 10.1033 | 10.0085 | 22.4077 | 13.526 | 9.867 | 8.2682 | 22.6006 | 13.3669 | 9.7509 | 7.9458 | 22.8188 | 13.165 | 9.6037 | 7.9287 | 22.9584 | 13.0967 | 9.5539 | 7.8181 | 23.1235 | 13.0118 | 9.492 | 7.6924 | 23.316 | 12.8586 | 9.3802 | 7.4935 | 23.5496 | 12.8118 | 9.346 | 7.3081 | 23.7315 | 12.7479 | 9.2994 | 7.0912 | 23.9063 | 12.6777 | 9.2482 | 6.8888 | 24.3801 | 12.2673 | 8.9488 | 5.3888 | 24.8852 | 11.7119 | 8.5437 | 2.7052 | 25.2491 | 11.2812 | 8.2295 | 0.50364 | 25.5433 | 11.4796 | 8.3742 | -1.6433 | 25.7149 | 10.9546 | 7.9912 | -3.3185 | 22.2786 | 13.8499 | 10.1033 | 10.0085 | 22.2925 | 13.653 | 9.9597 | 9.0304 | 22.3806 | 13.5041 | 9.851 | 8.8695 | 22.5134 | 13.29 | 9.6949 | 8.8795 | 22.7168 | 13.1893 | 9.6214 | 8.7706 | 22.8603 | 13.2573 | 9.671 | 8.6291 | 23.0587 | 13.0832 | 9.544 | 8.2828 | 23.3405 | 12.8218 | 9.3533 | 7.3979 | 23.543 | 12.5368 | 9.1454 | 6.4746 | 23.699 | 12.2685 | 8.9497 | 5.5602 | 24.1751 | 12.4268 | 9.0652 | 2.9167 | 24.6469 | 11.8018 | 8.6092 | 0.38296 | 24.9784 | 11.2601 | 8.2141 | -1.6262 | 25.2082 | 10.8308 | 7.9009 | -2.8153 | 25.2061 | 10.8097 | 7.8855 | -1.8181 | 22.2618 | 13.8499 | 10.1033 | 10.0085 | 22.3574 | 13.6653 | 9.9687 | 8.9945 | 22.4662 | 13.5771 | 9.9043 | 8.8127 | 22.598 | 13.4569 | 9.8166 | 8.8307 | 22.7741 | 13.2803 | 9.6878 | 8.824 | 22.8882 | 13.3215 | 9.7179 | 8.789 | 23.0436 | 13.2314 | 9.6521 | 8.6541 | 23.2198 | 13.0937 | 9.5517 | 8.4496 | 23.3648 | 13.0165 | 9.4954 | 8.1698 | 23.5112 | 12.9786 | 9.4677 | 7.8941 | 23.9917 | 12.7658 | 9.3125 | 6.9527 | 24.425 | 12.5919 | 9.1856 | 5.9274 | 24.7101 | 12.5317 | 9.1417 | 5.2165 | 24.946 | 13.1531 | 9.595 | 4.6185 | 25.0501 | 12.9775 | 9.4669 | 4.4602 | 22.2618 | 13.8499 | 10.1033 | 10.0085 | 22.3165 | 13.5231 | 9.8649 | 8.2579 | 22.4726 | 13.3437 | 9.7341 | 7.8973 | 22.6904 | 13.0999 | 9.5562 | 7.8222 | 22.8419 | 13.0091 | 9.49 | 7.6355 | 22.9856 | 13.0437 | 9.5152 | 7.4006 | 23.1716 | 12.8568 | 9.3788 | 6.9541 | 23.465 | 12.5802 | 9.1771 | 5.9659 | 23.6854 | 12.2721 | 8.9523 | 4.9528 | 23.8473 | 11.9924 | 8.7483 | 3.9529 | 24.3291 | 12.0983 | 8.8255 | 1.0748 | 24.7811 | 11.437 | 8.3431 | -1.6261 | 25.1029 | 10.8627 | 7.9242 | -3.8043 | 25.3139 | 10.3979 | 7.5852 | -5.1964 | 25.3187 | 10.3251 | 7.532 | -4.4554
AVENHAM | PRESTON EAST | PENWORTHAM EAST / ROCHDALE | 354028 | 429192 | 29.433 | 16.4159 | 11.9752 | 18.386 | 29.4894 | 16.3247 | 11.9086 | 17.8738 | 29.5608 | 16.1938 | 11.8132 | 17.4727 | 29.6373 | 15.949 | 11.6346 | 16.8874 | 29.7194 | 15.6349 | 11.4055 | 16.3009 | 29.8081 | 15.4304 | 11.2563 | 15.7147 | 29.8892 | 15.3212 | 11.1766 | 15.135 | 29.9731 | 15.1744 | 11.0695 | 14.707 | 30.0394 | 15.0371 | 10.9694 | 14.2639 | 30.102 | 14.8629 | 10.8423 | 13.8335 | 30.2991 | 14.232 | 10.382 | 12.3233 | 30.5052 | 13.8863 | 10.1299 | 10.5625 | 30.6462 | 13.588 | 9.9122 | 9.3481 | 30.7669 | 13.4384 | 9.8031 | 8.6879 | 30.8472 | 13.164 | 9.6029 | 8.2469 | 29.4258 | 16.4159 | 11.9752 | 18.386 | 29.51 | 16.4475 | 11.9982 | 18.1611 | 29.6133 | 16.4272 | 11.9834 | 17.8918 | 29.697 | 16.3534 | 11.9296 | 17.6328 | 29.7774 | 16.1903 | 11.8106 | 17.3649 | 29.8698 | 16.052 | 11.7097 | 17.0834 | 29.9795 | 15.8587 | 11.5687 | 16.686 | 30.1076 | 15.7403 | 11.4823 | 16.2212 | 30.1534 | 15.636 | 11.4063 | 16.0551 | 30.1998 | 15.5111 | 11.3151 | 15.8896 | 30.3332 | 15.1659 | 11.0633 | 15.4258 | 30.4547 | 14.8774 | 10.8528 | 15.0051 | 30.5566 | 14.4522 | 10.5427 | 14.6673 | 30.6579 | 14.5395 | 10.6063 | 14.3096 | 30.7333 | 14.1667 | 10.3344 | 14.0162 | 29.4361 | 16.4159 | 11.9752 | 18.386 | 29.5022 | 16.2836 | 11.8787 | 17.7979 | 29.5851 | 16.0362 | 11.6982 | 17.3525 | 29.6763 | 15.6293 | 11.4013 | 16.7229 | 29.7748 | 15.2009 | 11.0888 | 16.0902 | 29.8822 | 15.275 | 11.1429 | 15.4548 | 29.9775 | 15.0996 | 11.015 | 14.8208 | 30.0834 | 14.8934 | 10.8645 | 14.3347 | 30.1652 | 14.6724 | 10.7033 | 13.8577 | 30.2425 | 14.3811 | 10.4908 | 13.3924 | 30.4888 | 13.8754 | 10.1219 | 11.7843 | 30.7303 | 13.3467 | 9.7362 | 10.0595 | 30.891 | 12.9587 | 9.4532 | 8.9656 | 31.0262 | 12.7039 | 9.2673 | 8.5267 | 31.0948 | 12.5129 | 9.128 | 8.3943 | 29.4361 | 16.4159 | 11.9752 | 18.386 | 29.4557 | 16.304 | 11.8936 | 17.9652 | 29.5014 | 16.1654 | 11.7924 | 17.591 | 29.5495 | 15.5931 | 11.375 | 17.014 | 29.6053 | 15.6109 | 11.3879 | 16.4294 | 29.679 | 15.4737 | 11.2879 | 15.8261 | 29.766 | 15.2479 | 11.1231 | 15.1757 | 29.8615 | 15.0048 | 10.9458 | 14.5452 | 29.9432 | 14.7264 | 10.7427 | 13.8939 | 30.0219 | 14.5865 | 10.6406 | 13.2635 | 30.2621 | 14.2629 | 10.4046 | 11.4706 | 30.4972 | 13.7046 | 9.9973 | 9.879 | 30.6593 | 13.2597 | 9.6728 | 8.9196 | 30.7707 | 13.0187 | 9.497 | 8.7198 | 30.7797 | 12.7439 | 9.2965 | 8.9858 | 29.433 | 16.4159 | 11.9752 | 18.386 | 29.4863 | 16.3433 | 11.9222 | 18.0544 | 29.5479 | 16.2521 | 11.8557 | 17.7028 | 29.6092 | 16.0209 | 11.687 | 17.1511 | 29.6757 | 15.7179 | 11.466 | 16.6146 | 29.7583 | 15.5119 | 11.3157 | 16.0725 | 29.8377 | 15.4084 | 11.2402 | 15.5185 | 29.9136 | 15.2575 | 11.1302 | 15.1052 | 29.9747 | 15.1364 | 11.0418 | 14.6626 | 30.0346 | 14.964 | 10.916 | 14.2226 | 30.2146 | 14.3466 | 10.4657 | 12.9046 | 30.3917 | 14.1453 | 10.3188 | 11.6143 | 30.5159 | 13.9103 | 10.1474 | 10.7677 | 30.6308 | 13.8505 | 10.1037 | 10.432 | 30.7012 | 13.755 | 10.034 | 10.294 | 29.433 | 16.4159 | 11.9752 | 18.386 | 29.481 | 16.2789 | 11.8753 | 17.824 | 29.5585 | 16.1147 | 11.7555 | 17.3786 | 29.6438 | 15.559 | 11.3501 | 16.7398 | 29.7359 | 15.5161 | 11.3188 | 16.0971 | 29.8348 | 15.3803 | 11.2197 | 15.4555 | 29.9344 | 15.1431 | 11.0467 | 14.7691 | 30.0466 | 14.8949 | 10.8657 | 14.0816 | 30.1377 | 14.6283 | 10.6711 | 13.4095 | 30.2237 | 14.4481 | 10.5397 | 12.7606 | 30.4697 | 14.1155 | 10.2971 | 10.9277 | 30.6846 | 13.545 | 9.8809 | 9.3199 | 30.8235 | 13.0896 | 9.5487 | 8.3419 | 30.9276 | 12.8276 | 9.3576 | 8.1329 | 30.9595 | 12.5472 | 9.153 | 8.3426
BAGULEY | SALE | CARRINGTON | 380562 | 389035 | 29.4591 | 10.356 | 7.4431 | 11.1555 | 29.574 | 10.2862 | 7.3929 | 10.9535 | 29.695 | 9.9761 | 7.17 | 10.7198 | 29.8553 | 9.6145 | 6.9101 | 10.4453 | 30.085 | 9.1692 | 6.5901 | 9.9634 | 30.3713 | 8.6857 | 6.2426 | 9.4271 | 30.7202 | 8.2357 | 5.9191 | 8.8095 | 31.1405 | 8.054 | 5.7886 | 8.2156 | 31.5628 | 7.8508 | 5.6425 | 7.4047 | 32.0058 | 7.6508 | 5.4988 | 6.5904 | 33.5152 | 7.0386 | 5.0588 | 3.6462 | 34.829 | 6.4253 | 4.618 | 0.03489 | 35.5415 | 6.263 | 4.5013 | -2.541 | 36.0186 | 8.35 | 6.0013 | -4.5939 | 36.2434 | 9.2507 | 6.6486 | -6.0451 | 29.445 | 10.356 | 7.4431 | 11.1555 | 29.5082 | 10.2996 | 7.4025 | 11.021 | 29.5608 | 9.9621 | 7.16 | 10.9001 | 29.6295 | 9.6425 | 6.9303 | 10.77 | 29.7311 | 9.2955 | 6.6808 | 10.576 | 29.8594 | 8.9028 | 6.3986 | 10.3445 | 30.0256 | 8.396 | 6.0344 | 9.9955 | 30.2281 | 8.2663 | 5.9411 | 9.5703 | 30.4153 | 8.1404 | 5.8506 | 9.1557 | 30.6282 | 8.0081 | 5.7556 | 8.6848 | 31.4293 | 7.7363 | 5.5602 | 7.1506 | 32.3925 | 7.5353 | 5.4158 | 5.388 | 33.3342 | 7.4696 | 5.3685 | 3.7334 | 34.2987 | 8.8824 | 6.384 | 2.0632 | 34.9191 | 10.2829 | 7.3905 | 1.0423 | 29.465 | 10.356 | 7.4431 | 11.1555 | 29.5975 | 10.2884 | 7.3945 | 10.8869 | 29.7449 | 9.9376 | 7.1424 | 10.583 | 29.9347 | 9.4965 | 6.8253 | 10.2583 | 30.1924 | 9.0562 | 6.5089 | 9.7279 | 30.5031 | 8.5712 | 6.1603 | 9.1515 | 30.873 | 8.0491 | 5.7851 | 8.3433 | 31.3111 | 7.8184 | 5.6192 | 7.5588 | 31.733 | 7.571 | 5.4414 | 6.5686 | 32.1857 | 7.3338 | 5.2709 | 5.5384 | 33.8104 | 6.523 | 4.6882 | 2.0232 | 35.0273 | 5.8159 | 4.18 | -1.6594 | 34.6279 | 5.7012 | 4.0976 | -4.1042 | 36.2223 | 7.7409 | 5.5635 | -5.9051 | 36.3109 | 8.7638 | 6.2987 | -7.2342 | 29.4651 | 10.356 | 7.4431 | 11.1555 | 29.4818 | 10.3707 | 7.4536 | 11.2931 | 29.5785 | 10.3369 | 7.4293 | 11.0869 | 29.725 | 10.2124 | 7.3398 | 10.7837 | 29.955 | 10.0332 | 7.2111 | 10.2551 | 30.2756 | 9.7963 | 7.0408 | 9.6253 | 30.6942 | 9.4231 | 6.7726 | 8.6005 | 31.2427 | 8.847 | 6.3585 | 7.0923 | 31.7902 | 8.3082 | 5.9713 | 5.5483 | 32.3608 | 8.1609 | 5.8654 | 4.0138 | 33.7605 | 8.0803 | 5.8075 | 0.045181 | 34.8364 | 7.3823 | 5.3058 | -3.0647 | 35.4883 | 7.1066 | 5.1077 | -4.915 | 35.774 | 8.8954 | 6.3933 | -5.6143 | 35.5962 | 8.8252 | 6.3428 | -5.0971 | 29.459 | 10.356 | 7.4431 | 11.1555 | 29.5518 | 10.2836 | 7.391 | 10.9845 | 29.6339 | 10.0171 | 7.1995 | 10.8047 | 29.7275 | 9.6674 | 6.9481 | 10.66 | 29.8634 | 9.2728 | 6.6646 | 10.4581 | 30.0676 | 8.8626 | 6.3697 | 10.17 | 30.3424 | 8.444 | 6.0689 | 9.7502 | 30.6721 | 8.2773 | 5.9491 | 9.2816 | 31.0126 | 8.121 | 5.8367 | 8.6819 | 31.3869 | 7.9116 | 5.6862 | 7.917 | 32.6909 | 7.45 | 5.3544 | 5.684 | 33.9787 | 7.1211 | 5.118 | 3.4872 | 34.765 | 7.1692 | 5.1526 | 1.9477 | 35.2203 | 9.3308 | 6.7062 | 0.6507 | 35.3913 | 10.5155 | 7.5577 | -0.0076567 | 29.459 | 10.356 | 7.4431 | 11.1555 | 29.4882 | 10.3637 | 7.4486 | 11.23 | 29.6142 | 10.2694 | 7.3808 | 10.9343 | 29.7937 | 10.1439 | 7.2906 | 10.5265 | 30.0421 | 9.9371 | 7.142 | 9.8886 | 30.3358 | 9.6938 | 6.9671 | 9.2131 | 30.7034 | 9.307 | 6.6891 | 8.1311 | 31.2175 | 8.7166 | 6.2648 | 6.5414 | 31.7258 | 8.1479 | 5.856 | 4.9414 | 32.2623 | 8.0059 | 5.754 | 3.3332 | 33.7338 | 7.8724 | 5.6581 | -0.90204 | 34.9025 | 7.1203 | 5.1175 | -4.2978 | 35.6671 | 6.7939 | 4.8829 | -6.4239 | 36.1085 | 8.5394 | 6.1375 | -7.3559 | 35.9725 | 8.4658 | 6.0845 | -6.8274
BAMBER BRIDGE | RIBBLE | PENWORTHAM EAST / ROCHDALE | 356431 | 426698 | 29.7486 | 13.0579 | 9.385 | 14.5233 | 29.8096 | 12.8349 | 9.2247 | 13.0252 | 29.8963 | 12.3561 | 8.8806 | 11.3863 | 30.0162 | 11.9737 | 8.6057 | 10.6116 | 30.1927 | 11.8068 | 8.4858 | 9.7836 | 30.4312 | 11.761 | 8.4529 | 8.933 | 30.753 | 11.4341 | 8.2179 | 8.0592 | 31.1775 | 11.1628 | 8.0229 | 7.1481 | 31.6379 | 10.8952 | 7.8306 | 6.1596 | 32.1466 | 10.7276 | 7.7101 | 5.7693 | 33.7317 | 10.0575 | 7.2285 | 3.4754 | 34.9188 | 9.2079 | 6.6179 | 0.10127 | 35.6369 | 8.6067 | 6.1858 | -2.4621 | 36.1967 | 7.9276 | 5.6977 | -4.9397 | 36.5583 | 7.2564 | 5.2153 | -6.9562 | 29.729 | 13.0579 | 9.385 | 14.5233 | 29.7956 | 13.0783 | 9.3996 | 13.8443 | 29.8606 | 13.0119 | 9.3519 | 13.5928 | 29.9423 | 12.6979 | 9.1262 | 13.4676 | 30.0558 | 12.7251 | 9.1458 | 13.3303 | 30.2013 | 12.7034 | 9.1302 | 13.178 | 30.3897 | 12.448 | 8.9466 | 12.9467 | 30.6249 | 12.345 | 8.8726 | 12.6172 | 30.8102 | 12.2245 | 8.786 | 12.3276 | 31.0278 | 12.0798 | 8.682 | 11.903 | 31.8833 | 11.6399 | 8.3658 | 10.4058 | 32.9788 | 11.2424 | 8.0801 | 8.7343 | 34.1326 | 10.5855 | 7.608 | 7.0753 | 35.25 | 10.3903 | 7.4677 | 5.3128 | 35.8277 | 9.9476 | 7.1495 | 4.1972 | 29.754 | 13.0579 | 9.385 | 14.5233 | 29.818 | 12.7381 | 9.1551 | 12.796 | 29.9093 | 12.089 | 8.6886 | 11.1187 | 30.0326 | 11.8912 | 8.5465 | 10.346 | 30.208 | 11.766 | 8.4564 | 9.5243 | 30.4375 | 11.5153 | 8.2763 | 8.685 | 30.7391 | 11.1504 | 8.014 | 7.827 | 31.1297 | 10.8753 | 7.8163 | 6.9418 | 31.5323 | 10.5692 | 7.5963 | 6.0153 | 31.9861 | 10.3811 | 7.4611 | 5.6886 | 33.5085 | 9.6232 | 6.9164 | 3.9228 | 34.8182 | 8.799 | 6.324 | 0.65796 | 35.6407 | 8.0673 | 5.7981 | -1.9493 | 36.2428 | 7.2229 | 5.1912 | -4.3742 | 36.5699 | 6.4015 | 4.6009 | -6.1924 | 29.754 | 13.0579 | 9.385 | 14.5233 | 29.7318 | 12.8565 | 9.2402 | 13.461 | 29.7775 | 12.446 | 8.9452 | 11.9351 | 29.8583 | 12.0412 | 8.6543 | 11.202 | 30.0039 | 11.9912 | 8.6183 | 10.3997 | 30.2358 | 11.8002 | 8.481 | 9.5476 | 30.576 | 11.4671 | 8.2417 | 8.5328 | 31.0547 | 11.0147 | 7.9165 | 7.0885 | 31.5738 | 10.65 | 7.6544 | 5.5857 | 32.1132 | 10.3028 | 7.4049 | 4.6794 | 33.7558 | 9.4916 | 6.8218 | 1.9058 | 34.8424 | 8.6221 | 6.1969 | -1.2096 | 35.5135 | 7.8671 | 5.6543 | -3.4901 | 35.934 | 7.1129 | 5.1122 | -4.9932 | 35.9676 | 6.7744 | 4.8689 | -4.5108 | 29.7486 | 13.0579 | 9.385 | 14.5233 | 29.8 | 12.9074 | 9.2768 | 13.289 | 29.8625 | 12.4802 | 8.9698 | 11.728 | 29.9405 | 12.1252 | 8.7146 | 11.0158 | 30.0619 | 11.8566 | 8.5216 | 10.2939 | 30.2537 | 11.913 | 8.5621 | 9.5289 | 30.5259 | 11.5948 | 8.3334 | 8.7097 | 30.866 | 11.3312 | 8.144 | 7.8542 | 31.2311 | 11.0743 | 7.9593 | 6.904 | 31.6452 | 10.9146 | 7.8446 | 6.5393 | 33.0658 | 10.4199 | 7.489 | 5.2243 | 34.2944 | 9.8591 | 7.0859 | 3.3275 | 35.0236 | 9.5223 | 6.8438 | 2.0545 | 35.4829 | 9.1524 | 6.578 | 1.0945 | 35.6639 | 8.7826 | 6.3122 | 0.65387 | 29.7486 | 13.0579 | 9.385 | 14.5233 | 29.7475 | 12.6934 | 9.123 | 12.7431 | 29.8228 | 12.2709 | 8.8193 | 11.0439 | 29.9347 | 11.786 | 8.4708 | 10.2488 | 30.0986 | 11.7879 | 8.4722 | 9.3968 | 30.3112 | 11.5818 | 8.324 | 8.5344 | 30.6072 | 11.244 | 8.0813 | 7.5235 | 31.0447 | 10.7965 | 7.7597 | 6.0588 | 31.5024 | 10.4243 | 7.4921 | 4.552 | 32.0029 | 10.0745 | 7.2407 | 3.6434 | 33.6194 | 9.2015 | 6.6133 | 0.57498 | 34.9716 | 8.282 | 5.9524 | -2.8026 | 35.7668 | 7.4679 | 5.3673 | -5.359 | 36.2594 | 6.6699 | 4.7938 | -7.165 | 36.3243 | 6.2704 | 4.5067 | -6.8318
BARBARA ST | BOLTON | KEARSLEY | 370695 | 407609 | 25.8593 | 9.0358 | 6.5915 | 10.0163 | 25.9154 | 8.5715 | 6.2528 | 8.4225 | 25.9823 | 8.2958 | 6.0517 | 7.9093 | 26.0507 | 8.3457 | 6.0881 | 7.6773 | 26.1474 | 8.2188 | 5.9955 | 7.3422 | 26.2721 | 8.023 | 5.8527 | 6.9808 | 26.4324 | 7.8193 | 5.704 | 6.6304 | 26.6355 | 7.6386 | 5.5722 | 6.2848 | 26.8217 | 7.4447 | 5.4308 | 5.889 | 27.0135 | 7.2635 | 5.2987 | 5.4991 | 27.6753 | 6.7693 | 4.9381 | 3.4322 | 28.2979 | 6.2218 | 4.5387 | 0.47546 | 28.7103 | 5.7678 | 4.2075 | -1.7341 | 29.0184 | 5.2521 | 3.8313 | -3.6085 | 29.1846 | 4.8139 | 3.5116 | -4.7359 | 25.8441 | 9.0358 | 6.5915 | 10.0163 | 25.8949 | 8.8403 | 6.4489 | 9.4863 | 25.9466 | 8.6635 | 6.3199 | 9.2637 | 26.0082 | 8.4692 | 6.1782 | 9.1315 | 26.095 | 8.2904 | 6.0478 | 8.9542 | 26.2093 | 8.3349 | 6.0802 | 8.7418 | 26.3447 | 8.0935 | 5.9041 | 8.4711 | 26.504 | 8.0421 | 5.8666 | 8.1529 | 26.5857 | 7.9774 | 5.8194 | 7.8727 | 26.6787 | 7.9095 | 5.7699 | 7.5715 | 26.9923 | 7.6264 | 5.5633 | 6.6305 | 27.3533 | 7.3805 | 5.384 | 5.6765 | 27.7172 | 7.071 | 5.1582 | 4.7596 | 28.102 | 6.5546 | 4.7815 | 3.832 | 28.3592 | 6.3961 | 4.6658 | 3.2312 | 25.8649 | 9.0358 | 6.5915 | 10.0163 | 25.94 | 8.4365 | 6.1543 | 8.0993 | 26.0217 | 8.2794 | 6.0397 | 7.4419 | 26.1128 | 8.1781 | 5.9658 | 7.1168 | 26.2334 | 7.9241 | 5.7805 | 6.6799 | 26.3825 | 7.6581 | 5.5865 | 6.2137 | 26.5682 | 7.3386 | 5.3534 | 5.7685 | 26.7958 | 7.2479 | 5.2873 | 5.3167 | 26.993 | 7.0399 | 5.1355 | 4.8452 | 27.1748 | 6.9073 | 5.0387 | 4.3463 | 27.932 | 6.3858 | 4.6584 | 1.9595 | 28.6921 | 5.6714 | 4.1372 | -1.0065 | 29.1933 | 5.109 | 3.7269 | -2.9695 | 28.1295 | 4.5629 | 3.3286 | -4.3094 | 25.955 | 4.2102 | 3.0713 | -4.5019 | 25.8649 | 9.0358 | 6.5915 | 10.0163 | 25.8475 | 8.6028 | 6.2756 | 8.847 | 25.8765 | 8.488 | 6.1919 | 8.3884 | 25.9193 | 8.3829 | 6.1152 | 8.1275 | 25.9988 | 8.0879 | 5.9 | 7.7241 | 26.1248 | 7.7658 | 5.665 | 7.2471 | 26.3009 | 7.5205 | 5.4861 | 6.6205 | 26.5327 | 7.4607 | 5.4425 | 5.5081 | 26.7586 | 7.2452 | 5.2853 | 4.4025 | 26.9979 | 6.9977 | 5.1048 | 3.3127 | 27.7453 | 6.1824 | 4.51 | 0.25725 | 28.3979 | 5.4754 | 3.9942 | -2.2006 | 28.8096 | 4.932 | 3.5979 | -3.6477 | 27.9461 | 4.5331 | 3.3069 | -4.0281 | 27.1656 | 4.4065 | 3.2145 | -2.8607 | 25.8593 | 9.0358 | 6.5915 | 10.0163 | 25.9092 | 8.7041 | 6.3495 | 9.0239 | 25.9579 | 8.4027 | 6.1297 | 8.6847 | 25.9991 | 8.5065 | 6.2054 | 8.5577 | 26.0609 | 8.4182 | 6.141 | 8.407 | 26.1634 | 8.2547 | 6.0217 | 8.1974 | 26.3097 | 8.0743 | 5.8901 | 7.9334 | 26.4846 | 7.9069 | 5.7679 | 7.6333 | 26.6402 | 7.7231 | 5.6339 | 7.2512 | 26.81 | 7.491 | 5.4646 | 6.8481 | 27.3646 | 7.1661 | 5.2275 | 5.4751 | 27.9145 | 6.9108 | 5.0414 | 4.1146 | 28.2956 | 6.7303 | 4.9096 | 3.1761 | 28.5882 | 6.3947 | 4.6648 | 2.4011 | 28.6812 | 6.1932 | 4.5179 | 2.1311 | 25.8593 | 9.0358 | 6.5915 | 10.0163 | 25.8647 | 8.4399 | 6.1568 | 8.076 | 25.9294 | 8.3185 | 6.0682 | 7.3782 | 26.0093 | 8.1785 | 5.9661 | 7.0094 | 26.1204 | 7.8727 | 5.743 | 6.5137 | 26.2553 | 7.5388 | 5.4994 | 5.9937 | 26.4297 | 7.2282 | 5.2728 | 5.0211 | 26.6725 | 7.1023 | 5.181 | 3.5296 | 26.8884 | 6.8234 | 4.9776 | 2.0682 | 27.1168 | 6.5113 | 4.7499 | 0.62305 | 27.8603 | 5.5079 | 4.0179 | -3.5301 | 28.3875 | 4.6047 | 3.3591 | -7.0836 | 24.8023 | 4.0232 | 2.9348 | -8.7315 | 22.1154 | 3.5873 | 2.6169 | -9.3254 | 20.986 | 3.4041 | 2.4833 | -8.4115
BARROW | BARROW & SANDGATE | HARKER / HUTTON | 319709 | 470489 | 19.9095 | 13.6265 | 9.7936 | 16.923 | 20.051 | 13.5054 | 9.7066 | 16.8152 | 20.2391 | 12.9362 | 9.2975 | 16.6347 | 20.4723 | 12.3964 | 8.9095 | 16.479 | 20.7775 | 11.8619 | 8.5254 | 16.2616 | 21.0587 | 11.3379 | 8.1488 | 16.0541 | 21.2256 | 10.8294 | 7.7833 | 15.9071 | 21.4195 | 10.7576 | 7.7317 | 15.7966 | 21.5767 | 10.6813 | 7.6768 | 15.6245 | 21.7266 | 10.6064 | 7.623 | 15.4778 | 22.3754 | 10.1527 | 7.297 | 13.7023 | 23.2709 | 9.433 | 6.7796 | 10.1788 | 23.9905 | 8.7744 | 6.3063 | 7.1326 | 24.3877 | 8.5078 | 6.1147 | 3.9411 | 24.6374 | 8.3755 | 6.0196 | 1.447 | 19.8745 | 13.6265 | 9.7936 | 16.923 | 19.9577 | 13.4534 | 9.6692 | 16.8017 | 20.0284 | 13.2625 | 9.532 | 16.6207 | 20.1249 | 13.0727 | 9.3956 | 16.4562 | 20.2591 | 12.8673 | 9.248 | 16.2712 | 20.4117 | 12.6506 | 9.0922 | 16.0745 | 20.577 | 12.4024 | 8.9138 | 15.832 | 20.7635 | 12.2913 | 8.834 | 15.5551 | 20.9147 | 12.1962 | 8.7656 | 15.3132 | 21.0757 | 12.0978 | 8.695 | 15.0681 | 21.4646 | 11.8693 | 8.5307 | 14.3634 | 21.7524 | 11.7389 | 8.4369 | 13.7374 | 22.0548 | 11.5965 | 8.3346 | 13.1546 | 22.3563 | 11.7397 | 8.4376 | 12.5757 | 22.532 | 11.8833 | 8.5408 | 12.2008 | 19.9224 | 13.6265 | 9.7936 | 16.923 | 20.0727 | 13.48 | 9.6883 | 16.8397 | 20.2805 | 12.8733 | 9.2523 | 16.6872 | 20.5366 | 12.3211 | 8.8554 | 16.5802 | 20.8755 | 11.8032 | 8.4832 | 16.4124 | 21.1128 | 11.2789 | 8.1064 | 16.2625 | 21.2984 | 10.7774 | 7.746 | 16.1907 | 21.5156 | 10.7037 | 7.693 | 16.1674 | 21.6843 | 10.6171 | 7.6307 | 16.1083 | 21.8451 | 10.5507 | 7.583 | 16.0502 | 22.5379 | 10.0174 | 7.1997 | 14.5387 | 23.4855 | 9.2736 | 6.6651 | 11.2643 | 24.2448 | 8.6287 | 6.2016 | 8.4558 | 24.6593 | 8.3782 | 6.0216 | 5.5494 | 24.848 | 8.2164 | 5.9053 | 3.3463 | 19.9225 | 13.6265 | 9.7936 | 16.923 | 20.0071 | 13.5209 | 9.7177 | 16.9961 | 20.1405 | 12.9396 | 9.2999 | 16.9091 | 20.3386 | 12.3997 | 8.9119 | 16.815 | 20.6127 | 11.8255 | 8.4992 | 16.6428 | 20.9172 | 11.3029 | 8.1236 | 16.4553 | 21.1368 | 10.5778 | 7.6025 | 16.0781 | 21.4912 | 10.2499 | 7.3668 | 14.9487 | 21.8111 | 9.8741 | 7.0967 | 13.7726 | 22.1248 | 9.5087 | 6.8341 | 12.6021 | 22.8932 | 8.657 | 6.2219 | 9.2741 | 23.5663 | 7.973 | 5.7304 | 6.1828 | 24.0532 | 7.446 | 5.3516 | 3.6259 | 24.4187 | 7.6743 | 5.5157 | 2.1227 | 24.4592 | 7.7516 | 5.5712 | 3.8526 | 19.9094 | 13.6265 | 9.7936 | 16.923 | 20.0269 | 13.5332 | 9.7266 | 16.8397 | 20.1596 | 12.9737 | 9.3245 | 16.7056 | 20.317 | 12.4433 | 8.9433 | 16.6299 | 20.4976 | 11.9362 | 8.5788 | 16.5709 | 20.7471 | 11.4376 | 8.2204 | 16.4988 | 21.0358 | 10.9414 | 7.8638 | 16.421 | 21.202 | 10.8757 | 7.8166 | 16.3463 | 21.3376 | 10.8001 | 7.7623 | 16.1836 | 21.4746 | 10.7217 | 7.7059 | 16.0231 | 21.9221 | 10.4743 | 7.5281 | 15.4479 | 22.395 | 10.2429 | 7.3618 | 14.7849 | 22.742 | 10.001 | 7.1879 | 14.2593 | 23.0453 | 10.2522 | 7.3685 | 13.6657 | 23.1955 | 10.5005 | 7.547 | 13.3652 | 19.9094 | 13.6265 | 9.7936 | 16.923 | 20.0186 | 13.4871 | 9.6934 | 16.9341 | 20.2051 | 12.8932 | 9.2666 | 16.7577 | 20.4602 | 12.3367 | 8.8667 | 16.5616 | 20.7822 | 11.7452 | 8.4415 | 16.2966 | 21.0432 | 11.2113 | 8.0578 | 16.0467 | 21.2539 | 10.4757 | 7.5291 | 15.5989 | 21.6226 | 10.1246 | 7.2768 | 14.3624 | 21.9536 | 9.7367 | 6.998 | 13.1058 | 22.2769 | 9.3578 | 6.7256 | 11.8557 | 23.0667 | 8.4666 | 6.0851 | 8.2858 | 23.6976 | 7.7336 | 5.5583 | 4.9563 | 24.1583 | 7.1553 | 5.1427 | 2.107 | 24.4893 | 7.3379 | 5.2739 | 0.25218 | 24.5435 | 7.3253 | 5.2649 | 1.5959
BARTON DOCK RD | BARTON | CARRINGTON | 378864 | 395534 | 22.0901 | 13.1828 | 9.6166 | 9.7771 | 22.1385 | 13.0721 | 9.5359 | 9.3896 | 22.2511 | 12.9065 | 9.4151 | 9.1112 | 22.374 | 12.7735 | 9.3181 | 8.8526 | 22.532 | 12.6207 | 9.2066 | 8.5925 | 22.752 | 12.4583 | 9.0882 | 8.3089 | 23.0317 | 12.1944 | 8.8956 | 7.9995 | 23.3022 | 12.2044 | 8.9029 | 7.6515 | 23.6537 | 12.1104 | 8.8344 | 7.2056 | 25.0344 | 11.8488 | 8.6435 | 5.7543 | 26.8516 | 11.3231 | 8.26 | 3.2551 | 27.8322 | 10.8678 | 7.9279 | 1.2311 | 28.2979 | 10.5934 | 7.7277 | -0.18525 | 28.6729 | 10.3573 | 7.5555 | -1.6833 | 28.7725 | 10.1044 | 7.371 | -2.9761 | 22.0821 | 13.1828 | 9.6166 | 9.7771 | 22.1142 | 13.153 | 9.5949 | 9.6883 | 22.1856 | 13.0529 | 9.5219 | 9.5461 | 22.2546 | 12.9474 | 9.4449 | 9.4466 | 22.3315 | 12.8575 | 9.3794 | 9.3657 | 22.4234 | 12.7682 | 9.3142 | 9.2708 | 22.5403 | 12.573 | 9.1718 | 9.1442 | 22.7071 | 12.5169 | 9.1309 | 8.9753 | 22.9173 | 12.4565 | 9.0869 | 8.7453 | 23.1647 | 12.3907 | 9.0389 | 8.5006 | 24.8787 | 12.0121 | 8.7627 | 6.7829 | 25.984 | 11.7798 | 8.5932 | 5.6511 | 26.6998 | 11.6217 | 8.4779 | 4.7107 | 27.4638 | 11.4169 | 8.3285 | 3.3318 | 27.9168 | 11.2881 | 8.2345 | 2.3468 | 22.0935 | 13.1828 | 9.6166 | 9.7771 | 22.1438 | 13.0508 | 9.5204 | 9.3475 | 22.2575 | 12.8871 | 9.401 | 9.0617 | 22.3724 | 12.6973 | 9.2625 | 8.8055 | 22.5175 | 12.5435 | 9.1503 | 8.5529 | 22.7123 | 12.327 | 8.9924 | 8.2825 | 22.9595 | 12.2229 | 8.9164 | 7.9934 | 23.1808 | 12.1466 | 8.8608 | 7.6757 | 23.4603 | 12.0408 | 8.7836 | 7.2976 | 24.7566 | 11.7704 | 8.5863 | 5.9299 | 26.7732 | 11.1241 | 8.1149 | 3.3858 | 28.4386 | 10.5716 | 7.7119 | 0.75482 | 28.9376 | 10.293 | 7.5086 | -0.61686 | 29.3051 | 10.0336 | 7.3194 | -1.9929 | 29.2745 | 9.8136 | 7.1589 | -3.002 | 22.0935 | 13.1828 | 9.6166 | 9.7771 | 22.1135 | 13.0941 | 9.552 | 9.4925 | 22.2087 | 13.0163 | 9.4952 | 9.2517 | 22.326 | 12.8686 | 9.3875 | 9.0115 | 22.4769 | 12.6375 | 9.2189 | 8.7656 | 22.9342 | 12.6186 | 9.2051 | 8.249 | 24.2391 | 12.3469 | 9.0069 | 6.8625 | 25.5626 | 12.0087 | 8.7602 | 5.3216 | 26.7558 | 11.7089 | 8.5415 | 3.8737 | 26.9943 | 11.5614 | 8.4339 | 3.3627 | 27.688 | 11.0869 | 8.0877 | 1.6557 | 28.3524 | 10.6588 | 7.7755 | -8.3504e-07 | 28.7406 | 10.3033 | 7.5161 | -1.2244 | 29.0014 | 10.0888 | 7.3596 | -2.2634 | 28.8403 | 9.922 | 7.2379 | -2.5194 | 22.0901 | 13.1828 | 9.6166 | 9.7771 | 22.1292 | 13.1291 | 9.5775 | 9.6072 | 22.2256 | 12.9907 | 9.4765 | 9.3875 | 22.3278 | 12.8624 | 9.3829 | 9.1587 | 22.4453 | 12.7064 | 9.2692 | 8.9454 | 22.6172 | 12.5686 | 9.1686 | 8.7037 | 22.8543 | 12.367 | 9.0216 | 8.4319 | 23.1014 | 12.3161 | 8.9845 | 8.1299 | 23.3817 | 12.2362 | 8.9261 | 7.7271 | 24.6897 | 11.9796 | 8.7389 | 6.3153 | 26.4818 | 11.5145 | 8.3997 | 4.0793 | 27.4264 | 11.1595 | 8.1407 | 2.5289 | 27.92 | 10.9652 | 7.999 | 1.5065 | 28.2905 | 10.8153 | 7.8896 | 0.48946 | 28.3169 | 10.6749 | 7.7872 | -0.2328 | 22.0901 | 13.1828 | 9.6166 | 9.7771 | 22.1184 | 13.0409 | 9.5132 | 9.3516 | 22.2255 | 12.9427 | 9.4415 | 9.0617 | 22.3434 | 12.8051 | 9.3411 | 8.7962 | 22.4876 | 12.57 | 9.1696 | 8.533 | 22.9138 | 12.5405 | 9.1481 | 8.02 | 24.2082 | 12.265 | 8.9472 | 6.6512 | 25.4964 | 11.9303 | 8.703 | 5.1327 | 26.6319 | 11.6345 | 8.4872 | 3.7206 | 26.8584 | 11.4912 | 8.3826 | 3.2342 | 27.7527 | 11.0165 | 8.0364 | 1.5242 | 28.5123 | 10.569 | 7.7099 | -0.23735 | 29.0033 | 10.1959 | 7.4377 | -1.5807 | 29.3229 | 9.9554 | 7.2623 | -2.7033 | 29.1813 | 9.771 | 7.1278 | -3.0085
BEDFORD | ATHERTON | KEARSLEY | 366258 | 399876 | 28.7257 | 10.6351 | 7.6436 | 10.3188 | 28.9283 | 10.5261 | 7.5653 | 9.9262 | 29.1961 | 10.3483 | 7.4375 | 9.599 | 29.5061 | 10.1393 | 7.2873 | 9.3258 | 29.7443 | 9.9046 | 7.1186 | 8.9614 | 30.0279 | 9.6931 | 6.9666 | 8.5701 | 30.3369 | 9.4922 | 6.8222 | 8.125 | 30.7014 | 9.307 | 6.6891 | 7.6649 | 31.0588 | 9.1181 | 6.5533 | 7.1335 | 31.4212 | 8.9293 | 6.4176 | 6.6091 | 32.6758 | 8.1898 | 5.8862 | 4.0911 | 33.8234 | 7.2396 | 5.2032 | -0.026105 | 34.6245 | 6.3477 | 4.5622 | -3.6497 | 35.2951 | 6.1546 | 4.4234 | -7.485 | 35.7702 | 6.0397 | 4.3409 | -10.867 | 28.6793 | 10.6351 | 7.6436 | 10.3188 | 28.839 | 10.5926 | 7.6131 | 10.1173 | 29.0007 | 10.5057 | 7.5506 | 9.8927 | 29.2051 | 10.2877 | 7.3939 | 9.6311 | 29.4622 | 10.0967 | 7.2567 | 9.2938 | 29.716 | 9.7718 | 7.0232 | 8.9188 | 29.9564 | 9.4163 | 6.7677 | 8.4255 | 30.2458 | 9.2646 | 6.6586 | 7.765 | 30.4716 | 9.1114 | 6.5485 | 7.2777 | 30.7184 | 8.9687 | 6.446 | 6.784 | 31.5052 | 8.4674 | 6.0857 | 5.2517 | 32.3778 | 8.0399 | 5.7784 | 3.6107 | 33.1923 | 7.6418 | 5.4923 | 2.0002 | 34.0448 | 7.7509 | 5.5707 | 0.14399 | 34.6499 | 7.8765 | 5.661 | -1.1886 | 28.7453 | 10.6351 | 7.6436 | 10.3188 | 28.9581 | 10.5031 | 7.5488 | 9.8944 | 29.2517 | 10.2694 | 7.3808 | 9.5611 | 29.54 | 9.9259 | 7.1339 | 9.288 | 29.7863 | 9.7427 | 7.0023 | 8.9264 | 30.0649 | 9.4864 | 6.8181 | 8.5405 | 30.3682 | 9.2537 | 6.6508 | 8.101 | 30.7303 | 9.0441 | 6.5002 | 7.6535 | 31.0665 | 8.831 | 6.347 | 7.1894 | 31.3992 | 8.61 | 6.1882 | 6.7459 | 32.6705 | 7.7539 | 5.5729 | 4.3725 | 33.9192 | 6.7274 | 4.8351 | 0.62556 | 34.8149 | 5.8568 | 4.2094 | -2.3839 | 34.5809 | 5.6935 | 4.092 | -5.7206 | 33.5449 | 5.5229 | 3.9694 | -8.7679 | 28.7454 | 10.6351 | 7.6436 | 10.3188 | 28.8036 | 10.5827 | 7.606 | 10.2479 | 28.9612 | 10.4374 | 7.5016 | 10.0373 | 29.1827 | 10.1421 | 7.2893 | 9.8346 | 29.4304 | 9.9773 | 7.1709 | 9.5236 | 29.7002 | 9.6903 | 6.9646 | 9.1447 | 30.0758 | 9.3856 | 6.7456 | 8.4913 | 30.518 | 8.9779 | 6.4526 | 7.1992 | 30.9034 | 8.6068 | 6.1859 | 5.8661 | 31.3019 | 8.1824 | 5.8808 | 4.55 | 32.5329 | 7.2325 | 5.1981 | 0.80704 | 33.6624 | 6.2232 | 4.4728 | -3.0043 | 33.3077 | 5.4839 | 3.9414 | -6.0059 | 34.9694 | 6.0588 | 4.3546 | -8.0168 | 35.082 | 5.8337 | 4.1928 | -7.1971 | 28.7256 | 10.6351 | 7.6436 | 10.3188 | 28.8966 | 10.5586 | 7.5887 | 10.1008 | 29.0855 | 10.4313 | 7.4971 | 9.8525 | 29.3078 | 10.2306 | 7.353 | 9.6702 | 29.5475 | 10.0339 | 7.2115 | 9.4725 | 29.7728 | 9.8608 | 7.0871 | 9.226 | 30.0451 | 9.6785 | 6.9561 | 8.864 | 30.3571 | 9.5033 | 6.8302 | 8.4484 | 30.6752 | 9.3168 | 6.6962 | 7.9231 | 31.0162 | 9.1257 | 6.5588 | 7.3877 | 32.1534 | 8.5496 | 6.1447 | 5.6836 | 33.2114 | 8.0394 | 5.778 | 3.8713 | 33.9372 | 7.5672 | 5.4387 | 2.5537 | 34.5083 | 7.8478 | 5.6404 | 1.0079 | 34.7919 | 8.2164 | 5.9053 | 0.2 | 28.7256 | 10.6351 | 7.6436 | 10.3188 | 28.8364 | 10.5419 | 7.5767 | 10.0999 | 29.0847 | 10.3578 | 7.4443 | 9.7852 | 29.3869 | 10.0613 | 7.2313 | 9.4835 | 29.6177 | 9.8594 | 7.0861 | 9.0887 | 29.8857 | 9.5602 | 6.8711 | 8.6815 | 30.237 | 9.253 | 6.6503 | 8.0143 | 30.7452 | 8.8351 | 6.35 | 6.6627 | 31.1114 | 8.4532 | 6.0755 | 5.2839 | 31.4958 | 7.9997 | 5.7495 | 3.7899 | 32.7298 | 6.9402 | 4.988 | -0.48538 | 33.9109 | 5.8656 | 4.2157 | -4.6068 | 30.6122 | 5.0401 | 3.6224 | -8.0495 | 33.5525 | 5.5242 | 3.9703 | -10.5522 | 31.7353 | 5.225 | 3.7553 | -10.1379
BELGRAVE | GREENHILL | WHITEGATE | 393008 | 403366 | 22.6698 | 14.4952 | 10.574 | 11.9794 | 22.7319 | 14.3462 | 10.4654 | 11.5734 | 22.8054 | 14.1336 | 10.3103 | 11.3997 | 22.8931 | 13.9158 | 10.1514 | 11.2459 | 23.0045 | 13.7237 | 10.0113 | 10.9521 | 23.133 | 13.4442 | 9.8074 | 10.6339 | 23.2811 | 13.1927 | 9.6239 | 10.3363 | 23.4577 | 13.0689 | 9.5336 | 10.0861 | 23.6009 | 12.962 | 9.4556 | 9.8602 | 23.7395 | 12.8686 | 9.3875 | 9.6511 | 24.1908 | 12.4256 | 9.0643 | 8.1464 | 24.6658 | 11.8531 | 8.6467 | 5.622 | 25.0158 | 11.3425 | 8.2742 | 3.6315 | 25.329 | 11.0116 | 8.0328 | 1.8337 | 25.5532 | 10.5916 | 7.7264 | 0.41911 | 22.6524 | 14.4952 | 10.574 | 11.9794 | 22.698 | 14.448 | 10.5396 | 11.8104 | 22.7378 | 14.1279 | 10.3061 | 11.717 | 22.7809 | 14.047 | 10.2471 | 11.6252 | 22.8413 | 13.8711 | 10.1188 | 11.4867 | 22.9191 | 13.7366 | 10.0207 | 11.3277 | 23.015 | 13.3861 | 9.765 | 11.1135 | 23.1257 | 13.2822 | 9.6891 | 10.8318 | 23.1953 | 13.2017 | 9.6304 | 10.6457 | 23.2687 | 13.1215 | 9.5719 | 10.4503 | 23.5 | 12.8799 | 9.3957 | 9.841 | 23.7343 | 12.7131 | 9.274 | 9.1876 | 23.9502 | 12.545 | 9.1514 | 8.5013 | 24.1753 | 12.31 | 8.98 | 7.7025 | 24.3534 | 11.9718 | 8.7333 | 7.0613 | 22.6772 | 14.4952 | 10.574 | 11.9794 | 22.7597 | 14.3228 | 10.4483 | 11.4608 | 22.8614 | 14.0463 | 10.2466 | 11.2016 | 22.9839 | 13.8059 | 10.0712 | 10.9677 | 23.1354 | 13.5217 | 9.8639 | 10.5319 | 23.309 | 13.1969 | 9.6269 | 10.0689 | 23.5092 | 12.8911 | 9.4039 | 9.6332 | 23.7448 | 12.729 | 9.2856 | 9.2284 | 23.9342 | 12.5702 | 9.1698 | 8.8443 | 24.1196 | 12.4127 | 9.0549 | 8.4621 | 24.6426 | 11.804 | 8.6109 | 6.6716 | 25.1826 | 11.1425 | 8.1283 | 4.1695 | 25.4392 | 10.7587 | 7.8484 | 2.4496 | 25.6456 | 10.3452 | 7.5467 | 1.1087 | 25.7452 | 9.9782 | 7.279 | 0.42172 | 22.6772 | 14.4952 | 10.574 | 11.9794 | 22.6828 | 14.4015 | 10.5057 | 11.812 | 22.7404 | 14.2274 | 10.3787 | 11.6345 | 22.8147 | 14.0679 | 10.2623 | 11.4131 | 22.9229 | 13.8314 | 10.0898 | 10.9703 | 23.075 | 13.4726 | 9.8281 | 10.4909 | 23.2644 | 13.0101 | 9.4907 | 9.8992 | 23.4891 | 12.8074 | 9.3428 | 8.8876 | 23.6783 | 12.5483 | 9.1538 | 7.9092 | 23.8665 | 12.2583 | 8.9423 | 6.9694 | 24.4493 | 11.5686 | 8.4392 | 4.5061 | 24.981 | 10.9475 | 7.986 | 2.439 | 25.196 | 10.4694 | 7.6373 | 1.1687 | 25.3332 | 10.0825 | 7.355 | 0.763 | 25.3357 | 9.9212 | 7.2374 | 1.4329 | 22.6698 | 14.4952 | 10.574 | 11.9794 | 22.7258 | 14.3938 | 10.5 | 11.7352 | 22.779 | 14.1894 | 10.351 | 11.6179 | 22.8333 | 13.99 | 10.2055 | 11.5358 | 22.9057 | 13.8297 | 10.0886 | 11.4123 | 23.0152 | 13.5915 | 9.9148 | 11.2609 | 23.1597 | 13.3545 | 9.7419 | 11.076 | 23.3202 | 13.2399 | 9.6583 | 10.8627 | 23.4502 | 13.1257 | 9.575 | 10.6198 | 23.5812 | 13.0261 | 9.5024 | 10.3717 | 23.9998 | 12.7034 | 9.2669 | 9.4922 | 24.4297 | 12.4016 | 9.0468 | 8.4441 | 24.6884 | 12.0965 | 8.8242 | 7.6224 | 24.9324 | 11.987 | 8.7444 | 6.7991 | 25.0915 | 11.7148 | 8.5458 | 6.2143 | 22.6698 | 14.4952 | 10.574 | 11.9794 | 22.6944 | 14.358 | 10.474 | 11.6508 | 22.7793 | 14.1626 | 10.3314 | 11.3918 | 22.8871 | 13.988 | 10.2041 | 11.1058 | 23.0232 | 13.7356 | 10.0199 | 10.6029 | 23.1761 | 13.3707 | 9.7538 | 10.0798 | 23.3562 | 12.9149 | 9.4212 | 9.4312 | 23.5915 | 12.6816 | 9.251 | 8.3485 | 23.7892 | 12.4122 | 9.0546 | 7.3223 | 23.9833 | 12.1139 | 8.8369 | 6.3329 | 24.5657 | 11.3902 | 8.309 | 3.6953 | 25.0995 | 10.742 | 7.8362 | 1.4897 | 25.3359 | 10.2323 | 7.4643 | 0.078775 | 25.471 | 9.8118 | 7.1576 | -0.5043 | 25.4912 | 9.6153 | 7.0143 | -0.013034
BENCHILL | WEST DIDSBURY | SOUTH MANCHESTER | 382454 | 388020 | 14.8974 | 14.8974 | 14.8974 | 9.8493 | 14.9428 | 14.9428 | 14.9428 | 9.5842 | 14.9963 | 14.9963 | 14.9963 | 9.2128 | 15.0664 | 15.0664 | 15.0664 | 8.8748 | 15.1331 | 15.1331 | 15.1331 | 8.4826 | 15.176 | 15.176 | 15.176 | 8.0865 | 15.2233 | 15.2233 | 15.2233 | 7.4648 | 15.2779 | 15.2779 | 15.2779 | 6.8815 | 15.324 | 15.324 | 15.324 | 6.2978 | 15.3673 | 15.3673 | 15.3673 | 5.725 | 15.4901 | 15.4901 | 15.4901 | 4.9567 | 15.6141 | 15.6141 | 15.6141 | 4.1039 | 15.7018 | 15.7018 | 15.7018 | 3.4585 | 15.7701 | 15.7701 | 15.7701 | 2.9724 | 15.8135 | 15.8135 | 15.8135 | 2.5602 | 14.8867 | 14.8867 | 14.8867 | 9.8493 | 14.9091 | 14.9091 | 14.9091 | 9.796 | 14.9312 | 14.9312 | 14.9312 | 9.6563 | 14.9511 | 14.9511 | 14.9511 | 9.5276 | 14.9747 | 14.9747 | 14.9747 | 9.3943 | 14.9954 | 14.9954 | 14.9954 | 9.26 | 15.0215 | 15.0215 | 15.0215 | 9.0292 | 15.055 | 15.055 | 15.055 | 8.7835 | 15.0842 | 15.0842 | 15.0842 | 8.5355 | 15.1158 | 15.1158 | 15.1158 | 8.2852 | 15.2096 | 15.2096 | 15.2096 | 7.9586 | 15.3003 | 15.3003 | 15.3003 | 7.7353 | 15.3982 | 15.3982 | 15.3982 | 7.5255 | 15.5047 | 15.5047 | 15.5047 | 7.3077 | 15.548 | 15.548 | 15.548 | 7.1523 | 14.9014 | 14.9014 | 14.9014 | 9.8493 | 14.969 | 14.969 | 14.969 | 9.5254 | 15.0496 | 15.0496 | 15.0496 | 9.1213 | 15.1134 | 15.1134 | 15.1134 | 8.7601 | 15.1689 | 15.1689 | 15.1689 | 8.344 | 15.224 | 15.224 | 15.224 | 7.9242 | 15.2856 | 15.2856 | 15.2856 | 7.2815 | 15.3568 | 15.3568 | 15.3568 | 6.6724 | 15.4144 | 15.4144 | 15.4144 | 6.0728 | 15.4638 | 15.4638 | 15.4638 | 5.4721 | 15.6118 | 15.6118 | 15.6118 | 4.6428 | 15.7567 | 15.7567 | 15.7567 | 3.8576 | 15.8538 | 15.8538 | 15.8538 | 3.3591 | 15.9141 | 15.9141 | 15.9141 | 3.0844 | 15.9198 | 15.9198 | 15.9198 | 3.0568 | 14.9014 | 14.9014 | 14.9014 | 9.8493 | 14.9476 | 14.9476 | 14.9476 | 9.6598 | 15.0173 | 15.0173 | 15.0173 | 9.2903 | 15.063 | 15.063 | 15.063 | 8.9345 | 15.1045 | 15.1045 | 15.1045 | 8.5172 | 15.1524 | 15.1524 | 15.1524 | 8.089 | 15.21 | 15.21 | 15.21 | 7.3927 | 15.2765 | 15.2765 | 15.2765 | 6.5744 | 15.3335 | 15.3335 | 15.3335 | 5.7609 | 15.388 | 15.388 | 15.388 | 4.9573 | 15.544 | 15.544 | 15.544 | 3.8763 | 15.6793 | 15.6793 | 15.6793 | 3.2336 | 15.7679 | 15.7679 | 15.7679 | 2.8807 | 15.8272 | 15.8272 | 15.8272 | 2.9076 | 15.8039 | 15.8039 | 15.8039 | 3.3437 | 14.8974 | 14.8974 | 14.8974 | 9.8493 | 14.9391 | 14.9391 | 14.9391 | 9.762 | 14.9861 | 14.9861 | 14.9861 | 9.4382 | 15.0326 | 15.0326 | 15.0326 | 9.1393 | 15.085 | 15.085 | 15.085 | 8.8414 | 15.1278 | 15.1278 | 15.1278 | 8.5388 | 15.1721 | 15.1721 | 15.1721 | 7.9855 | 15.2204 | 15.2204 | 15.2204 | 7.4269 | 15.2625 | 15.2625 | 15.2625 | 6.8387 | 15.3039 | 15.3039 | 15.3039 | 6.25 | 15.432 | 15.432 | 15.432 | 5.6999 | 15.5389 | 15.5389 | 15.5389 | 5.3997 | 15.6149 | 15.6149 | 15.6149 | 5.1997 | 15.6817 | 15.6817 | 15.6817 | 5.0208 | 15.7143 | 15.7143 | 15.7143 | 4.9538 | 14.8974 | 14.8974 | 14.8974 | 9.8493 | 14.9512 | 14.9512 | 14.9512 | 9.5402 | 15.0297 | 15.0297 | 15.0297 | 9.1266 | 15.0929 | 15.0929 | 15.0929 | 8.7444 | 15.1419 | 15.1419 | 15.1419 | 8.3032 | 15.191 | 15.191 | 15.191 | 7.8591 | 15.2468 | 15.2468 | 15.2468 | 7.1436 | 15.3184 | 15.3184 | 15.3184 | 6.2978 | 15.3796 | 15.3796 | 15.3796 | 5.4633 | 15.4374 | 15.4374 | 15.4374 | 4.6391 | 15.5942 | 15.5942 | 15.5942 | 3.4981 | 15.721 | 15.721 | 15.721 | 2.8076 | 15.8035 | 15.8035 | 15.8035 | 2.4107 | 15.8563 | 15.8563 | 15.8563 | 2.3884 | 15.846 | 15.846 | 15.846 | 2.7653
BENTHAM | KENDAL (PARKSIDE RD) | HARKER / HUTTON | 366887 | 470130 | 6.9472 | 6.9472 | 6.9472 | 6.5518 | 6.9754 | 6.9754 | 6.9754 | 6.5046 | 6.9894 | 6.9894 | 6.9894 | 6.4346 | 7.0072 | 7.0072 | 7.0072 | 6.3834 | 7.034 | 7.034 | 7.034 | 6.3247 | 7.0641 | 7.0641 | 7.0641 | 6.2628 | 7.096 | 7.096 | 7.096 | 6.2088 | 7.1328 | 7.1328 | 7.1328 | 6.1549 | 7.1632 | 7.1632 | 7.1632 | 6.0927 | 7.1912 | 7.1912 | 7.1912 | 6.0383 | 7.3207 | 7.3207 | 7.3207 | 5.7239 | 7.5118 | 7.5118 | 7.5118 | 5.2013 | 7.6688 | 7.6688 | 7.6688 | 4.5039 | 7.8318 | 7.8318 | 7.8318 | 3.7702 | 7.9277 | 7.9277 | 7.9277 | 3.0967 | 6.944 | 6.944 | 6.944 | 6.5518 | 6.9748 | 6.9748 | 6.9748 | 6.4864 | 6.9969 | 6.9969 | 6.9969 | 6.3881 | 7.0208 | 7.0208 | 7.0208 | 6.3002 | 7.0536 | 7.0536 | 7.0536 | 6.2131 | 7.0934 | 7.0934 | 7.0934 | 6.118 | 7.1413 | 7.1413 | 7.1413 | 6.0032 | 7.1966 | 7.1966 | 7.1966 | 5.8632 | 7.2214 | 7.2214 | 7.2214 | 5.7901 | 7.2463 | 7.2463 | 7.2463 | 5.7187 | 7.321 | 7.321 | 7.321 | 5.5156 | 7.3922 | 7.3922 | 7.3922 | 5.3277 | 7.4499 | 7.4499 | 7.4499 | 5.1594 | 7.5063 | 7.5063 | 7.5063 | 4.9643 | 7.5496 | 7.5496 | 7.5496 | 4.8034 | 6.9489 | 6.9489 | 6.9489 | 6.5518 | 6.9759 | 6.9759 | 6.9759 | 6.5028 | 6.9902 | 6.9902 | 6.9902 | 6.4325 | 7.0087 | 7.0087 | 7.0087 | 6.3807 | 7.036 | 7.036 | 7.036 | 6.3219 | 7.0665 | 7.0665 | 7.0665 | 6.2601 | 7.0993 | 7.0993 | 7.0993 | 6.2057 | 7.1369 | 7.1369 | 7.1369 | 6.1518 | 7.168 | 7.168 | 7.168 | 6.1056 | 7.1961 | 7.1961 | 7.1961 | 6.0687 | 7.3252 | 7.3252 | 7.3252 | 5.8095 | 7.5133 | 7.5133 | 7.5133 | 5.3494 | 7.6659 | 7.6659 | 7.6659 | 4.8589 | 7.8225 | 7.8225 | 7.8225 | 4.2142 | 7.9154 | 7.9154 | 7.9154 | 3.6482 | 6.9489 | 6.9489 | 6.9489 | 6.5518 | 6.9469 | 6.9469 | 6.9469 | 6.562 | 6.9481 | 6.9481 | 6.9481 | 6.5171 | 6.9557 | 6.9557 | 6.9557 | 6.4782 | 6.973 | 6.973 | 6.973 | 6.438 | 6.9976 | 6.9976 | 6.9976 | 6.3923 | 7.0339 | 7.0339 | 7.0339 | 6.3226 | 7.0981 | 7.0981 | 7.0981 | 6.1635 | 7.1608 | 7.1608 | 7.1608 | 5.9902 | 7.2221 | 7.2221 | 7.2221 | 5.8232 | 7.3891 | 7.3891 | 7.3891 | 5.1909 | 7.534 | 7.534 | 7.534 | 4.4227 | 7.6433 | 7.6433 | 7.6433 | 3.8284 | 7.724 | 7.724 | 7.724 | 3.5119 | 7.7316 | 7.7316 | 7.7316 | 3.8612 | 6.9472 | 6.9472 | 6.9472 | 6.5518 | 6.9726 | 6.9726 | 6.9726 | 6.5105 | 6.9813 | 6.9813 | 6.9813 | 6.4458 | 6.991 | 6.991 | 6.991 | 6.4036 | 7.0064 | 7.0064 | 7.0064 | 6.371 | 7.0298 | 7.0298 | 7.0298 | 6.3363 | 7.0622 | 7.0622 | 7.0622 | 6.2952 | 7.1001 | 7.1001 | 7.1001 | 6.2439 | 7.1313 | 7.1313 | 7.1313 | 6.1762 | 7.1622 | 7.1622 | 7.1622 | 6.1102 | 7.2648 | 7.2648 | 7.2648 | 5.894 | 7.3776 | 7.3776 | 7.3776 | 5.6552 | 7.461 | 7.461 | 7.461 | 5.4965 | 7.5438 | 7.5438 | 7.5438 | 5.355 | 7.5839 | 7.5839 | 7.5839 | 5.3345 | 6.9472 | 6.9472 | 6.9472 | 6.5518 | 6.9546 | 6.9546 | 6.9546 | 6.5396 | 6.9663 | 6.9663 | 6.9663 | 6.4705 | 6.9861 | 6.9861 | 6.9861 | 6.4051 | 7.0146 | 7.0146 | 7.0146 | 6.339 | 7.0449 | 7.0449 | 7.0449 | 6.2736 | 7.086 | 7.086 | 7.086 | 6.1848 | 7.16 | 7.16 | 7.16 | 5.9983 | 7.2284 | 7.2284 | 7.2284 | 5.8163 | 7.2946 | 7.2946 | 7.2946 | 5.6415 | 7.4851 | 7.4851 | 7.4851 | 4.9407 | 7.6673 | 7.6673 | 7.6673 | 4.1294 | 7.7836 | 7.7836 | 7.7836 | 3.4902 | 7.8641 | 7.8641 | 7.8641 | 3.1124 | 7.878 | 7.878 | 7.878 | 3.39
BISPHAM | BISPHAM | PENWORTHAM WEST / STANAH | 331655 | 439667 | 31.7007 | 10.3871 | 7.5772 | 11.6122 | 31.7918 | 10.1937 | 7.4362 | 10.7999 | 31.9177 | 10.0785 | 7.3522 | 10.6375 | 32.0762 | 9.9569 | 7.2634 | 10.5926 | 32.2718 | 9.9049 | 7.2255 | 10.4435 | 32.4992 | 9.7846 | 7.1377 | 10.2687 | 32.7643 | 9.6382 | 7.0309 | 10.0999 | 33.0298 | 9.5489 | 6.9658 | 9.9596 | 33.2041 | 9.4559 | 6.898 | 9.8257 | 33.3667 | 9.3692 | 6.8347 | 9.692 | 33.8941 | 8.9022 | 6.494 | 7.9017 | 34.4326 | 8.2724 | 6.0346 | 4.2772 | 34.7889 | 7.8696 | 5.7408 | 1.2166 | 35.1065 | 8.1359 | 5.935 | -2.1304 | 35.3015 | 7.769 | 5.6674 | -5.0864 | 31.666 | 10.3871 | 7.5772 | 11.6122 | 31.7942 | 10.3164 | 7.5257 | 11.3708 | 31.9278 | 10.2489 | 7.4764 | 11.2144 | 32.0766 | 10.1457 | 7.4012 | 11.0325 | 32.2243 | 10.0121 | 7.3037 | 10.7577 | 32.413 | 9.868 | 7.1986 | 10.4664 | 32.6445 | 9.6522 | 7.0412 | 10.0817 | 32.8422 | 9.4868 | 6.9205 | 9.6179 | 32.9555 | 9.3666 | 6.8328 | 9.4039 | 33.0731 | 9.2463 | 6.745 | 9.1843 | 33.4357 | 8.8569 | 6.461 | 8.5116 | 33.7847 | 8.6375 | 6.301 | 7.7393 | 34.1037 | 8.5531 | 6.2394 | 6.9906 | 34.3844 | 9.001 | 6.5661 | 6.2006 | 34.5884 | 9.3063 | 6.7889 | 5.6235 | 31.7115 | 10.3871 | 7.5772 | 11.6122 | 31.8137 | 10.1573 | 7.4096 | 10.7076 | 31.9578 | 10.0036 | 7.2975 | 10.5559 | 32.1431 | 9.8218 | 7.1648 | 10.5586 | 32.3723 | 9.8058 | 7.1532 | 10.462 | 32.6402 | 9.6622 | 7.0485 | 10.3483 | 32.9172 | 9.5298 | 6.9519 | 10.2689 | 33.2229 | 9.4257 | 6.8759 | 10.2203 | 33.4225 | 9.3402 | 6.8135 | 10.1811 | 33.6082 | 9.2605 | 6.7554 | 10.1682 | 34.1518 | 8.7367 | 6.3733 | 8.7091 | 34.6638 | 8.0267 | 5.8554 | 5.3498 | 35.0327 | 7.6086 | 5.5504 | 2.5136 | 35.348 | 7.8097 | 5.6971 | -0.61863 | 35.5217 | 7.4184 | 5.4116 | -3.3546 | 31.7115 | 10.3871 | 7.5772 | 11.6122 | 31.6703 | 10.2721 | 7.4933 | 11.3627 | 31.7086 | 10.1868 | 7.4312 | 11.3719 | 31.7745 | 10.109 | 7.3744 | 11.4032 | 31.8909 | 10.0389 | 7.3232 | 11.3002 | 32.0887 | 9.9372 | 7.249 | 11.1527 | 32.3486 | 9.7511 | 7.1133 | 10.8 | 32.6444 | 9.5956 | 6.9998 | 9.7204 | 32.8376 | 9.3707 | 6.8358 | 8.5908 | 33.0255 | 9.1984 | 6.7101 | 7.472 | 33.6014 | 9.5628 | 6.976 | 4.2171 | 34.1325 | 8.7486 | 6.382 | 1.0406 | 34.4774 | 8.1356 | 5.9348 | -1.5308 | 34.7233 | 7.9588 | 5.8059 | -3.1266 | 34.6943 | 7.9193 | 5.777 | -1.8255 | 31.7007 | 10.3871 | 7.5772 | 11.6122 | 31.7797 | 10.3039 | 7.5165 | 11.4102 | 31.8644 | 10.2194 | 7.4549 | 11.4003 | 31.9589 | 10.1164 | 7.3798 | 11.4417 | 32.0884 | 10.0845 | 7.3565 | 11.4321 | 32.2905 | 9.9937 | 7.2903 | 11.3984 | 32.5571 | 9.8658 | 7.1969 | 11.3376 | 32.8294 | 9.7862 | 7.1389 | 11.26 | 32.9809 | 9.6983 | 7.0748 | 11.1442 | 33.1294 | 9.6121 | 7.0119 | 11.0218 | 33.6042 | 9.344 | 6.8163 | 10.3857 | 34.1039 | 9.1869 | 6.7017 | 9.5284 | 34.3949 | 9.2151 | 6.7223 | 8.9259 | 34.6522 | 10.0058 | 7.2991 | 8.2914 | 34.7691 | 10.1411 | 7.3978 | 7.9633 | 31.7007 | 10.3871 | 7.5772 | 11.6122 | 31.7143 | 10.1926 | 7.4353 | 10.925 | 31.8299 | 10.0716 | 7.3471 | 10.7522 | 31.9877 | 9.97 | 7.273 | 10.6468 | 32.1865 | 9.874 | 7.2029 | 10.4156 | 32.4143 | 9.7548 | 7.116 | 10.1723 | 32.688 | 9.5415 | 6.9604 | 9.7014 | 32.9972 | 9.3633 | 6.8304 | 8.4715 | 33.2097 | 9.1213 | 6.6539 | 7.2505 | 33.4123 | 8.9293 | 6.5138 | 6.04 | 33.992 | 9.2259 | 6.7302 | 2.4804 | 34.4737 | 8.3554 | 6.0951 | -0.93071 | 34.7857 | 7.697 | 5.6148 | -3.7061 | 34.9913 | 7.458 | 5.4405 | -5.5472 | 34.964 | 7.3782 | 5.3823 | -4.5516
BLACKBULL | RIBBLE | PENWORTHAM EAST / ROCHDALE | 353041 | 433005 | 29.6299 | 13.1379 | 9.5839 | 13.5032 | 29.6993 | 12.8007 | 9.338 | 11.5963 | 29.8209 | 12.5731 | 9.1719 | 10.9805 | 29.9795 | 12.407 | 9.0508 | 10.5621 | 30.1787 | 12.2307 | 8.9221 | 10.1272 | 30.4225 | 11.9716 | 8.7331 | 9.6737 | 30.6902 | 11.6465 | 8.4959 | 9.1946 | 30.9934 | 11.5974 | 8.4601 | 8.6782 | 31.2947 | 11.4933 | 8.3842 | 8.102 | 31.5566 | 11.3664 | 8.2916 | 7.5382 | 32.2977 | 10.9731 | 8.0047 | 6.1988 | 33.0205 | 10.4316 | 7.6097 | 3.9825 | 33.5075 | 9.98 | 7.2802 | 2.0857 | 33.8998 | 9.6607 | 7.0473 | 0.066476 | 34.1471 | 9.5864 | 6.9931 | -1.6717 | 29.5943 | 13.1379 | 9.5839 | 13.5032 | 29.6367 | 13.0739 | 9.5372 | 12.6994 | 29.6922 | 13.0425 | 9.5143 | 12.5883 | 29.7636 | 12.9804 | 9.469 | 12.4712 | 29.8651 | 12.9054 | 9.4143 | 12.3363 | 29.9986 | 12.7829 | 9.325 | 12.1688 | 30.1641 | 12.5439 | 9.1506 | 11.947 | 30.3583 | 12.4486 | 9.0811 | 11.666 | 30.5244 | 12.3543 | 9.0123 | 11.3855 | 30.7069 | 12.2548 | 8.9397 | 11.0861 | 31.3178 | 11.9666 | 8.7295 | 10.1768 | 31.9626 | 11.7053 | 8.5389 | 9.1913 | 32.6 | 11.4574 | 8.358 | 8.1827 | 33.1076 | 11.3472 | 8.2776 | 7.1387 | 33.435 | 11.1887 | 8.162 | 6.4962 | 29.6433 | 13.1379 | 9.5839 | 13.5032 | 29.7224 | 12.7011 | 9.2653 | 11.3099 | 29.8598 | 12.4486 | 9.0811 | 10.6447 | 30.0401 | 12.2306 | 8.9221 | 10.2257 | 30.2643 | 12.053 | 8.7925 | 9.7931 | 30.5196 | 11.7006 | 8.5354 | 9.3443 | 30.7676 | 11.6087 | 8.4684 | 8.8703 | 31.0822 | 11.4947 | 8.3852 | 8.3648 | 31.3208 | 11.3467 | 8.2772 | 7.8349 | 31.5224 | 11.1987 | 8.1693 | 7.321 | 32.246 | 10.7399 | 7.8346 | 6.1204 | 33.0129 | 10.1988 | 7.4399 | 4.0861 | 33.5418 | 9.7041 | 7.079 | 2.5115 | 33.9357 | 9.5274 | 6.9501 | 0.94499 | 34.1355 | 9.3847 | 6.846 | -0.35442 | 29.6433 | 13.1379 | 9.5839 | 13.5032 | 29.6266 | 12.852 | 9.3753 | 12.0988 | 29.6905 | 12.687 | 9.255 | 11.6212 | 29.7876 | 12.5075 | 9.1241 | 11.2684 | 29.94 | 12.3179 | 8.9858 | 10.8841 | 30.188 | 12.09 | 8.8195 | 10.448 | 30.5167 | 11.7316 | 8.558 | 9.8294 | 30.8651 | 11.5886 | 8.4537 | 8.8783 | 31.1244 | 11.3937 | 8.3116 | 7.8784 | 31.3953 | 11.1596 | 8.1408 | 6.8892 | 32.2144 | 10.5982 | 7.7313 | 4.8722 | 32.9061 | 10.0111 | 7.303 | 2.9507 | 33.354 | 9.5866 | 6.9933 | 1.5198 | 33.6376 | 9.7988 | 7.1481 | 0.52778 | 33.6289 | 9.7331 | 7.1001 | 1.167 | 29.6299 | 13.1379 | 9.5839 | 13.5032 | 29.6849 | 12.9186 | 9.4239 | 12.1252 | 29.7642 | 12.7136 | 9.2744 | 11.6375 | 29.8581 | 12.5548 | 9.1586 | 11.2784 | 29.9884 | 12.3992 | 9.045 | 10.9167 | 30.2001 | 12.157 | 8.8683 | 10.5053 | 30.4892 | 11.7903 | 8.6008 | 10.0418 | 30.7494 | 11.773 | 8.5882 | 9.5533 | 31 | 11.6849 | 8.524 | 8.999 | 31.2676 | 11.5609 | 8.4335 | 8.4458 | 31.9935 | 11.2789 | 8.2278 | 7.5973 | 32.6484 | 10.9791 | 8.0091 | 6.5833 | 33.094 | 10.7789 | 7.8631 | 5.9224 | 33.4212 | 10.7007 | 7.806 | 5.3692 | 33.5447 | 10.9806 | 8.0102 | 5.1803 | 29.6299 | 13.1379 | 9.5839 | 13.5032 | 29.6457 | 12.6746 | 9.2459 | 11.1954 | 29.7585 | 12.4621 | 9.091 | 10.5002 | 29.9121 | 12.2704 | 8.9511 | 10.0692 | 30.1053 | 12.0648 | 8.8011 | 9.6186 | 30.336 | 11.8324 | 8.6316 | 9.1591 | 30.6064 | 11.4856 | 8.3786 | 8.6155 | 30.9416 | 11.3411 | 8.2732 | 7.6483 | 31.2207 | 11.1354 | 8.1231 | 6.6239 | 31.4761 | 10.8969 | 7.9492 | 5.6138 | 32.3074 | 10.2904 | 7.5067 | 3.3641 | 33.039 | 9.6481 | 7.0382 | 1.1094 | 33.5362 | 9.1314 | 6.6612 | -0.62173 | 33.8381 | 9.3365 | 6.8109 | -1.7916 | 33.8419 | 9.2335 | 6.7357 | -1.3266
BLACKBURN | BLACKBURN | PENWORTHAM EAST / ROCHDALE | 370584 | 429294 | 30.4351 | 9.9467 | 7.256 | 13.9689 | 30.477 | 9.2188 | 6.725 | 12.2852 | 30.5419 | 9.3446 | 6.8167 | 11.548 | 30.6359 | 9.1896 | 6.7037 | 11.12 | 30.7887 | 8.8812 | 6.4787 | 10.6401 | 30.9745 | 8.3821 | 6.1146 | 10.1148 | 31.2306 | 7.9635 | 5.8093 | 9.5518 | 31.573 | 7.7041 | 5.6201 | 9.2317 | 31.951 | 7.4688 | 5.4484 | 8.7866 | 32.2915 | 7.2365 | 5.2789 | 8.1658 | 33.6795 | 6.5045 | 4.7449 | 5.4053 | 34.841 | 5.7706 | 4.2095 | 2.2206 | 32.0523 | 5.1992 | 3.7927 | -0.12194 | 28.4398 | 4.6132 | 3.3653 | -2.1853 | 24.9469 | 4.0466 | 2.952 | -3.7472 | 30.4209 | 9.9467 | 7.256 | 13.9689 | 30.4641 | 9.7356 | 7.102 | 13.5263 | 30.5128 | 9.5248 | 6.9482 | 13.3183 | 30.5654 | 9.1985 | 6.7102 | 13.2187 | 30.636 | 9.2313 | 6.7341 | 13.1255 | 30.721 | 9.185 | 6.7004 | 13.0075 | 30.8394 | 8.6148 | 6.2844 | 12.8426 | 30.9996 | 8.5259 | 6.2195 | 12.6286 | 31.161 | 8.4572 | 6.1694 | 12.3761 | 31.3538 | 8.3737 | 6.1085 | 12.0991 | 32.0629 | 8.0563 | 5.8769 | 10.9213 | 32.887 | 7.7624 | 5.6625 | 9.2842 | 33.7403 | 7.4852 | 5.4603 | 7.5961 | 34.6987 | 7.0047 | 5.1098 | 5.7635 | 35.3771 | 6.5336 | 4.7662 | 4.5625 | 30.4399 | 9.9467 | 7.256 | 13.9689 | 30.4814 | 9.1155 | 6.6496 | 12.0186 | 30.5471 | 9.2749 | 6.7659 | 11.238 | 30.6389 | 8.9977 | 6.5637 | 10.8163 | 30.7817 | 8.6535 | 6.3126 | 10.3501 | 30.9492 | 8.1014 | 5.9099 | 9.8484 | 31.1737 | 7.657 | 5.5857 | 9.3217 | 31.4685 | 7.4171 | 5.4107 | 9.0545 | 31.7932 | 7.1885 | 5.2439 | 8.7136 | 32.1209 | 6.9586 | 5.0762 | 8.3407 | 33.4084 | 6.1547 | 4.4898 | 5.7926 | 32.5122 | 5.2738 | 3.8472 | 2.5014 | 28.3072 | 4.5917 | 3.3496 | 0.03735 | 24.3511 | 3.95 | 2.8815 | -1.9736 | 20.9046 | 3.3909 | 2.4736 | -3.2771 | 30.4399 | 9.9467 | 7.256 | 13.9689 | 30.4166 | 9.3353 | 6.81 | 12.7057 | 30.4588 | 9.573 | 6.9834 | 12.0713 | 30.5413 | 9.1584 | 6.6809 | 11.6783 | 30.6498 | 8.8143 | 6.4299 | 11.2289 | 30.823 | 8.3554 | 6.0952 | 10.72 | 31.0905 | 8.0186 | 5.8495 | 10.0481 | 31.4975 | 7.6675 | 5.5933 | 9.256 | 31.9633 | 7.3157 | 5.3367 | 8.3607 | 32.4518 | 6.885 | 5.0225 | 7.3221 | 33.7982 | 5.8996 | 4.3037 | 3.9161 | 31.1134 | 5.0469 | 3.6816 | 0.96998 | 27.0175 | 4.3825 | 3.197 | -1.1003 | 23.3912 | 3.7943 | 2.7679 | -2.3021 | 21.9901 | 3.567 | 2.6021 | -1.8085 | 30.4351 | 9.9467 | 7.256 | 13.9689 | 30.4693 | 9.3385 | 6.8123 | 13.1502 | 30.5194 | 9.5494 | 6.9661 | 12.5854 | 30.5784 | 9.4092 | 6.8639 | 12.2081 | 30.6717 | 9.1312 | 6.6611 | 11.8341 | 30.8135 | 8.6614 | 6.3184 | 11.4126 | 31.013 | 8.2531 | 6.0205 | 10.921 | 31.2604 | 8.0041 | 5.8389 | 10.6555 | 31.5566 | 7.7712 | 5.669 | 10.2583 | 31.8907 | 7.5623 | 5.5166 | 9.8018 | 33.0868 | 6.9586 | 5.0762 | 7.6668 | 34.2428 | 6.4597 | 4.7123 | 5.5686 | 34.9546 | 6.0814 | 4.4363 | 4.1405 | 34.7993 | 5.6448 | 4.1178 | 3.1365 | 33.7805 | 5.4795 | 3.9972 | 2.8228 | 30.4351 | 9.9467 | 7.256 | 13.9689 | 30.4247 | 9.136 | 6.6646 | 11.8789 | 30.482 | 9.3539 | 6.8236 | 11.0648 | 30.578 | 8.9319 | 6.5157 | 10.6283 | 30.7162 | 8.5727 | 6.2536 | 10.1467 | 30.8749 | 8.117 | 5.9212 | 9.6365 | 31.108 | 7.7818 | 5.6767 | 8.9802 | 31.4753 | 7.4331 | 5.4223 | 8.1977 | 31.8763 | 7.0881 | 5.1707 | 7.3404 | 32.3299 | 6.6844 | 4.8762 | 6.4522 | 33.6735 | 5.7 | 4.1581 | 3.1438 | 29.5693 | 4.7964 | 3.4989 | -0.093753 | 25.0118 | 4.0572 | 2.9596 | -2.4979 | 21.1042 | 3.4233 | 2.4973 | -3.958 | 19.3782 | 3.1433 | 2.293 | -3.6236
BLACKFRIARS | FREDERICK RD | WHITEGATE | 383030 | 399104 | 31.4768 | 12.1101 | 8.8341 | 15.3042 | 31.5836 | 11.8582 | 8.6504 | 13.6948 | 31.7079 | 11.6626 | 8.5077 | 12.5608 | 31.8164 | 11.4418 | 8.3466 | 11.5141 | 31.9082 | 11.1954 | 8.1669 | 10.3553 | 31.9937 | 10.9303 | 7.9735 | 9.2545 | 32.0835 | 10.6807 | 7.7914 | 8.1638 | 32.179 | 10.4404 | 7.6162 | 7.2412 | 32.2807 | 10.2347 | 7.4661 | 6.3475 | 32.3779 | 10.0339 | 7.3196 | 5.4717 | 32.6837 | 9.4545 | 6.8969 | 3.0417 | 32.9572 | 9.1026 | 6.6402 | 1.3554 | 33.158 | 8.8754 | 6.4745 | 0.065482 | 33.3528 | 9.4254 | 6.8757 | -1.2666 | 33.5111 | 9.0359 | 6.5916 | -2.5169 | 31.4752 | 12.1101 | 8.8341 | 15.3042 | 31.5817 | 12.0374 | 8.7811 | 14.7304 | 31.7064 | 11.9482 | 8.716 | 14.3495 | 31.8189 | 11.8495 | 8.6441 | 14.0505 | 31.9289 | 11.7518 | 8.5728 | 13.732 | 32.0444 | 11.6505 | 8.4988 | 13.4108 | 32.1754 | 11.3765 | 8.299 | 13.0396 | 32.2962 | 11.2504 | 8.207 | 12.585 | 32.4073 | 11.1413 | 8.1274 | 12.2058 | 32.5158 | 11.0338 | 8.049 | 11.8219 | 32.8278 | 10.7256 | 7.8241 | 10.7081 | 33.1251 | 10.4767 | 7.6426 | 9.5894 | 33.3811 | 10.2597 | 7.4843 | 8.6023 | 33.6612 | 10.5793 | 7.7175 | 7.4925 | 33.9282 | 10.8663 | 7.9268 | 6.4511 | 31.4774 | 12.1101 | 8.8341 | 15.3042 | 31.598 | 11.8164 | 8.6199 | 13.441 | 31.7364 | 11.579 | 8.4467 | 12.2187 | 31.8521 | 11.3329 | 8.2672 | 11.1317 | 31.9461 | 11.0344 | 8.0494 | 9.9212 | 32.0437 | 10.7382 | 7.8334 | 8.763 | 32.1477 | 10.4494 | 7.6227 | 7.6315 | 32.2579 | 10.2074 | 7.4461 | 6.6547 | 32.36 | 9.9524 | 7.2602 | 5.7419 | 32.4565 | 9.7162 | 7.0878 | 4.8154 | 32.7618 | 9.0759 | 6.6207 | 2.2302 | 33.0613 | 8.6367 | 6.3004 | 0.48987 | 33.2635 | 8.3724 | 6.1076 | -0.73707 | 33.4348 | 8.8767 | 6.4755 | -1.9313 | 33.532 | 8.4758 | 6.183 | -2.9362 | 31.4774 | 12.1101 | 8.8341 | 15.3042 | 31.5445 | 11.9266 | 8.7003 | 14.0207 | 31.6604 | 11.777 | 8.5912 | 12.9378 | 31.7448 | 11.5591 | 8.4322 | 11.8862 | 31.8124 | 11.2933 | 8.2383 | 10.7026 | 31.8895 | 11.0453 | 8.0574 | 9.5655 | 31.9758 | 10.7596 | 7.849 | 8.4001 | 32.0686 | 10.4208 | 7.6019 | 7.2254 | 32.1686 | 10.2578 | 7.4829 | 6.107 | 32.2649 | 10.0456 | 7.3282 | 4.986 | 32.5464 | 10.2428 | 7.472 | 2.1871 | 32.8053 | 9.7341 | 7.1009 | 0.61983 | 32.9792 | 9.3107 | 6.792 | -0.43092 | 33.1252 | 8.918 | 6.5055 | -1.2646 | 33.2072 | 8.7108 | 6.3544 | -1.7664 | 31.4768 | 12.1101 | 8.8341 | 15.3042 | 31.5796 | 11.9954 | 8.7505 | 14.4384 | 31.6988 | 11.8408 | 8.6377 | 13.4659 | 31.7978 | 11.6243 | 8.4798 | 12.4434 | 31.8809 | 11.4009 | 8.3168 | 11.333 | 31.9606 | 11.139 | 8.1257 | 10.2806 | 32.05 | 10.904 | 7.9543 | 9.2262 | 32.1435 | 10.6771 | 7.7888 | 8.3176 | 32.2441 | 10.4643 | 7.6335 | 7.4096 | 32.3423 | 10.2607 | 7.485 | 6.5084 | 32.6291 | 9.7253 | 7.0945 | 4.2696 | 32.903 | 9.4808 | 6.9161 | 3.1231 | 33.1022 | 9.3541 | 6.8237 | 2.2781 | 33.2976 | 9.9929 | 7.2897 | 1.355 | 33.4593 | 9.6715 | 7.0552 | 0.47493 | 31.4768 | 12.1101 | 8.8341 | 15.3042 | 31.5556 | 11.8005 | 8.6083 | 13.3409 | 31.6867 | 11.5957 | 8.4589 | 12.0841 | 31.806 | 11.3654 | 8.2909 | 10.9849 | 31.8971 | 11.0883 | 8.0887 | 9.7549 | 31.9899 | 10.8291 | 7.8997 | 8.5805 | 32.0922 | 10.5368 | 7.6864 | 7.3656 | 32.2192 | 10.1525 | 7.4061 | 6.1353 | 32.3347 | 10.0108 | 7.3027 | 4.988 | 32.4343 | 9.7884 | 7.1405 | 3.8361 | 32.7177 | 9.966 | 7.27 | 0.93744 | 32.9707 | 9.4431 | 6.8886 | -0.68945 | 33.1416 | 9.0128 | 6.5747 | -1.7961 | 33.2862 | 8.6179 | 6.2866 | -2.7011 | 33.3815 | 8.3467 | 6.0888 | -3.3072
BLACKLEY | RED BANK | WHITEGATE | 383882 | 403258 | 29.7391 | 14.0105 | 10.2204 | 15.8719 | 29.8084 | 13.7919 | 10.061 | 15.1583 | 29.9058 | 13.2163 | 9.6411 | 12.3763 | 30.0264 | 12.4009 | 9.0463 | 7.7143 | 30.1731 | 12.281 | 8.9588 | 7.5059 | 30.3429 | 12.0626 | 8.7995 | 7.2723 | 30.5394 | 11.8604 | 8.652 | 7.0339 | 30.7787 | 11.7358 | 8.5611 | 6.8049 | 30.9134 | 11.5882 | 8.4534 | 6.5968 | 31.0063 | 11.4728 | 8.3693 | 6.4102 | 31.4326 | 11.0537 | 8.0635 | 5.3383 | 31.8754 | 10.6139 | 7.7427 | 3.6718 | 32.1255 | 10.2312 | 7.4635 | 2.4096 | 32.3359 | 9.7637 | 7.1225 | 1.2527 | 32.4497 | 9.3665 | 6.8327 | 0.43361 | 29.7012 | 14.0105 | 10.2204 | 15.8719 | 29.759 | 13.9353 | 10.1656 | 15.6451 | 29.8173 | 13.4596 | 9.8186 | 12.8955 | 29.885 | 12.679 | 9.2491 | 8.2882 | 29.978 | 12.6111 | 9.1996 | 8.1734 | 30.0978 | 12.5247 | 9.1366 | 8.0533 | 30.2445 | 12.3072 | 8.978 | 7.8922 | 30.3908 | 12.2248 | 8.9178 | 7.6964 | 30.4717 | 12.1319 | 8.8501 | 7.5407 | 30.5559 | 12.0527 | 8.7923 | 7.3808 | 30.8117 | 11.7843 | 8.5965 | 6.9056 | 31.0552 | 11.652 | 8.5 | 6.4472 | 31.2326 | 11.4158 | 8.3277 | 6.0124 | 31.4094 | 11.1505 | 8.1341 | 5.5499 | 31.5431 | 10.8826 | 7.9387 | 5.2036 | 29.7508 | 14.0105 | 10.2204 | 15.8719 | 29.838 | 13.7578 | 10.0361 | 15.0055 | 29.9621 | 13.1788 | 9.6138 | 12.1658 | 30.1177 | 12.2666 | 8.9483 | 7.4409 | 30.3059 | 12.0853 | 8.8161 | 7.1683 | 30.5237 | 11.8194 | 8.6221 | 6.8671 | 30.7768 | 11.619 | 8.4759 | 6.5532 | 31.0347 | 11.4091 | 8.3228 | 6.2435 | 31.1707 | 11.2621 | 8.2155 | 5.9637 | 31.3003 | 11.1453 | 8.1303 | 5.7001 | 31.8215 | 10.6882 | 7.7969 | 4.432 | 32.2294 | 10.1501 | 7.4044 | 2.7241 | 32.4994 | 9.7667 | 7.1247 | 1.5542 | 32.7078 | 9.2825 | 6.7715 | 0.6534 | 32.7704 | 8.8226 | 6.436 | 0.32344 | 29.7508 | 14.0105 | 10.2204 | 15.8719 | 29.7388 | 13.8639 | 10.1135 | 15.4873 | 29.7951 | 13.2669 | 9.678 | 12.6488 | 29.8738 | 12.3253 | 8.9911 | 7.9594 | 29.9919 | 12.131 | 8.8494 | 7.7061 | 30.1745 | 11.8935 | 8.6762 | 7.3993 | 30.4027 | 11.6307 | 8.4844 | 6.9958 | 30.6615 | 11.3827 | 8.3036 | 6.3484 | 30.8551 | 11.1714 | 8.1494 | 5.729 | 31.0273 | 10.9163 | 7.9633 | 5.1388 | 31.531 | 10.1665 | 7.4163 | 3.5012 | 31.9821 | 9.6917 | 7.0699 | 2.0936 | 32.2409 | 9.3683 | 6.8341 | 1.2135 | 32.397 | 8.9243 | 6.5102 | 0.8957 | 32.3565 | 8.997 | 6.5632 | 1.3985 | 29.7391 | 14.0105 | 10.2204 | 15.8719 | 29.799 | 13.8817 | 10.1265 | 15.4868 | 29.8639 | 13.3171 | 9.7147 | 12.7151 | 29.9341 | 12.486 | 9.1084 | 8.1201 | 30.0285 | 12.4178 | 9.0586 | 8.0247 | 30.1778 | 12.2473 | 8.9343 | 7.8935 | 30.3751 | 12.0547 | 8.7937 | 7.7301 | 30.5918 | 11.9346 | 8.7061 | 7.5452 | 30.7438 | 11.7888 | 8.5997 | 7.3438 | 30.8403 | 11.6708 | 8.5137 | 7.141 | 31.1617 | 11.3273 | 8.2631 | 6.4498 | 31.5056 | 11.0872 | 8.0879 | 5.7083 | 31.7513 | 10.8591 | 7.9216 | 5.1969 | 31.9889 | 10.4957 | 7.6564 | 4.706 | 32.1122 | 10.162 | 7.4131 | 4.4691 | 29.7391 | 14.0105 | 10.2204 | 15.8719 | 29.7585 | 13.7755 | 10.049 | 15.148 | 29.8598 | 13.1783 | 9.6134 | 12.3019 | 29.9929 | 12.2106 | 8.9075 | 7.5472 | 30.1562 | 12.0031 | 8.7561 | 7.2383 | 30.3416 | 11.7438 | 8.5669 | 6.9103 | 30.5585 | 11.4891 | 8.3811 | 6.493 | 30.8382 | 11.2143 | 8.1807 | 5.7991 | 31.0362 | 11.006 | 8.0287 | 5.1422 | 31.2187 | 10.7529 | 7.8441 | 4.5184 | 31.6881 | 10.0179 | 7.3079 | 2.8052 | 32.1082 | 9.4534 | 6.8961 | 1.3705 | 32.3505 | 9.1812 | 6.6976 | 0.44124 | 32.5091 | 8.7763 | 6.4022 | 0.06181 | 32.4839 | 8.7521 | 6.3845 | 0.45077
BLACKPOOL | BLACKPOOL | PENWORTHAM WEST / STANAH | 330835 | 435308 | 34.8327 | 9.3274 | 6.8042 | 19.4302 | 34.8595 | 9.0275 | 6.5854 | 18.57 | 34.9153 | 8.8361 | 6.4458 | 18.1563 | 34.9642 | 8.675 | 6.3283 | 17.7364 | 35.0106 | 8.4626 | 6.1734 | 17.2931 | 35.0622 | 8.2105 | 5.9894 | 16.8439 | 35.1202 | 8.0016 | 5.8371 | 16.4262 | 35.1862 | 7.8191 | 5.7039 | 16.3353 | 35.2168 | 7.7068 | 5.622 | 16.2331 | 35.2446 | 7.595 | 5.5404 | 16.143 | 35.3353 | 7.0871 | 5.1699 | 15.2272 | 35.435 | 6.5563 | 4.7827 | 13.4589 | 35.4953 | 6.2017 | 4.524 | 12.0386 | 35.3347 | 5.7316 | 4.1811 | 10.575 | 32.2016 | 5.2234 | 3.8104 | 9.2993 | 34.8294 | 9.3274 | 6.8042 | 19.4302 | 34.9113 | 9.1846 | 6.7001 | 18.9848 | 35.0317 | 9.0582 | 6.6078 | 18.7837 | 35.1614 | 8.8839 | 6.4807 | 18.5178 | 35.3101 | 8.7099 | 6.3538 | 18.2328 | 35.4165 | 8.5337 | 6.2252 | 17.9393 | 35.5401 | 8.1274 | 5.9289 | 17.5819 | 35.6451 | 7.8518 | 5.7278 | 16.6876 | 35.678 | 7.731 | 5.6397 | 16.6033 | 35.7114 | 7.6203 | 5.5589 | 16.5183 | 35.8091 | 7.2883 | 5.3167 | 16.2726 | 35.8976 | 7.0455 | 5.1396 | 16.0515 | 35.9686 | 6.856 | 5.0013 | 15.7907 | 36.032 | 6.7396 | 4.9164 | 15.5068 | 36.0636 | 6.5496 | 4.7778 | 15.2966 | 34.8337 | 9.3274 | 6.8042 | 19.4302 | 34.8632 | 8.982 | 6.5522 | 18.5283 | 34.9211 | 8.7432 | 6.3781 | 18.1134 | 34.974 | 8.5431 | 6.2321 | 17.7157 | 35.0242 | 8.2822 | 6.0418 | 17.2844 | 35.08 | 8.0252 | 5.8543 | 16.8463 | 35.1436 | 7.7887 | 5.6818 | 16.4473 | 35.216 | 7.5913 | 5.5377 | 16.3734 | 35.243 | 7.438 | 5.4259 | 16.3483 | 35.2641 | 7.2782 | 5.3093 | 16.3073 | 35.3339 | 6.7456 | 4.9208 | 15.5539 | 35.4097 | 6.2103 | 4.5303 | 13.9704 | 35.2752 | 5.722 | 4.1741 | 12.7517 | 32.019 | 5.1938 | 3.7888 | 11.5743 | 28.6257 | 4.6434 | 3.3873 | 10.6728 | 34.8337 | 9.3274 | 6.8042 | 19.4302 | 34.8152 | 9.0732 | 6.6187 | 18.7646 | 34.832 | 8.9232 | 6.5094 | 18.4395 | 34.8402 | 8.7444 | 6.3789 | 18.0969 | 34.8453 | 8.5535 | 6.2397 | 17.721 | 34.8603 | 8.3812 | 6.114 | 17.3343 | 34.8837 | 8.143 | 5.9402 | 16.8636 | 34.9152 | 7.9001 | 5.763 | 16.3345 | 34.9449 | 7.6763 | 5.5998 | 15.771 | 34.9702 | 7.3928 | 5.3929 | 15.1918 | 35.0429 | 7.0004 | 5.1067 | 13.5686 | 35.1127 | 6.4047 | 4.6722 | 12.0654 | 35.1404 | 5.8603 | 4.275 | 10.9459 | 33.0833 | 5.3664 | 3.9147 | 10.4272 | 31.9091 | 5.176 | 3.7758 | 11.307 | 34.8327 | 9.3274 | 6.8042 | 19.4302 | 34.8572 | 9.0908 | 6.6316 | 18.648 | 34.9064 | 8.9117 | 6.501 | 18.2588 | 34.9453 | 8.7559 | 6.3873 | 17.8692 | 34.9813 | 8.5612 | 6.2452 | 17.497 | 35.0275 | 8.3273 | 6.0747 | 17.1435 | 35.084 | 8.1327 | 5.9327 | 16.7906 | 35.1452 | 7.9563 | 5.804 | 16.7142 | 35.1716 | 7.8372 | 5.7171 | 16.6007 | 35.1971 | 7.7192 | 5.631 | 16.4839 | 35.2744 | 7.3232 | 5.3422 | 16.0861 | 35.3512 | 7.095 | 5.1757 | 15.6526 | 35.3964 | 7.0076 | 5.1119 | 15.3933 | 35.4168 | 6.8185 | 4.974 | 15.1704 | 35.3829 | 6.6281 | 4.8351 | 15.2867 | 34.8327 | 9.3274 | 6.8042 | 19.4302 | 34.846 | 8.9803 | 6.551 | 18.5397 | 34.8999 | 8.8037 | 6.4222 | 18.1155 | 34.9495 | 8.605 | 6.2772 | 17.6951 | 34.9965 | 8.3953 | 6.1243 | 17.241 | 35.0479 | 8.2063 | 5.9864 | 16.7844 | 35.108 | 7.9522 | 5.801 | 16.2372 | 35.1854 | 7.6895 | 5.6094 | 15.6166 | 35.2199 | 7.46 | 5.442 | 15.0317 | 35.2492 | 7.1737 | 5.2331 | 14.4311 | 35.3269 | 6.7414 | 4.9177 | 12.7459 | 35.3903 | 6.12 | 4.4645 | 11.1953 | 34.2318 | 5.5527 | 4.0506 | 10.0209 | 31.0578 | 5.0379 | 3.6751 | 9.4228 | 29.7049 | 4.8184 | 3.515 | 10.1957
BOLLINGTON | MACCLESFIELD | MACCLESFIELD | 393042 | 377873 | 16.0644 | 13.9816 | 10.0489 | 6.6617 | 16.1101 | 13.8071 | 9.9235 | 6.0303 | 16.1755 | 13.7258 | 9.865 | 5.7965 | 16.2584 | 13.7716 | 9.8979 | 5.6762 | 16.3611 | 13.8013 | 9.9193 | 5.5058 | 16.48 | 13.8376 | 9.9454 | 5.3309 | 16.619 | 13.8949 | 9.9865 | 5.1723 | 16.777 | 13.9022 | 9.9918 | 5.0196 | 16.8887 | 13.8497 | 9.9541 | 4.8216 | 16.9969 | 13.8216 | 9.9339 | 4.6436 | 17.3459 | 13.4631 | 9.6762 | 3.468 | 17.7102 | 12.9751 | 9.3254 | 1.4263 | 17.9728 | 12.5739 | 9.0371 | -0.26162 | 18.2011 | 12.1823 | 8.7557 | -2.0479 | 18.3572 | 11.8616 | 8.5251 | -3.5682 | 16.0469 | 13.9816 | 10.0489 | 6.6617 | 16.0873 | 13.9155 | 10.0014 | 6.4009 | 16.1329 | 13.8796 | 9.9755 | 6.2533 | 16.1924 | 13.8339 | 9.9427 | 6.1231 | 16.2734 | 13.7616 | 9.8907 | 5.9516 | 16.3748 | 13.6529 | 9.8126 | 5.7641 | 16.4969 | 13.6907 | 9.8397 | 5.5274 | 16.6379 | 13.588 | 9.7659 | 5.228 | 16.7117 | 13.484 | 9.6912 | 4.9769 | 16.7887 | 13.38 | 9.6165 | 4.7246 | 17.0326 | 13.0306 | 9.3654 | 3.974 | 17.2796 | 12.9997 | 9.3432 | 3.2312 | 17.4982 | 12.994 | 9.3391 | 2.5262 | 17.7029 | 13.1018 | 9.4165 | 1.7373 | 17.8507 | 12.9865 | 9.3337 | 1.16 | 16.0718 | 13.9816 | 10.0489 | 6.6617 | 16.1228 | 13.7527 | 9.8843 | 5.9605 | 16.1965 | 13.7963 | 9.9156 | 5.7298 | 16.2916 | 13.8694 | 9.9682 | 5.6439 | 16.4095 | 13.8741 | 9.9716 | 5.5109 | 16.5461 | 13.9063 | 9.9948 | 5.3799 | 16.7006 | 13.9267 | 10.0094 | 5.2817 | 16.8555 | 13.8677 | 9.967 | 5.1961 | 16.9743 | 13.7687 | 9.8958 | 5.0717 | 17.0888 | 13.6938 | 9.842 | 4.956 | 17.4641 | 13.3056 | 9.563 | 3.9685 | 17.861 | 12.8053 | 9.2034 | 2.0896 | 18.1474 | 12.3071 | 8.8453 | 0.5428 | 18.3874 | 11.8535 | 8.5194 | -1.0776 | 18.5394 | 11.5454 | 8.2979 | -2.4502 | 16.0718 | 13.9816 | 10.0489 | 6.6617 | 16.0551 | 13.8166 | 9.9303 | 6.3335 | 16.082 | 13.9617 | 10.0345 | 6.2027 | 16.1258 | 14.0962 | 10.1312 | 6.1342 | 16.1974 | 14.0559 | 10.1022 | 6.0039 | 16.3117 | 14.092 | 10.1282 | 5.8527 | 16.4592 | 13.926 | 10.0089 | 5.6115 | 16.6266 | 13.7815 | 9.905 | 5.0202 | 16.7481 | 13.6069 | 9.7795 | 4.3845 | 16.8691 | 13.406 | 9.6352 | 3.7526 | 17.2398 | 12.8449 | 9.2319 | 1.9259 | 17.6127 | 12.3496 | 8.8759 | 0.14499 | 17.8749 | 11.9204 | 8.5674 | -1.2559 | 18.0731 | 11.7699 | 8.4592 | -2.1708 | 18.1167 | 11.6798 | 8.3945 | -1.6139 | 16.0644 | 13.9816 | 10.0489 | 6.6617 | 16.1019 | 13.8562 | 9.9587 | 6.269 | 16.1446 | 13.7774 | 9.9021 | 6.1144 | 16.1938 | 13.8246 | 9.936 | 6.0445 | 16.2615 | 13.8722 | 9.9702 | 5.9563 | 16.3673 | 13.9175 | 10.0028 | 5.847 | 16.5068 | 13.9921 | 10.0564 | 5.7222 | 16.6614 | 14.0069 | 10.067 | 5.5903 | 16.7695 | 13.966 | 10.0376 | 5.3937 | 16.8679 | 13.9367 | 10.0166 | 5.2025 | 17.1868 | 13.6782 | 9.8308 | 4.5365 | 17.5198 | 13.4431 | 9.6618 | 3.75 | 17.7611 | 13.2415 | 9.5169 | 3.1498 | 17.9711 | 13.0776 | 9.3992 | 2.5384 | 18.0879 | 12.9565 | 9.3121 | 2.1972 | 16.0644 | 13.9816 | 10.0489 | 6.6617 | 16.0722 | 13.7564 | 9.887 | 6.0141 | 16.1322 | 13.8819 | 9.9772 | 5.7585 | 16.2142 | 14.0009 | 10.0627 | 5.611 | 16.3171 | 13.9421 | 10.0204 | 5.4105 | 16.4341 | 13.9678 | 10.0389 | 5.2138 | 16.575 | 13.7846 | 9.9072 | 4.9172 | 16.7517 | 13.6245 | 9.7922 | 4.2458 | 16.8796 | 13.4367 | 9.6572 | 3.5516 | 17.0051 | 13.2352 | 9.5124 | 2.862 | 17.3782 | 12.6321 | 9.079 | 0.86028 | 17.7323 | 12.1007 | 8.697 | -1.0724 | 17.9838 | 11.6533 | 8.3755 | -2.6165 | 18.1637 | 11.4699 | 8.2436 | -3.6906 | 18.2097 | 11.3497 | 8.1573 | -3.3254
BOLTON BY BOWLAND | PADIHAM | PADIHAM | 378320 | 449559 | 8.4684 | 8.4684 | 8.4684 | 4.6979 | 8.5049 | 8.5049 | 8.5049 | 4.631 | 8.5515 | 8.5515 | 8.5515 | 4.5663 | 8.6066 | 8.6066 | 8.6066 | 4.5154 | 8.6695 | 8.6695 | 8.6695 | 4.4537 | 8.7411 | 8.7411 | 8.7411 | 4.392 | 8.7953 | 8.7953 | 8.7953 | 4.3402 | 8.8553 | 8.8553 | 8.8553 | 4.2916 | 8.9072 | 8.9072 | 8.9072 | 4.2293 | 8.9526 | 8.9526 | 8.9526 | 4.1467 | 9.0972 | 9.0972 | 9.0972 | 3.7867 | 9.2756 | 9.2756 | 9.2756 | 3.2783 | 9.3761 | 9.3761 | 9.3761 | 2.8566 | 9.4595 | 9.4595 | 9.4595 | 2.4351 | 9.4914 | 9.4914 | 9.4914 | 2.0788 | 8.4542 | 8.4542 | 8.4542 | 4.6979 | 8.4812 | 8.4812 | 8.4812 | 4.6304 | 8.5182 | 8.5182 | 8.5182 | 4.5482 | 8.5635 | 8.5635 | 8.5635 | 4.4674 | 8.6211 | 8.6211 | 8.6211 | 4.3776 | 8.674 | 8.674 | 8.674 | 4.2819 | 8.7196 | 8.7196 | 8.7196 | 4.1693 | 8.7633 | 8.7633 | 8.7633 | 4.0404 | 8.7958 | 8.7958 | 8.7958 | 3.9582 | 8.8289 | 8.8289 | 8.8289 | 3.8759 | 8.9263 | 8.9263 | 8.9263 | 3.6344 | 9.0136 | 9.0136 | 9.0136 | 3.3795 | 9.0911 | 9.0911 | 9.0911 | 3.1493 | 9.1746 | 9.1746 | 9.1746 | 2.9229 | 9.2432 | 9.2432 | 9.2432 | 2.7664 | 8.4751 | 8.4751 | 8.4751 | 4.6979 | 8.5116 | 8.5116 | 8.5116 | 4.6338 | 8.5632 | 8.5632 | 8.5632 | 4.5751 | 8.6262 | 8.6262 | 8.6262 | 4.5369 | 8.6993 | 8.6993 | 8.6993 | 4.4876 | 8.769 | 8.769 | 8.769 | 4.4405 | 8.8287 | 8.8287 | 8.8287 | 4.4081 | 8.8998 | 8.8998 | 8.8998 | 4.3821 | 8.9468 | 8.9468 | 8.9468 | 4.3322 | 8.9873 | 8.9873 | 8.9873 | 4.2671 | 9.134 | 9.134 | 9.134 | 3.8135 | 9.2679 | 9.2679 | 9.2679 | 3.2726 | 9.3507 | 9.3507 | 9.3507 | 2.889 | 9.4135 | 9.4135 | 9.4135 | 2.6027 | 9.4406 | 9.4406 | 9.4406 | 2.4448 | 8.4751 | 8.4751 | 8.4751 | 4.6979 | 8.4896 | 8.4896 | 8.4896 | 4.6865 | 8.5182 | 8.5182 | 8.5182 | 4.6495 | 8.5523 | 8.5523 | 8.5523 | 4.6161 | 8.5963 | 8.5963 | 8.5963 | 4.5765 | 8.6636 | 8.6636 | 8.6636 | 4.5339 | 8.7464 | 8.7464 | 8.7464 | 4.4742 | 8.836 | 8.836 | 8.836 | 4.3316 | 8.8925 | 8.8925 | 8.8925 | 4.1722 | 8.9465 | 8.9465 | 8.9465 | 4.0097 | 9.1082 | 9.1082 | 9.1082 | 3.5497 | 9.2359 | 9.2359 | 9.2359 | 3.1171 | 9.3126 | 9.3126 | 9.3126 | 2.7863 | 9.344 | 9.344 | 9.344 | 2.6214 | 9.3181 | 9.3181 | 9.3181 | 2.8374 | 8.4684 | 8.4684 | 8.4684 | 4.6979 | 8.4994 | 8.4994 | 8.4994 | 4.645 | 8.5366 | 8.5366 | 8.5366 | 4.5898 | 8.5743 | 8.5743 | 8.5743 | 4.5504 | 8.6183 | 8.6183 | 8.6183 | 4.5141 | 8.6825 | 8.6825 | 8.6825 | 4.4768 | 8.75 | 8.75 | 8.75 | 4.4374 | 8.8026 | 8.8026 | 8.8026 | 4.3967 | 8.849 | 8.849 | 8.849 | 4.337 | 8.8946 | 8.8946 | 8.8946 | 4.2791 | 9.0214 | 9.0214 | 9.0214 | 4.0125 | 9.1513 | 9.1513 | 9.1513 | 3.7027 | 9.2413 | 9.2413 | 9.2413 | 3.4925 | 9.3183 | 9.3183 | 9.3183 | 3.2413 | 9.3454 | 9.3454 | 9.3454 | 3.1253 | 8.4684 | 8.4684 | 8.4684 | 4.6979 | 8.4988 | 8.4988 | 8.4988 | 4.6543 | 8.5454 | 8.5454 | 8.5454 | 4.5885 | 8.6013 | 8.6013 | 8.6013 | 4.5245 | 8.6647 | 8.6647 | 8.6647 | 4.4555 | 8.7363 | 8.7363 | 8.7363 | 4.3899 | 8.8029 | 8.8029 | 8.8029 | 4.304 | 8.8849 | 8.8849 | 8.8849 | 4.1257 | 8.9567 | 8.9567 | 8.9567 | 3.9452 | 9.0249 | 9.0249 | 9.0249 | 3.7622 | 9.1937 | 9.1937 | 9.1937 | 3.232 | 9.3143 | 9.3143 | 9.3143 | 2.7385 | 9.3831 | 9.3831 | 9.3831 | 2.3651 | 9.4034 | 9.4034 | 9.4034 | 2.1563 | 9.3761 | 9.3761 | 9.3761 | 2.3257
BOLTON LE SANDS | LANCASTER | HEYSHAM | 347707 | 467237 | 23.1645 | 13.6368 | 9.8011 | 10.303 | 23.423 | 13.2169 | 9.4992 | 8.6083 | 23.5963 | 12.9441 | 9.3032 | 8.2402 | 23.7983 | 12.7458 | 9.1606 | 8.1403 | 24.0757 | 12.5466 | 9.0175 | 7.9087 | 24.4418 | 12.1889 | 8.7604 | 7.6247 | 24.9227 | 11.8144 | 8.4913 | 7.319 | 25.4397 | 11.5282 | 8.2856 | 6.9662 | 25.9118 | 11.3195 | 8.1356 | 6.5432 | 26.4325 | 11.185 | 8.0388 | 6.1095 | 27.6979 | 10.5729 | 7.599 | 3.7511 | 28.6784 | 9.8195 | 7.0575 | 0.44559 | 29.3548 | 9.1962 | 6.6095 | -2.1215 | 29.9148 | 8.68 | 6.2385 | -4.5329 | 30.3146 | 8.033 | 5.7735 | -6.5822 | 23.1386 | 13.6368 | 9.8011 | 10.303 | 23.3125 | 13.4383 | 9.6583 | 9.5744 | 23.4557 | 13.1483 | 9.45 | 9.327 | 23.6382 | 13.0131 | 9.3528 | 9.1678 | 23.8197 | 12.7571 | 9.1688 | 8.9611 | 24.0472 | 12.5112 | 8.9921 | 8.7495 | 24.3296 | 12.1964 | 8.7658 | 8.4667 | 24.6719 | 12.0532 | 8.6629 | 8.0961 | 24.9413 | 11.9329 | 8.5764 | 7.8126 | 25.2027 | 11.819 | 8.4946 | 7.5077 | 26.1983 | 11.4645 | 8.2398 | 6.4383 | 27.3207 | 11.1008 | 7.9784 | 5.079 | 28.2243 | 10.6997 | 7.6901 | 3.5153 | 28.909 | 10.3376 | 7.4299 | 1.6645 | 29.3523 | 9.9911 | 7.1808 | 0.2902 | 23.1764 | 13.6368 | 9.8011 | 10.303 | 23.3999 | 13.1127 | 9.4244 | 8.3677 | 23.5652 | 12.7447 | 9.1599 | 7.9754 | 23.749 | 12.6005 | 9.0562 | 7.9128 | 23.9975 | 12.3077 | 8.8458 | 7.7244 | 24.318 | 11.9614 | 8.5969 | 7.4972 | 24.7314 | 11.5899 | 8.3299 | 7.2777 | 25.2434 | 11.2469 | 8.0834 | 7.0244 | 25.6293 | 11.0884 | 7.9694 | 6.7268 | 26.0735 | 10.9363 | 7.8601 | 6.3995 | 27.4937 | 10.2009 | 7.3316 | 4.0907 | 28.5346 | 9.3063 | 6.6886 | 0.71333 | 29.2769 | 8.5326 | 6.1325 | -2.0039 | 29.8467 | 7.847 | 5.6398 | -4.5184 | 30.1885 | 7.1642 | 5.1491 | -6.1499 | 23.1767 | 13.6368 | 9.8011 | 10.303 | 23.3414 | 13.2641 | 9.5332 | 9.1358 | 23.49 | 12.8804 | 9.2574 | 8.8875 | 23.6504 | 12.8077 | 9.2052 | 8.8036 | 23.8911 | 12.5487 | 9.019 | 8.6077 | 24.2445 | 12.2808 | 8.8264 | 8.3626 | 24.7283 | 11.8284 | 8.5013 | 7.9429 | 25.335 | 11.3071 | 8.1266 | 6.9735 | 25.9043 | 10.8611 | 7.8061 | 5.9344 | 26.4835 | 10.4051 | 7.4783 | 4.8695 | 27.7938 | 9.612 | 6.9083 | 1.6235 | 28.7161 | 8.7561 | 6.2932 | -1.4213 | 29.2463 | 8.0121 | 5.7585 | -3.6619 | 29.5405 | 7.3763 | 5.3015 | -5.034 | 29.5225 | 7.1109 | 5.1107 | -4.4909 | 23.1642 | 13.6368 | 9.8011 | 10.303 | 23.363 | 13.3102 | 9.5663 | 9.0398 | 23.5159 | 13.0437 | 9.3748 | 8.7612 | 23.6523 | 12.8736 | 9.2525 | 8.6956 | 23.8439 | 12.7 | 9.1278 | 8.5806 | 24.1212 | 12.3616 | 8.8845 | 8.4417 | 24.5009 | 12.0048 | 8.6281 | 8.2276 | 24.9807 | 11.7139 | 8.419 | 7.8695 | 25.458 | 11.5023 | 8.2669 | 7.3978 | 25.8907 | 11.3542 | 8.1605 | 6.8837 | 27.3877 | 10.8478 | 7.7965 | 4.9971 | 28.2444 | 10.3163 | 7.4145 | 2.6993 | 28.8348 | 9.8693 | 7.0933 | 0.92487 | 29.2594 | 9.5024 | 6.8295 | -0.91962 | 29.3774 | 9.123 | 6.5569 | -1.6513 | 23.1642 | 13.6368 | 9.8011 | 10.303 | 23.3231 | 13.0985 | 9.4142 | 8.3094 | 23.4928 | 12.726 | 9.1464 | 7.8716 | 23.6635 | 12.5948 | 9.0522 | 7.7325 | 23.8956 | 12.3235 | 8.8571 | 7.4912 | 24.1939 | 12.0574 | 8.6659 | 7.2249 | 24.5872 | 11.5965 | 8.3346 | 6.7852 | 25.1201 | 11.0714 | 7.9572 | 5.7952 | 25.6394 | 10.6289 | 7.6392 | 4.7751 | 26.1759 | 10.1758 | 7.3135 | 3.7215 | 27.8315 | 9.3723 | 6.7361 | 0.46702 | 28.851 | 8.4576 | 6.0786 | -2.8802 | 29.5683 | 7.6556 | 5.5022 | -5.4525 | 29.9991 | 6.9504 | 4.9954 | -7.1358 | 30.0063 | 6.6516 | 4.7806 | -6.769
BOTANY BAY | LEYLAND | PENWORTHAM WEST / STANAH | 359442 | 418850 | 19.9029 | 19.9029 | 19.5474 | 10.4475 | 20.0557 | 20.0557 | 19.4939 | 10.0273 | 20.2061 | 20.2061 | 19.3589 | 9.8556 | 20.3973 | 20.3973 | 19.2462 | 9.7191 | 20.6057 | 20.6057 | 19.1099 | 9.5059 | 20.8231 | 20.8231 | 19.0102 | 9.2796 | 21.002 | 21.002 | 18.9289 | 9.036 | 21.2148 | 21.2148 | 18.844 | 8.7059 | 21.4204 | 21.4204 | 18.764 | 8.3189 | 21.6272 | 21.6272 | 18.6872 | 7.9471 | 22.2495 | 22.2495 | 18.3165 | 5.6972 | 22.8444 | 22.8444 | 17.8803 | 2.6924 | 23.2461 | 23.2461 | 17.5331 | 0.46053 | 23.5848 | 23.5848 | 17.1965 | -1.5043 | 23.8049 | 23.5522 | 16.9274 | -2.8702 | 19.8813 | 19.8813 | 19.5474 | 10.4475 | 19.9798 | 19.9798 | 19.5135 | 10.2336 | 20.0608 | 20.0608 | 19.4732 | 10.1135 | 20.1652 | 20.1652 | 19.4068 | 9.9841 | 20.3031 | 20.3031 | 19.3463 | 9.801 | 20.4647 | 20.4647 | 19.2701 | 9.5908 | 20.6273 | 20.6273 | 19.1654 | 9.3206 | 20.8177 | 20.8177 | 19.0878 | 8.9757 | 20.975 | 20.975 | 19.0231 | 8.702 | 21.1484 | 21.1484 | 18.9333 | 8.3421 | 21.6009 | 21.6009 | 18.6898 | 7.1444 | 22.1056 | 22.1056 | 18.4527 | 5.8552 | 22.5099 | 22.5099 | 18.1892 | 4.3572 | 22.8495 | 22.8495 | 17.9105 | 2.9485 | 23.0762 | 23.0762 | 17.7189 | 2.1469 | 19.9117 | 19.9117 | 19.5474 | 10.4475 | 20.0494 | 20.0494 | 19.4774 | 10.0023 | 20.1974 | 20.1974 | 19.3079 | 9.8479 | 20.3885 | 20.3885 | 19.1803 | 9.7493 | 20.5987 | 20.5987 | 19.0313 | 9.5809 | 20.8114 | 20.8114 | 18.9566 | 9.4089 | 20.9844 | 20.9844 | 18.8763 | 9.2637 | 21.1902 | 21.1902 | 18.8035 | 9.0686 | 21.3803 | 21.3803 | 18.7272 | 8.7767 | 21.5762 | 21.5762 | 18.6492 | 8.4841 | 22.2354 | 22.2354 | 18.1606 | 5.5694 | 22.8574 | 22.8574 | 17.6445 | 2.213 | 23.2355 | 23.2355 | 17.2221 | -0.34643 | 23.4786 | 23.3712 | 16.7974 | -2.6241 | 23.6101 | 22.9232 | 16.4754 | -4.1989 | 19.9119 | 19.9119 | 19.5474 | 10.4475 | 20.0013 | 20.0013 | 19.5234 | 10.3094 | 20.1048 | 20.1048 | 19.3864 | 10.2412 | 20.2442 | 20.2442 | 19.2443 | 10.1765 | 20.4308 | 20.4308 | 19.0554 | 10.0196 | 20.6584 | 20.6584 | 19.0753 | 9.8322 | 20.8747 | 20.8747 | 18.9764 | 9.5224 | 21.1606 | 21.1606 | 18.8297 | 8.7936 | 21.378 | 21.378 | 18.689 | 8.0033 | 21.5881 | 21.5881 | 18.5463 | 7.2183 | 22.1781 | 22.1781 | 18.1012 | 4.6004 | 22.5833 | 22.5833 | 17.6176 | 1.5302 | 22.8527 | 22.8527 | 17.2237 | -0.72156 | 23.027 | 23.027 | 16.8747 | -2.3863 | 23.0015 | 23.0015 | 16.7259 | -2.613 | 19.9027 | 19.9027 | 19.5474 | 10.4475 | 20.0219 | 20.0219 | 19.5231 | 10.1778 | 20.1245 | 20.1245 | 19.404 | 10.0694 | 20.2462 | 20.2462 | 19.3026 | 9.9992 | 20.402 | 20.402 | 19.1781 | 9.8972 | 20.5913 | 20.5913 | 19.087 | 9.7626 | 20.8022 | 20.8022 | 19.0183 | 9.5952 | 20.9787 | 20.9787 | 18.9509 | 9.3933 | 21.1544 | 21.1544 | 18.8729 | 9.0413 | 21.3415 | 21.3415 | 18.797 | 8.6791 | 21.9771 | 21.9771 | 18.543 | 7.3471 | 22.4974 | 22.4974 | 18.1968 | 4.9721 | 22.877 | 22.877 | 17.9206 | 3.2158 | 23.1807 | 23.1807 | 17.6534 | 1.7248 | 23.3196 | 23.3196 | 17.4687 | 0.95635 | 19.9027 | 19.9027 | 19.5474 | 10.4475 | 19.9965 | 19.9965 | 19.488 | 10.1238 | 20.1263 | 20.1263 | 19.3231 | 9.9615 | 20.297 | 20.297 | 19.1816 | 9.8182 | 20.4953 | 20.4953 | 18.9941 | 9.5922 | 20.6981 | 20.6981 | 18.9968 | 9.3633 | 20.9161 | 20.9161 | 18.8927 | 9.0099 | 21.2106 | 21.2106 | 18.7361 | 8.2065 | 21.4216 | 21.4216 | 18.5884 | 7.3626 | 21.6378 | 21.6378 | 18.4369 | 6.5055 | 22.2767 | 22.2767 | 17.9982 | 3.9572 | 22.8535 | 22.8535 | 17.533 | 1.0718 | 23.2697 | 23.2697 | 17.1402 | -1.1512 | 23.5655 | 23.3729 | 16.7986 | -2.7483 | 23.6328 | 23.1447 | 16.6345 | -3.0911
BOW LANE | LEYLAND | PENWORTHAM WEST / STANAH | 354895 | 422392 | 28.2424 | 12.244 | 8.8 | 10.9018 | 28.3494 | 11.6772 | 8.3926 | 8.3775 | 28.4997 | 10.0185 | 7.2005 | 6.9447 | 28.6651 | 8.4066 | 6.042 | 5.9032 | 28.8882 | 6.7579 | 4.857 | 4.7334 | 29.1805 | 5.1501 | 3.7015 | 3.98 | 21.7594 | 3.5825 | 2.5748 | 3.494 | 19.7986 | 3.2597 | 2.3428 | 2.9666 | 18.9456 | 3.1193 | 2.2419 | 2.3248 | 18.1803 | 2.9933 | 2.1513 | 1.6754 | 14.5496 | 2.3955 | 1.7217 | -1.5714 | 13.4764 | 2.2188 | 1.5947 | -6.3348 | 20.3221 | 3.3459 | 2.4047 | -10.0982 | 29.4434 | 4.8476 | 3.4841 | -13.9769 | 28.953 | 4.7669 | 3.4261 | -17.3628 | 28.2108 | 12.244 | 8.8 | 10.9018 | 28.3406 | 12.0327 | 8.6481 | 10.0557 | 28.4816 | 10.5924 | 7.6129 | 9.5577 | 28.6489 | 9.1431 | 6.5713 | 9.1478 | 28.8303 | 7.6527 | 5.5001 | 8.6548 | 29.0281 | 6.1944 | 4.4521 | 8.2714 | 27.743 | 4.5677 | 3.2829 | 7.755 | 26.4324 | 4.3519 | 3.1278 | 7.0569 | 25.2871 | 4.1633 | 2.9923 | 6.4749 | 24.1135 | 3.9701 | 2.8534 | 5.8675 | 20.5349 | 3.3809 | 2.4299 | 3.9135 | 17.2686 | 2.8431 | 2.0434 | 1.7619 | 21.2794 | 3.5035 | 2.518 | -0.40765 | 29.1555 | 4.8002 | 3.45 | -2.8106 | 29.4839 | 4.8543 | 3.4889 | -4.3997 | 28.2512 | 12.244 | 8.8 | 10.9018 | 28.3647 | 11.5724 | 8.3173 | 8.0291 | 28.517 | 9.8244 | 7.061 | 6.5663 | 28.6884 | 8.1589 | 5.8639 | 5.5854 | 28.9136 | 6.4721 | 4.6516 | 4.486 | 29.2005 | 4.8545 | 3.489 | 3.8218 | 19.6695 | 3.2384 | 2.3275 | 3.468 | 18.4899 | 3.0442 | 2.1879 | 3.0922 | 17.2815 | 2.8453 | 2.045 | 2.6248 | 16.4277 | 2.7047 | 1.9439 | 2.1288 | 11.9155 | 1.9618 | 1.41 | -0.76736 | 9.851 | 1.6219 | 1.1657 | -5.3925 | 15.7549 | 2.5939 | 1.8643 | -9.0666 | 23.972 | 3.9468 | 2.8366 | -12.7599 | 22.7496 | 3.7455 | 2.692 | -15.8567 | 28.2512 | 12.244 | 8.8 | 10.9018 | 28.2339 | 11.8058 | 8.4851 | 9.1968 | 28.3116 | 11.4402 | 8.2223 | 7.9917 | 28.4068 | 11.0767 | 7.9611 | 7.0625 | 28.5702 | 10.7272 | 7.7098 | 5.9706 | 28.835 | 10.4541 | 7.5136 | 5.2684 | 29.2136 | 10.1495 | 7.2946 | 4.6339 | 29.7103 | 9.6783 | 6.956 | 3.2649 | 30.2423 | 9.2397 | 6.6407 | 1.7756 | 30.8263 | 8.8998 | 6.3964 | 0.25054 | 32.6691 | 7.7163 | 5.5459 | -4.2672 | 34.1429 | 6.5584 | 4.7137 | -8.578 | 33.8205 | 5.5683 | 4.002 | -11.8563 | 29.2121 | 4.8095 | 3.4567 | -14.0838 | 26.6956 | 4.3952 | 3.1589 | -13.4692 | 28.2424 | 12.244 | 8.8 | 10.9018 | 28.3354 | 11.894 | 8.5484 | 9.5187 | 28.4516 | 10.2859 | 7.3927 | 8.3368 | 28.5653 | 8.6936 | 6.2483 | 7.3978 | 28.7237 | 7.0825 | 5.0904 | 6.4009 | 28.9697 | 5.5037 | 3.9556 | 5.7933 | 24.0275 | 3.9559 | 2.8432 | 5.4171 | 22.1012 | 3.6388 | 2.6153 | 4.9949 | 21.3843 | 3.5208 | 2.5304 | 4.4225 | 20.6823 | 3.4052 | 2.4474 | 3.823 | 18.3916 | 3.028 | 2.1763 | 1.7301 | 20.0595 | 3.3026 | 2.3737 | -0.53996 | 29.1307 | 4.7962 | 3.4471 | -2.3411 | 35.2061 | 6.7419 | 4.8456 | -3.811 | 35.4936 | 7.1423 | 5.1333 | -4.6322 | 28.2424 | 12.244 | 8.8 | 10.9018 | 28.2674 | 11.5599 | 8.3083 | 7.9795 | 28.3983 | 11.129 | 7.9986 | 6.4582 | 28.5516 | 10.7444 | 7.7222 | 5.3964 | 28.759 | 10.3641 | 7.4489 | 4.1878 | 29.0211 | 10.07 | 7.2375 | 3.4166 | 29.3695 | 9.7462 | 7.0048 | 2.7043 | 29.8484 | 9.2543 | 6.6513 | 1.2325 | 30.3237 | 8.8061 | 6.3292 | -0.30589 | 30.8515 | 8.45 | 6.0732 | -1.8827 | 32.6622 | 7.2144 | 5.1852 | -6.6746 | 34.3289 | 5.9839 | 4.3008 | -11.356 | 29.8799 | 4.9195 | 3.5357 | -15.0036 | 24.8351 | 4.0889 | 2.9388 | -17.5848 | 22.0107 | 3.6239 | 2.6046 | -17.2898
BOWATERS | BARROW & SANDGATE | HARKER / HUTTON | 319579 | 472480 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844
BOWDON | ALTRINCHAM | CARRINGTON | 376743 | 386810 | 31.1076 | 13.3478 | 9.5933 | 13.1223 | 31.1832 | 13.1229 | 9.4317 | 12.4116 | 31.3069 | 12.9406 | 9.3007 | 12.1484 | 31.4503 | 12.8312 | 9.2221 | 12.0229 | 31.5668 | 12.6719 | 9.1075 | 11.8315 | 31.698 | 12.4519 | 8.9494 | 11.6365 | 31.8484 | 12.3109 | 8.8481 | 11.4772 | 32.0319 | 12.1574 | 8.7378 | 11.3361 | 32.1661 | 12.0277 | 8.6446 | 11.1354 | 32.291 | 11.8559 | 8.5211 | 10.963 | 32.7007 | 11.384 | 8.1819 | 9.3536 | 33.1669 | 10.8186 | 7.7755 | 6.2831 | 33.5213 | 10.2392 | 7.3591 | 3.7197 | 33.8347 | 9.6601 | 6.9429 | 0.97497 | 34.0222 | 9.1605 | 6.5838 | -1.2601 | 31.0327 | 13.3478 | 9.5933 | 13.1223 | 31.0856 | 13.254 | 9.5259 | 12.8173 | 31.1505 | 13.1682 | 9.4643 | 12.624 | 31.2558 | 13.0571 | 9.3844 | 12.4485 | 31.4114 | 12.9367 | 9.2978 | 12.2201 | 31.5826 | 12.785 | 9.1889 | 11.9799 | 31.7802 | 12.4689 | 8.9616 | 11.6737 | 32.0052 | 12.344 | 8.8719 | 11.2961 | 32.1192 | 12.2393 | 8.7966 | 11.0101 | 32.2231 | 12.1228 | 8.7129 | 10.7218 | 32.482 | 11.7823 | 8.4682 | 9.8674 | 32.7304 | 11.519 | 8.279 | 9.0257 | 32.9481 | 11.2092 | 8.0563 | 8.2788 | 33.1714 | 10.9883 | 7.8975 | 7.485 | 33.3384 | 10.6554 | 7.6583 | 6.933 | 31.1269 | 13.3478 | 9.5933 | 13.1223 | 31.2142 | 13.0725 | 9.3955 | 12.3381 | 31.3569 | 12.8546 | 9.2388 | 12.0828 | 31.4961 | 12.7029 | 9.1298 | 12.0053 | 31.6321 | 12.5225 | 9.0001 | 11.8613 | 31.7862 | 12.2999 | 8.8401 | 11.7194 | 31.9647 | 12.1127 | 8.7056 | 11.6344 | 32.1821 | 11.9615 | 8.597 | 11.572 | 32.3318 | 11.7465 | 8.4424 | 11.4748 | 32.4696 | 11.6451 | 8.3696 | 11.3839 | 32.8689 | 11.2814 | 8.1082 | 10.0324 | 33.3221 | 10.5906 | 7.6117 | 7.2006 | 33.6703 | 9.8699 | 7.0937 | 4.8582 | 33.9632 | 9.3316 | 6.7068 | 2.3846 | 34.1168 | 8.8107 | 6.3324 | 0.46337 | 31.1269 | 13.3478 | 9.5933 | 13.1223 | 31.0829 | 13.1639 | 9.4612 | 12.8415 | 31.1471 | 12.9945 | 9.3394 | 12.7366 | 31.2254 | 12.8032 | 9.2019 | 12.7306 | 31.3186 | 12.5704 | 9.0346 | 12.6251 | 31.4376 | 12.3237 | 8.8573 | 12.4889 | 31.5938 | 12.1654 | 8.7435 | 12.1992 | 31.7883 | 12.0283 | 8.645 | 11.2866 | 31.9423 | 11.7794 | 8.4661 | 10.3197 | 32.0905 | 11.4866 | 8.2556 | 9.3559 | 32.538 | 10.7906 | 7.7554 | 6.5889 | 33.013 | 10.0623 | 7.2319 | 3.922 | 33.2967 | 9.4347 | 6.7809 | 1.7805 | 33.5042 | 9.0793 | 6.5255 | 0.42495 | 33.4915 | 9.0099 | 6.4756 | 1.6367 | 31.1076 | 13.3478 | 9.5933 | 13.1223 | 31.1661 | 13.195 | 9.4835 | 12.6907 | 31.2426 | 13.0359 | 9.3692 | 12.5325 | 31.33 | 12.9376 | 9.2985 | 12.4842 | 31.4366 | 12.8083 | 9.2056 | 12.4186 | 31.5541 | 12.6068 | 9.0608 | 12.3306 | 31.7094 | 12.4773 | 8.9677 | 12.2277 | 31.877 | 12.3222 | 8.8562 | 12.1186 | 31.9967 | 12.1978 | 8.7668 | 11.9213 | 32.1135 | 12.0214 | 8.6401 | 11.7301 | 32.48 | 11.7241 | 8.4263 | 11.0742 | 32.8726 | 11.5884 | 8.3288 | 10.3188 | 33.1278 | 11.3844 | 8.1822 | 9.8047 | 33.3524 | 11.2062 | 8.0542 | 9.2178 | 33.4536 | 11.0625 | 7.9509 | 8.9645 | 31.1076 | 13.3478 | 9.5933 | 13.1223 | 31.127 | 13.0711 | 9.3945 | 12.4548 | 31.2425 | 12.8782 | 9.2559 | 12.183 | 31.3838 | 12.6634 | 9.1014 | 12.0635 | 31.5004 | 12.4152 | 8.9231 | 11.8585 | 31.6297 | 12.1568 | 8.7373 | 11.6578 | 31.7869 | 11.9733 | 8.6054 | 11.2884 | 32.0107 | 11.8152 | 8.4918 | 10.2617 | 32.1787 | 11.5515 | 8.3023 | 9.2175 | 32.3373 | 11.2582 | 8.0915 | 8.1768 | 32.7871 | 10.4997 | 7.5464 | 5.1802 | 33.2158 | 9.7286 | 6.9921 | 2.3174 | 33.5317 | 9.0586 | 6.5106 | -0.033938 | 33.715 | 8.65 | 6.2169 | -1.6815 | 33.7103 | 8.5261 | 6.1279 | -0.81841
BRADFORD | STUART ST | STALYBRIDGE | 387613 | 397710 | 23.8411 | 4.3526 | 3.1752 | 13.2335 | 22.9315 | 3.7197 | 2.7135 | 10.7093 | 17.3674 | 2.8172 | 2.0551 | 9.9205 | 12.3517 | 2.0036 | 1.4616 | 9.6703 | 7.178 | 1.1643 | 0.84938 | 7.178 | 2.0159 | 0.327 | 0.23854 | 2.0159 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 1.2865 | 2.6914 | 0.43658 | 0.31848 | -1.2058 | 2.6914 | 0.43658 | 0.31848 | -3.0311 | 0.76516 | 0.12412 | 0.090542 | -3.9584 | 23.835 | 4.3526 | 3.1752 | 13.2335 | 23.969 | 4.0891 | 2.9829 | 12.3941 | 20.3821 | 3.3062 | 2.4118 | 11.9969 | 15.8075 | 2.5641 | 1.8705 | 11.8113 | 11.4514 | 1.8575 | 1.355 | 11.4514 | 7.0308 | 1.1405 | 0.83195 | 7.0308 | 1.4734 | 0.239 | 0.17435 | 1.4734 | 0.9102 | 0.14764 | 0.1077 | 0.9102 | 0.18412 | 0.029866 | 0.021787 | 0.18412 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 1.1614 | 2.6914 | 0.43658 | 0.31848 | -0.536 | 23.843 | 4.3526 | 3.1752 | 13.2335 | 22.3221 | 3.6209 | 2.6414 | 10.3142 | 16.4665 | 2.671 | 1.9485 | 9.446 | 11.2707 | 1.8282 | 1.3337 | 9.1947 | 5.9692 | 0.96827 | 0.70634 | 5.9692 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 1.8182 | 2.6914 | 0.43658 | 0.31848 | -1.2102 | 2.6914 | 0.43658 | 0.31848 | -3.5136 | 2.6914 | 0.43658 | 0.31848 | -4.6213 | 23.8433 | 4.3526 | 3.1752 | 13.2335 | 23.5809 | 3.8251 | 2.7903 | 11.1701 | 22.1952 | 3.6003 | 2.6264 | 10.5022 | 20.8139 | 3.3762 | 2.4629 | 10.2763 | 19.2049 | 3.1152 | 2.2725 | 10.0491 | 18.136 | 2.9418 | 2.146 | 9.8008 | 15.8659 | 2.5736 | 1.8774 | 9.4511 | 14.5 | 2.352 | 1.7158 | 8.7604 | 12.9561 | 2.1016 | 1.5331 | 7.9835 | 12.3619 | 2.0052 | 1.4628 | 7.2215 | 9.0321 | 1.4651 | 1.0688 | 4.8006 | 3.4848 | 0.56527 | 0.41236 | 1.18 | 2.6914 | 0.43658 | 0.31848 | -1.2057 | 1.0784 | 0.17493 | 0.12761 | -2.7176 | 2.6914 | 0.43658 | 0.31848 | -2.8317 | 23.8407 | 4.3526 | 3.1752 | 13.2335 | 24.0014 | 3.9615 | 2.8898 | 11.6973 | 19.2201 | 3.1177 | 2.2743 | 11.1276 | 14.3449 | 2.3269 | 1.6974 | 10.9245 | 9.3219 | 1.5121 | 1.1031 | 9.3219 | 4.2551 | 0.69021 | 0.5035 | 4.2551 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 1.9117 | 2.8198 | 0.4574 | 0.33366 | -0.047023 | 5.9481 | 0.96484 | 0.70384 | -0.80872 | 23.8407 | 4.3526 | 3.1752 | 13.2335 | 21.8446 | 3.5434 | 2.5849 | 9.9689 | 19.9898 | 3.2425 | 2.3654 | 9.0222 | 18.5799 | 3.0138 | 2.1986 | 8.7505 | 16.8337 | 2.7306 | 1.9919 | 8.4849 | 15.7785 | 2.5594 | 1.8671 | 8.223 | 13.5114 | 2.1917 | 1.5988 | 7.8669 | 12.1359 | 1.9686 | 1.436 | 7.1525 | 10.6279 | 1.7239 | 1.2576 | 6.3672 | 9.9628 | 1.6161 | 1.1789 | 5.5981 | 6.8194 | 1.1062 | 0.80694 | 3.4088 | 2.7411 | 0.44463 | 0.32435 | 1.0745 | 2.6914 | 0.43658 | 0.31848 | -1.8751 | 2.6914 | 0.43658 | 0.31848 | -3.9345 | 2.6914 | 0.43658 | 0.31848 | -4.4058
BRADSHAWGATE | BOLTON | KEARSLEY | 371891 | 408910 | 33.9781 | 12.3172 | 8.9852 | 22.2963 | 34.0232 | 12.1126 | 8.8359 | 21.1951 | 34.0985 | 11.9848 | 8.7428 | 20.5951 | 34.1803 | 11.8525 | 8.6462 | 20.2175 | 34.2774 | 11.7258 | 8.5538 | 19.8244 | 34.3751 | 11.5597 | 8.4326 | 19.4257 | 34.4709 | 11.3673 | 8.2923 | 19.0327 | 34.5895 | 11.0963 | 8.0946 | 18.6249 | 34.6974 | 11.0742 | 8.0785 | 18.1878 | 34.8114 | 10.9784 | 8.0086 | 17.7533 | 35.1682 | 10.4953 | 7.6562 | 16.1221 | 35.4917 | 9.996 | 7.2919 | 14.0429 | 35.7036 | 9.5373 | 6.9573 | 12.2436 | 35.8599 | 9.48 | 6.9155 | 10.8614 | 35.9451 | 8.9348 | 6.5178 | 9.8745 | 33.9694 | 12.3172 | 8.9852 | 22.2963 | 34.0136 | 12.2533 | 8.9386 | 21.9258 | 34.0751 | 12.1549 | 8.8668 | 21.6145 | 34.1385 | 12.079 | 8.8115 | 21.3638 | 34.2135 | 11.9811 | 8.74 | 21.1012 | 34.3024 | 11.861 | 8.6525 | 20.8134 | 34.4107 | 11.6268 | 8.4816 | 20.4843 | 34.5443 | 11.4973 | 8.3871 | 20.0981 | 34.6312 | 11.3761 | 8.2987 | 19.8196 | 34.7264 | 11.2589 | 8.2132 | 19.5336 | 35.0447 | 10.9475 | 7.9861 | 18.6811 | 35.3616 | 10.6197 | 7.7469 | 17.8174 | 35.6549 | 10.4046 | 7.59 | 17.0201 | 35.9682 | 10.4344 | 7.6118 | 16.3358 | 36.1861 | 10.5011 | 7.6604 | 15.873 | 33.9817 | 12.3172 | 8.9852 | 22.2963 | 34.0311 | 12.0591 | 8.7969 | 21.0288 | 34.1113 | 11.8838 | 8.669 | 20.3956 | 34.2005 | 11.7146 | 8.5456 | 20.0169 | 34.3046 | 11.5153 | 8.4002 | 19.6251 | 34.3879 | 11.284 | 8.2315 | 19.228 | 34.4845 | 11.1511 | 8.1346 | 18.8363 | 34.6023 | 11.0081 | 8.0303 | 18.4323 | 34.6986 | 10.8313 | 7.9013 | 18.0282 | 34.8 | 10.6937 | 7.8009 | 17.6299 | 35.1437 | 10.1082 | 7.3738 | 16.1004 | 35.4849 | 9.4744 | 6.9114 | 14.1262 | 35.7127 | 8.9198 | 6.5068 | 12.4418 | 35.862 | 8.6924 | 6.341 | 11.2351 | 35.913 | 8.2926 | 6.0494 | 10.4885 | 33.9817 | 12.3172 | 8.9852 | 22.2963 | 33.9899 | 12.1526 | 8.8652 | 21.4604 | 34.0387 | 12.0489 | 8.7895 | 20.9545 | 34.0941 | 11.8782 | 8.6649 | 20.6265 | 34.1541 | 11.6806 | 8.5208 | 20.2787 | 34.2241 | 11.547 | 8.4233 | 19.9058 | 34.3036 | 11.4089 | 8.3226 | 19.4649 | 34.4037 | 11.1861 | 8.1601 | 18.8183 | 34.5085 | 10.9717 | 8.0037 | 18.1389 | 34.6196 | 10.7706 | 7.857 | 17.4636 | 34.9621 | 10.4321 | 7.61 | 15.4985 | 35.2673 | 9.8255 | 7.1676 | 13.5846 | 35.4572 | 9.2942 | 6.78 | 11.9734 | 35.5711 | 8.8055 | 6.4235 | 11.1518 | 35.5687 | 8.5359 | 6.2268 | 11.4308 | 33.9781 | 12.3172 | 8.9852 | 22.2963 | 34.0173 | 12.2109 | 8.9077 | 21.7333 | 34.0781 | 12.11 | 8.834 | 21.2637 | 34.1363 | 11.9998 | 8.7537 | 20.9256 | 34.2043 | 11.8801 | 8.6664 | 20.5962 | 34.2987 | 11.7255 | 8.5536 | 20.2439 | 34.4105 | 11.5492 | 8.425 | 19.8699 | 34.5139 | 11.3361 | 8.2695 | 19.4776 | 34.604 | 11.2361 | 8.1966 | 19.0448 | 34.7018 | 11.1464 | 8.1311 | 18.6045 | 35.0278 | 10.7508 | 7.8426 | 17.2476 | 35.3489 | 10.4151 | 7.5977 | 15.8497 | 35.5704 | 10.1 | 7.3678 | 14.672 | 35.7321 | 10.1783 | 7.425 | 13.9917 | 35.8015 | 9.8203 | 7.1638 | 13.803 | 33.9781 | 12.3172 | 8.9852 | 22.2963 | 34.0028 | 12.0474 | 8.7884 | 20.9314 | 34.0748 | 11.9147 | 8.6916 | 20.2714 | 34.157 | 11.7299 | 8.5568 | 19.8782 | 34.2538 | 11.5221 | 8.4052 | 19.4726 | 34.3456 | 11.3754 | 8.2982 | 19.0666 | 34.4365 | 11.2206 | 8.1853 | 18.5972 | 34.5558 | 10.9873 | 8.0151 | 17.8991 | 34.656 | 10.7668 | 7.8543 | 17.1993 | 34.7621 | 10.5611 | 7.7042 | 16.5061 | 35.1044 | 10.2473 | 7.4753 | 14.4957 | 35.4268 | 9.5761 | 6.9856 | 12.5518 | 35.6394 | 9.026 | 6.5843 | 10.9056 | 35.7618 | 8.5302 | 6.2226 | 10.0492 | 35.7657 | 8.2419 | 6.0123 | 10.2716
BRAMHALL | HAZEL GROVE | BREDBURY | 389440 | 386463 | 23.1956 | 12.9961 | 9.3405 | 10.1776 | 23.2627 | 12.8141 | 9.2098 | 9.9246 | 23.3654 | 12.7048 | 9.1312 | 9.836 | 23.4419 | 12.5056 | 8.988 | 9.7721 | 23.5337 | 12.2605 | 8.8119 | 9.6895 | 23.6397 | 11.9947 | 8.6209 | 9.6049 | 23.7641 | 11.6654 | 8.3841 | 9.5216 | 23.9184 | 11.4536 | 8.2319 | 9.4315 | 24.0283 | 11.2658 | 8.097 | 9.2824 | 24.1306 | 11.2461 | 8.0828 | 9.1581 | 24.4619 | 10.8938 | 7.8296 | 8.2067 | 24.8029 | 10.4039 | 7.4775 | 6.476 | 25.0416 | 9.8936 | 7.1107 | 4.5906 | 25.2706 | 9.4527 | 6.7938 | 2.4082 | 25.43 | 9.1276 | 6.5602 | 0.50828 | 23.1531 | 12.9961 | 9.3405 | 10.1776 | 23.1965 | 12.849 | 9.2349 | 10.0799 | 23.2368 | 12.8077 | 9.2051 | 10.0274 | 23.2977 | 12.6455 | 9.0886 | 9.9412 | 23.385 | 12.4503 | 8.9483 | 9.8096 | 23.4989 | 12.2406 | 8.7976 | 9.6463 | 23.6355 | 11.8834 | 8.5408 | 9.4394 | 23.788 | 11.7818 | 8.4678 | 9.2061 | 23.8842 | 11.691 | 8.4025 | 8.9991 | 23.9659 | 11.5906 | 8.3304 | 8.7905 | 24.1531 | 11.3845 | 8.1822 | 8.1831 | 24.3316 | 11.2488 | 8.0847 | 7.6351 | 24.4883 | 11.0657 | 7.9531 | 7.1333 | 24.6445 | 10.9612 | 7.878 | 6.6368 | 24.7614 | 10.8299 | 7.7836 | 6.3134 | 23.2093 | 12.9961 | 9.3405 | 10.1776 | 23.2876 | 12.8232 | 9.2163 | 9.9139 | 23.3902 | 12.6419 | 9.086 | 9.8412 | 23.4782 | 12.4279 | 8.9322 | 9.8141 | 23.5869 | 12.1962 | 8.7656 | 9.7685 | 23.7127 | 11.8687 | 8.5302 | 9.7258 | 23.8617 | 11.5371 | 8.2919 | 9.623 | 24.0454 | 11.3221 | 8.1374 | 9.5171 | 24.1729 | 11.1375 | 8.0047 | 9.3367 | 24.2907 | 11.0648 | 7.9525 | 9.165 | 24.6298 | 10.5932 | 7.6135 | 8.2358 | 24.962 | 10.0662 | 7.2348 | 6.6752 | 25.213 | 9.5084 | 6.8339 | 4.944 | 25.447 | 8.9912 | 6.4622 | 2.9329 | 25.5803 | 8.592 | 6.1752 | 1.2212 | 23.2093 | 12.9961 | 9.3405 | 10.1776 | 23.1954 | 12.9109 | 9.2793 | 10.2087 | 23.2412 | 12.8666 | 9.2475 | 10.2402 | 23.2893 | 12.7267 | 9.147 | 10.2658 | 23.3467 | 12.5747 | 9.0377 | 10.2413 | 23.4465 | 12.2977 | 8.8386 | 10.1775 | 23.5794 | 11.9913 | 8.6184 | 9.9456 | 23.7415 | 11.7338 | 8.4333 | 9.4076 | 23.8662 | 11.4443 | 8.2252 | 8.7661 | 23.9865 | 11.2557 | 8.0897 | 7.9934 | 24.3547 | 10.5675 | 7.595 | 5.8763 | 24.6964 | 9.9393 | 7.1436 | 3.9583 | 24.9332 | 9.3863 | 6.7461 | 2.3434 | 25.1228 | 8.9327 | 6.4201 | 1.2411 | 25.1434 | 8.7767 | 6.308 | 2.0257 | 23.1956 | 12.9961 | 9.3405 | 10.1776 | 23.2498 | 12.8333 | 9.2235 | 10.0954 | 23.3112 | 12.7735 | 9.1805 | 10.0931 | 23.3738 | 12.591 | 9.0494 | 10.1061 | 23.4298 | 12.3614 | 8.8844 | 10.1078 | 23.5245 | 12.1152 | 8.7074 | 10.0624 | 23.6524 | 11.7837 | 8.4692 | 9.991 | 23.7917 | 11.5774 | 8.3209 | 9.9286 | 23.8875 | 11.3868 | 8.1839 | 9.8037 | 23.9808 | 11.381 | 8.1798 | 9.6889 | 24.2774 | 11.1466 | 8.0113 | 9.2668 | 24.5901 | 10.9083 | 7.84 | 8.7502 | 24.7808 | 10.6848 | 7.6794 | 8.3692 | 24.9602 | 10.6093 | 7.6251 | 7.9766 | 25.0608 | 10.6509 | 7.655 | 7.8241 | 23.1956 | 12.9961 | 9.3405 | 10.1776 | 23.2145 | 12.8779 | 9.2556 | 10.0484 | 23.3108 | 12.802 | 9.2011 | 9.9666 | 23.3889 | 12.6352 | 9.0812 | 9.8878 | 23.4826 | 12.4617 | 8.9564 | 9.7745 | 23.5888 | 12.1756 | 8.7509 | 9.6646 | 23.7192 | 11.8727 | 8.5332 | 9.379 | 23.902 | 11.5894 | 8.3295 | 8.7518 | 24.0386 | 11.2736 | 8.1025 | 8.0637 | 24.168 | 11.0866 | 7.9682 | 7.2839 | 24.5375 | 10.3641 | 7.4489 | 4.9898 | 24.847 | 9.7057 | 6.9757 | 2.9363 | 25.0622 | 9.1227 | 6.5567 | 1.191 | 25.225 | 8.6391 | 6.2091 | -0.074173 | 25.2449 | 8.4498 | 6.0731 | 0.52214
BRIDGEWATER | BLOOM ST | SOUTH MANCHESTER | 383543 | 397628 | 30.4888 | 13.3331 | 9.7263 | 13.5055 | 30.5123 | 12.7741 | 9.3185 | 10.19 | 30.5619 | 12.502 | 9.1201 | 9.4235 | 30.5967 | 12.4522 | 9.0837 | 9.3162 | 30.6214 | 12.4018 | 9.0469 | 9.2368 | 30.6471 | 12.3748 | 9.0272 | 9.1569 | 30.6744 | 12.316 | 8.9844 | 9.0952 | 30.7059 | 12.2541 | 8.9392 | 9.035 | 30.7544 | 12.1619 | 8.8719 | 8.8685 | 30.8005 | 12.0738 | 8.8076 | 8.7122 | 30.9319 | 11.8585 | 8.6506 | 8.0447 | 31.0595 | 11.6098 | 8.4692 | 7.0889 | 31.1475 | 11.4267 | 8.3356 | 6.3311 | 31.2254 | 11.7859 | 8.5977 | 5.5406 | 31.2718 | 12.1853 | 8.889 | 4.862 | 30.4864 | 13.3331 | 9.7263 | 13.5055 | 30.5139 | 13.19 | 9.6219 | 12.4312 | 30.5683 | 13.1053 | 9.5602 | 12.0955 | 30.6097 | 13.1694 | 9.6069 | 11.9544 | 30.6422 | 13.1707 | 9.6078 | 11.8574 | 30.6789 | 13.1176 | 9.5691 | 11.7645 | 30.7194 | 12.8838 | 9.3986 | 11.6637 | 30.7658 | 12.8263 | 9.3566 | 11.5422 | 30.8225 | 12.7533 | 9.3034 | 11.3093 | 30.8788 | 12.687 | 9.255 | 11.0777 | 31.035 | 12.4984 | 9.1174 | 10.4384 | 31.178 | 12.3742 | 9.0268 | 9.8395 | 31.2927 | 12.3055 | 8.9767 | 9.3529 | 31.415 | 12.5862 | 9.1815 | 8.8191 | 31.5338 | 12.797 | 9.3352 | 8.2965 | 30.4898 | 13.3331 | 9.7263 | 13.5055 | 30.5159 | 12.67 | 9.2426 | 9.6764 | 30.5673 | 12.395 | 9.042 | 8.8103 | 30.6058 | 12.344 | 9.0048 | 8.726 | 30.6334 | 12.294 | 8.9683 | 8.6574 | 30.6623 | 12.2446 | 8.9323 | 8.5867 | 30.6942 | 12.1845 | 8.8884 | 8.5457 | 30.7304 | 12.1143 | 8.8372 | 8.4998 | 30.7735 | 12.0214 | 8.7694 | 8.4172 | 30.8105 | 11.9439 | 8.7129 | 8.3135 | 30.9135 | 11.7288 | 8.556 | 7.8189 | 31.0078 | 11.494 | 8.3847 | 7.0232 | 31.0589 | 11.3288 | 8.2642 | 6.4315 | 31.0835 | 11.713 | 8.5445 | 5.8706 | 31.0592 | 12.1423 | 8.8576 | 5.4887 | 30.4898 | 13.3331 | 9.7263 | 13.5055 | 30.4906 | 12.8634 | 9.3837 | 10.8274 | 30.5312 | 12.6613 | 9.2362 | 10.1991 | 30.5589 | 12.6231 | 9.2083 | 10.125 | 30.5769 | 12.5657 | 9.1665 | 10.0623 | 30.5987 | 12.5326 | 9.1424 | 9.9974 | 30.6254 | 12.4854 | 9.1079 | 9.916 | 30.6585 | 12.3862 | 9.0356 | 9.6836 | 30.7035 | 12.2824 | 8.9598 | 9.4069 | 30.7434 | 12.1153 | 8.838 | 9.1066 | 30.8473 | 11.8216 | 8.6237 | 8.2972 | 30.9345 | 11.604 | 8.465 | 7.5461 | 30.9786 | 11.5361 | 8.4154 | 7.0093 | 30.9864 | 12.4139 | 9.0558 | 6.7298 | 30.9244 | 12.3644 | 9.0197 | 7.0913 | 30.4888 | 13.3331 | 9.7263 | 13.5055 | 30.5113 | 13.0156 | 9.4947 | 11.5308 | 30.5577 | 12.7785 | 9.3217 | 11.0407 | 30.5877 | 12.7303 | 9.2866 | 10.9438 | 30.6069 | 12.6852 | 9.2537 | 10.8942 | 30.6304 | 12.6781 | 9.2485 | 10.8438 | 30.6578 | 12.6229 | 9.2082 | 10.7985 | 30.6875 | 12.564 | 9.1652 | 10.7431 | 30.7346 | 12.4717 | 9.098 | 10.5717 | 30.7801 | 12.3822 | 9.0326 | 10.4058 | 30.9041 | 12.2078 | 8.9054 | 9.9364 | 31.0157 | 12.0574 | 8.7957 | 9.4926 | 31.0897 | 11.9603 | 8.7249 | 9.2055 | 31.1536 | 12.4179 | 9.0587 | 8.9366 | 31.1869 | 12.9241 | 9.4279 | 8.794 | 30.4888 | 13.3331 | 9.7263 | 13.5055 | 30.4952 | 12.5791 | 9.1762 | 9.2282 | 30.5428 | 12.3253 | 8.9911 | 8.2627 | 30.5783 | 12.2784 | 8.9569 | 8.1725 | 30.6035 | 12.2209 | 8.915 | 8.0944 | 30.6287 | 12.1835 | 8.8877 | 8.0173 | 30.6572 | 12.1293 | 8.8482 | 7.9163 | 30.6961 | 12.0238 | 8.7712 | 7.6653 | 30.7428 | 11.9181 | 8.6941 | 7.3785 | 30.7839 | 11.7479 | 8.5699 | 7.0661 | 30.8876 | 11.4462 | 8.3498 | 6.2122 | 30.9711 | 11.2237 | 8.1875 | 5.4381 | 31.0137 | 11.1491 | 8.1331 | 4.8743 | 31.0209 | 12.0162 | 8.7657 | 4.5517 | 30.9652 | 11.9555 | 8.7214 | 4.8517
BRINKSWAY | ADSWOOD | BREDBURY | 388434 | 389885 | 29.8566 | 13.5197 | 9.8624 | 18.2101 | 30.089 | 12.6735 | 9.2451 | 13.2319 | 30.2574 | 12.2899 | 8.9653 | 11.6419 | 30.3631 | 11.9127 | 8.6902 | 10.4631 | 30.4913 | 11.5694 | 8.4397 | 9.5571 | 30.6432 | 11.3896 | 8.3086 | 8.6428 | 30.8257 | 11.1205 | 8.1122 | 7.7265 | 31.0398 | 10.8246 | 7.8964 | 6.8092 | 31.1855 | 10.5421 | 7.6903 | 5.8775 | 31.3321 | 10.2858 | 7.5034 | 4.962 | 31.8428 | 9.6439 | 7.0351 | 2.3335 | 32.3112 | 8.9962 | 6.5626 | -0.47671 | 32.6198 | 8.4873 | 6.1914 | -2.4115 | 32.8951 | 7.9886 | 5.8276 | -3.973 | 33.0275 | 7.5915 | 5.5379 | -4.845 | 29.8349 | 13.5197 | 9.8624 | 18.2101 | 29.9973 | 13.1547 | 9.5962 | 16.1126 | 30.1153 | 12.9785 | 9.4676 | 15.5812 | 30.2355 | 12.7037 | 9.2672 | 14.9274 | 30.3696 | 12.4463 | 9.0794 | 14.261 | 30.5288 | 12.1138 | 8.8369 | 13.5859 | 30.7178 | 11.6614 | 8.5068 | 12.8753 | 30.885 | 11.4971 | 8.387 | 12.1292 | 31.0069 | 11.3709 | 8.2949 | 11.4404 | 31.1437 | 11.252 | 8.2082 | 10.7679 | 31.5882 | 11.0973 | 8.0953 | 10.2568 | 31.9727 | 11.0007 | 8.0249 | 9.7437 | 32.1983 | 10.7967 | 7.8761 | 8.8389 | 32.4209 | 10.4927 | 7.6543 | 7.6195 | 32.5929 | 10.1423 | 7.3987 | 6.5628 | 29.8637 | 13.5197 | 9.8624 | 18.2101 | 30.0644 | 12.5533 | 9.1574 | 12.5775 | 30.2328 | 12.0624 | 8.7994 | 10.813 | 30.35 | 11.5591 | 8.4322 | 9.5725 | 30.4718 | 11.2029 | 8.1723 | 8.5999 | 30.6128 | 11.0892 | 8.0894 | 7.6126 | 30.7797 | 10.7567 | 7.8469 | 6.6172 | 30.9785 | 10.4171 | 7.5991 | 5.6165 | 31.1718 | 10.1247 | 7.3859 | 4.6137 | 31.3314 | 9.8445 | 7.1814 | 3.6753 | 31.8675 | 9.2424 | 6.7422 | 1.8869 | 32.3752 | 8.4793 | 6.1855 | -1.0494 | 32.6655 | 7.8334 | 5.7143 | -3.2455 | 32.8706 | 7.1662 | 5.2276 | -5.155 | 32.9364 | 6.657 | 4.8562 | -6.2538 | 29.8643 | 13.5197 | 9.8624 | 18.2101 | 30.049 | 12.78 | 9.3228 | 13.9171 | 30.1875 | 12.3002 | 8.9728 | 12.4484 | 30.2723 | 11.8853 | 8.6702 | 11.2404 | 30.3844 | 11.6112 | 8.4702 | 10.2855 | 30.5316 | 11.4864 | 8.3791 | 9.285 | 30.7198 | 11.2236 | 8.1875 | 8.2024 | 30.9544 | 10.8969 | 7.9491 | 6.8979 | 31.164 | 10.5836 | 7.7206 | 5.5922 | 31.3584 | 10.2602 | 7.4847 | 4.3808 | 31.9029 | 9.4174 | 6.8698 | 1.3664 | 32.2653 | 8.6768 | 6.3296 | -1.3044 | 32.4845 | 8.0953 | 5.9054 | -2.9963 | 32.5978 | 7.5585 | 5.5138 | -4.2246 | 32.5339 | 7.1767 | 5.2353 | -4.6224 | 29.8559 | 13.5197 | 9.8624 | 18.2101 | 30.0369 | 13.0264 | 9.5026 | 15.3626 | 30.1674 | 12.7212 | 9.2799 | 14.2252 | 30.2813 | 12.3558 | 9.0134 | 13.0847 | 30.3677 | 12.0321 | 8.7772 | 12.2432 | 30.4805 | 11.8533 | 8.6468 | 11.324 | 30.624 | 11.6035 | 8.4646 | 10.4591 | 30.7903 | 11.3137 | 8.2532 | 9.5639 | 30.957 | 11.0281 | 8.0449 | 8.6114 | 31.121 | 10.7661 | 7.8537 | 7.6857 | 31.5573 | 10.1912 | 7.4343 | 5.2989 | 31.9779 | 9.6568 | 7.0445 | 2.9002 | 32.2363 | 9.1905 | 6.7044 | 1.0108 | 32.435 | 8.7311 | 6.3692 | -0.55742 | 32.5455 | 8.3762 | 6.1103 | -1.3625 | 29.8559 | 13.5197 | 9.8624 | 18.2101 | 30.0209 | 12.4814 | 9.105 | 12.1032 | 30.177 | 11.9289 | 8.702 | 10.2309 | 30.2951 | 11.5066 | 8.3939 | 8.9748 | 30.4127 | 11.2177 | 8.1831 | 7.984 | 30.5469 | 11.084 | 8.0856 | 6.9861 | 30.7113 | 10.8155 | 7.8897 | 5.911 | 30.9288 | 10.48 | 7.645 | 4.5756 | 31.1418 | 10.1601 | 7.4117 | 3.2495 | 31.3717 | 9.8314 | 7.1718 | 2.0193 | 32.0184 | 9.113 | 6.6478 | -0.1796 | 32.4873 | 8.4162 | 6.1395 | -2.5251 | 32.7329 | 7.7645 | 5.6641 | -4.6016 | 32.8537 | 7.1863 | 5.2423 | -6.0606 | 32.8103 | 6.8023 | 4.9622 | -6.445
BROADHEATH | ALTRINCHAM | CARRINGTON | 376412 | 389026 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 0.85015 | 2.6844 | 0.44197 | 0.31765 | -2.9134 | 2.6844 | 0.44197 | 0.31765 | -5.972 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.1535 | 2.6844 | 0.44197 | 0.31765 | -1.1986 | 2.6844 | 0.44197 | 0.31765 | -4.1937 | 2.0879 | 0.44197 | 0.31765 | -6.1323 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 1.2019 | 2.6844 | 0.44197 | 0.31765 | -1.5574 | 2.6844 | 0.44197 | 0.31765 | -3.3803 | 2.1251 | 0.44197 | 0.31765 | -3.6072 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | -1.2909 | 2.6844 | 0.44197 | 0.31765 | -4.2108 | 2.6844 | 0.44197 | 0.31765 | -6.0754 | 0.79853 | 0.30309 | 0.24765 | -6.3028
BROADWAY | LANCASTER | HEYSHAM | 344792 | 464471 | 25.3304 | 8.6439 | 6.3056 | 16.0876 | 25.3778 | 8.4157 | 6.1391 | 15.4346 | 25.4463 | 8.247 | 6.016 | 15.1975 | 25.5351 | 8.037 | 5.8629 | 15.0692 | 25.6543 | 7.7563 | 5.6581 | 14.8936 | 25.7985 | 7.427 | 5.4179 | 14.7126 | 25.9724 | 7.0199 | 5.121 | 14.5475 | 26.1888 | 6.8403 | 4.9899 | 14.3867 | 26.3941 | 6.6554 | 4.855 | 14.1601 | 26.6056 | 6.5795 | 4.7997 | 13.955 | 27.3962 | 6.163 | 4.4958 | 12.3731 | 28.2918 | 5.6239 | 4.1025 | 9.5482 | 28.9465 | 5.3757 | 3.9215 | 7.1698 | 29.5419 | 7.2389 | 5.2807 | 4.5773 | 29.9086 | 6.6206 | 4.8296 | 2.3059 | 25.3121 | 8.6439 | 6.3056 | 16.0876 | 25.3562 | 8.5288 | 6.2216 | 15.7327 | 25.4054 | 8.3184 | 6.0681 | 15.5359 | 25.4613 | 8.0783 | 5.893 | 15.3826 | 25.5382 | 7.8497 | 5.7263 | 15.1991 | 25.6292 | 7.6382 | 5.5719 | 15.0208 | 25.7418 | 7.3291 | 5.3465 | 14.8003 | 25.8752 | 7.2127 | 5.2616 | 14.5392 | 25.9721 | 7.1124 | 5.1884 | 14.2934 | 26.0785 | 7.0139 | 5.1165 | 14.0456 | 26.4522 | 6.7331 | 4.9117 | 13.301 | 26.88 | 6.5098 | 4.7488 | 12.5676 | 27.3185 | 6.3101 | 4.6031 | 11.8375 | 27.7892 | 7.5088 | 5.4775 | 11.0415 | 28.1116 | 8.6486 | 6.309 | 10.4384 | 25.3347 | 8.6439 | 6.3056 | 16.0876 | 25.3863 | 8.3707 | 6.1063 | 15.3663 | 25.4609 | 8.1359 | 5.935 | 15.1362 | 25.5581 | 7.8782 | 5.7471 | 15.0476 | 25.6859 | 7.604 | 5.547 | 14.9131 | 25.8379 | 7.2868 | 5.3156 | 14.7808 | 26.0192 | 6.7872 | 4.9512 | 14.6845 | 26.2419 | 6.6966 | 4.8851 | 14.601 | 26.4404 | 6.4949 | 4.738 | 14.4772 | 26.6441 | 6.4211 | 4.6841 | 14.3555 | 27.4568 | 5.9518 | 4.3417 | 13.0037 | 28.4323 | 5.3441 | 3.8985 | 10.3564 | 29.1611 | 5.0232 | 3.6644 | 8.1616 | 29.8007 | 6.8234 | 4.9776 | 5.78 | 30.0468 | 6.189 | 4.5148 | 3.7715 | 25.3347 | 8.6439 | 6.3056 | 16.0876 | 25.3213 | 8.4683 | 6.1775 | 15.7427 | 25.3572 | 8.2884 | 6.0463 | 15.6035 | 25.4189 | 7.991 | 5.8293 | 15.5144 | 25.5182 | 7.7676 | 5.6663 | 15.3573 | 25.6662 | 7.5867 | 5.5344 | 15.1767 | 25.8769 | 7.1419 | 5.2099 | 14.8525 | 26.194 | 6.7912 | 4.9541 | 14.0009 | 26.5037 | 6.4692 | 4.7192 | 13.0855 | 26.8225 | 6.2779 | 4.5796 | 12.1629 | 27.7957 | 7.8991 | 5.7623 | 9.4927 | 28.6946 | 7.1956 | 5.2491 | 6.9812 | 29.2893 | 6.5782 | 4.7987 | 4.9827 | 29.5429 | 6.0441 | 4.4091 | 3.6917 | 29.5406 | 5.9245 | 4.3219 | 4.5823 | 25.3303 | 8.6439 | 6.3056 | 16.0876 | 25.3702 | 8.4608 | 6.172 | 15.5491 | 25.4172 | 8.3118 | 6.0634 | 15.3662 | 25.4711 | 8.1139 | 5.9189 | 15.299 | 25.5473 | 7.8508 | 5.7271 | 15.2237 | 25.6625 | 7.5382 | 5.499 | 15.1323 | 25.8147 | 7.1316 | 5.2024 | 15.0338 | 25.9922 | 6.9762 | 5.0891 | 14.9244 | 26.1601 | 6.7894 | 4.9528 | 14.7264 | 26.3396 | 6.7189 | 4.9013 | 14.5299 | 26.9588 | 6.4716 | 4.7209 | 13.8148 | 27.5894 | 6.3172 | 4.6083 | 13.0022 | 28.0293 | 6.3863 | 4.6588 | 12.3626 | 28.3686 | 8.6139 | 6.2837 | 11.7438 | 28.5366 | 8.3778 | 6.1115 | 11.5077 | 25.3303 | 8.6439 | 6.3056 | 16.0876 | 25.3357 | 8.3832 | 6.1154 | 15.4267 | 25.3998 | 8.1728 | 5.9619 | 15.1696 | 25.4944 | 7.867 | 5.7388 | 15.0008 | 25.619 | 7.6305 | 5.5663 | 14.7721 | 25.7636 | 7.4402 | 5.4275 | 14.5459 | 25.9585 | 7.0004 | 5.1067 | 14.1688 | 26.2745 | 6.6267 | 4.8341 | 13.2426 | 26.5766 | 6.2756 | 4.578 | 12.277 | 26.8866 | 6.1094 | 4.4567 | 11.3044 | 27.8583 | 7.6821 | 5.604 | 8.4595 | 28.7744 | 6.9413 | 5.0636 | 5.7654 | 29.3688 | 6.2823 | 4.5828 | 3.5531 | 29.6932 | 5.7104 | 4.1657 | 2.0596 | 29.6965 | 5.5524 | 4.0504 | 2.7414
BUCKSHAW | LEYLAND | PENWORTHAM WEST / STANAH | 356748 | 421312 | 28.6751 | 14.4115 | 10.3578 | 17.3926 | 28.7422 | 13.9079 | 9.9959 | 15.0072 | 28.8583 | 13.676 | 9.8292 | 14.3566 | 28.9892 | 13.499 | 9.702 | 14.1025 | 29.1484 | 13.2861 | 9.549 | 13.812 | 29.3457 | 13.0887 | 9.4071 | 13.5043 | 29.5816 | 12.9223 | 9.2875 | 13.1759 | 29.8028 | 12.7783 | 9.184 | 12.8185 | 30.0421 | 12.632 | 9.0788 | 12.3523 | 30.2937 | 12.5097 | 8.991 | 11.8664 | 31.0999 | 12.0507 | 8.6611 | 10.0237 | 31.841 | 11.5907 | 8.3304 | 7.9115 | 32.3365 | 11.3107 | 8.1293 | 6.4212 | 32.726 | 11.7419 | 8.4391 | 5.0885 | 32.9863 | 11.4831 | 8.2531 | 4.0549 | 28.6633 | 14.4115 | 10.3578 | 17.3926 | 28.7244 | 14.1957 | 10.2027 | 16.3255 | 28.8171 | 14.069 | 10.1117 | 15.9689 | 28.9035 | 13.956 | 10.0304 | 15.7878 | 28.986 | 13.842 | 9.9485 | 15.5931 | 29.0864 | 13.7208 | 9.8614 | 15.3888 | 29.2122 | 13.4872 | 9.6935 | 15.1313 | 29.3673 | 13.3766 | 9.614 | 14.7955 | 29.5342 | 13.2647 | 9.5336 | 14.4365 | 29.7255 | 13.1491 | 9.4505 | 14.0564 | 30.4439 | 12.8084 | 9.2056 | 12.8347 | 31.2898 | 12.4988 | 8.9831 | 11.4877 | 31.9081 | 12.2168 | 8.7805 | 10.1698 | 32.5163 | 12.3718 | 8.8919 | 8.7251 | 32.9498 | 12.5777 | 9.0398 | 7.6598 | 28.6801 | 14.4115 | 10.3578 | 17.3926 | 28.7573 | 13.8234 | 9.9351 | 14.6172 | 28.8851 | 13.5222 | 9.7186 | 13.8718 | 29.0284 | 13.2997 | 9.5587 | 13.5961 | 29.1973 | 13.0999 | 9.4151 | 13.28 | 29.4037 | 12.8959 | 9.2686 | 12.9501 | 29.5926 | 12.7165 | 9.1396 | 12.6147 | 29.8024 | 12.5574 | 9.0252 | 12.255 | 30.0203 | 12.4199 | 8.9264 | 11.8227 | 30.2503 | 12.2816 | 8.827 | 11.3415 | 31.0466 | 11.7454 | 8.4416 | 9.4337 | 31.8304 | 11.2276 | 8.0695 | 7.2724 | 32.3535 | 10.8955 | 7.8308 | 5.8186 | 32.7209 | 11.2213 | 8.0649 | 4.6727 | 32.8993 | 11.1315 | 8.0005 | 4.0051 | 28.6801 | 14.4115 | 10.3578 | 17.3926 | 28.709 | 14.0003 | 10.0623 | 15.4807 | 28.7996 | 13.7882 | 9.9098 | 14.9103 | 28.9041 | 13.5724 | 9.7548 | 14.6589 | 29.0428 | 13.4277 | 9.6507 | 14.3501 | 29.1995 | 13.294 | 9.5547 | 14.0058 | 29.3781 | 13.1328 | 9.4388 | 13.5804 | 29.6018 | 12.9471 | 9.3053 | 12.9336 | 29.8507 | 12.7575 | 9.1691 | 12.2195 | 30.1122 | 12.6143 | 9.0662 | 11.4724 | 30.9117 | 12.6848 | 9.1168 | 9.2791 | 31.5985 | 12.1863 | 8.7585 | 7.4026 | 32.023 | 11.8231 | 8.4975 | 6.2499 | 32.2956 | 11.7006 | 8.4095 | 5.5722 | 32.3832 | 11.4915 | 8.2592 | 5.4912 | 28.6751 | 14.4115 | 10.3578 | 17.3926 | 28.7349 | 14.0057 | 10.0662 | 15.4092 | 28.8309 | 13.8008 | 9.9189 | 14.8512 | 28.9283 | 13.6311 | 9.7969 | 14.641 | 29.0471 | 13.4303 | 9.6526 | 14.4239 | 29.2204 | 13.2457 | 9.52 | 14.1784 | 29.434 | 13.0883 | 9.4068 | 13.8999 | 29.6482 | 12.9552 | 9.3112 | 13.5961 | 29.8513 | 12.8138 | 9.2095 | 13.1729 | 30.0694 | 12.6983 | 9.1265 | 12.7241 | 30.799 | 12.3183 | 8.8534 | 11.2394 | 31.5106 | 11.984 | 8.6132 | 9.756 | 32.0082 | 11.8207 | 8.4957 | 8.7453 | 32.3958 | 12.3505 | 8.8765 | 7.8851 | 32.6143 | 12.2461 | 8.8015 | 7.2705 | 28.6751 | 14.4115 | 10.3578 | 17.3926 | 28.7226 | 13.7783 | 9.9027 | 14.3608 | 28.8391 | 13.5139 | 9.7127 | 13.5532 | 28.9704 | 13.2922 | 9.5534 | 13.2493 | 29.1255 | 13.1306 | 9.4372 | 12.8972 | 29.3169 | 12.9887 | 9.3352 | 12.533 | 29.5388 | 12.8212 | 9.2148 | 12.0884 | 29.7784 | 12.6277 | 9.0757 | 11.4156 | 30.023 | 12.4314 | 8.9347 | 10.699 | 30.2792 | 12.2924 | 8.8348 | 9.9475 | 31.1003 | 12.3468 | 8.8739 | 7.6554 | 31.8552 | 11.8137 | 8.4907 | 5.5929 | 32.3491 | 11.4179 | 8.2063 | 4.2556 | 32.6586 | 11.2698 | 8.0998 | 3.4287 | 32.7687 | 11.013 | 7.9153 | 3.2332
BURNLEY | BURNLEY | ROCHDALE | 385569 | 434469 | 14.8151 | 5.9183 | 4.3173 | 10.5885 | 14.8875 | 5.7559 | 4.1988 | 10.2118 | 14.944 | 5.6592 | 4.1283 | 10.0678 | 15.0242 | 5.5716 | 4.0644 | 9.996 | 15.1194 | 5.4889 | 4.0041 | 9.8684 | 15.2214 | 5.3699 | 3.9173 | 9.7358 | 15.3364 | 5.3218 | 3.8822 | 9.6321 | 15.4757 | 5.2541 | 3.8328 | 9.5352 | 15.6038 | 5.1638 | 3.7669 | 9.377 | 15.725 | 5.0887 | 3.7121 | 9.2365 | 16.1537 | 4.6391 | 3.3842 | 7.774 | 16.6562 | 4.0072 | 2.9232 | 4.9355 | 17.0348 | 3.5716 | 2.6054 | 2.5158 | 17.3887 | 3.9975 | 2.9161 | -0.092789 | 17.646 | 3.3656 | 2.4552 | -2.2036 | 14.8145 | 5.9183 | 4.3173 | 10.5885 | 14.8668 | 5.8461 | 4.2647 | 10.4409 | 14.8889 | 5.7721 | 4.2106 | 10.3315 | 14.9244 | 5.7107 | 4.1659 | 10.2459 | 14.9848 | 5.6516 | 4.1227 | 10.1391 | 15.0528 | 5.5728 | 4.0653 | 10.0106 | 15.1454 | 5.3371 | 3.8934 | 9.8373 | 15.2724 | 5.2285 | 3.8141 | 9.6094 | 15.384 | 5.145 | 3.7532 | 9.3963 | 15.4972 | 5.0509 | 3.6846 | 9.1828 | 15.8484 | 4.8272 | 3.5213 | 8.541 | 16.218 | 4.6456 | 3.3889 | 7.8634 | 16.5488 | 4.4897 | 3.2752 | 7.1832 | 16.7587 | 4.8832 | 3.5622 | 6.4618 | 16.8945 | 5.4913 | 4.0059 | 5.9732 | 14.8154 | 5.9183 | 4.3173 | 10.5885 | 14.8892 | 5.732 | 4.1814 | 10.1792 | 14.9465 | 5.6142 | 4.0954 | 10.0458 | 15.0281 | 5.503 | 4.0143 | 10.0082 | 15.1206 | 5.3193 | 3.8804 | 9.9147 | 15.2213 | 5.3139 | 3.8764 | 9.8215 | 15.335 | 5.2431 | 3.8248 | 9.7736 | 15.4715 | 5.1539 | 3.7597 | 9.7371 | 15.5967 | 5.0577 | 3.6895 | 9.6619 | 15.7125 | 4.959 | 3.6175 | 9.587 | 16.1307 | 4.4831 | 3.2704 | 8.3222 | 16.6272 | 3.809 | 2.7786 | 5.6702 | 17 | 3.3175 | 2.4201 | 3.4023 | 17.3404 | 3.69 | 2.6918 | 0.97467 | 17.5758 | 3.0857 | 2.2509 | -0.89884 | 14.8154 | 5.9183 | 4.3173 | 10.5885 | 14.7854 | 5.8041 | 4.234 | 10.4821 | 14.805 | 5.7187 | 4.1717 | 10.4248 | 14.8263 | 5.643 | 4.1165 | 10.3979 | 14.8758 | 5.5375 | 4.0396 | 10.2945 | 14.9598 | 5.4215 | 3.9549 | 10.1711 | 15.0753 | 5.1364 | 3.7469 | 9.891 | 15.2371 | 4.5867 | 3.3459 | 9.0149 | 15.3958 | 4.2721 | 3.1165 | 8.1004 | 15.55 | 4.0594 | 2.9613 | 7.1904 | 16.0149 | 4.6008 | 3.3562 | 4.57 | 16.4842 | 3.8617 | 2.817 | 2.0728 | 16.8296 | 3.2167 | 2.3465 | 0.015893 | 16.6996 | 2.7088 | 1.9761 | -1.2871 | 16.8658 | 2.7358 | 1.9957 | -0.168 | 14.8151 | 5.9183 | 4.3173 | 10.5885 | 14.8731 | 5.8121 | 4.2398 | 10.406 | 14.9078 | 5.721 | 4.1734 | 10.325 | 14.9477 | 5.6614 | 4.1299 | 10.3082 | 15.0009 | 5.597 | 4.0829 | 10.2883 | 15.0898 | 5.5017 | 4.0134 | 10.2416 | 15.21 | 5.459 | 3.9823 | 10.1746 | 15.3381 | 5.403 | 3.9414 | 10.0963 | 15.4515 | 5.3175 | 3.879 | 9.939 | 15.5637 | 5.2417 | 3.8237 | 9.7853 | 15.928 | 4.9739 | 3.6284 | 9.2172 | 16.312 | 4.7931 | 3.4965 | 8.4848 | 16.5872 | 4.7465 | 3.4625 | 7.8895 | 16.8291 | 5.6413 | 4.1152 | 7.3629 | 16.9455 | 5.4232 | 3.9561 | 7.1662 | 14.8151 | 5.9183 | 4.3173 | 10.5885 | 14.8032 | 5.75 | 4.1945 | 10.285 | 14.8566 | 5.6347 | 4.1104 | 10.1387 | 14.9542 | 5.548 | 4.0472 | 10.0412 | 15.0483 | 5.4264 | 3.9585 | 9.8735 | 15.1492 | 5.3064 | 3.8709 | 9.7072 | 15.2758 | 4.9996 | 3.6472 | 9.3752 | 15.4724 | 4.4761 | 3.2652 | 8.4259 | 15.6561 | 4.1042 | 2.9939 | 7.4581 | 15.8321 | 3.8879 | 2.8361 | 6.4943 | 16.3446 | 4.3782 | 3.1939 | 3.7017 | 16.8293 | 3.5996 | 2.6259 | 1.0389 | 17.1885 | 2.9121 | 2.1243 | -1.1987 | 14.4665 | 2.3466 | 1.7118 | -2.7678 | 14.2451 | 2.3107 | 1.6856 | -1.9433
BURNLEY CENTRE | BURNLEY | ROCHDALE | 384308 | 432288 | 22.4628 | 12.231 | 8.9224 | 9.1035 | 22.5393 | 12.0211 | 8.7692 | 8.7193 | 22.6275 | 11.779 | 8.5926 | 8.2469 | 22.7218 | 11.698 | 8.5335 | 7.8434 | 22.8284 | 11.5859 | 8.4518 | 7.4097 | 22.9485 | 11.4194 | 8.3303 | 6.9662 | 23.0738 | 11.2225 | 8.1867 | 6.5436 | 23.2054 | 11.0076 | 8.0299 | 6.3616 | 23.2793 | 10.9624 | 7.9969 | 6.1696 | 23.3473 | 10.8906 | 7.9445 | 5.9947 | 23.5764 | 10.4764 | 7.6424 | 4.8041 | 23.8173 | 9.9525 | 7.2602 | 2.7112 | 23.9975 | 9.5953 | 6.9996 | 0.7453 | 24.1618 | 10.0496 | 7.3311 | -1.5055 | 24.2682 | 9.6672 | 7.0521 | -3.3841 | 22.4566 | 12.231 | 8.9224 | 9.1035 | 22.589 | 12.1626 | 8.8725 | 8.8935 | 22.743 | 12.093 | 8.8217 | 8.5727 | 22.8732 | 11.991 | 8.7473 | 8.2714 | 23.0108 | 11.8698 | 8.6589 | 7.9612 | 23.1764 | 11.7197 | 8.5494 | 7.6251 | 23.3185 | 11.5436 | 8.4209 | 7.2336 | 23.4762 | 11.3768 | 8.2992 | 6.838 | 23.5353 | 11.2502 | 8.2068 | 6.6213 | 23.5943 | 11.1334 | 8.1217 | 6.4098 | 23.7773 | 10.7558 | 7.8462 | 5.7863 | 23.9621 | 10.4122 | 7.5955 | 5.1584 | 24.1227 | 10.0761 | 7.3504 | 4.6175 | 24.2837 | 10.5581 | 7.702 | 4.0453 | 24.3958 | 10.9175 | 7.9642 | 3.6257 | 22.4654 | 12.231 | 8.9224 | 9.1035 | 22.543 | 11.9674 | 8.73 | 8.6782 | 22.6345 | 11.6108 | 8.4699 | 8.1988 | 22.7344 | 11.5541 | 8.4286 | 7.7935 | 22.8476 | 11.3681 | 8.2929 | 7.3591 | 22.9754 | 11.1461 | 8.1309 | 6.9152 | 23.1107 | 10.8548 | 7.9184 | 6.4901 | 23.2336 | 10.7976 | 7.8767 | 6.3074 | 23.3049 | 10.6771 | 7.7888 | 6.1458 | 23.3707 | 10.5389 | 7.688 | 6.0047 | 23.5998 | 9.916 | 7.2336 | 4.9217 | 23.8406 | 9.2958 | 6.7812 | 2.9598 | 24.0161 | 8.8218 | 6.4354 | 1.2811 | 24.1666 | 9.1049 | 6.6419 | -0.76777 | 24.2461 | 8.5565 | 6.2419 | -2.3923 | 22.4654 | 12.231 | 8.9224 | 9.1035 | 22.4668 | 11.9915 | 8.7476 | 8.9228 | 22.502 | 11.8454 | 8.6411 | 8.5294 | 22.5404 | 11.7087 | 8.5413 | 8.1825 | 22.5934 | 11.4081 | 8.322 | 7.7995 | 22.6709 | 11.2531 | 8.209 | 7.3963 | 22.7713 | 11.1069 | 8.1024 | 6.8748 | 22.9004 | 10.8388 | 7.9068 | 6.1858 | 23.0071 | 10.5275 | 7.6797 | 5.4747 | 23.0952 | 10.268 | 7.4904 | 4.787 | 23.3207 | 10.3177 | 7.5266 | 2.744 | 23.5405 | 9.5505 | 6.9669 | 0.51365 | 23.6953 | 8.886 | 6.4822 | -1.2784 | 23.7967 | 8.663 | 6.3196 | -2.4199 | 23.7612 | 8.3404 | 6.0842 | -1.5854 | 22.4628 | 12.231 | 8.9224 | 9.1035 | 22.5328 | 12.0591 | 8.797 | 8.9306 | 22.6074 | 11.8239 | 8.6254 | 8.5111 | 22.6809 | 11.7709 | 8.5867 | 8.144 | 22.7638 | 11.67 | 8.5131 | 7.7892 | 22.8712 | 11.5151 | 8.4001 | 7.4208 | 22.9911 | 11.321 | 8.2585 | 7.0366 | 23.1066 | 11.1342 | 8.1222 | 6.8649 | 23.1732 | 11.0818 | 8.084 | 6.6565 | 23.2388 | 11.0046 | 8.0277 | 6.4502 | 23.4494 | 10.682 | 7.7924 | 5.7865 | 23.6587 | 10.3551 | 7.5539 | 5.0809 | 23.7938 | 10.3791 | 7.5714 | 4.606 | 23.913 | 11.2415 | 8.2005 | 4.1625 | 23.9693 | 11.1534 | 8.1363 | 4.0322 | 22.4628 | 12.231 | 8.9224 | 9.1035 | 22.5006 | 11.9598 | 8.7245 | 8.7627 | 22.5816 | 11.774 | 8.589 | 8.2914 | 22.6719 | 11.6315 | 8.4851 | 7.8793 | 22.7757 | 11.3388 | 8.2715 | 7.4336 | 22.8909 | 11.164 | 8.1439 | 6.9845 | 23.0148 | 10.9939 | 8.0199 | 6.4187 | 23.1705 | 10.7066 | 7.8103 | 5.6634 | 23.282 | 10.392 | 7.5808 | 4.9299 | 23.3736 | 10.1292 | 7.3891 | 4.2211 | 23.6051 | 10.0939 | 7.3634 | 2.029 | 23.822 | 9.2929 | 6.779 | -0.30266 | 23.9787 | 8.6256 | 6.2922 | -2.2204 | 24.0835 | 8.3744 | 6.109 | -3.5574 | 24.0636 | 8.0101 | 5.8433 | -2.9641
BURNLEY NORTH | BURNLEY | ROCHDALE | 384418 | 434168 | 17.73 | 17.73 | 17.3765 | 11.3338 | 17.9845 | 17.9845 | 17.244 | 10.2446 | 18.0821 | 18.0821 | 17.1686 | 9.9286 | 18.1868 | 18.1868 | 17.1798 | 9.7744 | 18.3188 | 18.3188 | 17.1552 | 9.5737 | 18.4681 | 18.4681 | 17.1136 | 9.3623 | 18.6331 | 18.6331 | 17.0714 | 9.134 | 18.8172 | 18.8172 | 17.0068 | 8.6814 | 18.967 | 18.967 | 16.8865 | 7.8193 | 19.1107 | 19.1107 | 16.7772 | 6.9453 | 19.6196 | 19.6196 | 16.4126 | 4.009 | 20.2144 | 20.2144 | 16.0794 | 0.98606 | 20.6492 | 20.6492 | 15.9194 | -1.2118 | 21.0481 | 21.0481 | 16.7709 | -3.0708 | 21.2596 | 21.2596 | 16.6344 | -4.1724 | 17.7144 | 17.7144 | 17.3765 | 11.3338 | 17.8646 | 17.8646 | 17.3173 | 10.8159 | 17.9718 | 17.9718 | 17.28 | 10.6312 | 18.0729 | 18.0729 | 17.2395 | 10.5078 | 18.1536 | 18.1536 | 17.2025 | 10.3548 | 18.2506 | 18.2506 | 17.1685 | 10.1795 | 18.3664 | 18.3664 | 17.1374 | 9.961 | 18.5037 | 18.5037 | 17.0772 | 9.6724 | 18.6306 | 18.6306 | 17.0189 | 9.3879 | 18.7659 | 18.7659 | 16.9504 | 9.0766 | 19.237 | 19.237 | 16.7197 | 7.2764 | 19.6172 | 19.6172 | 16.4279 | 4.8226 | 19.9204 | 19.9204 | 16.1619 | 2.7131 | 20.204 | 20.204 | 16.6384 | 0.80307 | 20.3827 | 20.3827 | 17.1839 | -0.25574 | 17.7358 | 17.7358 | 17.3765 | 11.3338 | 17.9461 | 17.9461 | 17.2166 | 10.1094 | 18.0681 | 18.0681 | 17.1653 | 9.7871 | 18.1669 | 18.1669 | 17.1474 | 9.665 | 18.2908 | 18.2908 | 17.1091 | 9.4996 | 18.429 | 18.429 | 17.0681 | 9.3304 | 18.5802 | 18.5802 | 17.0287 | 9.1913 | 18.7526 | 18.7526 | 16.982 | 9.0374 | 18.919 | 18.919 | 16.9033 | 8.577 | 19.0824 | 19.0824 | 16.8001 | 7.8189 | 19.5893 | 19.5893 | 16.3922 | 4.798 | 20.1923 | 20.1923 | 15.9654 | 1.2304 | 20.6136 | 20.6136 | 15.7108 | -1.4815 | 20.9598 | 20.9598 | 16.4613 | -3.849 | 21.1284 | 21.1284 | 16.2681 | -5.2557 | 17.7363 | 17.7363 | 17.3765 | 11.3338 | 17.934 | 17.934 | 17.2631 | 10.5685 | 17.9927 | 17.9927 | 17.2683 | 10.3553 | 18.0686 | 18.0686 | 17.2392 | 10.2692 | 18.1784 | 18.1784 | 17.2049 | 10.1201 | 18.3235 | 18.3235 | 17.178 | 9.9418 | 18.4864 | 18.4864 | 17.1235 | 9.6389 | 18.6855 | 18.6855 | 17.0081 | 8.8523 | 18.882 | 18.882 | 16.864 | 7.7482 | 19.0766 | 19.0766 | 16.7741 | 6.6317 | 19.635 | 19.635 | 17.3906 | 3.3469 | 20.1635 | 20.1635 | 16.9616 | 0.31729 | 20.4964 | 20.4964 | 16.6255 | -1.9541 | 20.7137 | 20.7137 | 16.4628 | -3.6044 | 20.7125 | 20.7125 | 16.3595 | -3.7606 | 17.7296 | 17.7296 | 17.3765 | 11.3338 | 17.9237 | 17.9237 | 17.2668 | 10.439 | 18.0343 | 18.0343 | 17.2029 | 10.1886 | 18.1002 | 18.1002 | 17.2194 | 10.0905 | 18.1815 | 18.1815 | 17.2075 | 9.9801 | 18.2918 | 18.2918 | 17.1751 | 9.8409 | 18.4293 | 18.4293 | 17.1407 | 9.6847 | 18.5866 | 18.5866 | 17.1076 | 9.4977 | 18.7515 | 18.7515 | 17.0504 | 9.1954 | 18.9258 | 18.9258 | 16.9644 | 8.5197 | 19.3702 | 19.3702 | 16.6587 | 6.0584 | 19.8238 | 19.8238 | 16.3859 | 3.6311 | 20.1553 | 20.1553 | 16.308 | 1.8738 | 20.4415 | 20.4415 | 17.2159 | 0.27503 | 20.5834 | 20.5834 | 17.1178 | -0.52817 | 17.7296 | 17.7296 | 17.3765 | 11.3338 | 17.9039 | 17.9039 | 17.2074 | 10.0687 | 18.0126 | 18.0126 | 17.1926 | 9.721 | 18.1087 | 18.1087 | 17.1556 | 9.5748 | 18.2306 | 18.2306 | 17.1156 | 9.3747 | 18.3638 | 18.3638 | 17.0846 | 9.1712 | 18.5317 | 18.5317 | 17.0284 | 8.8582 | 18.7424 | 18.7424 | 16.9161 | 8.1085 | 18.955 | 18.955 | 16.8085 | 7.298 | 19.1741 | 19.1741 | 16.745 | 6.4843 | 19.8454 | 19.8454 | 17.3678 | 3.2729 | 20.4287 | 20.4287 | 16.9088 | 0.0042241 | 20.7929 | 20.7929 | 16.5478 | -2.4685 | 21.0061 | 21.0061 | 16.3584 | -4.329 | 21.0225 | 21.0225 | 16.2372 | -4.6262
BURROW BECK | LANCASTER | HEYSHAM | 347903 | 458401 | 11.4924 | 4.2966 | 3.0881 | 10.9337 | 11.5937 | 3.5784 | 2.5718 | 7.7488 | 11.7689 | 2.1874 | 1.5722 | 5.4663 | 4.4414 | 0.73125 | 0.52556 | 4.0586 | 2.6844 | 0.44197 | 0.31765 | 2.5823 | 2.6844 | 0.44197 | 0.31765 | 1.0599 | 2.6844 | 0.44197 | 0.31765 | -0.49768 | 2.6844 | 0.44197 | 0.31765 | -2.1227 | 2.6844 | 0.44197 | 0.31765 | -3.9104 | 2.6844 | 0.44197 | 0.31765 | -4.4959 | 2.6844 | 0.44197 | 0.31765 | -8.2433 | 2.6844 | 0.44197 | 0.31765 | -12.3267 | 2.6844 | 0.44197 | 0.31765 | -15.0758 | 2.6844 | 0.44197 | 0.31765 | -17.2224 | 2.6844 | 0.44197 | 0.31765 | -19.0026 | 11.4573 | 4.2966 | 3.0881 | 10.9337 | 11.5195 | 3.9497 | 2.8387 | 9.4932 | 11.6014 | 3.5753 | 2.5697 | 9.1117 | 11.7122 | 3.41 | 2.4508 | 8.6695 | 11.8694 | 3.08 | 2.2137 | 8.178 | 12.0759 | 2.7441 | 1.9722 | 7.6424 | 12.3324 | 2.3085 | 1.6591 | 7.0263 | 12.5983 | 2.0987 | 1.5084 | 6.3275 | 11.6482 | 1.9178 | 1.3784 | 5.6776 | 10.7241 | 1.7656 | 1.269 | 5.2071 | 7.87 | 1.2957 | 0.93127 | 3.6608 | 4.7005 | 0.7739 | 0.55622 | 1.5127 | 1.0448 | 0.17203 | 0.12364 | -1.2758 | 3.5719 | 0.58809 | 0.42267 | -4.2969 | 6.9984 | 1.1522 | 0.82813 | -6.2775 | 11.5073 | 4.2966 | 3.0881 | 10.9337 | 11.6199 | 3.4345 | 2.4685 | 7.3116 | 11.7925 | 1.9415 | 1.3954 | 4.9812 | 3.6448 | 0.60009 | 0.4313 | 3.6367 | 2.6844 | 0.44197 | 0.31765 | 2.2283 | 2.6844 | 0.44197 | 0.31765 | 0.79159 | 2.6844 | 0.44197 | 0.31765 | -0.64114 | 2.6844 | 0.44197 | 0.31765 | -2.1169 | 2.6844 | 0.44197 | 0.31765 | -3.7009 | 2.6844 | 0.44197 | 0.31765 | -4.1179 | 2.6844 | 0.44197 | 0.31765 | -7.726 | 2.6844 | 0.44197 | 0.31765 | -12.0904 | 2.6844 | 0.44197 | 0.31765 | -15.155 | 2.6844 | 0.44197 | 0.31765 | -17.3614 | 2.6844 | 0.44197 | 0.31765 | -18.9775 | 11.5073 | 4.2966 | 3.0881 | 10.9337 | 11.5165 | 3.6787 | 2.6439 | 8.5293 | 11.6236 | 2.241 | 1.6107 | 6.4657 | 5.9683 | 0.98263 | 0.70623 | 5.1708 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.3259 | 2.6844 | 0.44197 | 0.31765 | 0.72366 | 2.6844 | 0.44197 | 0.31765 | -1.3145 | 2.6844 | 0.44197 | 0.31765 | -3.4978 | 2.6844 | 0.44197 | 0.31765 | -4.6531 | 2.6844 | 0.44197 | 0.31765 | -8.7638 | 2.6844 | 0.44197 | 0.31765 | -12.6102 | 2.6844 | 0.44197 | 0.31765 | -15.325 | 2.6844 | 0.44197 | 0.31765 | -17.0729 | 2.6844 | 0.44197 | 0.31765 | -16.6675 | 11.4924 | 4.2966 | 3.0881 | 10.9337 | 11.5757 | 3.7403 | 2.6882 | 8.5347 | 11.6967 | 2.3879 | 1.7162 | 6.4392 | 5.5909 | 0.9205 | 0.66158 | 5.1177 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.3637 | 2.6844 | 0.44197 | 0.31765 | 0.88169 | 2.6844 | 0.44197 | 0.31765 | -0.66138 | 2.6844 | 0.44197 | 0.31765 | -2.3683 | 2.6844 | 0.44197 | 0.31765 | -2.8904 | 2.6844 | 0.44197 | 0.31765 | -5.6008 | 2.6844 | 0.44197 | 0.31765 | -8.9262 | 2.6844 | 0.44197 | 0.31765 | -11.1216 | 2.6844 | 0.44197 | 0.31765 | -12.5374 | 2.6844 | 0.44197 | 0.31765 | -12.9443 | 11.4924 | 4.2966 | 3.0881 | 10.9337 | 11.5368 | 3.387 | 2.4343 | 7.0461 | 11.556 | 1.9026 | 1.3674 | 4.6293 | 3.6167 | 0.59547 | 0.42797 | 3.2151 | 2.6844 | 0.44197 | 0.31765 | 1.729 | 2.6844 | 0.44197 | 0.31765 | 0.21736 | 2.6844 | 0.44197 | 0.31765 | -1.4345 | 2.6844 | 0.44197 | 0.31765 | -3.5437 | 2.6844 | 0.44197 | 0.31765 | -5.7451 | 2.6844 | 0.44197 | 0.31765 | -6.7895 | 2.6844 | 0.44197 | 0.31765 | -10.7002 | 2.6844 | 0.44197 | 0.31765 | -14.4061 | 2.6844 | 0.44197 | 0.31765 | -17.3679 | 2.6844 | 0.44197 | 0.31765 | -19.4814 | 2.6844 | 0.44197 | 0.31765 | -19.2588
BURSCOUGH BRIDGE | WRIGHTINGTON | PENWORTHAM WEST / STANAH | 344595 | 412486 | 15.2848 | 15.2848 | 13.787 | 9.7791 | 15.4266 | 15.4266 | 13.6639 | 9.2966 | 15.6369 | 15.6369 | 13.5317 | 9.0976 | 15.9228 | 15.9228 | 13.4053 | 8.9919 | 16.1977 | 16.1977 | 13.2163 | 8.839 | 16.4553 | 16.4553 | 12.9776 | 8.6548 | 16.7861 | 16.7861 | 12.7536 | 8.4676 | 17.0649 | 17.0649 | 12.5385 | 8.2463 | 17.32 | 17.32 | 12.4566 | 7.9723 | 17.5785 | 17.1407 | 12.3193 | 7.7035 | 18.7991 | 16.5178 | 11.8716 | 6.1803 | 20.4711 | 15.7282 | 11.3042 | 3.8827 | 21.0356 | 14.342 | 10.3079 | 2.197 | 21.4692 | 14.1062 | 10.1384 | 0.73586 | 21.6739 | 13.0845 | 9.4041 | -0.38982 | 15.2454 | 15.2454 | 13.787 | 9.7791 | 15.3289 | 15.3289 | 13.7284 | 9.5654 | 15.4175 | 15.4175 | 13.668 | 9.3889 | 15.5442 | 15.5442 | 13.598 | 9.2406 | 15.7267 | 15.7267 | 13.5082 | 9.0676 | 15.9637 | 15.9637 | 13.4108 | 8.8602 | 16.2491 | 16.2491 | 13.2859 | 8.5974 | 16.5749 | 16.5749 | 13.18 | 8.27 | 16.7345 | 16.7345 | 13.0954 | 8.066 | 16.9036 | 16.9036 | 13.0069 | 7.8575 | 17.4686 | 17.4686 | 12.7479 | 7.1674 | 18.1159 | 17.3132 | 12.4433 | 5.9088 | 18.7692 | 16.9146 | 12.1569 | 4.7209 | 19.5258 | 16.5121 | 11.8676 | 3.4262 | 20.0679 | 16.039 | 11.5276 | 2.6698 | 15.3037 | 15.3037 | 13.787 | 9.7791 | 15.4555 | 15.4555 | 13.6216 | 9.2262 | 15.688 | 15.688 | 13.4148 | 9.0162 | 16.0054 | 16.0054 | 13.2158 | 8.9121 | 16.2335 | 16.2335 | 12.9768 | 8.762 | 16.4945 | 16.4945 | 12.6336 | 8.586 | 16.799 | 16.799 | 12.412 | 8.4101 | 17.0307 | 17.0152 | 12.2291 | 8.2075 | 17.2643 | 16.7455 | 12.0353 | 7.9845 | 17.5003 | 16.4816 | 11.8457 | 7.7688 | 18.7073 | 15.3792 | 11.0533 | 6.6615 | 20.0238 | 14.1845 | 10.1947 | 4.5958 | 20.5475 | 13.6221 | 9.7905 | 2.6069 | 20.9205 | 11.8746 | 8.5345 | 0.97654 | 21.0984 | 11.231 | 8.072 | -0.11643 | 15.3038 | 15.3038 | 13.787 | 9.7791 | 15.3511 | 15.3511 | 13.6709 | 9.5401 | 15.4796 | 15.4796 | 13.5009 | 9.4319 | 15.6728 | 15.6728 | 13.2978 | 9.363 | 15.9636 | 15.9636 | 13.087 | 9.2432 | 16.2157 | 16.2157 | 12.8738 | 9.0832 | 16.5459 | 16.5459 | 12.6045 | 8.8302 | 16.9643 | 16.9643 | 12.3167 | 8.3088 | 17.3914 | 16.7571 | 12.0437 | 7.7458 | 17.8542 | 16.2603 | 11.6866 | 7.187 | 19.309 | 15.6298 | 11.2334 | 5.4659 | 20.0674 | 14.604 | 10.4962 | 3.5234 | 20.4935 | 13.5084 | 9.7088 | 2.0713 | 20.6991 | 12.3 | 8.8403 | 1.2277 | 20.519 | 11.5355 | 8.2908 | 1.3697 | 15.2847 | 15.2847 | 13.787 | 9.7791 | 15.3989 | 15.3989 | 13.7026 | 9.4961 | 15.5397 | 15.5397 | 13.5818 | 9.3574 | 15.7177 | 15.7177 | 13.4636 | 9.2967 | 15.9618 | 15.9618 | 13.2881 | 9.229 | 16.2548 | 16.2548 | 13.0598 | 9.1231 | 16.5301 | 16.5301 | 12.8369 | 8.9671 | 16.7592 | 16.7592 | 12.6208 | 8.7561 | 17.0151 | 17.0151 | 12.534 | 8.4692 | 17.2885 | 17.2543 | 12.401 | 8.1682 | 18.244 | 16.6762 | 11.9855 | 7.0531 | 19.2751 | 15.8954 | 11.4243 | 5.3427 | 20.0015 | 15.1148 | 10.8633 | 4.1617 | 20.6408 | 14.4653 | 10.3965 | 3.2527 | 20.9398 | 13.7549 | 9.8859 | 3.0274 | 15.2847 | 15.2847 | 13.787 | 9.7791 | 15.372 | 15.372 | 13.6291 | 9.2837 | 15.5694 | 15.5694 | 13.4438 | 9.0748 | 15.8431 | 15.8431 | 13.2341 | 8.9583 | 16.12 | 16.12 | 13.0179 | 8.7905 | 16.3521 | 16.3521 | 12.8034 | 8.6105 | 16.6485 | 16.6485 | 12.5383 | 8.3482 | 17.047 | 17.047 | 12.2525 | 7.7943 | 17.4286 | 16.6717 | 11.9823 | 7.2221 | 17.8473 | 16.237 | 11.6698 | 6.6563 | 19.2715 | 15.4165 | 11.0802 | 4.6622 | 20.5428 | 14.3664 | 10.3254 | 2.4113 | 21.0851 | 13.2756 | 9.5414 | 0.74059 | 21.3438 | 11.9563 | 8.5932 | -0.27524 | 21.2544 | 11.2692 | 8.0994 | 0.008249
BURY TOWN CENTRE | BURY | KEARSLEY | 380863 | 410807 | 29.7714 | 7.1702 | 5.2306 | 14.417 | 29.8593 | 6.8471 | 4.9949 | 12.7518 | 29.9807 | 6.628 | 4.835 | 12.0823 | 30.1307 | 6.4437 | 4.7006 | 11.7415 | 30.3109 | 6.2203 | 4.5376 | 11.3524 | 30.5156 | 5.955 | 4.3441 | 10.9467 | 30.75 | 5.9322 | 4.3274 | 10.5464 | 31.0334 | 5.8253 | 4.2495 | 10.1451 | 31.2439 | 5.6963 | 4.1553 | 9.7123 | 31.4448 | 5.563 | 4.0581 | 9.3022 | 31.3892 | 5.0916 | 3.7143 | 7.3778 | 28.3538 | 4.5993 | 3.3551 | 4.5047 | 26.7581 | 4.3404 | 3.1663 | 2.0317 | 25.2204 | 4.091 | 2.9843 | -0.68033 | 22.0007 | 3.5687 | 2.6033 | -3.0079 | 29.7473 | 7.1702 | 5.2306 | 14.417 | 29.8387 | 7.0787 | 5.1638 | 13.9832 | 29.9392 | 6.9907 | 5.0996 | 13.7182 | 30.0629 | 6.8841 | 5.0218 | 13.5288 | 30.223 | 6.7573 | 4.9293 | 13.3224 | 30.4209 | 6.6206 | 4.8296 | 13.0863 | 30.6567 | 6.4211 | 4.6841 | 12.7937 | 30.9272 | 6.2848 | 4.5847 | 12.4405 | 31.0414 | 6.1643 | 4.4968 | 12.1496 | 31.1599 | 6.0409 | 4.4067 | 11.858 | 31.5285 | 5.6811 | 4.1443 | 10.9813 | 31.8908 | 5.3522 | 3.9043 | 10.1055 | 32.0146 | 5.1931 | 3.7883 | 9.3128 | 32.5446 | 5.3168 | 3.8786 | 8.456 | 31.6523 | 5.1343 | 3.7454 | 7.7788 | 29.7816 | 7.1702 | 5.2306 | 14.417 | 29.8787 | 6.7816 | 4.9471 | 12.4982 | 30.0148 | 6.4974 | 4.7398 | 11.7778 | 30.1868 | 6.2539 | 4.5622 | 11.4361 | 30.394 | 5.9304 | 4.3262 | 11.0475 | 30.6309 | 5.8772 | 4.2874 | 10.6429 | 30.9041 | 5.7396 | 4.187 | 10.2426 | 31.2351 | 5.5251 | 4.0305 | 9.8432 | 31.4733 | 5.435 | 3.9648 | 9.4484 | 31.6991 | 5.3113 | 3.8745 | 9.08 | 29.23 | 4.7414 | 3.4588 | 7.2851 | 25.5632 | 4.1466 | 3.0249 | 4.5585 | 23.497 | 3.8114 | 2.7804 | 2.2431 | 21.4987 | 3.4873 | 2.5439 | -0.24369 | 18.0171 | 2.9225 | 2.132 | -2.2773 | 29.7816 | 7.1702 | 5.2306 | 14.417 | 29.7799 | 6.916 | 5.0451 | 13.2258 | 29.8368 | 6.7003 | 4.8878 | 12.7033 | 29.9173 | 6.4438 | 4.7007 | 12.4336 | 30.0397 | 6.2338 | 4.5475 | 12.0987 | 30.2298 | 6.1401 | 4.4791 | 11.7134 | 30.4701 | 5.9847 | 4.3658 | 11.1967 | 30.7522 | 5.8237 | 4.2483 | 10.2904 | 30.9756 | 5.6284 | 4.1058 | 9.3546 | 31.194 | 5.4594 | 3.9826 | 8.4389 | 31.8626 | 5.7045 | 4.1613 | 5.7657 | 30.3268 | 4.9193 | 3.5886 | 3.1421 | 25.8597 | 4.1947 | 3.06 | 0.83045 | 21.5828 | 3.5009 | 2.5539 | -0.96744 | 19.7204 | 3.1988 | 2.3335 | -0.82353 | 29.7714 | 7.1702 | 5.2306 | 14.417 | 29.8477 | 7.0244 | 5.1242 | 13.7445 | 29.9334 | 6.8506 | 4.9974 | 13.3156 | 30.0285 | 6.685 | 4.8766 | 13.0504 | 30.1503 | 6.4861 | 4.7315 | 12.7876 | 30.3327 | 6.2224 | 4.5391 | 12.4816 | 30.5682 | 6.2069 | 4.5279 | 12.134 | 30.8259 | 6.1131 | 4.4595 | 11.764 | 31.0126 | 5.9887 | 4.3687 | 11.3325 | 31.1983 | 5.8573 | 4.2728 | 10.9023 | 31.7882 | 5.4891 | 4.0042 | 9.5256 | 32.2991 | 5.2724 | 3.8462 | 8.0564 | 32.5336 | 5.2773 | 3.8497 | 6.8665 | 32.8956 | 5.3363 | 3.8927 | 5.55 | 31.6062 | 5.1268 | 3.7399 | 4.7523 | 29.7714 | 7.1702 | 5.2306 | 14.417 | 29.8099 | 6.7678 | 4.937 | 12.4154 | 29.9242 | 6.5082 | 4.7477 | 11.6619 | 30.0725 | 6.2351 | 4.5484 | 11.3029 | 30.253 | 6.0226 | 4.3934 | 10.8894 | 30.4557 | 5.9137 | 4.3139 | 10.4672 | 30.6944 | 5.7468 | 4.1922 | 9.9203 | 31.0087 | 5.5708 | 4.0638 | 8.9452 | 31.247 | 5.365 | 3.9137 | 7.9663 | 31.4761 | 5.1864 | 3.7834 | 7.0116 | 32.1429 | 5.3931 | 3.9342 | 4.2485 | 28.2622 | 4.5844 | 3.3443 | 1.5778 | 23.7626 | 3.8545 | 2.8118 | -0.70021 | 19.2706 | 3.1259 | 2.2803 | -2.6815 | 17.227 | 2.7944 | 2.0385 | -2.6832
CRAGGS ROW & BUSHELL ST | RIBBLE | PENWORTHAM EAST / ROCHDALE | 353809 | 430094 | 32.3756 | 12.4245 | 9.0635 | 10.2347 | 32.4289 | 11.9479 | 8.7158 | 7.6468 | 32.5293 | 11.7456 | 8.5683 | 7.0159 | 32.6126 | 11.6123 | 8.471 | 6.8463 | 32.6953 | 11.5102 | 8.3965 | 6.6279 | 32.7879 | 11.3291 | 8.2644 | 6.4062 | 32.8948 | 11.1438 | 8.1292 | 6.2189 | 33.0218 | 11.0084 | 8.0305 | 6.0586 | 33.1235 | 10.8482 | 7.9136 | 5.8232 | 33.2162 | 10.6405 | 7.7621 | 5.6218 | 33.512 | 10.2611 | 7.4854 | 4.0183 | 33.8347 | 9.6088 | 7.0095 | 1.0623 | 34.0591 | 8.9866 | 6.5556 | -1.3611 | 34.2422 | 8.3208 | 6.0699 | -3.9052 | 34.3205 | 7.681 | 5.6032 | -6.0183 | 32.3652 | 12.4245 | 9.0635 | 10.2347 | 32.4478 | 12.2851 | 8.9618 | 9.4258 | 32.5732 | 12.1658 | 8.8748 | 9.0737 | 32.7013 | 12.0199 | 8.7683 | 8.8513 | 32.8475 | 11.9292 | 8.7022 | 8.609 | 33.0252 | 11.8369 | 8.6349 | 8.3639 | 33.1975 | 11.5914 | 8.4557 | 8.0524 | 33.3268 | 11.4304 | 8.3383 | 7.6659 | 33.4198 | 11.2872 | 8.2338 | 7.3528 | 33.5114 | 11.1915 | 8.164 | 7.0447 | 33.7722 | 10.8191 | 7.8924 | 6.1703 | 34.0061 | 10.5172 | 7.6721 | 5.3514 | 34.1982 | 10.2687 | 7.4909 | 4.6726 | 34.3826 | 10.0302 | 7.3169 | 3.9915 | 34.4998 | 9.7647 | 7.1232 | 3.5431 | 32.38 | 12.4245 | 9.0635 | 10.2347 | 32.439 | 11.8546 | 8.6478 | 7.2637 | 32.5449 | 11.5663 | 8.4375 | 6.5832 | 32.6344 | 11.449 | 8.3519 | 6.4546 | 32.7269 | 11.2828 | 8.2307 | 6.27 | 32.8312 | 11.0926 | 8.0919 | 6.085 | 32.9534 | 10.884 | 7.9397 | 5.9533 | 33.0981 | 10.6798 | 7.7908 | 5.8488 | 33.1933 | 10.5199 | 7.6741 | 5.7268 | 33.2762 | 10.4953 | 7.6562 | 5.607 | 33.5685 | 9.9762 | 7.2775 | 4.2653 | 33.8691 | 9.1959 | 6.7083 | 1.5633 | 34.0617 | 8.5412 | 6.2307 | -0.61041 | 34.1906 | 7.8173 | 5.7026 | -2.8299 | 34.19 | 7.2087 | 5.2587 | -4.5459 | 32.38 | 12.4245 | 9.0635 | 10.2347 | 32.3494 | 12.0537 | 8.793 | 8.3274 | 32.396 | 11.9053 | 8.6848 | 7.8792 | 32.4273 | 11.7524 | 8.5732 | 7.8065 | 32.4632 | 11.6388 | 8.4904 | 7.657 | 32.5266 | 11.4663 | 8.3645 | 7.4837 | 32.6158 | 11.2922 | 8.2375 | 7.161 | 32.732 | 10.9951 | 8.0208 | 6.2472 | 32.8396 | 10.6906 | 7.7987 | 5.2811 | 32.9396 | 10.3988 | 7.5858 | 4.3175 | 33.2272 | 9.6977 | 7.0743 | 1.6137 | 33.509 | 8.946 | 6.526 | -0.94309 | 33.6851 | 8.2722 | 6.0345 | -2.9318 | 33.7665 | 7.7449 | 5.6498 | -4.0561 | 33.6276 | 7.6378 | 5.5717 | -2.7695 | 32.3756 | 12.4245 | 9.0635 | 10.2347 | 32.4222 | 12.1679 | 8.8763 | 8.8576 | 32.5019 | 12.0129 | 8.7632 | 8.4701 | 32.5623 | 11.9018 | 8.6822 | 8.3667 | 32.6168 | 11.8219 | 8.6239 | 8.2742 | 32.698 | 11.668 | 8.5116 | 8.1761 | 32.8055 | 11.494 | 8.3847 | 8.0632 | 32.9228 | 11.366 | 8.2913 | 7.9227 | 33.0161 | 11.2056 | 8.1743 | 7.664 | 33.1054 | 11.0002 | 8.0245 | 7.4107 | 33.3738 | 10.7413 | 7.8356 | 6.581 | 33.64 | 10.4918 | 7.6536 | 5.7055 | 33.8193 | 10.2169 | 7.4531 | 5.1504 | 33.9599 | 9.9351 | 7.2475 | 4.6638 | 33.9763 | 9.724 | 7.0935 | 4.7022 | 32.3756 | 12.4245 | 9.0635 | 10.2347 | 32.3804 | 11.8116 | 8.6164 | 7.0474 | 32.4736 | 11.603 | 8.4642 | 6.3018 | 32.5529 | 11.4443 | 8.3485 | 6.1318 | 32.6363 | 11.2972 | 8.2411 | 5.8919 | 32.7275 | 11.1119 | 8.106 | 5.6552 | 32.8396 | 10.9273 | 7.9713 | 5.2573 | 32.9982 | 10.6108 | 7.7404 | 4.241 | 33.1179 | 10.2942 | 7.5095 | 3.2123 | 33.2277 | 9.992 | 7.289 | 2.1862 | 33.5254 | 9.2402 | 6.7406 | -0.70269 | 33.7871 | 8.4535 | 6.1667 | -3.4055 | 33.9494 | 7.7498 | 5.6534 | -5.5519 | 34.0149 | 7.1712 | 5.2313 | -6.8962 | 33.8859 | 7.0172 | 5.119 | -5.8837
CAMPBELL ST | KEARSLEY LOCAL | KEARSLEY | 372937 | 406428 | 22.0698 | 10.7429 | 7.7211 | 9.0849 | 22.4093 | 10.5066 | 7.5513 | 8.3227 | 22.5515 | 10.3197 | 7.417 | 8.1322 | 22.7008 | 10.1219 | 7.2748 | 8.0817 | 22.9055 | 10.0311 | 7.2095 | 7.9327 | 23.1571 | 9.9127 | 7.1245 | 7.6586 | 23.4416 | 9.78 | 7.0291 | 7.2852 | 23.7189 | 9.7175 | 6.9841 | 6.8138 | 23.9468 | 9.6088 | 6.9061 | 6.2698 | 24.0982 | 9.4624 | 6.8008 | 5.5546 | 24.6317 | 8.6624 | 6.2259 | 1.5121 | 25.2277 | 7.8212 | 5.6212 | -2.8748 | 25.6675 | 7.1741 | 5.1562 | -6.1275 | 26.0056 | 7.6539 | 5.501 | -8.8865 | 26.2196 | 8.3 | 5.9654 | -10.6548 | 22.0435 | 10.7429 | 7.7211 | 9.0849 | 22.2743 | 10.6509 | 7.655 | 8.8116 | 22.4035 | 10.5842 | 7.6071 | 8.701 | 22.5113 | 10.5173 | 7.559 | 8.6318 | 22.6405 | 10.4533 | 7.513 | 8.5257 | 22.7863 | 10.3587 | 7.445 | 8.3943 | 22.9676 | 10.3003 | 7.403 | 8.2081 | 23.1849 | 10.1946 | 7.3271 | 7.8995 | 23.3756 | 10.0878 | 7.2503 | 7.5835 | 23.5875 | 9.962 | 7.1599 | 7.1699 | 24.2226 | 9.5278 | 6.8478 | 5.5977 | 24.7282 | 8.886 | 6.3865 | 2.7803 | 25.0829 | 8.19 | 5.8863 | -0.048127 | 25.4181 | 8.5121 | 6.1178 | -2.7184 | 25.6237 | 9.1893 | 6.6045 | -4.2534 | 22.0756 | 10.7429 | 7.7211 | 9.0849 | 22.3554 | 10.458 | 7.5163 | 8.2211 | 22.5033 | 10.2053 | 7.3348 | 8.0243 | 22.6305 | 9.9886 | 7.179 | 7.9957 | 22.8054 | 9.9387 | 7.1431 | 7.8762 | 23.0168 | 9.7837 | 7.0318 | 7.7403 | 23.2713 | 9.8212 | 7.0587 | 7.6094 | 23.5415 | 9.7344 | 6.9963 | 7.2701 | 23.7858 | 9.62 | 6.9141 | 6.8744 | 24.0155 | 9.495 | 6.8243 | 6.4374 | 24.5539 | 8.6308 | 6.2031 | 2.4484 | 25.1698 | 7.5885 | 5.454 | -2.5271 | 25.6086 | 6.7886 | 4.8791 | -6.38 | 25.8995 | 7.0439 | 5.0626 | -9.7348 | 26.0614 | 7.6177 | 5.475 | -11.8495 | 22.0763 | 10.7429 | 7.7211 | 9.0849 | 22.3354 | 10.5676 | 7.5951 | 8.71 | 22.438 | 10.3379 | 7.43 | 8.6223 | 22.5608 | 10.1884 | 7.3226 | 8.6033 | 22.7465 | 10.0321 | 7.2103 | 8.469 | 22.9965 | 10.0565 | 7.2278 | 8.2591 | 23.3277 | 10.0125 | 7.1962 | 7.7832 | 23.5963 | 9.7872 | 7.0342 | 6.7183 | 23.7813 | 9.5175 | 6.8404 | 5.5325 | 23.9726 | 9.2114 | 6.6204 | 4.2092 | 24.559 | 8.1313 | 5.8442 | -0.22224 | 25.1015 | 7.2858 | 5.2364 | -4.5778 | 25.4104 | 6.7709 | 4.8664 | -7.7474 | 25.6066 | 8.1583 | 5.8636 | -9.9249 | 25.5395 | 7.968 | 5.7267 | -9.9884 | 22.0689 | 10.7429 | 7.7211 | 9.0849 | 22.3327 | 10.5896 | 7.6109 | 8.6587 | 22.4574 | 10.4269 | 7.494 | 8.5659 | 22.553 | 10.2535 | 7.3694 | 8.584 | 22.6718 | 10.147 | 7.2928 | 8.5758 | 22.8359 | 10.1047 | 7.2625 | 8.5388 | 23.052 | 9.971 | 7.1664 | 8.4066 | 23.3135 | 9.9504 | 7.1516 | 8.1061 | 23.5424 | 9.8672 | 7.0918 | 7.6675 | 23.7927 | 9.7674 | 7.02 | 7.1866 | 24.3889 | 9.2352 | 6.6375 | 4.6096 | 24.888 | 8.5834 | 6.1691 | 1.0423 | 25.2511 | 8.0848 | 5.8107 | -1.6028 | 25.5151 | 8.7088 | 6.2592 | -3.7736 | 25.5985 | 9.517 | 6.8401 | -4.7608 | 22.0689 | 10.7429 | 7.7211 | 9.0849 | 22.288 | 10.4756 | 7.529 | 8.3431 | 22.417 | 10.2101 | 7.3382 | 8.1355 | 22.54 | 10.0773 | 7.2427 | 8.0578 | 22.7126 | 9.8898 | 7.108 | 7.8727 | 22.9173 | 9.9336 | 7.1395 | 7.6762 | 23.1886 | 9.8405 | 7.0725 | 6.9641 | 23.5629 | 9.5646 | 6.8742 | 5.6474 | 23.8953 | 9.264 | 6.6582 | 4.2869 | 24.0957 | 8.94 | 6.4254 | 2.8974 | 24.7138 | 7.8584 | 5.648 | -1.7368 | 25.3054 | 6.9124 | 4.9681 | -6.3372 | 25.7069 | 6.3756 | 4.5823 | -9.6071 | 25.9102 | 7.7016 | 5.5353 | -12.0831 | 25.8665 | 7.4488 | 5.3536 | -12.5022
CANNON ST | RED BANK | WHITEGATE | 384064 | 398635 | 3.0315 | 0.49174 | 0.35872 | 3.0315 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 3.0315 | 0.49174 | 0.35872 | 3.0315 | 1.325 | 0.21492 | 0.15678 | 1.325 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 3.0315 | 0.49174 | 0.35872 | 3.0315 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 3.0315 | 0.49174 | 0.35872 | 3.0315 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 3.0315 | 0.49174 | 0.35872 | 3.0315 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 3.0315 | 0.49174 | 0.35872 | 3.0315 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914
CAPONTREE | CARLISLE | HARKER / HUTTON | 352906 | 559671 | 18.8856 | 18.8856 | 15.888 | 17.7443 | 18.9358 | 18.9358 | 15.7581 | 17.2113 | 19.0105 | 19.0105 | 15.6828 | 17.0234 | 19.1123 | 19.1123 | 15.6166 | 16.9125 | 19.2513 | 19.2513 | 15.5305 | 16.7109 | 19.433 | 19.433 | 15.4403 | 16.4793 | 19.6339 | 19.6339 | 15.3558 | 16.2549 | 19.8318 | 19.8318 | 15.2748 | 16.0172 | 20.0427 | 20.0427 | 15.1881 | 15.7409 | 20.2733 | 20.2733 | 15.1379 | 15.4657 | 21.1055 | 20.7289 | 14.8982 | 14.0574 | 21.8193 | 20.4792 | 14.7188 | 12.0114 | 22.1844 | 20.7463 | 14.9108 | 10.4339 | 22.4639 | 22.4639 | 18.6168 | 9.0258 | 22.648 | 22.648 | 18.2817 | 7.7795 | 18.8749 | 18.8749 | 15.888 | 17.7443 | 18.9435 | 18.9435 | 15.8359 | 17.5318 | 19.0274 | 19.0274 | 15.7775 | 17.3769 | 19.1324 | 19.1324 | 15.7094 | 17.2277 | 19.2671 | 19.2671 | 15.6313 | 17.048 | 19.4349 | 19.4349 | 15.5532 | 16.8734 | 19.569 | 19.569 | 15.4736 | 16.6472 | 19.7174 | 19.7174 | 15.3931 | 16.3553 | 19.8077 | 19.8077 | 15.3257 | 16.1437 | 19.9122 | 19.9122 | 15.2529 | 15.9198 | 20.3146 | 20.3146 | 15.0254 | 15.1868 | 20.8225 | 20.5867 | 14.7961 | 14.3814 | 21.3587 | 20.3889 | 14.6539 | 13.5552 | 21.9556 | 21.9556 | 16.7867 | 12.5691 | 22.3592 | 22.3592 | 19.0007 | 11.8265 | 18.8901 | 18.8901 | 15.888 | 17.7443 | 18.9435 | 18.9435 | 15.731 | 17.1504 | 19.0233 | 19.0233 | 15.6242 | 16.964 | 19.1307 | 19.1307 | 15.532 | 16.88 | 19.2742 | 19.2742 | 15.4274 | 16.7082 | 19.457 | 19.457 | 15.3249 | 16.5148 | 19.6134 | 19.6134 | 15.231 | 16.3471 | 19.7911 | 19.7911 | 15.1369 | 16.1768 | 19.9708 | 19.9708 | 15.0407 | 15.989 | 20.1713 | 20.1713 | 14.9804 | 15.7886 | 20.9888 | 20.4347 | 14.6868 | 14.5395 | 21.7501 | 20.0736 | 14.4273 | 12.5466 | 22.1496 | 20.2135 | 14.5279 | 11.0023 | 22.4345 | 22.4345 | 18.1385 | 9.6846 | 22.5545 | 22.5545 | 17.7445 | 8.5922 | 18.8901 | 18.8901 | 15.888 | 17.7443 | 18.8877 | 18.8877 | 15.7814 | 17.4421 | 18.9247 | 18.9247 | 15.7099 | 17.3198 | 18.9871 | 18.9871 | 15.6209 | 17.2083 | 19.0889 | 19.0889 | 15.5235 | 17.0345 | 19.2521 | 19.2521 | 15.4836 | 16.8301 | 19.4785 | 19.4785 | 15.4476 | 16.5364 | 19.771 | 19.771 | 15.4175 | 15.9178 | 20.0683 | 20.0683 | 15.4681 | 15.2479 | 20.3233 | 20.3233 | 15.6804 | 14.5582 | 20.9867 | 20.9867 | 19.0701 | 12.5346 | 21.5043 | 21.5043 | 18.624 | 10.6921 | 21.8423 | 21.8423 | 18.2343 | 9.3861 | 22.0094 | 22.0094 | 17.6341 | 8.7263 | 21.9839 | 21.9839 | 16.9926 | 9.318 | 18.8856 | 18.8856 | 15.888 | 17.7443 | 18.9296 | 18.9296 | 15.8147 | 17.468 | 18.9869 | 18.9869 | 15.7506 | 17.3331 | 19.0592 | 19.0592 | 15.6883 | 17.2436 | 19.1603 | 19.1603 | 15.615 | 17.1318 | 19.3126 | 19.3126 | 15.5406 | 17.0156 | 19.5101 | 19.5101 | 15.4676 | 16.8717 | 19.677 | 19.677 | 15.3937 | 16.6709 | 19.8587 | 19.8587 | 15.3102 | 16.3992 | 20.0641 | 20.0641 | 15.2603 | 16.1067 | 20.8005 | 20.8005 | 15.0654 | 15.0213 | 21.5137 | 20.8574 | 14.9906 | 13.8139 | 21.9009 | 21.2573 | 15.278 | 13.0101 | 22.1589 | 22.1589 | 19.0834 | 12.3416 | 22.2575 | 22.2575 | 18.8788 | 12.1097 | 18.8856 | 18.8856 | 15.888 | 17.7443 | 18.9081 | 18.9081 | 15.7292 | 17.1824 | 18.9777 | 18.9777 | 15.6425 | 16.9694 | 19.0762 | 19.0762 | 15.5459 | 16.8001 | 19.2068 | 19.2068 | 15.4422 | 16.575 | 19.3722 | 19.3722 | 15.3992 | 16.339 | 19.5851 | 19.5851 | 15.3619 | 16.013 | 19.8427 | 19.8427 | 15.3302 | 15.3524 | 20.0916 | 20.0916 | 15.3819 | 14.6718 | 20.3383 | 20.3383 | 15.594 | 13.97 | 21.1248 | 21.1248 | 18.9638 | 11.8428 | 21.8681 | 21.8681 | 18.4907 | 9.8266 | 22.2567 | 22.2567 | 18.0778 | 8.3434 | 22.4958 | 22.4958 | 17.6598 | 7.5195 | 22.533 | 22.533 | 17.0529 | 7.9717
CARLETON | EGREMONT | HARKER / HUTTON | 308796 | 498305 | 7.9129 | 7.9129 | 7.9129 | 5.1301 | 7.9893 | 7.9893 | 7.9893 | 4.9649 | 8.0527 | 8.0527 | 8.0527 | 4.8922 | 8.1071 | 8.1071 | 8.1071 | 4.8461 | 8.1655 | 8.1655 | 8.1655 | 4.7831 | 8.2264 | 8.2264 | 8.2264 | 4.7164 | 8.2899 | 8.2899 | 8.2899 | 4.5327 | 8.3625 | 8.3625 | 8.3625 | 4.2835 | 8.4174 | 8.4174 | 8.4174 | 4.0663 | 8.4667 | 8.4667 | 8.4667 | 3.8595 | 8.6018 | 8.6018 | 8.6018 | 3.1977 | 8.74 | 8.74 | 8.74 | 2.5089 | 8.8375 | 8.8375 | 8.8375 | 2.0158 | 8.9129 | 8.9129 | 8.9129 | 1.6507 | 8.9561 | 8.9561 | 8.9561 | 1.4188 | 7.9151 | 7.9151 | 7.9151 | 5.1301 | 7.9728 | 7.9728 | 7.9728 | 5.0893 | 8.0289 | 8.0289 | 8.0289 | 5.0398 | 8.0942 | 8.0942 | 8.0942 | 4.9931 | 8.1297 | 8.1297 | 8.1297 | 4.9435 | 8.1719 | 8.1719 | 8.1719 | 4.8952 | 8.2214 | 8.2214 | 8.2214 | 4.7136 | 8.2774 | 8.2774 | 8.2774 | 4.5097 | 8.3134 | 8.3134 | 8.3134 | 4.4031 | 8.3517 | 8.3517 | 8.3517 | 4.2941 | 8.4775 | 8.4775 | 8.4775 | 3.9708 | 8.6035 | 8.6035 | 8.6035 | 3.5669 | 8.7109 | 8.7109 | 8.7109 | 3.1986 | 8.7759 | 8.7759 | 8.7759 | 2.8432 | 8.815 | 8.815 | 8.815 | 2.6157 | 7.9121 | 7.9121 | 7.9121 | 5.1301 | 7.9825 | 7.9825 | 7.9825 | 4.9419 | 8.0513 | 8.0513 | 8.0513 | 4.8651 | 8.1062 | 8.1062 | 8.1062 | 4.8186 | 8.1639 | 8.1639 | 8.1639 | 4.7554 | 8.224 | 8.224 | 8.224 | 4.6537 | 8.2866 | 8.2866 | 8.2866 | 4.4172 | 8.3425 | 8.3425 | 8.3425 | 4.1338 | 8.3752 | 8.3752 | 8.3752 | 3.9013 | 8.4011 | 8.4011 | 8.4011 | 3.6774 | 8.5294 | 8.5294 | 8.5294 | 2.9396 | 8.656 | 8.656 | 8.656 | 2.1563 | 8.7166 | 8.7166 | 8.7166 | 1.5902 | 8.7494 | 8.7494 | 8.7494 | 1.1675 | 8.7492 | 8.7492 | 8.7492 | 0.90865 | 7.9121 | 7.9121 | 7.9121 | 5.1301 | 7.9576 | 7.9576 | 7.9576 | 5.012 | 7.9973 | 7.9973 | 7.9973 | 4.9557 | 8.0261 | 8.0261 | 8.0261 | 4.9007 | 8.0582 | 8.0582 | 8.0582 | 4.843 | 8.1037 | 8.1037 | 8.1037 | 4.7748 | 8.1559 | 8.1559 | 8.1559 | 4.6007 | 8.2137 | 8.2137 | 8.2137 | 4.307 | 8.2667 | 8.2667 | 8.2667 | 4.0498 | 8.3176 | 8.3176 | 8.3176 | 3.7975 | 8.4691 | 8.4691 | 8.4691 | 3.0445 | 8.5847 | 8.5847 | 8.5847 | 2.3081 | 8.6383 | 8.6383 | 8.6383 | 1.8041 | 8.6551 | 8.6551 | 8.6551 | 1.4742 | 8.6079 | 8.6079 | 8.6079 | 1.4604 | 7.9128 | 7.9128 | 7.9128 | 5.1301 | 7.9756 | 7.9756 | 7.9756 | 5.0832 | 8.0368 | 8.0368 | 8.0368 | 5.0362 | 8.0742 | 8.0742 | 8.0742 | 4.999 | 8.1155 | 8.1155 | 8.1155 | 4.9618 | 8.1715 | 8.1715 | 8.1715 | 4.9261 | 8.2376 | 8.2376 | 8.2376 | 4.8429 | 8.3055 | 8.3055 | 8.3055 | 4.6381 | 8.3545 | 8.3545 | 8.3545 | 4.4569 | 8.4024 | 8.4024 | 8.4024 | 4.2728 | 8.5324 | 8.5324 | 8.5324 | 3.6572 | 8.6613 | 8.6613 | 8.6613 | 3.0006 | 8.7521 | 8.7521 | 8.7521 | 2.5312 | 8.8263 | 8.8263 | 8.8263 | 2.1184 | 8.853 | 8.853 | 8.853 | 1.9181 | 7.9128 | 7.9128 | 7.9128 | 5.1301 | 7.9779 | 7.9779 | 7.9779 | 4.9313 | 8.0464 | 8.0464 | 8.0464 | 4.8443 | 8.1015 | 8.1015 | 8.1015 | 4.7672 | 8.1608 | 8.1608 | 8.1608 | 4.6903 | 8.2221 | 8.2221 | 8.2221 | 4.6148 | 8.2885 | 8.2885 | 8.2885 | 4.4885 | 8.3718 | 8.3718 | 8.3718 | 4.1996 | 8.4332 | 8.4332 | 8.4332 | 3.9417 | 8.4843 | 8.4843 | 8.4843 | 3.6885 | 8.6324 | 8.6324 | 8.6324 | 2.9399 | 8.7678 | 8.7678 | 8.7678 | 2.2513 | 8.8608 | 8.8608 | 8.8608 | 1.7768 | 8.9188 | 8.9188 | 8.9188 | 1.4749 | 8.9117 | 8.9117 | 8.9117 | 1.4553
CARLISLE NORTH | - | HARKER / HUTTON | 338547 | 560280 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795
CARR ST | KEARSLEY LOCAL | KEARSLEY | 376984 | 401329 | 30.1023 | 14.4393 | 10.3778 | 15.1463 | 30.1444 | 14.3597 | 10.3206 | 15.0637 | 30.1928 | 14.1828 | 10.1935 | 15.0036 | 30.2649 | 14.1451 | 10.1664 | 14.9497 | 30.3832 | 13.9532 | 10.0285 | 14.7806 | 30.5368 | 13.6533 | 9.8129 | 14.5797 | 30.7312 | 13.4158 | 9.6422 | 14.3713 | 30.9768 | 13.3174 | 9.5715 | 14.1623 | 31.2127 | 13.1802 | 9.4729 | 13.828 | 31.4605 | 13.0391 | 9.3715 | 13.4617 | 32.3404 | 12.4652 | 8.959 | 11.3391 | 33.0744 | 11.6904 | 8.4022 | 7.9979 | 33.5534 | 10.9833 | 7.8939 | 5.3078 | 33.9456 | 10.221 | 7.3461 | 2.5935 | 34.2009 | 9.5406 | 6.857 | 0.18091 | 30.0745 | 14.4393 | 10.3778 | 15.1463 | 30.1263 | 14.3553 | 10.3175 | 15.0476 | 30.16 | 14.3544 | 10.3168 | 14.9929 | 30.205 | 14.2991 | 10.2771 | 14.9186 | 30.2777 | 14.2102 | 10.2132 | 14.7775 | 30.3729 | 14.0273 | 10.0817 | 14.6062 | 30.4987 | 13.9398 | 10.0188 | 14.3634 | 30.6539 | 13.8418 | 9.9483 | 14.0503 | 30.7607 | 13.7327 | 9.87 | 13.8095 | 30.8801 | 13.6079 | 9.7803 | 13.559 | 31.3197 | 13.2537 | 9.5257 | 12.6495 | 31.8493 | 12.8905 | 9.2646 | 11.5558 | 32.3967 | 12.5214 | 8.9994 | 10.4935 | 32.9858 | 12.0713 | 8.6759 | 9.3957 | 33.3788 | 11.7534 | 8.4474 | 8.6959 | 30.1075 | 14.4393 | 10.3778 | 15.1463 | 30.1531 | 14.336 | 10.3036 | 15.0827 | 30.2077 | 14.1502 | 10.17 | 15.0479 | 30.2873 | 14.0093 | 10.0688 | 15.0332 | 30.4131 | 13.7664 | 9.8942 | 14.9106 | 30.5727 | 13.4983 | 9.7015 | 14.7665 | 30.7718 | 13.3502 | 9.595 | 14.6426 | 31.0186 | 13.2196 | 9.5012 | 14.5077 | 31.2407 | 13.0764 | 9.3982 | 14.2148 | 31.4758 | 12.951 | 9.3081 | 13.9252 | 32.348 | 12.2967 | 8.8379 | 11.9816 | 33.1005 | 11.4444 | 8.2253 | 8.7069 | 33.6359 | 10.7156 | 7.7015 | 6.0582 | 34.0508 | 9.8506 | 7.0798 | 3.43 | 34.2864 | 9.3134 | 6.6938 | 1.3351 | 30.1075 | 14.4393 | 10.3778 | 15.1463 | 30.0458 | 14.4192 | 10.3633 | 15.4351 | 30.0524 | 14.2346 | 10.2307 | 15.4903 | 30.0909 | 14.0711 | 10.1132 | 15.4941 | 30.1859 | 13.7707 | 9.8973 | 15.3551 | 30.3407 | 13.6502 | 9.8107 | 15.1663 | 30.5604 | 13.3851 | 9.6201 | 14.7846 | 30.8209 | 13.0383 | 9.3709 | 13.7528 | 31.0783 | 12.7197 | 9.1419 | 12.6662 | 31.3531 | 12.3794 | 8.8973 | 11.5814 | 32.2151 | 11.3942 | 8.1892 | 8.4013 | 32.9754 | 10.518 | 7.5595 | 5.3683 | 33.4268 | 10.0264 | 7.2062 | 2.9539 | 33.7196 | 9.563 | 6.8731 | 1.4463 | 33.7231 | 9.5505 | 6.8642 | 2.4785 | 30.1023 | 14.4393 | 10.3778 | 15.1463 | 30.1357 | 14.371 | 10.3287 | 15.0889 | 30.1606 | 14.2001 | 10.2059 | 15.0744 | 30.1925 | 14.1961 | 10.203 | 15.1021 | 30.2563 | 14.038 | 10.0894 | 15.0812 | 30.3695 | 13.8066 | 9.9231 | 15.0118 | 30.5334 | 13.5478 | 9.7371 | 14.8932 | 30.7323 | 13.465 | 9.6775 | 14.7463 | 30.9246 | 13.3619 | 9.6034 | 14.5311 | 31.1343 | 13.2299 | 9.5086 | 14.1942 | 31.8766 | 12.823 | 9.2161 | 12.9781 | 32.6365 | 12.4353 | 8.9375 | 11.6416 | 33.0633 | 12.0382 | 8.6521 | 10.7367 | 33.3702 | 11.6312 | 8.3596 | 9.9788 | 33.4993 | 11.2435 | 8.081 | 9.6491 | 30.1023 | 14.4393 | 10.3778 | 15.1463 | 30.062 | 14.3845 | 10.3384 | 15.3721 | 30.0999 | 14.2122 | 10.2146 | 15.3424 | 30.1738 | 14.0029 | 10.0642 | 15.2526 | 30.2955 | 13.6979 | 9.845 | 15.0312 | 30.4452 | 13.5406 | 9.7319 | 14.7923 | 30.6622 | 13.2716 | 9.5386 | 14.3486 | 30.9446 | 12.9005 | 9.2718 | 13.2338 | 31.1874 | 12.5709 | 9.035 | 12.0924 | 31.4463 | 12.2241 | 8.7857 | 10.9511 | 32.2997 | 11.2082 | 8.0556 | 7.5551 | 33.1152 | 10.2984 | 7.4017 | 4.2911 | 33.6344 | 9.7215 | 6.987 | 1.6374 | 33.9526 | 9.2182 | 6.6253 | -0.14484 | 33.9755 | 9.1617 | 6.5847 | 0.59983
CASTLETON | CASTLETON | ROCHDALE | 388461 | 411290 | 28.2335 | 8.8162 | 6.4313 | 14.3874 | 28.277 | 8.5253 | 6.2191 | 13.4585 | 28.3407 | 8.1647 | 5.956 | 13.1696 | 28.4162 | 7.847 | 5.7243 | 13.0438 | 28.5264 | 7.4812 | 5.4574 | 12.8363 | 28.6673 | 7.1464 | 5.2132 | 12.6032 | 28.83 | 6.8553 | 5.0009 | 12.3785 | 29.0296 | 6.7645 | 4.9346 | 12.1637 | 29.2487 | 6.6634 | 4.8609 | 11.871 | 29.4814 | 6.5669 | 4.7904 | 11.5873 | 30.4123 | 6.1103 | 4.4574 | 9.7921 | 31.1622 | 5.5177 | 4.0251 | 6.8044 | 31.3283 | 5.0818 | 3.7071 | 4.3445 | 29.9824 | 4.8634 | 3.5478 | 1.8301 | 26.9304 | 4.3684 | 3.1867 | -0.38336 | 28.2177 | 8.8162 | 6.4313 | 14.3874 | 28.2635 | 8.7153 | 6.3577 | 14.0991 | 28.3155 | 8.5606 | 6.2449 | 13.9363 | 28.3664 | 8.4058 | 6.1319 | 13.8124 | 28.4318 | 8.2315 | 6.0047 | 13.671 | 28.5141 | 8.0317 | 5.859 | 13.5153 | 28.6212 | 7.7846 | 5.6788 | 13.3046 | 28.7568 | 7.6424 | 5.575 | 13.0165 | 28.8766 | 7.558 | 5.5135 | 12.7155 | 29.0091 | 7.5195 | 5.4854 | 12.4061 | 29.4778 | 7.318 | 5.3384 | 11.4275 | 30.0432 | 7.106 | 5.1837 | 10.3599 | 30.6161 | 6.9485 | 5.0689 | 9.3063 | 31.2445 | 6.8566 | 5.0018 | 8.1213 | 31.6897 | 6.8083 | 4.9666 | 7.25 | 28.2368 | 8.8162 | 6.4313 | 14.3874 | 28.2833 | 8.4845 | 6.1893 | 13.3447 | 28.3509 | 8.0757 | 5.8911 | 13.048 | 28.431 | 7.689 | 5.609 | 12.5674 | 28.5446 | 7.2726 | 5.3052 | 12.0335 | 28.6759 | 6.8716 | 5.0127 | 11.4803 | 28.8328 | 6.519 | 4.7556 | 10.9265 | 29.0215 | 6.423 | 4.6855 | 10.7792 | 29.2154 | 6.324 | 4.6133 | 10.5931 | 29.4231 | 6.2238 | 4.5402 | 10.3932 | 30.339 | 5.7525 | 4.1963 | 8.819 | 31.1106 | 5.1369 | 3.7473 | 5.9767 | 28.8339 | 4.6771 | 3.4119 | 3.6485 | 27.3259 | 4.4325 | 3.2335 | 1.3353 | 24.2714 | 3.9371 | 2.872 | -0.60315 | 28.2368 | 8.8162 | 6.4313 | 14.3874 | 28.2023 | 8.5863 | 6.2636 | 13.8471 | 28.2344 | 8.2592 | 6.0249 | 13.669 | 28.2837 | 8.0076 | 5.8414 | 13.2064 | 28.3751 | 7.6651 | 5.5916 | 12.6678 | 28.5143 | 7.3163 | 5.3371 | 12.0901 | 28.7201 | 6.9815 | 5.0929 | 11.339 | 29.0408 | 6.7463 | 4.9213 | 10.4572 | 29.314 | 6.5177 | 4.7546 | 9.5167 | 29.5723 | 6.3027 | 4.5977 | 8.5613 | 30.3791 | 5.869 | 4.2813 | 5.779 | 31.0661 | 5.2344 | 3.8184 | 3.1193 | 28.9802 | 4.7009 | 3.4292 | 1.0248 | 26.5591 | 4.3081 | 3.1427 | -0.25867 | 26.3475 | 4.2738 | 3.1177 | 0.50686 | 28.2335 | 8.8162 | 6.4313 | 14.3874 | 28.2702 | 8.6378 | 6.3012 | 13.9788 | 28.3168 | 8.3083 | 6.0608 | 13.8221 | 28.3615 | 8.0033 | 5.8383 | 13.7605 | 28.426 | 7.6595 | 5.5875 | 13.6889 | 28.5273 | 7.3518 | 5.363 | 13.5865 | 28.6563 | 7.0779 | 5.1632 | 13.4529 | 28.8185 | 6.9976 | 5.1046 | 13.2896 | 29.0059 | 6.8995 | 5.0331 | 13.0116 | 29.2116 | 6.803 | 4.9627 | 12.7244 | 29.9358 | 6.4888 | 4.7335 | 11.706 | 30.6721 | 6.2294 | 4.5442 | 10.5733 | 31.1844 | 6.1007 | 4.4504 | 9.7924 | 31.4973 | 6.2276 | 4.5429 | 9.0891 | 31.6317 | 6.0792 | 4.4347 | 8.7258 | 28.2335 | 8.8162 | 6.4313 | 14.3874 | 28.2142 | 8.4818 | 6.1874 | 13.4055 | 28.2685 | 8.1103 | 5.9163 | 13.0873 | 28.3428 | 7.8604 | 5.734 | 12.5592 | 28.452 | 7.5059 | 5.4754 | 11.9626 | 28.5845 | 7.1497 | 5.2156 | 11.3501 | 28.7715 | 6.8084 | 4.9666 | 10.5573 | 29.0817 | 6.5621 | 4.787 | 9.6204 | 29.348 | 6.3298 | 4.6175 | 8.6478 | 29.5862 | 6.1085 | 4.4561 | 7.6583 | 30.3826 | 5.6473 | 4.1196 | 4.7269 | 30.6877 | 4.9778 | 3.6313 | 1.8871 | 27.1663 | 4.4066 | 3.2146 | -0.4034 | 24.4878 | 3.9722 | 2.8976 | -1.9179 | 23.9958 | 3.8924 | 2.8394 | -1.3997
CATTERALL WATERWORKS | RIBBLE | PENWORTHAM EAST / ROCHDALE | 349381 | 442178 | 8.6255 | 8.6255 | 8.6255 | -0.83623 | 8.6793 | 8.6793 | 8.6793 | -0.99633 | 8.7541 | 8.7541 | 8.7541 | -1.1238 | 8.8427 | 8.8427 | 8.8427 | -1.1806 | 8.9457 | 8.9457 | 8.9457 | -1.2152 | 9.0656 | 9.0656 | 9.0656 | -1.2489 | 9.2073 | 9.2073 | 9.2073 | -1.2771 | 9.3823 | 9.3823 | 9.3823 | -1.3091 | 9.5737 | 9.5737 | 9.5737 | -1.4195 | 9.7731 | 9.7731 | 9.7731 | -1.5263 | 10.3819 | 10.3819 | 10.3819 | -1.937 | 10.6094 | 10.6094 | 10.6094 | -2.4169 | 10.7437 | 10.7437 | 10.7437 | -2.7214 | 10.8376 | 10.8376 | 10.8376 | -2.9821 | 10.8807 | 10.8807 | 10.8807 | -3.1366 | 8.6224 | 8.6224 | 8.6224 | -0.83623 | 8.6525 | 8.6525 | 8.6525 | -0.86161 | 8.6882 | 8.6882 | 8.6882 | -0.95213 | 8.7307 | 8.7307 | 8.7307 | -0.99274 | 8.785 | 8.785 | 8.785 | -1.0042 | 8.8528 | 8.8528 | 8.8528 | -1.0148 | 8.9329 | 8.9329 | 8.9329 | -1.0298 | 9.0272 | 9.0272 | 9.0272 | -1.0589 | 9.1334 | 9.1334 | 9.1334 | -1.1951 | 9.25 | 9.25 | 9.25 | -1.3459 | 9.6625 | 9.6625 | 9.6625 | -1.8181 | 10.1253 | 10.1253 | 10.1253 | -2.2975 | 10.5549 | 10.5549 | 10.5549 | -2.7237 | 10.8787 | 10.8787 | 10.8787 | -3.1511 | 10.9866 | 10.9866 | 10.9866 | -3.4136 | 8.6271 | 8.6271 | 8.6271 | -0.83623 | 8.6775 | 8.6775 | 8.6775 | -1.0211 | 8.7506 | 8.7506 | 8.7506 | -1.1528 | 8.8381 | 8.8381 | 8.8381 | -1.2111 | 8.9372 | 8.9372 | 8.9372 | -1.245 | 9.0502 | 9.0502 | 9.0502 | -1.2768 | 9.1812 | 9.1812 | 9.1812 | -1.3025 | 9.3425 | 9.3425 | 9.3425 | -1.33 | 9.5144 | 9.5144 | 9.5144 | -1.4027 | 9.695 | 9.695 | 9.695 | -1.4674 | 10.3031 | 10.3031 | 10.3031 | -1.7461 | 10.519 | 10.519 | 10.519 | -2.1089 | 10.6354 | 10.6354 | 10.6354 | -2.3151 | 10.6928 | 10.6928 | 10.6928 | -2.4008 | 10.6789 | 10.6789 | 10.6789 | -2.3182 | 8.6271 | 8.6271 | 8.6271 | -0.83623 | 8.664 | 8.664 | 8.664 | -0.95177 | 8.7184 | 8.7184 | 8.7184 | -1.062 | 8.7852 | 8.7852 | 8.7852 | -1.1111 | 8.8696 | 8.8696 | 8.8696 | -1.1365 | 8.9883 | 8.9883 | 8.9883 | -1.1668 | 9.1355 | 9.1355 | 9.1355 | -1.2126 | 9.3089 | 9.3089 | 9.3089 | -1.3123 | 9.4951 | 9.4951 | 9.4951 | -1.462 | 9.6884 | 9.6884 | 9.6884 | -1.6043 | 10.2824 | 10.2824 | 10.2824 | -2.001 | 10.4716 | 10.4716 | 10.4716 | -2.3378 | 10.5688 | 10.5688 | 10.5688 | -2.5119 | 10.6014 | 10.6014 | 10.6014 | -2.4881 | 10.5393 | 10.5393 | 10.5393 | -2.1311 | 8.6255 | 8.6255 | 8.6255 | -0.83623 | 8.667 | 8.667 | 8.667 | -0.87318 | 8.7216 | 8.7216 | 8.7216 | -0.97307 | 8.7808 | 8.7808 | 8.7808 | -1.0178 | 8.8511 | 8.8511 | 8.8511 | -1.0316 | 8.9497 | 8.9497 | 8.9497 | -1.0484 | 9.0739 | 9.0739 | 9.0739 | -1.0672 | 9.2156 | 9.2156 | 9.2156 | -1.091 | 9.3711 | 9.3711 | 9.3711 | -1.1977 | 9.5392 | 9.5392 | 9.5392 | -1.3039 | 10.1085 | 10.1085 | 10.1085 | -1.6323 | 10.5088 | 10.5088 | 10.5088 | -2.0173 | 10.636 | 10.636 | 10.636 | -2.2543 | 10.7191 | 10.7191 | 10.7191 | -2.3747 | 10.7286 | 10.7286 | 10.7286 | -2.3059 | 8.6255 | 8.6255 | 8.6255 | -0.83623 | 8.6694 | 8.6694 | 8.6694 | -1.03 | 8.7396 | 8.7396 | 8.7396 | -1.165 | 8.824 | 8.824 | 8.824 | -1.2284 | 8.9187 | 8.9187 | 8.9187 | -1.2656 | 9.026 | 9.026 | 9.026 | -1.2994 | 9.1519 | 9.1519 | 9.1519 | -1.346 | 9.3128 | 9.3128 | 9.3128 | -1.4519 | 9.487 | 9.487 | 9.487 | -1.6037 | 9.6703 | 9.6703 | 9.6703 | -1.7476 | 10.2748 | 10.2748 | 10.2748 | -2.1555 | 10.5739 | 10.5739 | 10.5739 | -2.5104 | 10.6878 | 10.6878 | 10.6878 | -2.7037 | 10.7276 | 10.7276 | 10.7276 | -2.6916 | 10.6701 | 10.6701 | 10.6701 | -2.3457
CECIL ST | BLACKPOOL | PENWORTHAM WEST / STANAH | 331301 | 437023 | 30.8253 | 16.3887 | 11.9553 | 15.9949 | 30.869 | 16.0867 | 11.735 | 13.4685 | 30.9302 | 16.0075 | 11.6772 | 12.424 | 31.0017 | 15.8881 | 11.5901 | 11.5745 | 31.0932 | 15.822 | 11.5419 | 10.6324 | 31.2022 | 15.5378 | 11.3346 | 9.6683 | 31.3314 | 15.16 | 11.059 | 8.7245 | 31.488 | 14.8663 | 10.8448 | 7.8098 | 31.5935 | 14.6101 | 10.6579 | 6.9136 | 31.6935 | 14.508 | 10.5834 | 6.7818 | 32.0384 | 13.9459 | 10.1734 | 5.2382 | 32.4425 | 13.2342 | 9.6542 | 2.1726 | 32.7451 | 12.5966 | 9.189 | -0.37596 | 33.0143 | 11.9262 | 8.7 | -3.097 | 33.1884 | 11.3192 | 8.2572 | -5.4137 | 30.8147 | 16.3887 | 11.9553 | 15.9949 | 30.8833 | 16.3358 | 11.9167 | 15.0355 | 30.9652 | 16.3123 | 11.8996 | 14.6129 | 31.0617 | 16.2306 | 11.84 | 14.1704 | 31.1867 | 16.1244 | 11.7626 | 13.6684 | 31.3425 | 16.0068 | 11.6767 | 13.1562 | 31.5344 | 15.6514 | 11.4175 | 12.3981 | 31.7614 | 15.4293 | 11.2554 | 11.5183 | 31.8239 | 15.2732 | 11.1416 | 11.1129 | 31.8896 | 15.2056 | 11.0923 | 10.9372 | 32.0962 | 14.9222 | 10.8855 | 10.3795 | 32.3026 | 14.7023 | 10.7251 | 9.7714 | 32.4827 | 14.5187 | 10.5912 | 9.2138 | 32.6647 | 14.2956 | 10.4285 | 8.4745 | 32.8063 | 13.9994 | 10.2124 | 7.8989 | 30.8297 | 16.3887 | 11.9553 | 15.9949 | 30.8789 | 16.0456 | 11.705 | 13.2197 | 30.9483 | 15.9494 | 11.6348 | 12.1435 | 31.0322 | 15.8006 | 11.5263 | 11.3181 | 31.1389 | 15.6942 | 11.4487 | 10.3984 | 31.2663 | 15.2527 | 11.1266 | 9.4595 | 31.4187 | 14.9391 | 10.8979 | 8.5561 | 31.6031 | 14.6185 | 10.664 | 7.6794 | 31.7224 | 14.355 | 10.4718 | 6.8424 | 31.8346 | 14.2023 | 10.3604 | 6.7573 | 32.2148 | 13.6236 | 9.9382 | 5.3682 | 32.6424 | 12.8356 | 9.3634 | 2.444 | 32.9252 | 12.1327 | 8.8506 | 0.033066 | 33.1746 | 11.4836 | 8.3771 | -2.5281 | 33.3217 | 10.8276 | 7.8986 | -4.7055 | 30.8297 | 16.3887 | 11.9553 | 15.9949 | 30.7884 | 16.1798 | 11.8029 | 14.0087 | 30.8006 | 16.1688 | 11.7949 | 13.112 | 30.8214 | 16.1291 | 11.7659 | 12.338 | 30.8686 | 15.9768 | 11.6549 | 11.4543 | 30.955 | 15.6582 | 11.4224 | 10.5411 | 31.0771 | 15.2783 | 11.1453 | 9.4562 | 31.2378 | 14.7873 | 10.7871 | 7.7406 | 31.3664 | 14.3531 | 10.4704 | 6.0104 | 31.4926 | 14.0324 | 10.2364 | 5.0352 | 31.8798 | 13.3319 | 9.7254 | 2.2188 | 32.2888 | 12.6072 | 9.1967 | -0.52216 | 32.5784 | 11.9605 | 8.725 | -2.7059 | 32.7676 | 11.4423 | 8.347 | -4.0803 | 32.7556 | 11.3755 | 8.2983 | -3.0671 | 30.8253 | 16.3887 | 11.9553 | 15.9949 | 30.8629 | 16.2093 | 11.8245 | 14.1553 | 30.9052 | 16.1457 | 11.7781 | 13.2494 | 30.9469 | 16.0551 | 11.7119 | 12.4466 | 31.0057 | 15.9971 | 11.6696 | 11.611 | 31.0996 | 15.7606 | 11.4971 | 10.7767 | 31.2276 | 15.427 | 11.2538 | 9.9247 | 31.3703 | 15.13 | 11.0371 | 9.0435 | 31.4643 | 14.8709 | 10.8481 | 8.135 | 31.5581 | 14.7567 | 10.7648 | 7.9686 | 31.8619 | 14.3739 | 10.4855 | 7.3304 | 32.1903 | 14.0893 | 10.2779 | 6.5384 | 32.4162 | 13.8156 | 10.0783 | 5.9811 | 32.5948 | 13.5635 | 9.8944 | 5.4089 | 32.6957 | 13.354 | 9.7416 | 5.1079 | 30.8253 | 16.3887 | 11.9553 | 15.9949 | 30.814 | 16.0403 | 11.7012 | 13.1613 | 30.8674 | 15.9865 | 11.6619 | 12.0503 | 30.9369 | 15.9191 | 11.6128 | 11.1894 | 31.0289 | 15.7317 | 11.4761 | 10.2212 | 31.1365 | 15.385 | 11.2231 | 9.2391 | 31.2723 | 14.9887 | 10.934 | 8.0721 | 31.4676 | 14.4783 | 10.5617 | 6.2558 | 31.6068 | 14.0368 | 10.2396 | 4.4792 | 31.7412 | 13.7069 | 9.999 | 3.4559 | 32.1304 | 12.9668 | 9.4591 | 0.48531 | 32.5036 | 12.2052 | 8.9035 | -2.3916 | 32.7753 | 11.5263 | 8.4082 | -4.7377 | 32.9457 | 10.9547 | 7.9913 | -6.3588 | 32.9439 | 10.8234 | 7.8955 | -5.6668
CENTRAL MANCHESTER | STUART ST | STALYBRIDGE | 384852 | 397718 | 42.5063 | 7.7676 | 5.6664 | 25.0542 | 41.8911 | 6.7951 | 4.957 | 20.0248 | 32.8244 | 5.3244 | 3.8841 | 18.545 | 24.9092 | 4.0405 | 2.9475 | 17.9654 | 16.7751 | 2.7211 | 1.985 | 16.7751 | 8.7346 | 1.4168 | 1.0336 | 8.7346 | 1.0648 | 0.17273 | 0.126 | 1.0648 | 0.41354 | 0.06708 | 0.048934 | 0.41354 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 0.94812 | 0.15379 | 0.11219 | 0.94812 | 10.0949 | 1.6375 | 1.1945 | 10.0949 | 22.9902 | 3.7292 | 2.7204 | 13.1733 | 27.7836 | 4.5068 | 3.2876 | 12.5915 | 42.5034 | 7.7676 | 5.6664 | 25.0542 | 42.5911 | 7.4598 | 5.4418 | 23.515 | 38.0476 | 6.1717 | 4.5022 | 23.0039 | 30.4209 | 4.9346 | 3.5997 | 22.7371 | 22.8563 | 3.7075 | 2.7046 | 22.5006 | 15.2286 | 2.4702 | 1.802 | 15.2286 | 6.6106 | 1.0723 | 0.78223 | 6.6106 | 5.8712 | 0.95237 | 0.69474 | 5.8712 | 5.2934 | 0.85865 | 0.62637 | 5.2934 | 4.6615 | 0.75614 | 0.55159 | 4.6615 | 3.0069 | 0.48774 | 0.3558 | 3.0069 | 1.602 | 0.25986 | 0.18957 | 1.602 | 6.7814 | 1.1 | 0.80244 | 6.7814 | 17.1048 | 2.7746 | 2.024 | 17.1048 | 20.1436 | 3.2675 | 2.3836 | 17.676 | 42.5073 | 7.7676 | 5.6664 | 25.0542 | 41.0041 | 6.6513 | 4.852 | 19.2741 | 31.6357 | 5.1316 | 3.7434 | 17.6374 | 23.4189 | 3.7988 | 2.7712 | 17.048 | 15.16 | 2.4591 | 1.7939 | 15.16 | 7.0504 | 1.1436 | 0.83427 | 7.0504 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 7.2061 | 1.1689 | 0.8527 | 7.2061 | 20.5721 | 3.337 | 2.4343 | 13.0252 | 25.3212 | 4.1074 | 2.9963 | 12.7544 | 42.5073 | 7.7676 | 5.6664 | 25.0542 | 42.5311 | 6.9481 | 5.0685 | 20.8208 | 41.0119 | 6.6525 | 4.8529 | 19.5257 | 39.5402 | 6.4138 | 4.6788 | 18.9738 | 38.6011 | 6.2615 | 4.5677 | 18.4625 | 37.0774 | 6.0143 | 4.3874 | 17.9444 | 36.0084 | 5.8409 | 4.2609 | 17.7852 | 34.5843 | 5.6099 | 4.0924 | 17.5542 | 33.7915 | 5.4813 | 3.9985 | 17.2622 | 32.9271 | 5.3411 | 3.8963 | 16.9803 | 30.5783 | 4.9601 | 3.6183 | 16.2239 | 28.7408 | 4.662 | 3.4009 | 15.554 | 27.2605 | 4.4219 | 3.2257 | 15.1079 | 29.0176 | 4.7069 | 3.4336 | 14.8357 | 27.8586 | 4.5189 | 3.2965 | 14.9355 | 42.5063 | 7.7676 | 5.6664 | 25.0542 | 42.5583 | 7.1369 | 5.2063 | 21.8988 | 35.4923 | 5.7572 | 4.1998 | 20.81 | 27.6734 | 4.4889 | 3.2746 | 20.2478 | 19.6037 | 3.1799 | 2.3197 | 19.6037 | 11.6006 | 1.8817 | 1.3727 | 11.6006 | 3.8607 | 0.62625 | 0.45684 | 3.8607 | 3.311 | 0.53707 | 0.39179 | 3.311 | 2.4613 | 0.39924 | 0.29124 | 2.4613 | 2.151 | 0.34891 | 0.25452 | 2.151 | 1.4784 | 0.2398 | 0.17493 | 1.4784 | 4.4139 | 0.71598 | 0.5223 | 4.4139 | 13.9808 | 2.2678 | 1.6543 | 13.9808 | 26.7229 | 4.3347 | 3.1621 | 16.2787 | 32.7537 | 5.313 | 3.8757 | 16.0124 | 42.5063 | 7.7676 | 5.6664 | 25.0542 | 40.2395 | 6.5272 | 4.7615 | 18.5711 | 37.7972 | 6.1311 | 4.4725 | 16.7894 | 36.2249 | 5.876 | 4.2865 | 16.1986 | 35.2564 | 5.7189 | 4.1719 | 15.6503 | 33.7173 | 5.4693 | 3.9898 | 15.1053 | 32.5683 | 5.2829 | 3.8538 | 14.9201 | 31.1879 | 5.059 | 3.6905 | 14.6514 | 30.3074 | 4.9162 | 3.5863 | 14.3495 | 29.4424 | 4.7758 | 3.4839 | 14.058 | 26.9657 | 4.3741 | 3.1908 | 13.2825 | 25.1465 | 4.079 | 2.9756 | 12.606 | 23.6318 | 3.8333 | 2.7963 | 12.152 | 25.3526 | 4.1124 | 3 | 11.8695 | 24.1478 | 3.917 | 2.8574 | 11.9388
CHADDERTON | CHADDERTON | WHITEGATE | 389161 | 403872 | 31.29 | 5.0755 | 3.7025 | 31.29 | 28.1475 | 4.5658 | 3.3307 | 28.1475 | 26.6176 | 4.3176 | 3.1497 | 26.6176 | 25.4993 | 4.1362 | 3.0173 | 25.4993 | 24.269 | 3.9367 | 2.8717 | 24.269 | 22.9364 | 3.7205 | 2.7141 | 22.9364 | 21.9023 | 3.5528 | 2.5917 | 21.9023 | 21.2513 | 3.4472 | 2.5147 | 21.2513 | 20.5047 | 3.3261 | 2.4263 | 20.5047 | 19.8332 | 3.2171 | 2.3469 | 19.8332 | 16.7088 | 2.7103 | 1.9771 | 16.7088 | 12.742 | 2.0669 | 1.5078 | 12.742 | 11.387 | 1.8471 | 1.3474 | 11.387 | 10.9029 | 1.7686 | 1.2901 | 10.9029 | 9.0015 | 1.4601 | 1.0652 | 9.0015 | 31.29 | 5.0755 | 3.7025 | 31.29 | 30.4409 | 4.9378 | 3.6021 | 30.4409 | 29.2221 | 4.7401 | 3.4578 | 29.2221 | 27.924 | 4.5295 | 3.3042 | 27.924 | 27.2247 | 4.4161 | 3.2215 | 27.2247 | 26.2985 | 4.2659 | 3.1119 | 26.2985 | 24.3236 | 3.9455 | 2.8782 | 24.3236 | 23.739 | 3.8507 | 2.809 | 23.739 | 23.1422 | 3.7539 | 2.7384 | 23.1422 | 22.5578 | 3.6591 | 2.6693 | 22.5578 | 20.7424 | 3.3646 | 2.4544 | 20.7424 | 18.9626 | 3.0759 | 2.2438 | 18.9626 | 17.7177 | 2.874 | 2.0965 | 17.7177 | 17.1317 | 2.7789 | 2.0272 | 17.1317 | 15.3817 | 2.4951 | 1.8201 | 15.3817 | 31.29 | 5.0755 | 3.7025 | 31.29 | 27.4014 | 4.4448 | 3.2424 | 27.4014 | 25.7233 | 4.1726 | 3.0438 | 25.7233 | 24.291 | 3.9402 | 2.8744 | 24.291 | 22.6716 | 3.6776 | 2.6827 | 22.6716 | 21.366 | 3.4658 | 2.5282 | 21.366 | 20.0423 | 3.2511 | 2.3716 | 20.0423 | 19.1168 | 3.1009 | 2.2621 | 19.1168 | 18.1523 | 2.9445 | 2.148 | 18.1523 | 17.2459 | 2.7975 | 2.0407 | 17.2459 | 13.7681 | 2.2333 | 1.6292 | 13.7681 | 9.0466 | 1.4674 | 1.0705 | 9.0466 | 6.6815 | 1.0838 | 0.79063 | 6.6815 | 5.2942 | 0.85877 | 0.62646 | 5.2942 | 2.9279 | 0.47494 | 0.34646 | 2.9279 | 31.29 | 5.0755 | 3.7025 | 31.29 | 28.5314 | 4.6281 | 3.3761 | 28.5314 | 27.8983 | 4.5254 | 3.3012 | 27.8983 | 27.1352 | 4.4016 | 3.2109 | 27.1352 | 26.1287 | 4.2383 | 3.0918 | 26.1287 | 25.3024 | 4.1043 | 2.994 | 25.3024 | 24.2188 | 3.9285 | 2.8658 | 24.2188 | 23.06 | 3.7406 | 2.7287 | 23.06 | 21.7928 | 3.535 | 2.5787 | 21.7928 | 20.6248 | 3.3455 | 2.4405 | 20.6248 | 20.8241 | 3.3779 | 2.4641 | 20.8241 | 15.1071 | 2.4505 | 1.7876 | 15.1071 | 10.5182 | 1.7061 | 1.2446 | 10.5182 | 6.682 | 1.0839 | 0.79068 | 6.682 | 4.47 | 0.72508 | 0.52893 | 4.47 | 31.29 | 5.0755 | 3.7025 | 31.29 | 29.8389 | 4.8402 | 3.5308 | 29.8389 | 28.5708 | 4.6345 | 3.3808 | 28.5708 | 27.5631 | 4.471 | 3.2615 | 27.5631 | 26.4984 | 4.2983 | 3.1355 | 26.4984 | 25.3072 | 4.1051 | 2.9946 | 25.3072 | 24.2668 | 3.9363 | 2.8715 | 24.2668 | 23.6777 | 3.8408 | 2.8018 | 23.6777 | 22.9671 | 3.7255 | 2.7177 | 22.9671 | 22.3011 | 3.6175 | 2.6389 | 22.3011 | 19.9223 | 3.2316 | 2.3574 | 19.9223 | 16.7789 | 2.7217 | 1.9854 | 16.7789 | 16.0737 | 2.6073 | 1.902 | 16.0737 | 16.3044 | 2.6447 | 1.9293 | 16.3044 | 15.0517 | 2.4415 | 1.7811 | 15.0517 | 31.29 | 5.0755 | 3.7025 | 31.29 | 27.2311 | 4.4171 | 3.2222 | 27.2311 | 26.2956 | 4.2654 | 3.1116 | 26.2956 | 25.4076 | 4.1214 | 3.0065 | 25.4076 | 24.3523 | 3.9502 | 2.8816 | 24.3523 | 23.4683 | 3.8068 | 2.777 | 23.4683 | 22.3576 | 3.6266 | 2.6456 | 22.3576 | 21.1417 | 3.4294 | 2.5017 | 21.1417 | 19.8384 | 3.218 | 2.3475 | 19.8384 | 18.6298 | 3.0219 | 2.2045 | 18.6298 | 18.807 | 3.0507 | 2.2254 | 18.807 | 13.3626 | 2.1675 | 1.5812 | 13.3626 | 8.9523 | 1.4521 | 1.0593 | 8.9523 | 5.2183 | 0.84647 | 0.61749 | 5.2183 | 2.7312 | 0.44303 | 0.32318 | 2.7312
CHAMBERHALL | BURY | KEARSLEY | 380280 | 411215 | 30.0734 | 8.9817 | 6.552 | 10.1448 | 30.1914 | 8.947 | 6.5267 | 9.6964 | 30.3702 | 8.8976 | 6.4907 | 9.2864 | 30.6042 | 8.6962 | 6.3438 | 8.9372 | 30.8977 | 8.6063 | 6.2782 | 8.3786 | 31.2477 | 8.4335 | 6.1521 | 7.7919 | 31.6696 | 8.269 | 6.0321 | 7.3269 | 32.2012 | 8.1121 | 5.9177 | 6.8391 | 32.6595 | 7.9482 | 5.7981 | 6.2993 | 33.126 | 7.7956 | 5.6868 | 5.7819 | 34.4017 | 7.1324 | 5.203 | 3.0491 | 35.5582 | 6.3742 | 4.6499 | -1.2749 | 36.2462 | 5.9117 | 4.3125 | -5.0634 | 33.8204 | 5.486 | 4.002 | -9.3091 | 29.5106 | 4.7869 | 3.492 | -13.0008 | 30.0258 | 8.9817 | 6.552 | 10.1448 | 30.1296 | 8.9889 | 6.5573 | 9.923 | 30.245 | 8.9266 | 6.5118 | 9.6671 | 30.3936 | 8.8645 | 6.4666 | 9.4226 | 30.5965 | 8.7718 | 6.3989 | 9.1296 | 30.8544 | 8.6378 | 6.3012 | 8.7938 | 31.1664 | 8.4111 | 6.1358 | 8.4209 | 31.5274 | 8.2753 | 6.0367 | 7.9779 | 31.7351 | 8.1484 | 5.9442 | 7.6207 | 31.9622 | 8.0141 | 5.8462 | 7.2568 | 32.7457 | 7.5693 | 5.5217 | 6.1287 | 33.6193 | 7.262 | 5.2975 | 4.9051 | 34.4714 | 7.1278 | 5.1996 | 3.58 | 35.3667 | 7.1513 | 5.2168 | 2.0959 | 35.9929 | 6.946 | 5.067 | 1.0979 | 30.0914 | 8.9817 | 6.552 | 10.1448 | 30.2232 | 8.9467 | 6.5265 | 9.6519 | 30.4247 | 8.815 | 6.4304 | 9.2346 | 30.6906 | 8.6329 | 6.2976 | 8.8869 | 31.0215 | 8.458 | 6.17 | 8.2728 | 31.4126 | 8.2312 | 6.0045 | 7.5733 | 31.8791 | 8.0203 | 5.8507 | 6.9956 | 32.4624 | 7.834 | 5.7148 | 6.5228 | 32.9347 | 7.6443 | 5.5764 | 6.0385 | 33.3294 | 7.4688 | 5.4484 | 5.5797 | 34.3953 | 6.7341 | 4.9124 | 2.9992 | 35.6272 | 5.8752 | 4.2859 | -1.2056 | 33.2552 | 5.3943 | 3.9351 | -4.3879 | 30.6727 | 4.9754 | 3.6295 | -7.7996 | 26.1893 | 4.2482 | 3.099 | -11.1448 | 30.0914 | 8.9817 | 6.552 | 10.1448 | 30.0794 | 9.0168 | 6.5776 | 10.0614 | 30.1653 | 8.9708 | 6.5441 | 9.794 | 30.2991 | 8.8489 | 6.4552 | 9.5379 | 30.5127 | 8.6642 | 6.3204 | 8.9842 | 30.8545 | 8.4356 | 6.1537 | 8.2866 | 31.3028 | 8.1817 | 5.9684 | 7.4743 | 31.8521 | 7.9176 | 5.7758 | 6.1013 | 32.3358 | 7.6341 | 5.5689 | 4.6607 | 32.8356 | 7.3727 | 5.3783 | 3.235 | 34.3082 | 7.4256 | 5.4169 | -0.93197 | 35.3097 | 6.3232 | 4.6127 | -5.1907 | 33.1281 | 5.3737 | 3.92 | -8.6556 | 28.8495 | 4.6797 | 3.4138 | -10.9416 | 27.9151 | 4.5281 | 3.3032 | -9.727 | 30.0734 | 8.9817 | 6.552 | 10.1448 | 30.1717 | 8.9654 | 6.5402 | 9.9083 | 30.2909 | 8.9712 | 6.5444 | 9.6047 | 30.4328 | 8.8235 | 6.4366 | 9.3731 | 30.627 | 8.7391 | 6.375 | 9.0029 | 30.9318 | 8.5981 | 6.2722 | 8.56 | 31.3389 | 8.4506 | 6.1646 | 8.1639 | 31.8028 | 8.3022 | 6.0564 | 7.7242 | 32.189 | 8.1422 | 5.9396 | 7.2015 | 32.5947 | 7.9895 | 5.8283 | 6.6704 | 33.8738 | 7.5034 | 5.4736 | 4.9091 | 34.8468 | 7.1912 | 5.2459 | 3.0237 | 35.4987 | 7.2276 | 5.2724 | 1.9295 | 36.0172 | 7.4222 | 5.4144 | 0.92024 | 36.233 | 7.3401 | 5.3545 | 0.51909 | 30.0734 | 8.9817 | 6.552 | 10.1448 | 30.1173 | 8.9856 | 6.5549 | 9.859 | 30.2842 | 8.8902 | 6.4853 | 9.457 | 30.5122 | 8.7463 | 6.3803 | 9.0767 | 30.7997 | 8.5358 | 6.2267 | 8.419 | 31.1358 | 8.3002 | 6.0549 | 7.6866 | 31.5482 | 8.0411 | 5.8659 | 6.8551 | 32.1076 | 7.7599 | 5.6608 | 5.405 | 32.5835 | 7.4686 | 5.4482 | 3.9355 | 33.0706 | 7.1972 | 5.2503 | 2.4716 | 34.5037 | 7.1543 | 5.219 | -2.1272 | 35.5309 | 5.9304 | 4.3261 | -7.0289 | 30.3051 | 4.9158 | 3.586 | -10.8193 | 25.5943 | 4.1517 | 3.0286 | -13.4905 | 24.1941 | 3.9245 | 2.8629 | -12.6988
CHAPEL WHARF | FREDERICK RD | KEARSLEY | 383499 | 398634 | 30.1284 | 10.1868 | 7.4311 | 17.1126 | 30.2193 | 9.2636 | 6.7577 | 11.775 | 30.3141 | 8.8934 | 6.4876 | 10.0024 | 30.4038 | 8.6203 | 6.2884 | 8.6792 | 30.4931 | 8.3399 | 6.0838 | 7.3661 | 30.5843 | 8.0626 | 5.8815 | 6.1818 | 30.6806 | 7.8291 | 5.7112 | 5.3022 | 30.7834 | 7.6119 | 5.5527 | 4.4266 | 30.8821 | 7.3928 | 5.3929 | 3.5067 | 30.9785 | 7.2416 | 5.2826 | 3.2018 | 31.2455 | 7.0377 | 5.1339 | 2.2191 | 31.5014 | 6.7487 | 4.9231 | 1.1092 | 31.7065 | 6.5183 | 4.755 | 0.18669 | 31.9312 | 6.2834 | 4.5837 | -0.88101 | 32.1584 | 5.9949 | 4.3732 | -2.028 | 30.1264 | 10.1868 | 7.4311 | 17.1126 | 30.2254 | 9.8734 | 7.2025 | 15.3345 | 30.3298 | 9.7247 | 7.0941 | 14.5877 | 30.4316 | 9.6102 | 7.0105 | 14.1611 | 30.5361 | 9.4948 | 6.9263 | 13.7461 | 30.6468 | 9.3718 | 6.8366 | 13.3335 | 30.7611 | 9.1647 | 6.6855 | 13.0058 | 30.877 | 9.0679 | 6.6149 | 12.6539 | 30.9747 | 8.9772 | 6.5487 | 12.2976 | 31.0722 | 8.882 | 6.4793 | 11.9437 | 31.3549 | 8.6077 | 6.2792 | 10.9142 | 31.6286 | 8.399 | 6.1269 | 9.8891 | 31.8645 | 8.2084 | 5.9879 | 8.9966 | 32.1361 | 7.9985 | 5.8348 | 7.9464 | 32.4365 | 7.8027 | 5.6919 | 6.7606 | 30.129 | 10.1868 | 7.4311 | 17.1126 | 30.2225 | 9.1112 | 6.6465 | 10.9385 | 30.3199 | 8.7146 | 6.3572 | 8.9966 | 30.4136 | 8.4156 | 6.139 | 7.6735 | 30.5078 | 8.0922 | 5.9031 | 6.3619 | 30.6048 | 7.8154 | 5.7013 | 5.1796 | 30.7093 | 7.543 | 5.5025 | 4.3005 | 30.821 | 7.3169 | 5.3376 | 3.4279 | 30.9213 | 7.1449 | 5.2121 | 2.5304 | 31.013 | 7.0553 | 5.1467 | 2.2503 | 31.276 | 6.7356 | 4.9135 | 1.3439 | 31.5247 | 6.4368 | 4.6956 | 0.32494 | 31.718 | 6.188 | 4.514 | -0.50203 | 31.9215 | 5.9209 | 4.3192 | -1.4375 | 32.1166 | 5.6423 | 4.116 | -2.413 | 30.129 | 10.1868 | 7.4311 | 17.1126 | 30.1926 | 9.4185 | 6.8707 | 12.6995 | 30.2731 | 9.1149 | 6.6492 | 11.1245 | 30.3484 | 8.8215 | 6.4351 | 9.8205 | 30.4251 | 8.5116 | 6.2091 | 8.5237 | 30.5085 | 8.2321 | 6.0052 | 7.3584 | 30.5996 | 8.0314 | 5.8588 | 6.4788 | 30.6931 | 7.8003 | 5.6902 | 5.5441 | 30.7844 | 7.5483 | 5.5064 | 4.5731 | 30.8729 | 7.4045 | 5.4015 | 4.2159 | 31.1177 | 7.0203 | 5.1212 | 3.2002 | 31.3547 | 6.6263 | 4.8338 | 2.2256 | 31.5373 | 6.4109 | 4.6767 | 1.4485 | 31.7246 | 6.3112 | 4.604 | 0.68387 | 31.8947 | 6.0999 | 4.4498 | 0.076772 | 30.1284 | 10.1868 | 7.4311 | 17.1126 | 30.2182 | 9.6359 | 7.0292 | 13.9184 | 30.3087 | 9.3389 | 6.8126 | 12.5832 | 30.3917 | 9.0709 | 6.6171 | 11.2645 | 30.474 | 8.8078 | 6.4252 | 9.963 | 30.5626 | 8.5327 | 6.2245 | 8.7922 | 30.6594 | 8.3087 | 6.0611 | 7.9234 | 30.759 | 8.09 | 5.9015 | 7.052 | 30.8549 | 7.8699 | 5.741 | 6.1275 | 30.9496 | 7.7347 | 5.6424 | 5.8152 | 31.2188 | 7.5377 | 5.4986 | 4.9061 | 31.4768 | 7.2986 | 5.3242 | 4.0088 | 31.6847 | 7.1333 | 5.2036 | 3.2853 | 31.9147 | 6.9429 | 5.0648 | 2.4421 | 32.1514 | 6.6538 | 4.8539 | 1.5373 | 30.1284 | 10.1868 | 7.4311 | 17.1126 | 30.1992 | 8.9829 | 6.5529 | 10.182 | 30.2901 | 8.5795 | 6.2586 | 8.0838 | 30.3778 | 8.2836 | 6.0428 | 6.7645 | 30.466 | 7.9681 | 5.8126 | 5.4523 | 30.5552 | 7.6832 | 5.6048 | 4.2727 | 30.6493 | 7.4766 | 5.4541 | 3.3795 | 30.7516 | 7.2327 | 5.2762 | 2.4259 | 30.8446 | 6.9842 | 5.0949 | 1.4489 | 30.9352 | 6.8368 | 4.9873 | 1.0863 | 31.1804 | 6.4459 | 4.7022 | 0.055902 | 31.4097 | 6.0706 | 4.4284 | -0.94199 | 31.588 | 5.8297 | 4.2527 | -1.7467 | 31.7731 | 5.6946 | 4.1541 | -2.5552 | 31.9541 | 5.4684 | 3.9891 | -3.2337
CHASSEN RD | BARTON | CARRINGTON | 375542 | 394453 | 29.6506 | 11.8022 | 8.6095 | 14.3665 | 29.8503 | 11.7023 | 8.5367 | 14.0537 | 30.1163 | 11.5572 | 8.4308 | 13.7541 | 30.3318 | 11.4486 | 8.3516 | 13.4819 | 30.5985 | 11.2647 | 8.2174 | 13.1472 | 30.8933 | 11.0348 | 8.0497 | 12.8071 | 31.2145 | 10.8698 | 7.9294 | 12.4961 | 31.5841 | 10.7451 | 7.8384 | 12.2131 | 31.8848 | 10.6179 | 7.7456 | 11.8783 | 32.1024 | 10.5024 | 7.6614 | 11.5646 | 32.771 | 9.985 | 7.2839 | 9.5934 | 33.4434 | 9.2642 | 6.7581 | 6.452 | 33.9262 | 8.7266 | 6.3659 | 4.0401 | 34.3254 | 8.2196 | 5.9961 | 1.7564 | 34.5415 | 7.9237 | 5.7802 | 0.19541 | 29.5852 | 11.8022 | 8.6095 | 14.3665 | 29.6739 | 11.7622 | 8.5803 | 14.1858 | 29.7562 | 11.6456 | 8.4953 | 13.9872 | 29.8884 | 11.4807 | 8.375 | 13.7945 | 30.0863 | 11.3732 | 8.2966 | 13.5628 | 30.2169 | 11.2086 | 8.1765 | 13.3186 | 30.369 | 10.9708 | 8.003 | 13.016 | 30.5451 | 10.8721 | 7.931 | 12.6516 | 30.684 | 10.767 | 7.8544 | 12.3406 | 30.8328 | 10.6577 | 7.7747 | 12.0171 | 31.3079 | 10.4203 | 7.6015 | 11.0537 | 31.7899 | 10.2203 | 7.4556 | 10.1181 | 32.2484 | 10.0287 | 7.3158 | 9.2097 | 32.7333 | 9.8629 | 7.1949 | 8.2203 | 33.106 | 9.7106 | 7.0838 | 7.4737 | 29.6822 | 11.8022 | 8.6095 | 14.3665 | 29.916 | 11.6419 | 8.4926 | 13.9644 | 30.2273 | 11.5069 | 8.3941 | 13.5798 | 30.5107 | 11.3253 | 8.2616 | 13.2343 | 30.8537 | 11.073 | 8.0776 | 12.6372 | 31.2337 | 10.821 | 7.8938 | 12.0322 | 31.6079 | 10.5705 | 7.7111 | 11.4653 | 31.9478 | 10.3857 | 7.5762 | 10.9195 | 32.2109 | 10.2064 | 7.4454 | 10.3441 | 32.4662 | 10.031 | 7.3175 | 9.7535 | 33.2744 | 9.2065 | 6.716 | 7.026 | 34.0707 | 8.397 | 6.1255 | 3.5598 | 34.4837 | 7.8292 | 5.7113 | 1.0831 | 34.7898 | 7.317 | 5.3377 | -1.0881 | 34.9121 | 7.2153 | 5.2635 | -1.3903 | 29.6823 | 11.8022 | 8.6095 | 14.3665 | 29.7794 | 11.715 | 8.546 | 14.2422 | 29.9721 | 11.6742 | 8.5162 | 13.9495 | 30.2434 | 11.5727 | 8.4421 | 13.6319 | 30.5626 | 11.3876 | 8.3071 | 13.0362 | 30.926 | 11.1541 | 8.1367 | 12.4008 | 31.2437 | 10.8871 | 7.942 | 11.6178 | 31.5504 | 10.4877 | 7.6507 | 10.3114 | 31.8051 | 10.1009 | 7.3685 | 9.0046 | 32.0551 | 9.7723 | 7.1288 | 7.7276 | 32.8143 | 8.7781 | 6.4035 | 4.1698 | 33.5589 | 8.1968 | 5.9795 | 1.2098 | 34.0706 | 7.6455 | 5.5773 | -0.74405 | 34.3784 | 7.408 | 5.4041 | -1.8301 | 34.3796 | 7.4169 | 5.4105 | -0.55312 | 29.6506 | 11.8022 | 8.6095 | 14.3665 | 29.8123 | 11.7501 | 8.5715 | 14.1215 | 30.0009 | 11.5704 | 8.4405 | 13.8828 | 30.1976 | 11.4939 | 8.3847 | 13.6981 | 30.3765 | 11.359 | 8.2862 | 13.5065 | 30.6195 | 11.1669 | 8.1461 | 13.2848 | 30.9163 | 11.0135 | 8.0342 | 13.0513 | 31.2404 | 10.8908 | 7.9447 | 12.8153 | 31.5088 | 10.783 | 7.866 | 12.4924 | 31.782 | 10.6438 | 7.7645 | 12.1663 | 32.4517 | 10.2909 | 7.5071 | 11.0774 | 33.0882 | 9.9159 | 7.2335 | 9.9331 | 33.5599 | 9.6483 | 7.0383 | 9.0824 | 33.9754 | 9.2699 | 6.7623 | 8.1112 | 34.1774 | 9.2883 | 6.7757 | 7.5318 | 29.6506 | 11.8022 | 8.6095 | 14.3665 | 29.8097 | 11.6433 | 8.4936 | 14.122 | 30.1051 | 11.6245 | 8.4799 | 13.7209 | 30.4047 | 11.4741 | 8.3702 | 13.293 | 30.7283 | 11.2668 | 8.219 | 12.5981 | 31.0801 | 11.0195 | 8.0386 | 11.897 | 31.4281 | 10.7411 | 7.8355 | 11.0357 | 31.7585 | 10.3192 | 7.5277 | 9.6157 | 32.0252 | 9.92 | 7.2365 | 8.2268 | 32.2843 | 9.5831 | 6.9907 | 6.8684 | 33.0487 | 8.5218 | 6.2166 | 3.0681 | 33.7461 | 7.9162 | 5.7748 | -0.098718 | 34.2325 | 7.3546 | 5.3651 | -2.244 | 34.5568 | 7.0505 | 5.1432 | -3.5493 | 34.5807 | 7.0163 | 5.1183 | -2.5222
CHATSWORTH ST | BARROW & SANDGATE | HARKER / HUTTON | 319188 | 470003 | 29.3401 | 11.1771 | 8.0332 | 15.602 | 29.4587 | 10.9999 | 7.9059 | 15.197 | 29.5656 | 10.7917 | 7.7562 | 14.828 | 29.7095 | 10.6075 | 7.6238 | 14.532 | 29.9256 | 10.3821 | 7.4618 | 14.1455 | 30.1724 | 10.1634 | 7.3046 | 13.7501 | 30.4368 | 10.0097 | 7.1942 | 13.3915 | 30.7345 | 9.8738 | 7.0965 | 13.0575 | 30.9868 | 9.7535 | 7.01 | 12.7814 | 31.2355 | 9.6464 | 6.9331 | 12.5262 | 32.2653 | 9.0972 | 6.5384 | 10.67 | 32.9379 | 8.339 | 5.9934 | 7.3856 | 33.254 | 7.6823 | 5.5214 | 4.8293 | 33.4979 | 6.9829 | 5.0188 | 2.3466 | 33.6094 | 6.2984 | 4.5268 | 0.30541 | 29.3287 | 11.1771 | 8.0332 | 15.602 | 29.413 | 10.9731 | 7.8866 | 15.4151 | 29.4775 | 10.762 | 7.7348 | 15.1696 | 29.5643 | 10.5284 | 7.567 | 14.9351 | 29.6827 | 10.257 | 7.3719 | 14.669 | 29.8093 | 9.9992 | 7.1866 | 14.3991 | 29.968 | 9.6628 | 6.9448 | 14.0633 | 30.1586 | 9.4971 | 6.8258 | 13.6699 | 30.2795 | 9.3774 | 6.7397 | 13.4565 | 30.4136 | 9.254 | 6.6511 | 13.2396 | 30.9041 | 8.9146 | 6.4071 | 12.5898 | 31.4612 | 8.6735 | 6.2338 | 11.942 | 31.8429 | 8.4431 | 6.0682 | 11.4685 | 32.2177 | 8.2104 | 5.901 | 11.0402 | 32.4716 | 7.9735 | 5.7307 | 10.7713 | 29.3446 | 11.1771 | 8.0332 | 15.602 | 29.4565 | 10.9617 | 7.8784 | 15.1661 | 29.5637 | 10.6986 | 7.6893 | 14.8064 | 29.7113 | 10.4648 | 7.5213 | 14.5417 | 29.9305 | 10.2325 | 7.3543 | 14.185 | 30.1792 | 10.0234 | 7.204 | 13.8237 | 30.4454 | 9.859 | 7.0858 | 13.5043 | 30.7468 | 9.7023 | 6.9732 | 13.1348 | 30.9949 | 9.5653 | 6.8748 | 12.8574 | 31.2442 | 9.4271 | 6.7755 | 12.6017 | 32.3099 | 8.7402 | 6.2818 | 11.0196 | 32.9537 | 7.9268 | 5.6971 | 8.0398 | 33.2971 | 7.2142 | 5.185 | 5.6308 | 33.5531 | 6.4667 | 4.6477 | 3.3391 | 33.6463 | 5.8248 | 4.1864 | 1.5335 | 29.3448 | 11.1771 | 8.0332 | 15.602 | 29.3908 | 11.036 | 7.9318 | 15.5089 | 29.4618 | 10.8253 | 7.7804 | 15.2399 | 29.5797 | 10.5626 | 7.5916 | 15.003 | 29.7689 | 10.299 | 7.4021 | 14.6741 | 30.0144 | 10.12 | 7.2734 | 14.3306 | 30.3732 | 9.7618 | 7.016 | 13.8171 | 31.0038 | 9.284 | 6.6726 | 12.656 | 31.2729 | 8.9412 | 6.4262 | 11.5549 | 31.5173 | 8.541 | 6.1386 | 10.4635 | 32.2199 | 7.6135 | 5.472 | 7.352 | 32.7842 | 6.786 | 4.8772 | 4.3932 | 33.0731 | 6.0983 | 4.383 | 2.2071 | 33.2405 | 5.5512 | 3.9898 | 1.0527 | 33.0672 | 5.4443 | 3.9129 | 2.3905 | 29.34 | 11.1771 | 8.0332 | 15.602 | 29.4345 | 11.0642 | 7.9521 | 15.447 | 29.511 | 10.8763 | 7.817 | 15.1409 | 29.6043 | 10.6982 | 7.689 | 14.891 | 29.7311 | 10.5014 | 7.5475 | 14.6317 | 29.8896 | 10.2988 | 7.402 | 14.3755 | 30.0993 | 10.1548 | 7.2985 | 14.0811 | 30.3786 | 10.0138 | 7.1971 | 13.7065 | 30.6394 | 9.8783 | 7.0997 | 13.3408 | 30.9211 | 9.7503 | 7.0077 | 12.9627 | 31.8831 | 9.3209 | 6.6991 | 11.695 | 32.6235 | 8.9327 | 6.4201 | 10.3441 | 32.9586 | 8.6152 | 6.1919 | 9.5433 | 33.1771 | 8.2968 | 5.9631 | 8.9734 | 33.2151 | 8.1206 | 5.8364 | 9.1086 | 29.34 | 11.1771 | 8.0332 | 15.602 | 29.3913 | 10.9756 | 7.8884 | 15.3104 | 29.485 | 10.7444 | 7.7222 | 14.9457 | 29.6314 | 10.4673 | 7.523 | 14.6296 | 29.8399 | 10.1935 | 7.3263 | 14.2255 | 30.07 | 10.0028 | 7.1892 | 13.8254 | 30.3971 | 9.6369 | 6.9262 | 13.245 | 31.0249 | 9.0985 | 6.5393 | 11.9979 | 31.3889 | 8.7838 | 6.3131 | 10.8526 | 31.6194 | 8.3759 | 6.0199 | 9.7147 | 32.3459 | 7.4155 | 5.3297 | 6.4457 | 32.9445 | 6.5525 | 4.7094 | 3.3368 | 33.2597 | 5.8229 | 4.185 | 0.98098 | 31.8034 | 5.2362 | 3.7634 | -0.4119 | 30.8561 | 5.0802 | 3.6512 | 0.64741
CHEADLE HEATH | ADSWOOD | BREDBURY | 387062 | 389054 | 21.0616 | 11.9157 | 8.6923 | 11.2097 | 21.1143 | 11.6984 | 8.5338 | 10.6139 | 21.1709 | 11.5728 | 8.4422 | 10.4809 | 21.2459 | 11.4505 | 8.353 | 10.4616 | 21.3488 | 11.2862 | 8.2332 | 10.3737 | 21.4776 | 10.9207 | 7.9665 | 10.2694 | 21.6383 | 10.7693 | 7.8561 | 10.1695 | 21.8445 | 10.7471 | 7.8399 | 10.0697 | 22.0413 | 10.617 | 7.745 | 9.918 | 22.2429 | 10.4495 | 7.6228 | 9.7146 | 22.8695 | 10.0066 | 7.2997 | 8.2967 | 23.3984 | 9.4698 | 6.9081 | 6.0537 | 23.7516 | 9.0128 | 6.5747 | 4.1955 | 24.0156 | 8.4743 | 6.1819 | 2.0526 | 24.1568 | 7.9912 | 5.8295 | 0.25138 | 21.0185 | 11.9157 | 8.6923 | 11.2097 | 21.059 | 11.8356 | 8.6339 | 11.0933 | 21.1068 | 11.6987 | 8.534 | 11.0299 | 21.1549 | 11.6366 | 8.4888 | 10.9699 | 21.2109 | 11.5199 | 8.4036 | 10.8706 | 21.2867 | 11.3415 | 8.2735 | 10.7437 | 21.3828 | 11.0605 | 8.0685 | 10.5731 | 21.4958 | 10.9656 | 7.9992 | 10.3724 | 21.587 | 10.8825 | 7.9386 | 10.2007 | 21.6881 | 10.8057 | 7.8826 | 10.0206 | 22.0428 | 10.5871 | 7.7232 | 9.457 | 22.4477 | 10.3946 | 7.5827 | 8.6992 | 22.8516 | 10.1902 | 7.4336 | 7.9925 | 23.2747 | 9.8742 | 7.2031 | 7.3006 | 23.5572 | 9.7035 | 7.0786 | 6.8755 | 21.082 | 11.9157 | 8.6923 | 11.2097 | 21.1266 | 11.6576 | 8.5041 | 10.5349 | 21.1919 | 11.5093 | 8.3959 | 10.398 | 21.2785 | 11.3474 | 8.2778 | 10.4056 | 21.3944 | 11.1618 | 8.1423 | 10.3469 | 21.5366 | 10.8055 | 7.8825 | 10.2778 | 21.7083 | 10.7115 | 7.8139 | 10.2442 | 21.9256 | 10.6169 | 7.7449 | 10.2159 | 22.1165 | 10.459 | 7.6297 | 10.1481 | 22.3135 | 10.2811 | 7.4999 | 9.9724 | 22.9089 | 9.807 | 7.1541 | 8.7025 | 23.494 | 9.2385 | 6.7394 | 6.5406 | 23.8976 | 8.7415 | 6.3768 | 4.7619 | 24.1816 | 8.1808 | 5.9678 | 2.9607 | 24.3047 | 7.6716 | 5.5963 | 1.363 | 21.082 | 11.9157 | 8.6923 | 11.2097 | 21.054 | 11.745 | 8.5678 | 10.952 | 21.0763 | 11.6422 | 8.4928 | 10.916 | 21.1185 | 11.4674 | 8.3653 | 10.9417 | 21.1976 | 11.2583 | 8.2128 | 10.878 | 21.3293 | 11.0071 | 8.0295 | 10.7836 | 21.5138 | 10.8821 | 7.9384 | 10.5657 | 21.7736 | 10.5908 | 7.7258 | 9.8731 | 21.9906 | 10.4446 | 7.6192 | 9.1321 | 22.1753 | 10.301 | 7.5144 | 8.388 | 22.7534 | 9.6819 | 7.0628 | 6.2211 | 23.2801 | 9.0902 | 6.6312 | 4.1626 | 23.6227 | 8.5794 | 6.2586 | 2.4689 | 23.8392 | 8.1304 | 5.931 | 1.4105 | 23.8394 | 8.0309 | 5.8584 | 2.2354 | 21.0616 | 11.9157 | 8.6923 | 11.2097 | 21.1065 | 11.8043 | 8.6111 | 11.0782 | 21.1398 | 11.7025 | 8.5368 | 11.0702 | 21.1778 | 11.5941 | 8.4577 | 11.1094 | 21.237 | 11.4566 | 8.3574 | 11.1264 | 21.3412 | 11.072 | 8.0769 | 11.1087 | 21.4891 | 10.9482 | 7.9866 | 11.0536 | 21.6629 | 10.9477 | 7.9862 | 10.978 | 21.8256 | 10.824 | 7.896 | 10.8372 | 21.9975 | 10.663 | 7.7785 | 10.6862 | 22.587 | 10.3332 | 7.5379 | 9.8721 | 23.1114 | 10.0482 | 7.33 | 8.9896 | 23.4557 | 9.8128 | 7.1583 | 8.374 | 23.7041 | 9.5656 | 6.978 | 7.8739 | 23.7971 | 9.3715 | 6.8364 | 7.7351 | 21.0616 | 11.9157 | 8.6923 | 11.2097 | 21.0671 | 11.6625 | 8.5076 | 10.6351 | 21.118 | 11.5351 | 8.4147 | 10.4818 | 21.1932 | 11.3495 | 8.2793 | 10.4383 | 21.2969 | 11.1291 | 8.1185 | 10.3131 | 21.4221 | 10.8693 | 7.929 | 10.1804 | 21.5869 | 10.7411 | 7.8355 | 9.9152 | 21.8435 | 10.4488 | 7.6223 | 9.1579 | 22.0813 | 10.2709 | 7.4925 | 8.3728 | 22.2582 | 10.12 | 7.3824 | 7.5838 | 22.8324 | 9.4775 | 6.9137 | 5.2572 | 23.3758 | 8.8582 | 6.4619 | 3.0357 | 23.7464 | 8.309 | 6.0613 | 1.1585 | 23.9687 | 7.8227 | 5.7066 | -0.11404 | 23.977 | 7.6862 | 5.607 | 0.49629
CHEADLE HULME | ADSWOOD | BREDBURY | 387386 | 386308 | 30.5425 | 13.6435 | 9.8058 | 13.6073 | 30.6503 | 13.3695 | 9.6089 | 13.03 | 30.7962 | 13.341 | 9.5884 | 12.7492 | 30.9801 | 13.2156 | 9.4983 | 12.5491 | 31.2007 | 13.0477 | 9.3776 | 12.2895 | 31.4487 | 12.7893 | 9.1919 | 12.0235 | 31.7322 | 12.4977 | 8.9823 | 11.7577 | 32.0773 | 12.2443 | 8.8002 | 11.4871 | 32.3413 | 11.8971 | 8.5507 | 10.9689 | 32.5912 | 11.9027 | 8.5547 | 10.5852 | 33.2457 | 11.3661 | 8.1691 | 8.7501 | 33.7836 | 10.7053 | 7.6941 | 6.0117 | 34.1454 | 10.1424 | 7.2896 | 3.9097 | 34.4758 | 9.5148 | 6.8385 | 1.8552 | 34.6835 | 9.0279 | 6.4885 | 0.43885 | 30.5006 | 13.6435 | 9.8058 | 13.6073 | 30.57 | 13.5514 | 9.7396 | 13.3654 | 30.6328 | 13.4872 | 9.6935 | 13.2187 | 30.7137 | 13.4136 | 9.6406 | 13.0734 | 30.8326 | 13.2677 | 9.5357 | 12.8562 | 30.985 | 13.0622 | 9.3881 | 12.6051 | 31.168 | 12.7595 | 9.1705 | 12.2847 | 31.3734 | 12.6354 | 9.0813 | 11.9039 | 31.5 | 12.5166 | 8.9959 | 11.5816 | 31.6324 | 12.4112 | 8.9202 | 11.2478 | 32.0347 | 12.0845 | 8.6853 | 10.1786 | 32.4187 | 11.8381 | 8.5083 | 9.1505 | 32.7585 | 11.5592 | 8.3078 | 8.2012 | 33.1039 | 11.2057 | 8.0538 | 7.2253 | 33.378 | 10.7389 | 7.7183 | 6.5487 | 30.5586 | 13.6435 | 9.8058 | 13.6073 | 30.6967 | 13.2615 | 9.5313 | 12.905 | 30.8858 | 13.2291 | 9.5081 | 12.5465 | 31.1254 | 13.0583 | 9.3853 | 12.2888 | 31.4115 | 12.8519 | 9.2369 | 11.9677 | 31.7347 | 12.5438 | 9.0155 | 11.6384 | 32.1041 | 12.2081 | 8.7742 | 11.2525 | 32.5499 | 11.8584 | 8.5229 | 10.6554 | 32.8555 | 11.6366 | 8.3634 | 9.9642 | 33.0706 | 11.4484 | 8.2282 | 9.3911 | 33.6967 | 10.7336 | 7.7144 | 7.187 | 34.1867 | 9.981 | 7.1735 | 4.4972 | 34.5254 | 9.3573 | 6.7253 | 2.6198 | 34.8067 | 8.7249 | 6.2708 | 1.0459 | 34.9345 | 8.2652 | 5.9403 | 0.3826 | 30.5586 | 13.6435 | 9.8058 | 13.6073 | 30.5754 | 13.404 | 9.6337 | 13.3811 | 30.6728 | 13.3943 | 9.6267 | 13.1667 | 30.8061 | 13.2192 | 9.5009 | 12.969 | 30.9967 | 13.0456 | 9.3761 | 12.6692 | 31.2776 | 12.8025 | 9.2014 | 12.3171 | 31.6208 | 12.5658 | 9.0313 | 11.7556 | 32.0072 | 12.2177 | 8.7811 | 10.5736 | 32.3078 | 11.8135 | 8.4906 | 9.3751 | 32.5624 | 11.5488 | 8.3003 | 8.3235 | 33.1661 | 10.6708 | 7.6693 | 5.6086 | 33.7875 | 10.0493 | 7.2226 | 3.4586 | 34.0873 | 9.5071 | 6.8329 | 2.0753 | 34.3039 | 8.996 | 6.4656 | 1.3605 | 34.326 | 8.7569 | 6.2938 | 1.8796 | 30.5425 | 13.6435 | 9.8058 | 13.6073 | 30.6355 | 13.4613 | 9.6749 | 13.2398 | 30.7332 | 13.4347 | 9.6558 | 13.0633 | 30.8444 | 13.3207 | 9.5739 | 12.9614 | 30.9921 | 13.1874 | 9.478 | 12.8243 | 31.217 | 12.9423 | 9.3019 | 12.6296 | 31.508 | 12.6633 | 9.1014 | 12.3962 | 31.8225 | 12.4011 | 8.9129 | 12.1642 | 32.0574 | 12.074 | 8.6778 | 11.7075 | 32.2889 | 12.0856 | 8.6861 | 11.3418 | 32.9906 | 11.6855 | 8.3986 | 10.2028 | 33.5242 | 11.3061 | 8.1259 | 8.9661 | 33.862 | 10.9629 | 7.8792 | 8.0437 | 34.139 | 10.5457 | 7.5794 | 7.0722 | 34.2967 | 10.205 | 7.3345 | 6.3875 | 30.5425 | 13.6435 | 9.8058 | 13.6073 | 30.6003 | 13.3699 | 9.6092 | 13.1043 | 30.7588 | 13.2856 | 9.5486 | 12.7303 | 30.9662 | 13.089 | 9.4073 | 12.3977 | 31.2162 | 12.8891 | 9.2636 | 11.9797 | 31.4935 | 12.6335 | 9.08 | 11.5574 | 31.8133 | 12.3855 | 8.9017 | 10.9105 | 32.2213 | 12.0173 | 8.637 | 9.601 | 32.5443 | 11.6128 | 8.3464 | 8.3017 | 32.8309 | 11.3165 | 8.1334 | 7.152 | 33.4402 | 10.3696 | 7.4528 | 4.1622 | 34.0023 | 9.7131 | 6.981 | 1.7725 | 34.3005 | 9.1383 | 6.5679 | 0.24019 | 34.4915 | 8.6139 | 6.191 | -0.54909 | 34.5222 | 8.3519 | 6.0027 | -0.13443
CHEETHAM HILL | AGECROFT | KEARSLEY | 383606 | 402218 | 22.235 | 16.0416 | 11.7021 | 2.4727 | 22.3023 | 15.711 | 11.461 | 1.9157 | 22.3809 | 15.285 | 11.1502 | 1.4363 | 22.4699 | 14.7996 | 10.7961 | 0.99909 | 22.5835 | 14.5378 | 10.6051 | 0.50987 | 22.689 | 14.3463 | 10.4654 | -0.00034204 | 22.8078 | 14.1367 | 10.3125 | -0.50742 | 22.9485 | 13.9785 | 10.1971 | -0.99261 | 23.0439 | 13.832 | 10.0902 | -1.497 | 23.1331 | 13.6842 | 9.9824 | -1.9729 | 23.4396 | 13.1533 | 9.5952 | -3.7872 | 23.7877 | 12.5814 | 9.178 | -6.3898 | 24.0362 | 12.2798 | 8.958 | -8.2924 | 24.258 | 12.1578 | 8.8689 | -10.0275 | 24.3868 | 11.8239 | 8.6254 | -11.1412 | 22.2179 | 16.0416 | 11.7021 | 2.4727 | 22.2803 | 15.8196 | 11.5402 | 2.1947 | 22.3408 | 15.514 | 11.3172 | 1.9229 | 22.4111 | 15.206 | 11.0926 | 1.6598 | 22.5042 | 14.8871 | 10.8599 | 1.3614 | 22.613 | 14.5891 | 10.6426 | 1.0699 | 22.7494 | 14.3611 | 10.4763 | 0.71287 | 22.9116 | 14.1155 | 10.2971 | 0.29015 | 22.9808 | 13.9056 | 10.144 | -0.025918 | 23.0526 | 13.6808 | 9.98 | -0.34659 | 23.271 | 13.1675 | 9.6055 | -1.0995 | 23.4864 | 13.0637 | 9.5298 | -1.7442 | 23.6769 | 13.0805 | 9.542 | -2.3149 | 23.8723 | 13.0804 | 9.5419 | -2.9204 | 24.0212 | 12.6984 | 9.2633 | -3.3365 | 22.2402 | 16.0416 | 11.7021 | 2.4727 | 22.334 | 15.6544 | 11.4197 | 1.8498 | 22.4436 | 15.1313 | 11.0381 | 1.3116 | 22.5703 | 14.6802 | 10.709 | 0.82575 | 22.6835 | 14.4874 | 10.5684 | 0.28135 | 22.8149 | 14.1875 | 10.3496 | -0.28623 | 22.971 | 13.9165 | 10.1519 | -0.95709 | 23.1527 | 13.693 | 9.9889 | -1.6683 | 23.2786 | 13.4691 | 9.8255 | -2.3305 | 23.3979 | 13.2467 | 9.6633 | -2.9757 | 23.8001 | 12.4811 | 9.1048 | -5.1693 | 24.2116 | 11.9458 | 8.7143 | -7.6703 | 24.4922 | 11.8158 | 8.6195 | -9.2341 | 24.7301 | 11.5909 | 8.4554 | -10.3306 | 24.8441 | 11.3797 | 8.3014 | -10.4055 | 22.2402 | 16.0416 | 11.7021 | 2.4727 | 22.2242 | 15.7312 | 11.4757 | 2.2259 | 22.2801 | 15.3089 | 11.1676 | 1.7893 | 22.3452 | 15.0291 | 10.9635 | 1.3533 | 22.406 | 14.8511 | 10.8337 | 0.83275 | 22.5004 | 14.5654 | 10.6252 | 0.2745 | 22.6268 | 14.1157 | 10.2972 | -0.56706 | 22.7849 | 13.9065 | 10.1446 | -1.891 | 22.917 | 13.6862 | 9.9839 | -3.1747 | 23.0455 | 13.3916 | 9.769 | -4.4064 | 23.4355 | 12.8642 | 9.3843 | -7.2838 | 23.8086 | 12.2508 | 8.9368 | -9.3202 | 24.0531 | 11.7955 | 8.6046 | -10.4125 | 24.2318 | 11.4413 | 8.3463 | -10.5565 | 24.2561 | 11.3924 | 8.3106 | -9.2666 | 22.235 | 16.0416 | 11.7021 | 2.4727 | 22.2951 | 15.734 | 11.4778 | 1.973 | 22.3532 | 15.3314 | 11.184 | 1.5342 | 22.4096 | 14.8646 | 10.8435 | 1.1531 | 22.4847 | 14.5844 | 10.6391 | 0.75747 | 22.5914 | 14.4267 | 10.5241 | 0.34815 | 22.7186 | 14.2376 | 10.3861 | -0.078764 | 22.8483 | 14.0854 | 10.2751 | -0.52921 | 22.9355 | 13.9399 | 10.169 | -1.0436 | 23.0214 | 13.7835 | 10.0549 | -1.5564 | 23.2949 | 13.3984 | 9.7739 | -2.5942 | 23.5793 | 13.1097 | 9.5633 | -3.5117 | 23.786 | 13.0928 | 9.551 | -4.1174 | 23.9824 | 13.1977 | 9.6276 | -4.6916 | 24.0956 | 13.0307 | 9.5057 | -4.9461 | 22.235 | 16.0416 | 11.7021 | 2.4727 | 22.2436 | 15.7038 | 11.4557 | 2.1197 | 22.3346 | 15.2551 | 11.1284 | 1.5947 | 22.4492 | 14.9686 | 10.9194 | 1.0708 | 22.5607 | 14.7686 | 10.7735 | 0.46861 | 22.6778 | 14.4747 | 10.5591 | -0.14957 | 22.8214 | 14.0238 | 10.2302 | -0.95099 | 23.0158 | 13.7971 | 10.0648 | -2.3454 | 23.1585 | 13.5689 | 9.8984 | -3.6658 | 23.2953 | 13.267 | 9.6781 | -4.9322 | 23.6924 | 12.7133 | 9.2742 | -7.9027 | 24.0468 | 12.0695 | 8.8045 | -10.0731 | 24.2805 | 11.585 | 8.4511 | -11.3019 | 24.449 | 11.2137 | 8.1802 | -11.5823 | 24.4948 | 11.0917 | 8.0912 | -10.4288
ALDERLEY & CHELFORD | MOSS NOOK | SOUTH MANCHESTER | 382184 | 373490 | 20.4951 | 3.3744 | 2.4252 | 15.876 | 18.7685 | 3.0901 | 2.2209 | 15.169 | 18.8824 | 3.1088 | 2.2344 | 14.6972 | 17.6887 | 2.9123 | 2.0931 | 14.3739 | 16.5484 | 2.7246 | 1.9582 | 14.0104 | 18.2615 | 3.0066 | 2.1609 | 13.6523 | 15.9688 | 2.6291 | 1.8896 | 10.3785 | 14.7956 | 2.436 | 1.7508 | 10.0949 | 13.6619 | 2.2493 | 1.6166 | 9.667 | 11.5345 | 1.8991 | 1.3649 | 8.6069 | 7.6929 | 1.2666 | 0.91031 | 6.5743 | 3.5511 | 0.58467 | 0.42021 | 2.6745 | 2.9075 | 0.47869 | 0.34405 | 0.048816 | 11.0352 | 1.8169 | 1.3058 | -2.7115 | 20.83 | 3.4295 | 2.4648 | -5.0822 | 20.4951 | 3.3744 | 2.4252 | 15.876 | 18.769 | 3.0902 | 2.221 | 15.5606 | 16.2552 | 2.6763 | 1.9235 | 15.2209 | 16.3297 | 2.6886 | 1.9323 | 14.9066 | 14.8132 | 2.4389 | 1.7529 | 14.5407 | 14.3351 | 2.3602 | 1.6963 | 14.1496 | 11.0828 | 1.8247 | 1.3115 | 11.0828 | 10.6511 | 1.7536 | 1.2604 | 10.6511 | 10.1438 | 1.6701 | 1.2003 | 10.1438 | 8.8939 | 1.4643 | 1.0524 | 8.8939 | 7.5061 | 1.2358 | 0.88821 | 7.5061 | 6.2521 | 1.0294 | 0.73983 | 6.2521 | 8.0187 | 1.3202 | 0.94887 | 6.5712 | 19.9973 | 3.2924 | 2.3663 | 4.9542 | 27.6128 | 4.5462 | 3.2675 | 3.7716 | 20.4951 | 3.3744 | 2.4252 | 15.876 | 18.8032 | 3.0958 | 2.225 | 15.1292 | 18.8343 | 3.1009 | 2.2287 | 14.6818 | 17.9104 | 2.9488 | 2.1194 | 14.4309 | 15.0154 | 2.4722 | 1.7768 | 12.183 | 16.3988 | 2.6999 | 1.9405 | 11.9251 | 13.1863 | 2.171 | 1.5604 | 8.8238 | 12.0477 | 1.9836 | 1.4256 | 8.6535 | 10.5473 | 1.7365 | 1.2481 | 8.4128 | 7.9147 | 1.3031 | 0.93656 | 7.2016 | 3.2903 | 0.54173 | 0.38935 | 3.2903 | 2.6844 | 0.44197 | 0.31765 | 2.17 | 2.6844 | 0.44197 | 0.31765 | 0.16014 | 9.7086 | 1.5984 | 1.1488 | -1.6191 | 18.1215 | 2.9836 | 2.1444 | -3.4743 | 20.4951 | 3.3744 | 2.4252 | 15.876 | 19.6952 | 3.2427 | 2.3306 | 15.6382 | 20.5595 | 3.385 | 2.4328 | 15.3612 | 20.352 | 3.3508 | 2.4083 | 15.1805 | 18.2629 | 3.0068 | 2.1611 | 14.9213 | 18.0051 | 2.9644 | 2.1306 | 13.9298 | 14.4577 | 2.3804 | 1.7108 | 10.6187 | 13.3618 | 2.1999 | 1.5811 | 9.7795 | 12.4068 | 2.0427 | 1.4681 | 8.8316 | 10.3457 | 1.7033 | 1.2242 | 6.6604 | 12.9779 | 2.1367 | 1.5357 | 3.2407 | 8.1239 | 1.3375 | 0.96131 | 0.50931 | 5.0989 | 0.8395 | 0.60336 | -1.5725 | 21.0526 | 3.4662 | 2.4912 | -2.8965 | 20.0884 | 3.3074 | 2.3771 | -2.0586 | 20.4951 | 3.3744 | 2.4252 | 15.876 | 19.1588 | 3.1544 | 2.2671 | 15.5142 | 19.4419 | 3.201 | 2.3006 | 15.1826 | 18.3616 | 3.0231 | 2.1728 | 14.9667 | 17.3662 | 2.8592 | 2.055 | 14.7521 | 19.2377 | 3.1673 | 2.2764 | 14.4914 | 17.0659 | 2.8098 | 2.0194 | 11.2622 | 16.1927 | 2.666 | 1.9161 | 11.0248 | 14.7513 | 2.4287 | 1.7456 | 10.613 | 12.7863 | 2.1052 | 1.513 | 9.5435 | 9.791 | 1.612 | 1.1586 | 8.2497 | 7.6283 | 1.2559 | 0.90267 | 6.1407 | 8.3008 | 1.3667 | 0.98225 | 4.6405 | 18.9008 | 3.1119 | 2.2366 | 3.2801 | 30.2926 | 4.9875 | 3.5846 | 2.5501 | 20.4951 | 3.3744 | 2.4252 | 15.876 | 19.2683 | 3.1724 | 2.2801 | 15.2825 | 19.8386 | 3.2663 | 2.3475 | 14.8082 | 19.4798 | 3.2072 | 2.3051 | 14.4653 | 17.1852 | 2.8294 | 2.0336 | 14.0657 | 16.8382 | 2.7723 | 1.9925 | 12.9913 | 13.1637 | 2.1673 | 1.5577 | 9.5806 | 11.8608 | 1.9528 | 1.4035 | 8.5886 | 10.7527 | 1.7703 | 1.2724 | 7.5285 | 8.6458 | 1.4235 | 1.0231 | 5.2487 | 10.9153 | 1.7971 | 1.2916 | 1.5196 | 5.6379 | 0.92824 | 0.66715 | -1.4466 | 2.8312 | 0.46613 | 0.33502 | -3.744 | 18.0582 | 2.9731 | 2.1369 | -5.3149 | 16.8606 | 2.776 | 1.9951 | -4.7639
CHESTER RD T11 & T12 | STRETFORD | SOUTH MANCHESTER | 381030 | 396165 | 25.6334 | 9.4014 | 6.8582 | 10.5138 | 25.6949 | 8.9783 | 6.5495 | 7.9919 | 25.8273 | 8.7374 | 6.3738 | 7.0656 | 25.959 | 8.6693 | 6.3241 | 6.7525 | 26.0989 | 8.5931 | 6.2685 | 6.4495 | 26.2692 | 8.5116 | 6.2091 | 6.1407 | 26.4814 | 8.4126 | 6.1369 | 5.8348 | 26.7539 | 8.3113 | 6.063 | 5.5204 | 27.0634 | 8.1869 | 5.9723 | 5.1192 | 27.3462 | 8.0625 | 5.8815 | 4.7175 | 28.2181 | 7.7507 | 5.6541 | 3.4948 | 28.9471 | 7.4725 | 5.4511 | 1.9552 | 29.4012 | 7.3829 | 5.3857 | 0.64968 | 29.6983 | 7.4743 | 5.4524 | -0.72019 | 29.8272 | 7.3973 | 5.3962 | -1.8901 | 25.6204 | 9.4014 | 6.8582 | 10.5138 | 25.6679 | 9.3613 | 6.829 | 9.9907 | 25.7627 | 9.2809 | 6.7703 | 9.6911 | 25.8441 | 9.2988 | 6.7833 | 9.5037 | 25.926 | 9.2487 | 6.7468 | 9.3435 | 26.0265 | 9.162 | 6.6836 | 9.1851 | 26.1452 | 8.941 | 6.5224 | 9.0103 | 26.2827 | 8.8664 | 6.4679 | 8.8066 | 26.4431 | 8.7834 | 6.4073 | 8.5203 | 26.6196 | 8.6957 | 6.3434 | 8.2277 | 27.2377 | 8.4365 | 6.1543 | 7.4325 | 27.9534 | 8.2995 | 6.0544 | 6.4713 | 28.6725 | 8.2105 | 5.9894 | 5.5249 | 29.4387 | 8.2681 | 6.0315 | 4.4638 | 29.959 | 8.3402 | 6.0841 | 3.6446 | 25.6398 | 9.4014 | 6.8582 | 10.5138 | 25.7078 | 8.9027 | 6.4944 | 7.5983 | 25.8487 | 8.5469 | 6.2348 | 6.2929 | 25.992 | 8.3998 | 6.1275 | 5.6783 | 26.1424 | 8.2626 | 6.0274 | 5.077 | 26.321 | 8.1964 | 5.9791 | 4.4721 | 26.5381 | 8.0301 | 5.8579 | 3.8718 | 26.8079 | 7.866 | 5.7381 | 3.2675 | 27.0263 | 7.6836 | 5.6051 | 2.6147 | 27.2641 | 7.5048 | 5.4747 | 1.9666 | 28.0861 | 7.0135 | 5.1162 | -0.02084 | 28.8689 | 6.5813 | 4.801 | -2.3244 | 29.3749 | 6.3788 | 4.6533 | -4.1655 | 29.656 | 6.494 | 4.7372 | -5.1926 | 29.6863 | 6.4657 | 4.7166 | -5.9383 | 25.6398 | 9.4014 | 6.8582 | 10.5138 | 25.665 | 9.0453 | 6.5984 | 8.4448 | 25.7655 | 8.8268 | 6.439 | 7.3301 | 25.8628 | 8.7488 | 6.3821 | 6.7387 | 25.9752 | 8.5557 | 6.2413 | 6.1537 | 26.1465 | 8.4546 | 6.1675 | 5.5496 | 26.3713 | 8.3418 | 6.0852 | 4.8792 | 26.6451 | 8.2074 | 5.9872 | 3.9857 | 26.9402 | 8.0332 | 5.8601 | 3.0217 | 27.2056 | 7.864 | 5.7367 | 2.0619 | 28.0294 | 7.9116 | 5.7714 | -0.45672 | 28.7134 | 7.3611 | 5.3698 | -2.7098 | 29.1129 | 6.93 | 5.0554 | -4.4524 | 29.3201 | 6.8319 | 4.9837 | -5.0653 | 29.29 | 6.7674 | 4.9367 | -4.7311 | 25.6334 | 9.4014 | 6.8582 | 10.5138 | 25.6869 | 9.2532 | 6.7501 | 9.6393 | 25.7952 | 9.0878 | 6.6294 | 9.0625 | 25.8891 | 9.0218 | 6.5813 | 8.7787 | 25.9875 | 8.9557 | 6.5331 | 8.5254 | 26.1336 | 8.8753 | 6.4744 | 8.263 | 26.3272 | 8.792 | 6.4136 | 7.9881 | 26.5538 | 8.696 | 6.3436 | 7.6962 | 26.8095 | 8.5749 | 6.2553 | 7.3053 | 27.0874 | 8.4532 | 6.1665 | 6.905 | 27.8956 | 8.2017 | 5.983 | 5.9554 | 28.655 | 8.0782 | 5.8929 | 5.1506 | 29.1704 | 8.1304 | 5.931 | 4.5191 | 29.5137 | 8.3977 | 6.126 | 3.9284 | 29.6361 | 8.5157 | 6.2121 | 3.6318 | 25.6334 | 9.4014 | 6.8582 | 10.5138 | 25.6767 | 8.8307 | 6.4419 | 7.2604 | 25.8048 | 8.5848 | 6.2625 | 5.8812 | 25.9327 | 8.4919 | 6.1948 | 5.2592 | 26.0649 | 8.2762 | 6.0373 | 4.6495 | 26.221 | 8.1884 | 5.9733 | 4.0393 | 26.4135 | 8.0668 | 5.8846 | 3.369 | 26.666 | 7.9301 | 5.7849 | 2.4885 | 26.9347 | 7.758 | 5.6593 | 1.5474 | 27.1753 | 7.5863 | 5.5341 | 0.58857 | 27.9783 | 7.6184 | 5.5575 | -1.9522 | 28.7269 | 7.0511 | 5.1437 | -4.2628 | 29.2066 | 6.6018 | 4.8159 | -6.0759 | 29.4528 | 6.486 | 4.7315 | -6.7616 | 29.4331 | 6.405 | 4.6723 | -6.5068
CHESTER RD T13 | STRETFORD | SOUTH MANCHESTER | 381040 | 396175 | 18.8421 | 18.8421 | 17.2202 | 14.6684 | 18.9085 | 18.9085 | 17.0409 | 13.143 | 18.9442 | 18.9442 | 16.8897 | 12.1301 | 18.9792 | 18.9792 | 16.7404 | 11.2356 | 19.0157 | 19.0157 | 16.6099 | 10.188 | 19.0541 | 19.0541 | 16.4568 | 9.1385 | 19.0945 | 19.0945 | 16.2956 | 8.2419 | 19.1386 | 19.1386 | 16.2466 | 7.6438 | 19.1769 | 19.1769 | 16.159 | 7.0349 | 19.2139 | 19.2139 | 16.0699 | 6.4295 | 19.3317 | 19.3317 | 15.856 | 5.0085 | 19.4517 | 19.4517 | 15.7685 | 4.444 | 19.529 | 19.529 | 15.7202 | 4.0106 | 19.6084 | 19.6084 | 15.7777 | 3.5621 | 19.6799 | 19.6799 | 15.8093 | 3.1584 | 18.8457 | 18.8457 | 17.2202 | 14.6684 | 18.9075 | 18.9075 | 17.1975 | 14.283 | 18.9421 | 18.9421 | 17.1729 | 14.0822 | 18.9766 | 18.9766 | 17.1382 | 13.8901 | 19.0146 | 19.0146 | 17.0995 | 13.6465 | 19.0569 | 19.0569 | 17.0528 | 13.3986 | 19.1017 | 19.1017 | 16.9891 | 13.1878 | 19.1444 | 19.1444 | 16.9585 | 13.0552 | 19.1747 | 19.1747 | 16.9318 | 12.9385 | 19.2058 | 19.2058 | 16.9047 | 12.8192 | 19.298 | 19.298 | 16.8234 | 12.466 | 19.3878 | 19.3878 | 16.7492 | 12.1127 | 19.4702 | 19.4702 | 16.6968 | 11.7886 | 19.5631 | 19.5631 | 16.7533 | 11.418 | 19.6463 | 19.6463 | 16.7701 | 11.089 | 18.8406 | 18.8406 | 17.2202 | 14.6684 | 18.9125 | 18.9125 | 17.0022 | 12.9155 | 18.9517 | 18.9517 | 16.8475 | 11.8462 | 18.9912 | 18.9912 | 16.7177 | 10.936 | 19.0327 | 19.0327 | 16.5701 | 9.8718 | 19.0768 | 19.0768 | 16.3884 | 8.8041 | 19.1239 | 19.1239 | 16.254 | 7.8872 | 19.1755 | 19.1755 | 16.1709 | 7.2669 | 19.2185 | 19.2185 | 16.0753 | 6.6442 | 19.2601 | 19.2601 | 15.9774 | 6.0243 | 19.3935 | 19.3935 | 15.7405 | 4.5591 | 19.5315 | 19.5315 | 15.6333 | 3.9944 | 19.6297 | 19.6297 | 15.5779 | 3.5899 | 19.7188 | 19.7188 | 15.6278 | 3.1986 | 19.7916 | 19.7916 | 15.6573 | 2.8583 | 18.8406 | 18.8406 | 17.2202 | 14.6684 | 18.8841 | 18.8841 | 17.0543 | 13.3799 | 18.9261 | 18.9261 | 16.9318 | 12.419 | 18.9539 | 18.9539 | 16.7994 | 11.5282 | 18.9846 | 18.9846 | 16.6717 | 10.4805 | 19.0218 | 19.0218 | 16.5183 | 9.4215 | 19.0639 | 19.0639 | 16.3758 | 8.4944 | 19.1119 | 19.1119 | 16.2852 | 7.8185 | 19.1567 | 19.1567 | 16.1769 | 7.1369 | 19.2003 | 19.2003 | 16.0933 | 6.4608 | 19.331 | 19.331 | 15.9607 | 4.9373 | 19.4494 | 19.4494 | 15.8419 | 4.4249 | 19.5293 | 19.5293 | 15.7665 | 4.0733 | 19.6071 | 19.6071 | 15.85 | 3.7753 | 19.6694 | 19.6694 | 15.7801 | 3.5817 | 18.8421 | 18.8421 | 17.2202 | 14.6684 | 18.9043 | 18.9043 | 17.1455 | 13.9247 | 18.9388 | 18.9388 | 16.996 | 13.079 | 18.968 | 18.968 | 16.8886 | 12.1995 | 18.998 | 18.998 | 16.7545 | 11.1732 | 19.0328 | 19.0328 | 16.5837 | 10.1396 | 19.0705 | 19.0705 | 16.4403 | 9.2518 | 19.1098 | 19.1098 | 16.3816 | 8.6613 | 19.1461 | 19.1461 | 16.2955 | 8.0531 | 19.1821 | 19.1821 | 16.2059 | 7.4444 | 19.2917 | 19.2917 | 16.0056 | 6.0926 | 19.4047 | 19.4047 | 15.9468 | 5.6971 | 19.4918 | 19.4918 | 15.9227 | 5.4 | 19.5859 | 19.5859 | 16.0064 | 5.0752 | 19.6606 | 19.6606 | 16.0633 | 4.7908 | 18.8421 | 18.8421 | 17.2202 | 14.6684 | 18.9025 | 18.9025 | 16.9589 | 12.7289 | 18.9404 | 18.9404 | 16.8271 | 11.6198 | 18.9781 | 18.9781 | 16.6899 | 10.7077 | 19.0177 | 19.0177 | 16.5594 | 9.6411 | 19.0593 | 19.0593 | 16.4027 | 8.5727 | 19.1047 | 19.1047 | 16.2624 | 7.6378 | 19.1601 | 19.1601 | 16.1671 | 6.9451 | 19.2076 | 19.2076 | 16.0568 | 6.2534 | 19.2536 | 19.2536 | 15.9719 | 5.5683 | 19.3871 | 19.3871 | 15.8329 | 4.0256 | 19.5017 | 19.5017 | 15.7112 | 3.5069 | 19.5836 | 19.5836 | 15.6333 | 3.1483 | 19.6618 | 19.6618 | 15.716 | 2.854 | 19.7266 | 19.7266 | 15.6421 | 2.6359
CHORLEY SOUTH | WRIGHTINGTON | PENWORTHAM WEST / STANAH | 358658 | 417041 | 23.7397 | 14.5063 | 10.426 | 6.9631 | 23.8932 | 14.2612 | 10.2498 | 5.7556 | 24.1063 | 13.9691 | 10.0399 | 5.1222 | 24.3796 | 13.6191 | 9.7883 | 4.6375 | 24.6878 | 13.2577 | 9.5285 | 3.9701 | 24.9893 | 12.7136 | 9.1375 | 3.3 | 25.334 | 12.5405 | 9.0131 | 2.8211 | 25.6609 | 12.3368 | 8.8667 | 2.364 | 25.8856 | 12.1396 | 8.725 | 1.8426 | 26.1026 | 11.9522 | 8.5903 | 1.3576 | 26.942 | 11.1914 | 8.0435 | -1.2769 | 27.9102 | 10.2207 | 7.3458 | -5.591 | 28.4327 | 9.396 | 6.7531 | -9.0208 | 28.8547 | 8.4768 | 6.0925 | -12.633 | 29.1641 | 7.6171 | 5.4746 | -15.8745 | 23.696 | 14.5063 | 10.426 | 6.9631 | 23.8086 | 14.4092 | 10.3562 | 6.4294 | 23.9189 | 14.3028 | 10.2797 | 6.1052 | 24.0632 | 14.1435 | 10.1652 | 5.8135 | 24.2594 | 13.9775 | 10.0459 | 5.4612 | 24.501 | 13.7705 | 9.8971 | 5.052 | 24.7868 | 13.4525 | 9.6686 | 4.494 | 25.111 | 13.1925 | 9.4817 | 3.7535 | 25.2889 | 13.01 | 9.3505 | 3.2205 | 25.474 | 12.8252 | 9.2177 | 2.6871 | 26.0514 | 12.2049 | 8.7719 | 0.90441 | 26.6168 | 11.731 | 8.4313 | -0.95386 | 27.0707 | 11.202 | 8.0511 | -2.701 | 27.5451 | 10.5898 | 7.6111 | -4.6569 | 27.9042 | 9.8707 | 7.0942 | -5.9628 | 23.7588 | 14.5063 | 10.426 | 6.9631 | 23.929 | 14.209 | 10.2123 | 5.633 | 24.1704 | 13.7746 | 9.9001 | 5.0054 | 24.4853 | 13.4652 | 9.6777 | 4.5745 | 24.8062 | 13.0179 | 9.3562 | 3.964 | 25.1542 | 12.5254 | 9.0022 | 3.3606 | 25.4837 | 12.3188 | 8.8537 | 2.9745 | 25.7738 | 12.106 | 8.7008 | 2.6198 | 26.0089 | 11.906 | 8.5571 | 2.2211 | 26.235 | 11.7013 | 8.41 | 1.8372 | 27.1139 | 10.8673 | 7.8106 | -0.49154 | 28.1368 | 9.8025 | 7.0452 | -4.5414 | 28.6297 | 8.9026 | 6.3985 | -7.7397 | 29.0457 | 7.9012 | 5.6787 | -11.0751 | 29.3187 | 7.0386 | 5.0588 | -14.0007 | 23.7588 | 14.5063 | 10.426 | 6.9631 | 23.7979 | 14.3296 | 10.299 | 6.233 | 23.9213 | 13.9704 | 10.0408 | 5.7701 | 24.0942 | 13.68 | 9.8321 | 5.3942 | 24.3454 | 13.2739 | 9.5402 | 4.8085 | 24.6752 | 12.7445 | 9.1597 | 4.1873 | 25.0475 | 12.6008 | 9.0565 | 3.548 | 25.4566 | 12.2124 | 8.7773 | 2.2394 | 25.7492 | 11.8463 | 8.5142 | 0.87713 | 26.0391 | 11.4655 | 8.2405 | -0.47111 | 26.9208 | 10.4374 | 7.5016 | -4.3589 | 27.7788 | 9.4128 | 6.7652 | -8.2201 | 28.2294 | 8.5317 | 6.1319 | -11.1632 | 28.5648 | 7.8098 | 5.613 | -13.183 | 28.6257 | 7.5411 | 5.4199 | -12.527 | 23.7397 | 14.5063 | 10.426 | 6.9631 | 23.8717 | 14.3534 | 10.316 | 6.1764 | 24.0215 | 14.1039 | 10.1367 | 5.6651 | 24.1971 | 13.7741 | 9.8997 | 5.2744 | 24.424 | 13.4509 | 9.6675 | 4.7748 | 24.7305 | 12.917 | 9.2837 | 4.2482 | 25.0756 | 12.7823 | 9.1869 | 3.8643 | 25.4157 | 12.5922 | 9.0503 | 3.4587 | 25.6268 | 12.3959 | 8.9092 | 2.9168 | 25.8391 | 12.1931 | 8.7634 | 2.3821 | 26.5213 | 11.6014 | 8.3382 | 0.65551 | 27.2509 | 11.0615 | 7.9501 | -1.2946 | 27.7701 | 10.6249 | 7.6364 | -2.5912 | 28.2516 | 10.1371 | 7.2857 | -3.82 | 28.5707 | 9.7347 | 6.9965 | -4.628 | 23.7397 | 14.5063 | 10.426 | 6.9631 | 23.8296 | 14.2176 | 10.2184 | 5.6993 | 24.0328 | 13.8153 | 9.9293 | 5.0406 | 24.3031 | 13.4881 | 9.6942 | 4.5316 | 24.6183 | 13.0758 | 9.3979 | 3.8259 | 24.9158 | 12.469 | 8.9617 | 3.1276 | 25.2654 | 12.3571 | 8.8813 | 2.3973 | 25.6723 | 11.9486 | 8.5877 | 0.95521 | 25.9784 | 11.5647 | 8.3118 | -0.50488 | 26.2771 | 11.1665 | 8.0256 | -1.9496 | 27.1555 | 10.0813 | 7.2456 | -6.1276 | 27.9899 | 9.0032 | 6.4708 | -10.2371 | 28.4347 | 8.0774 | 5.8054 | -13.4275 | 28.7456 | 7.2859 | 5.2365 | -15.7564 | 28.8146 | 6.9574 | 5.0004 | -15.4621
CHORLTON | WEST DIDSBURY | SOUTH MANCHESTER | 381411 | 393754 | 19.5555 | 19.5555 | 18.1802 | 10.9261 | 19.603 | 19.603 | 18.1072 | 10.5211 | 19.6693 | 19.6693 | 18.0538 | 10.2652 | 19.7455 | 19.7455 | 17.9958 | 10.0437 | 19.8223 | 19.8223 | 17.9286 | 9.7764 | 19.9046 | 19.9046 | 17.8263 | 9.5068 | 19.984 | 19.984 | 17.7405 | 9.2585 | 20.0779 | 20.0779 | 17.6586 | 9.0237 | 20.1482 | 20.1482 | 17.5954 | 8.7813 | 20.2142 | 20.2142 | 17.5635 | 8.5597 | 20.4402 | 20.4402 | 17.3537 | 7.3803 | 20.6959 | 20.6959 | 17.0992 | 5.6388 | 20.8776 | 20.8776 | 16.8976 | 4.3929 | 21.0322 | 21.0322 | 16.7022 | 3.3358 | 21.1189 | 21.1189 | 16.5777 | 2.7621 | 19.542 | 19.542 | 18.1802 | 10.9261 | 19.5769 | 19.5769 | 18.1607 | 10.8103 | 19.616 | 19.616 | 18.1347 | 10.689 | 19.6675 | 19.6675 | 18.098 | 10.5463 | 19.7371 | 19.7371 | 18.053 | 10.3575 | 19.8169 | 19.8169 | 18.002 | 10.1685 | 19.9128 | 19.9128 | 17.9147 | 9.943 | 20.022 | 20.022 | 17.8556 | 9.6871 | 20.0679 | 20.0679 | 17.8032 | 9.4815 | 20.1158 | 20.1158 | 17.7466 | 9.2691 | 20.2596 | 20.2596 | 17.6078 | 8.6577 | 20.3935 | 20.3935 | 17.4894 | 8.1169 | 20.5057 | 20.5057 | 17.378 | 7.6723 | 20.6081 | 20.6081 | 17.2621 | 7.2712 | 20.6672 | 20.6672 | 17.1553 | 7.0507 | 19.5611 | 19.5611 | 18.1802 | 10.9261 | 19.6209 | 19.6209 | 18.0899 | 10.427 | 19.7028 | 19.7028 | 18.0121 | 10.1073 | 19.7996 | 19.7996 | 17.9325 | 9.8322 | 19.8881 | 19.8881 | 17.8479 | 9.5068 | 19.9765 | 19.9765 | 17.7233 | 9.1764 | 20.0767 | 20.0767 | 17.6142 | 8.871 | 20.1942 | 20.1942 | 17.5303 | 8.5713 | 20.2827 | 20.2827 | 17.4958 | 8.2719 | 20.3665 | 20.3665 | 17.4362 | 7.9763 | 20.646 | 20.646 | 17.1761 | 6.6102 | 20.9329 | 20.9329 | 16.899 | 4.9162 | 21.1258 | 21.1258 | 16.689 | 3.8587 | 21.2773 | 21.2773 | 16.5127 | 3.1522 | 21.3381 | 21.3381 | 16.4347 | 3.1441 | 19.5611 | 19.5611 | 18.1802 | 10.9261 | 19.5664 | 19.5664 | 18.1243 | 10.6783 | 19.6084 | 19.6084 | 18.0749 | 10.4591 | 19.6677 | 19.6677 | 17.9978 | 10.252 | 19.7368 | 19.7368 | 17.9364 | 9.9705 | 19.8085 | 19.8085 | 17.8516 | 9.6424 | 19.9 | 19.9 | 17.7413 | 9.2363 | 20.0147 | 20.0147 | 17.6343 | 8.5544 | 20.1112 | 20.1112 | 17.5022 | 7.8878 | 20.2043 | 20.2043 | 17.3813 | 7.2469 | 20.4808 | 20.4808 | 17.1005 | 5.4828 | 20.7435 | 20.7435 | 16.8497 | 4.0638 | 20.9143 | 20.9143 | 16.673 | 3.2775 | 21.0287 | 21.0287 | 16.5572 | 3.1082 | 21.0263 | 21.0263 | 16.571 | 3.9062 | 19.5555 | 19.5555 | 18.1802 | 10.9261 | 19.5956 | 19.5956 | 18.1401 | 10.7509 | 19.6422 | 19.6422 | 18.1002 | 10.587 | 19.6949 | 19.6949 | 18.0539 | 10.4406 | 19.751 | 19.751 | 18.0016 | 10.2755 | 19.827 | 19.827 | 17.9086 | 10.0876 | 19.9127 | 19.9127 | 17.8297 | 9.8878 | 19.9991 | 19.9991 | 17.7492 | 9.687 | 20.063 | 20.063 | 17.6851 | 9.4562 | 20.126 | 20.126 | 17.6569 | 9.2264 | 20.3245 | 20.3245 | 17.506 | 8.4972 | 20.5291 | 20.5291 | 17.3826 | 7.7807 | 20.6759 | 20.6759 | 17.2796 | 7.3061 | 20.8086 | 20.8086 | 17.17 | 6.8999 | 20.8743 | 20.8743 | 17.104 | 6.7579 | 19.5555 | 19.5555 | 18.1802 | 10.9261 | 19.5808 | 19.5808 | 18.0981 | 10.4925 | 19.6516 | 19.6516 | 18.0317 | 10.1652 | 19.743 | 19.743 | 17.9432 | 9.8659 | 19.8288 | 19.8288 | 17.8717 | 9.5065 | 19.9087 | 19.9087 | 17.7831 | 9.1431 | 20.0043 | 20.0043 | 17.663 | 8.6989 | 20.1367 | 20.1367 | 17.5516 | 7.9427 | 20.2426 | 20.2426 | 17.4079 | 7.2143 | 20.3435 | 20.3435 | 17.2851 | 6.5142 | 20.6298 | 20.6298 | 16.9797 | 4.5918 | 20.8801 | 20.8801 | 16.7129 | 3.0676 | 21.0431 | 21.0431 | 16.5209 | 2.1782 | 21.1485 | 21.1485 | 16.3893 | 1.8855 | 21.1589 | 21.1589 | 16.3819 | 2.5108
CHURCH | HUNCOAT | PADIHAM | 374687 | 428919 | 13.8611 | 13.8611 | 13.8611 | 8.0129 | 13.9292 | 13.9292 | 13.9292 | 7.8493 | 13.9877 | 13.9877 | 13.9877 | 7.8128 | 14.0467 | 14.0467 | 14.0467 | 7.8016 | 14.1259 | 14.1259 | 14.1259 | 7.7387 | 14.2266 | 14.2266 | 14.2266 | 7.6609 | 14.3381 | 14.3381 | 14.3381 | 7.584 | 14.4465 | 14.4465 | 14.4465 | 7.5049 | 14.563 | 14.563 | 14.563 | 7.4036 | 14.6877 | 14.6877 | 14.6877 | 7.2999 | 14.9912 | 14.9912 | 14.9912 | 6.1762 | 15.3447 | 15.3447 | 15.3447 | 4.3802 | 15.6095 | 15.6095 | 15.6095 | 2.8794 | 15.8611 | 15.8611 | 15.8611 | 1.3111 | 16.051 | 16.051 | 16.051 | 0.051732 | 13.849 | 13.849 | 13.849 | 8.0129 | 13.8994 | 13.8994 | 13.8994 | 7.9081 | 13.9335 | 13.9335 | 13.9335 | 7.8602 | 13.9754 | 13.9754 | 13.9754 | 7.8221 | 14.0321 | 14.0321 | 14.0321 | 7.7639 | 14.1051 | 14.1051 | 14.1051 | 7.6954 | 14.1893 | 14.1893 | 14.1893 | 7.5935 | 14.2866 | 14.2866 | 14.2866 | 7.4547 | 14.3711 | 14.3711 | 14.3711 | 7.3512 | 14.4525 | 14.4525 | 14.4525 | 7.2415 | 14.7067 | 14.7067 | 14.7067 | 6.8715 | 15.0155 | 15.0155 | 15.0155 | 6.2915 | 15.2101 | 15.2101 | 15.2101 | 5.719 | 15.4129 | 15.4129 | 15.4129 | 5.1026 | 15.552 | 15.552 | 15.552 | 4.7039 | 13.8642 | 13.8642 | 13.8642 | 8.0129 | 13.9234 | 13.9234 | 13.9234 | 7.8384 | 13.9787 | 13.9787 | 13.9787 | 7.8083 | 14.039 | 14.039 | 14.039 | 7.8128 | 14.1139 | 14.1139 | 14.1139 | 7.767 | 14.2074 | 14.2074 | 14.2074 | 7.7099 | 14.315 | 14.315 | 14.315 | 7.6651 | 14.4116 | 14.4116 | 14.4116 | 7.6192 | 14.5112 | 14.5112 | 14.5112 | 7.5589 | 14.6215 | 14.6215 | 14.6215 | 7.4937 | 14.9547 | 14.9547 | 14.9547 | 6.483 | 15.3256 | 15.3256 | 15.3256 | 4.6808 | 15.608 | 15.608 | 15.608 | 3.1473 | 15.8547 | 15.8547 | 15.8547 | 1.5955 | 16.0157 | 16.0157 | 16.0157 | 0.48757 | 13.8643 | 13.8643 | 13.8643 | 8.0129 | 13.8905 | 13.8905 | 13.8905 | 8.0255 | 13.9293 | 13.9293 | 13.9293 | 8.0374 | 13.9747 | 13.9747 | 13.9747 | 8.0568 | 14.0404 | 14.0404 | 14.0404 | 8.0137 | 14.1369 | 14.1369 | 14.1369 | 7.954 | 14.277 | 14.277 | 14.277 | 7.7825 | 14.4536 | 14.4536 | 14.4536 | 7.2291 | 14.5819 | 14.5819 | 14.5819 | 6.6592 | 14.6975 | 14.6975 | 14.6975 | 6.0903 | 15.055 | 15.055 | 15.055 | 4.4349 | 15.3858 | 15.3858 | 15.3858 | 2.7585 | 15.625 | 15.625 | 15.625 | 1.4028 | 15.7758 | 15.7758 | 15.7758 | 0.5022 | 15.7568 | 15.7568 | 15.7568 | 1.0621 | 13.8609 | 13.8609 | 13.8609 | 8.0129 | 13.9136 | 13.9136 | 13.9136 | 7.8808 | 13.9522 | 13.9522 | 13.9522 | 7.861 | 13.9975 | 13.9975 | 13.9975 | 7.874 | 14.0497 | 14.0497 | 14.0497 | 7.8698 | 14.122 | 14.122 | 14.122 | 7.8511 | 14.221 | 14.221 | 14.221 | 7.8084 | 14.3231 | 14.3231 | 14.3231 | 7.7428 | 14.4199 | 14.4199 | 14.4199 | 7.6391 | 14.529 | 14.529 | 14.529 | 7.5262 | 14.861 | 14.861 | 14.861 | 6.9871 | 15.1174 | 15.1174 | 15.1174 | 6.2688 | 15.3008 | 15.3008 | 15.3008 | 5.7583 | 15.4532 | 15.4532 | 15.4532 | 5.328 | 15.519 | 15.519 | 15.519 | 5.1229 | 13.8609 | 13.8609 | 13.8609 | 8.0129 | 13.8849 | 13.8849 | 13.8849 | 7.9487 | 13.9302 | 13.9302 | 13.9302 | 7.9248 | 13.9924 | 13.9924 | 13.9924 | 7.9159 | 14.0627 | 14.0627 | 14.0627 | 7.8473 | 14.1489 | 14.1489 | 14.1489 | 7.7703 | 14.2724 | 14.2724 | 14.2724 | 7.5763 | 14.446 | 14.446 | 14.446 | 6.9963 | 14.5772 | 14.5772 | 14.5772 | 6.4134 | 14.7221 | 14.7221 | 14.7221 | 5.8282 | 15.0938 | 15.0938 | 15.0938 | 4.0946 | 15.4493 | 15.4493 | 15.4493 | 2.2974 | 15.7174 | 15.7174 | 15.7174 | 0.78765 | 15.9033 | 15.9033 | 15.9033 | -0.3118 | 15.9025 | 15.9025 | 15.9025 | 0.038125
CLARENDON RD | BLACKBURN | PENWORTHAM EAST / ROCHDALE | 369051 | 429883 | 26.2778 | 13.0752 | 9.5382 | 13.8644 | 26.3351 | 12.6052 | 9.1953 | 11.2634 | 26.4183 | 12.383 | 9.0332 | 10.6423 | 26.5189 | 12.1824 | 8.8869 | 10.4603 | 26.6507 | 11.9696 | 8.7316 | 10.2245 | 26.8046 | 11.2325 | 8.194 | 9.9742 | 26.9849 | 11.2721 | 8.2229 | 9.7216 | 27.2078 | 11.1198 | 8.1117 | 9.4535 | 27.392 | 10.9224 | 7.9678 | 9.1515 | 27.5409 | 10.714 | 7.8157 | 8.8656 | 28.1267 | 10.1351 | 7.3934 | 7.2806 | 28.7449 | 9.4889 | 6.922 | 4.7071 | 29.1586 | 8.899 | 6.4917 | 2.2326 | 29.4557 | 8.1987 | 5.9808 | -0.73538 | 29.6402 | 7.4917 | 5.4651 | -3.3651 | 26.2432 | 13.0752 | 9.5382 | 13.8644 | 26.308 | 12.9012 | 9.4112 | 13.0259 | 26.3567 | 12.7347 | 9.2898 | 12.7964 | 26.4134 | 12.5546 | 9.1584 | 12.7122 | 26.4947 | 12.4513 | 9.0831 | 12.6071 | 26.5993 | 12.2647 | 8.9469 | 12.479 | 26.7303 | 11.9065 | 8.6857 | 12.2972 | 26.8854 | 11.7869 | 8.5983 | 12.0563 | 26.9863 | 11.697 | 8.5328 | 11.8351 | 27.0926 | 11.5757 | 8.4443 | 11.6115 | 27.4276 | 11.3918 | 8.3102 | 10.9533 | 27.7687 | 11.2527 | 8.2087 | 10.2454 | 28.0851 | 11.0286 | 8.0452 | 9.4981 | 28.4112 | 10.441 | 7.6166 | 8.7022 | 28.64 | 10.3948 | 7.5828 | 8.1721 | 26.2846 | 13.0752 | 9.5382 | 13.8644 | 26.3486 | 12.5184 | 9.132 | 10.7977 | 26.4431 | 12.1984 | 8.8986 | 10.046 | 26.5599 | 12.0193 | 8.7679 | 9.8017 | 26.7117 | 11.6986 | 8.534 | 9.505 | 26.8892 | 11.1662 | 8.1456 | 9.1943 | 27.0981 | 10.9736 | 8.0051 | 8.8791 | 27.3403 | 10.7149 | 7.8164 | 8.5514 | 27.5018 | 10.4713 | 7.6386 | 8.2211 | 27.6574 | 10.2265 | 7.4601 | 7.9101 | 28.2606 | 9.5542 | 6.9697 | 6.2473 | 28.8296 | 8.8068 | 6.4244 | 3.6083 | 29.2527 | 8.196 | 5.9788 | 1.3576 | 29.6267 | 7.4963 | 5.4684 | -1.0543 | 29.8133 | 6.7793 | 4.9454 | -3.3297 | 26.2846 | 13.0752 | 9.5382 | 13.8644 | 26.253 | 12.7206 | 9.2795 | 11.8558 | 26.2884 | 12.5493 | 9.1545 | 11.33 | 26.3416 | 12.0245 | 8.7717 | 11.1367 | 26.4369 | 12.0028 | 8.7559 | 10.8728 | 26.5893 | 11.7081 | 8.5409 | 10.5653 | 26.7995 | 11.3413 | 8.2733 | 10.1067 | 27.0501 | 10.9476 | 7.9861 | 9.2165 | 27.2446 | 10.6079 | 7.7383 | 8.3084 | 27.4384 | 10.2519 | 7.4786 | 7.4153 | 28.0303 | 9.3812 | 6.8435 | 4.8247 | 28.6243 | 8.5908 | 6.2669 | 2.0235 | 28.961 | 7.8765 | 5.7458 | -0.38165 | 29.1994 | 7.1308 | 5.2018 | -2.0986 | 29.2035 | 7.0207 | 5.1215 | -1.5147 | 26.2778 | 13.0752 | 9.5382 | 13.8644 | 26.3252 | 12.7796 | 9.3225 | 12.2116 | 26.3794 | 12.5955 | 9.1882 | 11.7897 | 26.4338 | 12.3899 | 9.0383 | 11.6725 | 26.5119 | 12.2198 | 8.9142 | 11.545 | 26.6397 | 11.5472 | 8.4235 | 11.3766 | 26.8132 | 11.5685 | 8.439 | 11.1608 | 27.0091 | 11.4216 | 8.3319 | 10.9143 | 27.1714 | 11.2263 | 8.1895 | 10.6097 | 27.3254 | 11.0162 | 8.0362 | 10.3031 | 27.7744 | 10.5528 | 7.6981 | 9.3024 | 28.2543 | 10.1886 | 7.4324 | 8.2039 | 28.5986 | 9.9086 | 7.2282 | 7.3599 | 28.9009 | 9.5966 | 7.0006 | 6.4708 | 29.0345 | 9.2584 | 6.7539 | 5.8701 | 26.2778 | 13.0752 | 9.5382 | 13.8644 | 26.2712 | 12.498 | 9.1171 | 10.6068 | 26.3461 | 12.275 | 8.9544 | 9.8072 | 26.4475 | 11.6917 | 8.5289 | 9.5387 | 26.5825 | 11.6794 | 8.52 | 9.21 | 26.7363 | 11.3781 | 8.3002 | 8.8763 | 26.9342 | 11.0143 | 8.0348 | 8.4005 | 27.2392 | 10.6115 | 7.741 | 7.4572 | 27.4507 | 10.264 | 7.4875 | 6.5112 | 27.6516 | 9.9032 | 7.2243 | 5.584 | 28.2443 | 8.9893 | 6.5576 | 2.7299 | 28.8039 | 8.1354 | 5.9347 | -0.37993 | 29.1371 | 7.3736 | 5.379 | -3.0401 | 29.3518 | 6.6265 | 4.8339 | -5.02 | 29.36 | 6.41 | 4.676 | -4.6946
CLAUGHTON | LANCASTER | HEYSHAM | 355872 | 466268 | 8.1874 | 8.1874 | 8.1874 | 4.4355 | 8.2005 | 8.2005 | 8.2005 | 4.3765 | 8.2177 | 8.2177 | 8.2177 | 4.3353 | 8.2396 | 8.2396 | 8.2396 | 4.3168 | 8.2692 | 8.2692 | 8.2692 | 4.303 | 8.3059 | 8.3059 | 8.3059 | 4.2875 | 8.3512 | 8.3512 | 8.3512 | 4.2691 | 8.4058 | 8.4058 | 8.4058 | 4.2464 | 8.5287 | 8.5287 | 8.5287 | 4.1258 | 8.5675 | 8.5675 | 8.5675 | 4.0943 | 8.702 | 8.702 | 8.702 | 3.9664 | 8.8368 | 8.8368 | 8.8368 | 3.4001 | 8.9274 | 8.9274 | 8.9274 | 2.9293 | 8.9958 | 8.9958 | 8.9958 | 2.4643 | 9.0402 | 9.0402 | 9.0402 | 2.0388 | 8.1815 | 8.1815 | 8.1815 | 4.4355 | 8.1982 | 8.1982 | 8.1982 | 4.3934 | 8.2157 | 8.2157 | 8.2157 | 4.3431 | 8.239 | 8.239 | 8.239 | 4.3065 | 8.2713 | 8.2713 | 8.2713 | 4.272 | 8.3119 | 8.3119 | 8.3119 | 4.2307 | 8.3605 | 8.3605 | 8.3605 | 4.1569 | 8.4163 | 8.4163 | 8.4163 | 3.958 | 8.5208 | 8.5208 | 8.5208 | 3.8352 | 8.542 | 8.542 | 8.542 | 3.7991 | 8.6237 | 8.6237 | 8.6237 | 3.6875 | 8.7147 | 8.7147 | 8.7147 | 3.5765 | 8.7997 | 8.7997 | 8.7997 | 3.4794 | 8.8893 | 8.8893 | 8.8893 | 3.3803 | 8.9509 | 8.9509 | 8.9509 | 3.315 | 8.1889 | 8.1889 | 8.1889 | 4.4355 | 8.2033 | 8.2033 | 8.2033 | 4.3683 | 8.2225 | 8.2225 | 8.2225 | 4.3257 | 8.2473 | 8.2473 | 8.2473 | 4.3069 | 8.2802 | 8.2802 | 8.2802 | 4.2932 | 8.3204 | 8.3204 | 8.3204 | 4.2782 | 8.3698 | 8.3698 | 8.3698 | 4.2603 | 8.4983 | 8.4983 | 8.4983 | 4.1609 | 8.5339 | 8.5339 | 8.5339 | 4.1389 | 8.5706 | 8.5706 | 8.5706 | 4.1214 | 8.7105 | 8.7105 | 8.7105 | 4.019 | 8.8602 | 8.8602 | 8.8602 | 3.4809 | 8.964 | 8.964 | 8.964 | 3.0403 | 9.0389 | 9.0389 | 9.0389 | 2.6223 | 9.0813 | 9.0813 | 9.0813 | 2.2619 | 8.1889 | 8.1889 | 8.1889 | 4.4355 | 8.1818 | 8.1818 | 8.1818 | 4.4214 | 8.1879 | 8.1879 | 8.1879 | 4.3973 | 8.2932 | 8.2932 | 8.2932 | 4.2975 | 8.3072 | 8.3072 | 8.3072 | 4.3018 | 8.3342 | 8.3342 | 8.3342 | 4.3012 | 8.3738 | 8.3738 | 8.3738 | 4.2923 | 8.427 | 8.427 | 8.427 | 4.2451 | 8.4708 | 8.4708 | 8.4708 | 4.0533 | 8.5135 | 8.5135 | 8.5135 | 3.8638 | 8.6578 | 8.6578 | 8.6578 | 3.3154 | 8.7933 | 8.7933 | 8.7933 | 2.7995 | 8.8817 | 8.8817 | 8.8817 | 2.4136 | 8.9495 | 8.9495 | 8.9495 | 2.1904 | 8.9551 | 8.9551 | 8.9551 | 2.3953 | 8.1874 | 8.1874 | 8.1874 | 4.4355 | 8.1988 | 8.1988 | 8.1988 | 4.3867 | 8.2111 | 8.2111 | 8.2111 | 4.3514 | 8.2254 | 8.2254 | 8.2254 | 4.3396 | 8.2459 | 8.2459 | 8.2459 | 4.334 | 8.2772 | 8.2772 | 8.2772 | 4.3231 | 8.3201 | 8.3201 | 8.3201 | 4.3054 | 8.3712 | 8.3712 | 8.3712 | 4.2841 | 8.4932 | 8.4932 | 8.4932 | 4.1647 | 8.5283 | 8.5283 | 8.5283 | 4.1332 | 8.6548 | 8.6548 | 8.6548 | 4.0325 | 8.7867 | 8.7867 | 8.7867 | 3.7891 | 8.8782 | 8.8782 | 8.8782 | 3.5845 | 8.9471 | 8.9471 | 8.9471 | 3.3871 | 8.9751 | 8.9751 | 8.9751 | 3.3165 | 8.1874 | 8.1874 | 8.1874 | 4.4355 | 8.1872 | 8.1872 | 8.1872 | 4.3887 | 8.2025 | 8.2025 | 8.2025 | 4.3486 | 8.3184 | 8.3184 | 8.3184 | 4.2354 | 8.3415 | 8.3415 | 8.3415 | 4.2272 | 8.371 | 8.371 | 8.371 | 4.2184 | 8.4101 | 8.4101 | 8.4101 | 4.2021 | 8.4671 | 8.4671 | 8.4671 | 4.1651 | 8.5059 | 8.5059 | 8.5059 | 3.998 | 8.5466 | 8.5466 | 8.5466 | 3.8088 | 8.6888 | 8.6888 | 8.6888 | 3.252 | 8.8262 | 8.8262 | 8.8262 | 2.7214 | 8.9195 | 8.9195 | 8.9195 | 2.3147 | 8.9876 | 8.9876 | 8.9876 | 2.0615 | 8.9952 | 8.9952 | 8.9952 | 2.2289
BLACKBURN RD CLAYTON | HUNCOAT | PADIHAM | 374632 | 430529 | 25.1133 | 12.5418 | 9.149 | 19.2924 | 25.2082 | 12.2833 | 8.9605 | 18.602 | 25.282 | 11.8566 | 8.6492 | 18.3145 | 25.3784 | 11.357 | 8.2848 | 18.1089 | 25.5026 | 10.9122 | 7.9603 | 17.8506 | 25.6499 | 10.5677 | 7.709 | 17.5909 | 25.8244 | 10.2446 | 7.4733 | 17.3562 | 26.0377 | 10.0463 | 7.3286 | 17.1222 | 26.2433 | 9.911 | 7.2299 | 16.8425 | 26.4634 | 9.7586 | 7.1188 | 16.5613 | 27.2 | 9.4163 | 6.869 | 15.0656 | 27.8965 | 8.9316 | 6.5155 | 12.4327 | 28.3658 | 8.7353 | 6.3723 | 10.3824 | 28.7262 | 8.6433 | 6.3052 | 8.6238 | 28.9413 | 8.3187 | 6.0684 | 7.6045 | 25.0965 | 12.5418 | 9.149 | 19.2924 | 25.1743 | 12.4627 | 9.0914 | 19.1549 | 25.2252 | 12.2758 | 8.955 | 18.9904 | 25.2938 | 12.0199 | 8.7684 | 18.8548 | 25.3821 | 11.7736 | 8.5887 | 18.7192 | 25.486 | 11.5259 | 8.408 | 18.5634 | 25.6101 | 11.2043 | 8.1734 | 18.3774 | 25.7565 | 11.1144 | 8.1078 | 18.1592 | 25.8587 | 11.0255 | 8.0429 | 18.0079 | 25.9689 | 10.9275 | 7.9715 | 17.8491 | 26.382 | 10.6066 | 7.7374 | 17.2067 | 26.8661 | 10.2457 | 7.4741 | 16.2163 | 27.3184 | 10.1002 | 7.3679 | 15.3107 | 27.7798 | 10.012 | 7.3036 | 14.423 | 28.078 | 9.7521 | 7.114 | 13.7783 | 25.1177 | 12.5418 | 9.149 | 19.2924 | 25.2168 | 12.2064 | 8.9044 | 18.4573 | 25.3 | 11.6666 | 8.5106 | 18.0273 | 25.4069 | 11.0551 | 8.0646 | 17.6922 | 25.5402 | 10.6333 | 7.7569 | 17.3163 | 25.6943 | 10.2709 | 7.4925 | 16.9311 | 25.8722 | 9.9091 | 7.2285 | 16.5616 | 26.0859 | 9.6373 | 7.0303 | 16.1837 | 26.2889 | 9.5372 | 6.9573 | 15.7872 | 26.5103 | 9.4219 | 6.8732 | 15.3826 | 27.3169 | 8.8752 | 6.4744 | 13.5201 | 28.1301 | 8.3361 | 6.081 | 11.2428 | 28.6946 | 8.0538 | 5.8751 | 9.6116 | 29.1117 | 7.893 | 5.7578 | 8.2465 | 29.3215 | 7.6339 | 5.5688 | 7.8504 | 25.1178 | 12.5418 | 9.149 | 19.2924 | 25.1961 | 12.2912 | 8.9662 | 18.7107 | 25.2582 | 11.9343 | 8.7059 | 18.3317 | 25.3434 | 11.4604 | 8.3602 | 18.0135 | 25.4594 | 11.1875 | 8.1611 | 17.6495 | 25.6121 | 10.9702 | 8.0026 | 17.2566 | 25.809 | 10.6887 | 7.7972 | 16.7435 | 26.0706 | 10.2828 | 7.5011 | 15.852 | 26.3346 | 10.1062 | 7.3723 | 14.9653 | 26.6111 | 9.8851 | 7.211 | 14.1095 | 27.4516 | 9.8775 | 7.2055 | 11.5208 | 28.1609 | 9.1681 | 6.688 | 9.3855 | 28.617 | 8.5533 | 6.2395 | 8.0662 | 28.9121 | 8.0314 | 5.8588 | 7.6218 | 28.9147 | 7.925 | 5.7811 | 8.5709 | 25.1131 | 12.5418 | 9.149 | 19.2924 | 25.1955 | 12.4088 | 9.052 | 19.1001 | 25.255 | 12.0201 | 8.7685 | 18.9194 | 25.3255 | 11.5348 | 8.4145 | 18.7538 | 25.4157 | 11.1054 | 8.1013 | 18.5905 | 25.5356 | 10.7676 | 7.8548 | 18.4119 | 25.6869 | 10.4433 | 7.6182 | 18.215 | 25.8647 | 10.2421 | 7.4715 | 17.9976 | 26.0316 | 10.1036 | 7.3704 | 17.7194 | 26.2173 | 9.9419 | 7.2525 | 17.4271 | 26.8601 | 9.7448 | 7.1087 | 16.4875 | 27.4834 | 9.6242 | 7.0207 | 15.488 | 27.9201 | 9.6969 | 7.0738 | 14.4743 | 28.2505 | 9.8909 | 7.2153 | 13.6082 | 28.414 | 9.7307 | 7.0984 | 13.2178 | 25.1131 | 12.5418 | 9.149 | 19.2924 | 25.2034 | 12.1914 | 8.8934 | 18.3877 | 25.284 | 11.801 | 8.6086 | 17.9381 | 25.3886 | 11.3206 | 8.2582 | 17.5795 | 25.5184 | 11.0477 | 8.0591 | 17.1816 | 25.667 | 10.8285 | 7.8992 | 16.7771 | 25.8503 | 10.5508 | 7.6966 | 16.2578 | 26.1037 | 10.1261 | 7.3869 | 15.3424 | 26.3468 | 9.9522 | 7.26 | 14.4401 | 26.6054 | 9.7284 | 7.0968 | 13.5692 | 27.4481 | 9.6962 | 7.0733 | 10.9896 | 28.2179 | 8.9449 | 6.5252 | 8.683 | 28.7454 | 8.2994 | 6.0543 | 7.2268 | 29.0974 | 7.6812 | 5.6034 | 6.4671 | 29.2236 | 7.5244 | 5.489 | 7.02
CLEVELEYS | BISPHAM | PENWORTHAM WEST / STANAH | 332286 | 443104 | 23.7906 | 13.2034 | 9.6317 | 8.991 | 23.8863 | 12.978 | 9.4672 | 8.1624 | 24.0298 | 12.842 | 9.3681 | 7.9724 | 24.2154 | 12.7246 | 9.2824 | 7.9171 | 24.4397 | 12.5653 | 9.1662 | 7.801 | 24.6958 | 12.4137 | 9.0556 | 7.6763 | 24.9894 | 12.2795 | 8.9577 | 7.5595 | 25.2957 | 12.1758 | 8.8821 | 7.447 | 25.4264 | 12.0842 | 8.8153 | 7.314 | 25.5407 | 11.9934 | 8.7491 | 7.2117 | 26.348 | 11.5691 | 8.4395 | 5.8243 | 26.9208 | 11.0237 | 8.0416 | 2.9967 | 27.2762 | 10.6588 | 7.7755 | 0.55546 | 27.5907 | 10.565 | 7.707 | -2.2201 | 27.7694 | 9.9754 | 7.2769 | -4.6752 | 23.7585 | 13.2034 | 9.6317 | 8.991 | 23.8356 | 13.1327 | 9.5801 | 8.7774 | 23.9175 | 13.0661 | 9.5315 | 8.6478 | 24.0247 | 12.975 | 9.4651 | 8.5145 | 24.1734 | 12.8591 | 9.3806 | 8.3192 | 24.3617 | 12.7381 | 9.2923 | 8.1027 | 24.5861 | 12.5407 | 9.1483 | 7.8235 | 24.8401 | 12.4053 | 9.0495 | 7.4905 | 24.9706 | 12.3029 | 8.9748 | 7.2925 | 25.0589 | 12.2045 | 8.903 | 7.0929 | 25.2978 | 11.9145 | 8.6914 | 6.4977 | 25.5312 | 11.6859 | 8.5247 | 5.9376 | 25.8479 | 11.55 | 8.4256 | 5.3451 | 26.2555 | 11.6675 | 8.5113 | 4.6858 | 26.5564 | 11.6748 | 8.5166 | 4.167 | 23.8042 | 13.2034 | 9.6317 | 8.991 | 23.9131 | 12.9302 | 9.4324 | 8.0593 | 24.0789 | 12.7427 | 9.2956 | 7.8726 | 24.2974 | 12.5774 | 9.175 | 7.8566 | 24.5632 | 12.4163 | 9.0575 | 7.7831 | 24.8692 | 12.2413 | 8.9299 | 7.7079 | 25.2044 | 12.1218 | 8.8427 | 7.6621 | 25.413 | 12.003 | 8.756 | 7.6241 | 25.5614 | 11.8889 | 8.6728 | 7.572 | 25.6905 | 11.7967 | 8.6055 | 7.539 | 26.564 | 11.3134 | 8.253 | 6.3719 | 27.1876 | 10.6935 | 7.8007 | 3.7393 | 27.479 | 10.2572 | 7.4825 | 1.4706 | 27.7294 | 10.0636 | 7.3412 | -1.1047 | 27.8547 | 9.3949 | 6.8534 | -3.3396 | 23.8042 | 13.2034 | 9.6317 | 8.991 | 23.8044 | 13.0409 | 9.5131 | 8.6033 | 23.875 | 12.9087 | 9.4168 | 8.5438 | 23.9808 | 12.7227 | 9.281 | 8.5305 | 24.1412 | 12.5897 | 9.184 | 8.4318 | 24.3962 | 12.4695 | 9.0963 | 8.3045 | 24.7177 | 12.2878 | 8.9638 | 8.0203 | 25.0911 | 12.0784 | 8.811 | 7.1776 | 25.3737 | 11.8786 | 8.6653 | 6.2921 | 25.5925 | 11.6957 | 8.5318 | 5.413 | 26.1682 | 11.9132 | 8.6905 | 2.8455 | 26.7423 | 11.222 | 8.1863 | 0.33726 | 27.0992 | 10.5757 | 7.7148 | -1.7207 | 27.3091 | 9.9912 | 7.2884 | -3.0789 | 27.2556 | 9.8019 | 7.1503 | -2.1472 | 23.7906 | 13.2034 | 9.6317 | 8.991 | 23.8718 | 13.0979 | 9.5547 | 8.7561 | 23.9669 | 12.9932 | 9.4783 | 8.7107 | 24.0773 | 12.8888 | 9.4022 | 8.7249 | 24.2241 | 12.7498 | 9.3008 | 8.7104 | 24.4531 | 12.6132 | 9.2011 | 8.6633 | 24.7514 | 12.4854 | 9.1079 | 8.5966 | 24.9961 | 12.3901 | 9.0384 | 8.5266 | 25.1033 | 12.3025 | 8.9745 | 8.4154 | 25.2079 | 12.2116 | 8.9082 | 8.3146 | 25.6165 | 11.9539 | 8.7202 | 7.8543 | 26.1516 | 11.7951 | 8.6044 | 7.2062 | 26.5639 | 11.7864 | 8.598 | 6.7423 | 26.9385 | 12.1388 | 8.8551 | 6.2585 | 27.116 | 11.9119 | 8.6896 | 6.0192 | 23.7906 | 13.2034 | 9.6317 | 8.991 | 23.8329 | 12.9478 | 9.4452 | 8.1658 | 23.9699 | 12.7852 | 9.3267 | 7.9483 | 24.1573 | 12.5824 | 9.1787 | 7.8288 | 24.3858 | 12.4327 | 9.0695 | 7.6321 | 24.644 | 12.3013 | 8.9737 | 7.436 | 24.9479 | 12.1059 | 8.8311 | 7.0678 | 25.3502 | 11.8766 | 8.6638 | 6.1128 | 25.6258 | 11.6605 | 8.5062 | 5.1521 | 25.8644 | 11.4631 | 8.3621 | 4.1987 | 26.4515 | 11.6276 | 8.4821 | 1.416 | 26.9664 | 10.9006 | 7.9518 | -1.2536 | 27.2815 | 10.2215 | 7.4565 | -3.4624 | 27.4829 | 9.6003 | 7.0033 | -5.0031 | 27.4278 | 9.3872 | 6.8479 | -4.2821
CLIFTON JUNCTION | KEARSLEY LOCAL | KEARSLEY | 379289 | 403073 | 21.8395 | 9.9525 | 7.1531 | 12.2816 | 21.8871 | 9.5553 | 6.8676 | 10.9553 | 21.9309 | 9.5478 | 6.8622 | 10.5773 | 21.9834 | 9.4807 | 6.814 | 10.477 | 22.056 | 9.3529 | 6.7221 | 10.3545 | 22.1409 | 9.1976 | 6.6105 | 10.2189 | 22.2404 | 9.0775 | 6.5242 | 10.0785 | 22.3578 | 8.9878 | 6.4597 | 9.9318 | 22.4918 | 8.892 | 6.3908 | 9.6986 | 22.6306 | 8.7873 | 6.3156 | 9.4686 | 23.1493 | 8.3712 | 6.0166 | 8.3404 | 23.7267 | 8.0752 | 5.8038 | 6.7091 | 24.1349 | 8.0209 | 5.7648 | 5.4433 | 24.4836 | 7.8992 | 5.6773 | 4.2361 | 24.637 | 7.5843 | 5.451 | 3.1323 | 21.849 | 9.9525 | 7.1531 | 12.2816 | 21.9082 | 9.703 | 6.9738 | 11.8422 | 21.9592 | 9.5771 | 6.8832 | 11.6589 | 22.0261 | 9.4805 | 6.8138 | 11.5825 | 22.0914 | 9.3679 | 6.7329 | 11.5157 | 22.169 | 9.2397 | 6.6408 | 11.442 | 22.2645 | 9.3507 | 6.7206 | 11.3012 | 22.3777 | 9.2233 | 6.629 | 11.1074 | 22.489 | 9.1042 | 6.5434 | 10.8964 | 22.6021 | 8.9757 | 6.451 | 10.6707 | 23.0101 | 8.6197 | 6.1951 | 9.942 | 23.4987 | 8.6534 | 6.2193 | 9.1581 | 23.84 | 8.6244 | 6.1985 | 8.4011 | 24.1672 | 8.416 | 6.0488 | 7.5794 | 24.3913 | 8.1504 | 5.8579 | 6.9972 | 21.8345 | 9.9525 | 7.1531 | 12.2816 | 21.8759 | 9.5714 | 6.8791 | 10.7463 | 21.9095 | 9.544 | 6.8594 | 10.3264 | 21.9465 | 9.4239 | 6.7732 | 10.2262 | 21.9985 | 9.2509 | 6.6488 | 10.1061 | 22.057 | 9.0719 | 6.5201 | 9.9748 | 22.12 | 8.9243 | 6.4141 | 9.8402 | 22.1932 | 8.8012 | 6.3256 | 9.7071 | 22.288 | 8.6695 | 6.2309 | 9.5477 | 22.3892 | 8.5177 | 6.1218 | 9.3959 | 22.8286 | 8.2905 | 5.9585 | 8.5992 | 23.3835 | 8.1478 | 5.856 | 7.1061 | 23.7849 | 7.9957 | 5.7467 | 5.9188 | 24.1088 | 7.7452 | 5.5667 | 4.8453 | 24.3381 | 7.5659 | 5.4378 | 3.9352 | 21.8345 | 9.9525 | 7.1531 | 12.2816 | 21.7975 | 9.6248 | 6.9175 | 11.2708 | 21.7972 | 9.7237 | 6.9886 | 10.967 | 21.8089 | 9.6069 | 6.9047 | 10.8785 | 21.8471 | 9.3978 | 6.7544 | 10.7605 | 21.9062 | 9.163 | 6.5856 | 10.6192 | 21.9885 | 8.9758 | 6.4511 | 10.4152 | 22.1265 | 9.0455 | 6.5012 | 10.0364 | 22.2967 | 9.0011 | 6.4693 | 9.6175 | 22.4762 | 8.8762 | 6.3795 | 9.1066 | 23.0259 | 8.5506 | 6.1455 | 7.5747 | 23.5273 | 8.1727 | 5.8739 | 6.1411 | 23.867 | 7.8619 | 5.6505 | 5.0905 | 24.0652 | 7.6238 | 5.4794 | 4.5186 | 24.0273 | 7.58 | 5.4479 | 4.8777 | 21.8395 | 9.9525 | 7.1531 | 12.2816 | 21.8796 | 9.6168 | 6.9118 | 11.4768 | 21.9056 | 9.6501 | 6.9357 | 11.2177 | 21.9312 | 9.601 | 6.9005 | 11.1501 | 21.9723 | 9.4842 | 6.8165 | 11.0917 | 22.0374 | 9.3553 | 6.7238 | 11.0194 | 22.125 | 9.2454 | 6.6449 | 10.9291 | 22.2235 | 9.1614 | 6.5845 | 10.819 | 22.3345 | 9.0796 | 6.5257 | 10.6404 | 22.4538 | 8.9904 | 6.4616 | 10.4578 | 22.8759 | 8.672 | 6.2327 | 9.7343 | 23.3075 | 8.493 | 6.1041 | 8.8557 | 23.5971 | 8.5746 | 6.1627 | 8.2595 | 23.8132 | 8.6281 | 6.2012 | 7.7891 | 23.9093 | 8.5314 | 6.1317 | 7.5696 | 21.8395 | 9.9525 | 7.1531 | 12.2816 | 21.8287 | 9.5411 | 6.8573 | 10.6328 | 21.8644 | 9.5879 | 6.891 | 10.1794 | 21.9156 | 9.4545 | 6.7951 | 10.0648 | 21.9886 | 9.2367 | 6.6386 | 9.9259 | 22.0693 | 9.0063 | 6.473 | 9.7798 | 22.1745 | 8.8213 | 6.34 | 9.5771 | 22.3437 | 8.8821 | 6.3837 | 9.1713 | 22.5274 | 8.8163 | 6.3364 | 8.6523 | 22.7203 | 8.6828 | 6.2405 | 8.1135 | 23.3397 | 8.3382 | 5.9928 | 6.4856 | 23.9383 | 7.9298 | 5.6993 | 4.9219 | 24.2449 | 7.5955 | 5.4591 | 3.7427 | 24.4138 | 7.3358 | 5.2724 | 3.0521 | 24.4066 | 7.2738 | 5.2278 | 3.3061
CLOVER HILL | NELSON | PADIHAM | 386638 | 437064 | 28.5473 | 13.5814 | 9.9075 | 18.9506 | 28.6052 | 13.5057 | 9.8522 | 18.8492 | 28.6658 | 13.365 | 9.7496 | 18.751 | 28.7379 | 13.1458 | 9.5897 | 18.6648 | 28.8202 | 12.8523 | 9.3756 | 18.5114 | 28.9151 | 12.5824 | 9.1787 | 18.3547 | 29.0242 | 12.3064 | 8.9773 | 18.2367 | 29.1568 | 12.0888 | 8.8186 | 18.1337 | 29.2522 | 11.9476 | 8.7156 | 17.9249 | 29.3431 | 11.8349 | 8.6334 | 17.7249 | 29.6666 | 11.2585 | 8.2129 | 16.1033 | 30.0482 | 10.7475 | 7.8402 | 13.1451 | 30.3382 | 10.2708 | 7.4924 | 10.5994 | 30.6077 | 9.6314 | 7.026 | 7.6803 | 30.7965 | 9.0932 | 6.6334 | 5.4212 | 28.5336 | 13.5814 | 9.9075 | 18.9506 | 28.5926 | 13.512 | 9.8568 | 18.8662 | 28.6467 | 13.3441 | 9.7343 | 18.7731 | 28.7118 | 13.2399 | 9.6583 | 18.6888 | 28.8008 | 13.1426 | 9.5873 | 18.5878 | 28.9127 | 12.9851 | 9.4725 | 18.4765 | 29.0476 | 12.6855 | 9.2539 | 18.3263 | 29.195 | 12.6045 | 9.1948 | 18.1269 | 29.2472 | 12.5288 | 9.1396 | 17.9281 | 29.3013 | 12.4763 | 9.1013 | 17.6789 | 29.4706 | 12.2351 | 8.9253 | 16.9487 | 29.636 | 12.0487 | 8.7894 | 16.2789 | 29.7811 | 11.9021 | 8.6824 | 15.6871 | 29.9226 | 11.6849 | 8.5239 | 15.1149 | 30.0189 | 11.4036 | 8.3188 | 14.7948 | 28.5531 | 13.5814 | 9.9075 | 18.9506 | 28.6146 | 13.4873 | 9.8388 | 18.8453 | 28.6831 | 13.3186 | 9.7158 | 18.753 | 28.7587 | 13.0722 | 9.536 | 18.6764 | 28.8514 | 12.7568 | 9.3059 | 18.5368 | 28.9585 | 12.44 | 9.0748 | 18.3974 | 29.0829 | 12.1672 | 8.8758 | 18.2986 | 29.2336 | 11.9088 | 8.6873 | 18.222 | 29.3409 | 11.7693 | 8.5856 | 18.1292 | 29.4427 | 11.6071 | 8.4673 | 18.0277 | 29.8016 | 11.2285 | 8.1911 | 16.5506 | 30.2193 | 10.6351 | 7.7582 | 13.6909 | 30.5369 | 10.0676 | 7.3442 | 11.1576 | 30.8285 | 9.4235 | 6.8743 | 8.4592 | 31.0316 | 8.8847 | 6.4813 | 6.4418 | 28.5531 | 13.5814 | 9.9075 | 18.9506 | 28.5521 | 13.5335 | 9.8725 | 19.0037 | 28.5773 | 13.4927 | 9.8428 | 18.9649 | 28.615 | 13.3209 | 9.7174 | 18.9081 | 28.667 | 13.1303 | 9.5783 | 18.775 | 28.7504 | 13.0018 | 9.4846 | 18.6241 | 28.8647 | 12.7605 | 9.3086 | 18.2742 | 29.0221 | 12.2576 | 8.9417 | 17.2232 | 29.1533 | 11.6558 | 8.5028 | 16.1519 | 29.2822 | 11.5418 | 8.4196 | 15.1107 | 29.6726 | 10.8055 | 7.8824 | 12.1405 | 30.0682 | 10.1548 | 7.4078 | 9.3602 | 30.3645 | 9.542 | 6.9607 | 7.0506 | 30.5941 | 9.0438 | 6.5973 | 5.5909 | 30.6166 | 9.0769 | 6.6214 | 6.9753 | 28.5473 | 13.5814 | 9.9075 | 18.9506 | 28.5979 | 13.5245 | 9.866 | 18.8731 | 28.6394 | 13.4042 | 9.7782 | 18.8026 | 28.6876 | 13.1862 | 9.6192 | 18.765 | 28.7428 | 12.9316 | 9.4334 | 18.724 | 28.8252 | 12.6876 | 9.2554 | 18.6707 | 28.9344 | 12.4121 | 9.0544 | 18.6007 | 29.0558 | 12.2002 | 8.8999 | 18.5091 | 29.1408 | 12.0678 | 8.8033 | 18.3581 | 29.2257 | 11.946 | 8.7145 | 18.1409 | 29.5005 | 11.5084 | 8.3952 | 17.3901 | 29.7889 | 11.423 | 8.3329 | 16.5735 | 30 | 11.3203 | 8.258 | 16.0161 | 30.1867 | 11.1565 | 8.1385 | 15.5549 | 30.284 | 11.0146 | 8.035 | 15.4849 | 28.5473 | 13.5814 | 9.9075 | 18.9506 | 28.5709 | 13.4938 | 9.8435 | 18.9497 | 28.6269 | 13.4235 | 9.7922 | 18.8571 | 28.6962 | 13.2643 | 9.6761 | 18.7421 | 28.7792 | 13.0618 | 9.5284 | 18.5557 | 28.8732 | 12.9197 | 9.4247 | 18.3714 | 28.9917 | 12.6699 | 9.2425 | 17.9885 | 29.1698 | 12.1567 | 8.8681 | 16.8786 | 29.3103 | 11.5355 | 8.415 | 15.7657 | 29.4463 | 11.4258 | 8.335 | 14.6835 | 29.8435 | 10.6651 | 7.78 | 11.5875 | 30.2194 | 9.9845 | 7.2835 | 8.6658 | 30.5046 | 9.3285 | 6.805 | 6.1188 | 30.7208 | 8.7715 | 6.3987 | 4.3212 | 30.7542 | 8.7578 | 6.3887 | 5.3459
COG LANE | HUNCOAT | PADIHAM | 382462 | 432232 | 42.4632 | 11.3963 | 8.3134 | 18.4077 | 42.5231 | 11.1468 | 8.1314 | 17.4438 | 42.6142 | 10.9125 | 7.9605 | 16.6234 | 42.7308 | 10.3286 | 7.5346 | 15.9787 | 42.9125 | 9.8197 | 7.1634 | 15.8038 | 43.1413 | 9.4405 | 6.8867 | 15.5932 | 43.4166 | 9.1119 | 6.647 | 15.4043 | 43.7586 | 8.8832 | 6.4802 | 15.2249 | 44.0878 | 8.74 | 6.3757 | 14.9655 | 44.3683 | 8.5965 | 6.271 | 14.7259 | 45.4828 | 8.0002 | 5.836 | 12.3609 | 44.7441 | 7.2579 | 5.2946 | 7.909 | 41.7564 | 6.7733 | 4.941 | 4.0919 | 38.5918 | 6.26 | 4.5666 | 0.029295 | 34.1384 | 5.5376 | 4.0396 | -3.4129 | 42.4451 | 11.3963 | 8.3134 | 18.4077 | 42.4908 | 11.2827 | 8.2306 | 18.1145 | 42.5403 | 11.0826 | 8.0846 | 17.7566 | 42.5966 | 10.9313 | 7.9742 | 17.4521 | 42.6738 | 10.7342 | 7.8304 | 17.316 | 42.7732 | 10.5305 | 7.6818 | 17.1542 | 42.908 | 10.2367 | 7.4675 | 16.9118 | 43.0855 | 10.0982 | 7.3665 | 16.5637 | 43.2479 | 9.9882 | 7.2862 | 16.2647 | 43.4269 | 9.8593 | 7.1922 | 15.9624 | 44.0768 | 9.4381 | 6.885 | 14.9944 | 44.8588 | 9.0448 | 6.598 | 13.9209 | 45.672 | 8.8539 | 6.4588 | 12.8473 | 46.5354 | 8.6704 | 6.325 | 11.6404 | 47.019 | 8.3001 | 6.0548 | 10.7835 | 42.4697 | 11.3963 | 8.3134 | 18.4077 | 42.537 | 11.09 | 8.09 | 17.3261 | 42.6385 | 10.7898 | 7.871 | 16.5056 | 42.7691 | 10.1008 | 7.3684 | 15.9057 | 42.9645 | 9.5721 | 6.9827 | 15.7742 | 43.2054 | 9.2228 | 6.7279 | 15.6147 | 43.4919 | 8.8661 | 6.4677 | 15.5077 | 43.8399 | 8.5757 | 6.2559 | 15.4113 | 44.0755 | 8.4548 | 6.1677 | 15.2784 | 44.3265 | 8.3822 | 6.1147 | 15.1403 | 45.4299 | 7.7619 | 5.6622 | 13.0544 | 42.496 | 6.8933 | 5.0285 | 8.7862 | 38.7493 | 6.2855 | 4.5852 | 5.1177 | 34.9284 | 5.6657 | 4.1331 | 1.2899 | 29.6596 | 4.8111 | 3.5096 | -1.8341 | 42.4697 | 11.3963 | 8.3134 | 18.4077 | 42.4109 | 11.2277 | 8.1904 | 18.0245 | 42.4578 | 11.0891 | 8.0894 | 17.3456 | 42.5437 | 10.5224 | 7.676 | 16.7596 | 42.7035 | 10.2103 | 7.4483 | 16.6108 | 42.9415 | 9.9171 | 7.2344 | 16.4211 | 43.3065 | 9.6453 | 7.0361 | 15.9825 | 43.7988 | 9.1736 | 6.692 | 14.6122 | 44.2367 | 8.7274 | 6.3665 | 13.1813 | 44.634 | 8.4264 | 6.147 | 11.7464 | 45.7477 | 8.2754 | 6.0368 | 7.5762 | 44.7508 | 7.259 | 5.2954 | 3.5882 | 38.8165 | 6.2964 | 4.5931 | 0.28163 | 33.5386 | 5.4403 | 3.9686 | -1.7752 | 32.5542 | 5.2806 | 3.8521 | -0.24456 | 42.4632 | 11.3963 | 8.3134 | 18.4077 | 42.511 | 11.2656 | 8.2181 | 18.0214 | 42.5738 | 11.0536 | 8.0634 | 17.3297 | 42.638 | 10.5442 | 7.6918 | 16.7585 | 42.7359 | 10.0397 | 7.3239 | 16.7658 | 42.8966 | 9.6862 | 7.0659 | 16.7353 | 43.1243 | 9.3755 | 6.8393 | 16.6596 | 43.4062 | 9.149 | 6.6741 | 16.5323 | 43.697 | 9.0071 | 6.5706 | 16.2752 | 44.0105 | 8.8596 | 6.4629 | 16.0137 | 44.8472 | 8.492 | 6.1948 | 14.9957 | 45.6912 | 8.352 | 6.0926 | 13.8041 | 46.2656 | 8.4384 | 6.1557 | 12.9943 | 46.6812 | 8.5575 | 6.2426 | 12.2631 | 46.8593 | 8.4689 | 6.1779 | 11.9873 | 42.4632 | 11.3963 | 8.3134 | 18.4077 | 42.4249 | 11.1183 | 8.1106 | 17.5413 | 42.5061 | 10.9533 | 7.9903 | 16.7143 | 42.628 | 10.3443 | 7.546 | 16.0468 | 42.8151 | 10.0231 | 7.3117 | 15.8229 | 43.0397 | 9.7237 | 7.0933 | 15.5797 | 43.3699 | 9.4415 | 6.8875 | 15.0717 | 43.899 | 8.9626 | 6.5381 | 13.6208 | 44.3146 | 8.5097 | 6.2077 | 12.1469 | 44.6987 | 8.1941 | 5.9775 | 10.6643 | 45.7812 | 7.9892 | 5.828 | 6.2875 | 42.6009 | 6.9103 | 5.041 | 2.0342 | 36.307 | 5.8893 | 4.2962 | -1.5542 | 30.632 | 4.9688 | 3.6247 | -3.973 | 29.0686 | 4.7152 | 3.4397 | -2.8403
CONISTON | ULVERSTON | HARKER / HUTTON | 329874 | 497641 | 4.638 | 4.638 | 4.638 | 1.6635 | 4.6674 | 4.6674 | 4.6674 | 1.5868 | 4.7103 | 4.7103 | 4.7103 | 1.5384 | 4.7491 | 4.7491 | 4.7491 | 1.4873 | 4.7846 | 4.7846 | 4.7846 | 1.42 | 4.8255 | 4.8255 | 4.8255 | 1.3492 | 4.8721 | 4.8721 | 4.8721 | 1.2816 | 4.9277 | 4.9277 | 4.9277 | 1.2071 | 4.9649 | 4.9649 | 4.9649 | 1.1437 | 4.9991 | 4.9991 | 4.9991 | 1.0874 | 5.0905 | 5.0905 | 5.0905 | 0.7801 | 5.1838 | 5.1838 | 5.1838 | 0.13536 | 5.2485 | 5.2485 | 5.2485 | -0.40561 | 5.2966 | 5.2966 | 5.2966 | -0.95746 | 5.3177 | 5.3177 | 5.3177 | -1.4639 | 4.6381 | 4.6381 | 4.6381 | 1.6635 | 4.6637 | 4.6637 | 4.6637 | 1.5853 | 4.6925 | 4.6925 | 4.6925 | 1.5025 | 4.7352 | 4.7352 | 4.7352 | 1.4089 | 4.7944 | 4.7944 | 4.7944 | 1.2946 | 4.8463 | 4.8463 | 4.8463 | 1.165 | 4.8933 | 4.8933 | 4.8933 | 1.0105 | 4.9477 | 4.9477 | 4.9477 | 0.81893 | 4.9691 | 4.9691 | 4.9691 | 0.76349 | 4.991 | 4.991 | 4.991 | 0.69676 | 5.0571 | 5.0571 | 5.0571 | 0.50242 | 5.1173 | 5.1173 | 5.1173 | 0.32768 | 5.1676 | 5.1676 | 5.1676 | 0.17811 | 5.2153 | 5.2153 | 5.2153 | 0.01868 | 5.2488 | 5.2488 | 5.2488 | -0.10218 | 4.6381 | 4.6381 | 4.6381 | 1.6635 | 4.6679 | 4.6679 | 4.6679 | 1.5857 | 4.711 | 4.711 | 4.711 | 1.5408 | 4.7579 | 4.7579 | 4.7579 | 1.4968 | 4.798 | 4.798 | 4.798 | 1.437 | 4.8446 | 4.8446 | 4.8446 | 1.3725 | 4.8983 | 4.8983 | 4.8983 | 1.3112 | 4.9629 | 4.9629 | 4.9629 | 1.2473 | 5.0001 | 5.0001 | 5.0001 | 1.1996 | 5.0325 | 5.0325 | 5.0325 | 1.1554 | 5.1323 | 5.1323 | 5.1323 | 0.91852 | 5.231 | 5.231 | 5.231 | 0.32339 | 5.284 | 5.284 | 5.284 | -0.17646 | 5.3188 | 5.3188 | 5.3188 | -0.67574 | 5.3288 | 5.3288 | 5.3288 | -1.1183 | 4.6381 | 4.6381 | 4.6381 | 1.6635 | 4.64 | 4.64 | 4.64 | 1.6475 | 4.6619 | 4.6619 | 4.6619 | 1.6245 | 4.7017 | 4.7017 | 4.7017 | 1.5896 | 4.7247 | 4.7247 | 4.7247 | 1.5369 | 4.7576 | 4.7576 | 4.7576 | 1.4807 | 4.7994 | 4.7994 | 4.7994 | 1.3952 | 4.8483 | 4.8483 | 4.8483 | 1.194 | 4.8865 | 4.8865 | 4.8865 | 0.98585 | 4.9233 | 4.9233 | 4.9233 | 0.77946 | 5.0244 | 5.0244 | 5.0244 | 0.18384 | 5.1201 | 5.1201 | 5.1201 | -0.38936 | 5.1832 | 5.1832 | 5.1832 | -0.83979 | 5.2112 | 5.2112 | 5.2112 | -1.1105 | 5.1973 | 5.1973 | 5.1973 | -0.93347 | 4.638 | 4.638 | 4.638 | 1.6635 | 4.6622 | 4.6622 | 4.6622 | 1.6012 | 4.6929 | 4.6929 | 4.6929 | 1.5606 | 4.7311 | 4.7311 | 4.7311 | 1.5238 | 4.7596 | 4.7596 | 4.7596 | 1.479 | 4.7961 | 4.7961 | 4.7961 | 1.4276 | 4.8424 | 4.8424 | 4.8424 | 1.369 | 4.8934 | 4.8934 | 4.8934 | 1.3013 | 4.9265 | 4.9265 | 4.9265 | 1.2405 | 4.9591 | 4.9591 | 4.9591 | 1.1815 | 5.051 | 5.051 | 5.051 | 0.98022 | 5.1404 | 5.1404 | 5.1404 | 0.75255 | 5.2026 | 5.2026 | 5.2026 | 0.57352 | 5.2527 | 5.2527 | 5.2527 | 0.38228 | 5.2675 | 5.2675 | 5.2675 | 0.28274 | 4.638 | 4.638 | 4.638 | 1.6635 | 4.6554 | 4.6554 | 4.6554 | 1.6162 | 4.6992 | 4.6992 | 4.6992 | 1.5612 | 4.7408 | 4.7408 | 4.7408 | 1.4998 | 4.7767 | 4.7767 | 4.7767 | 1.427 | 4.8174 | 4.8174 | 4.8174 | 1.3535 | 4.865 | 4.865 | 4.865 | 1.244 | 4.926 | 4.926 | 4.926 | 1.0124 | 4.9676 | 4.9676 | 4.9676 | 0.78946 | 5.0056 | 5.0056 | 5.0056 | 0.56835 | 5.101 | 5.101 | 5.101 | -0.069978 | 5.1873 | 5.1873 | 5.1873 | -0.67785 | 5.244 | 5.244 | 5.244 | -1.1609 | 5.2705 | 5.2705 | 5.2705 | -1.4716 | 5.2575 | 5.2575 | 5.2575 | -1.3409
COPSE RD | THORNTON | PENWORTHAM WEST / STANAH | 333013 | 446934 | 22.6839 | 3.6848 | 2.688 | 9.176 | 22.5525 | 3.6582 | 2.6686 | 8.6403 | 21.3446 | 3.4623 | 2.5257 | 8.3466 | 19.9934 | 3.2431 | 2.3658 | 8.1311 | 18.939 | 3.0721 | 2.241 | 7.8192 | 16.9698 | 2.7527 | 2.008 | 7.4948 | 14.7501 | 2.3926 | 1.7454 | 7.2197 | 12.8317 | 2.0814 | 1.5184 | 6.9924 | 11.4964 | 1.8648 | 1.3604 | 6.713 | 10.1552 | 1.6473 | 1.2017 | 6.4636 | 5.2728 | 0.85529 | 0.62393 | 4.2516 | 2.6914 | 0.43658 | 0.31848 | 0.09327 | 2.6914 | 0.43658 | 0.31848 | -3.388 | 19.66 | 3.189 | 2.3264 | -7.1235 | 27.1001 | 7.1945 | 5.2483 | -10.4482 | 22.7048 | 3.6848 | 2.688 | 9.176 | 22.6481 | 3.6737 | 2.6799 | 8.8245 | 22.5025 | 3.6501 | 2.6627 | 8.5563 | 22.0658 | 3.5793 | 2.611 | 8.3294 | 21.8275 | 3.5406 | 2.5828 | 8.0702 | 21.5105 | 3.4892 | 2.5453 | 7.8151 | 20.3328 | 3.2982 | 2.406 | 7.4852 | 19.3089 | 3.1321 | 2.2848 | 7.0413 | 18.5039 | 3.0015 | 2.1896 | 6.694 | 18.2442 | 2.9594 | 2.1588 | 6.3465 | 16.1181 | 2.6145 | 1.9073 | 5.3024 | 13.7235 | 2.2261 | 1.6239 | 4.2533 | 12.861 | 2.0862 | 1.5218 | 3.2485 | 25.7605 | 5.462 | 3.9845 | 2.141 | 26.054 | 8.8039 | 6.4223 | 1.3305 | 22.6749 | 3.6848 | 2.688 | 9.176 | 22.4604 | 3.6433 | 2.6577 | 8.609 | 20.9951 | 3.4056 | 2.4843 | 8.3299 | 19.3676 | 3.1416 | 2.2918 | 8.1599 | 18.2637 | 2.9625 | 2.1611 | 7.8898 | 15.8602 | 2.5727 | 1.8767 | 7.6131 | 12.3779 | 2.0078 | 1.4647 | 7.3818 | 10.6004 | 1.7195 | 1.2543 | 7.2069 | 8.8767 | 1.4399 | 1.0504 | 7.0153 | 7.3201 | 1.1874 | 0.86619 | 6.8544 | 1.3168 | 0.21359 | 0.15581 | 1.3168 | 2.6914 | 0.43658 | 0.31848 | 1.0691 | 2.6914 | 0.43658 | 0.31848 | -2.1481 | 14.7646 | 2.395 | 1.7471 | -5.5719 | 27.0593 | 6.4193 | 4.6828 | -8.5116 | 22.675 | 3.6848 | 2.688 | 9.176 | 22.6782 | 3.7015 | 2.7002 | 8.9648 | 21.7291 | 3.5247 | 2.5712 | 8.781 | 20.085 | 3.258 | 2.3767 | 8.6177 | 19.0332 | 3.0874 | 2.2522 | 8.3344 | 16.5182 | 2.6794 | 1.9546 | 8.0236 | 12.6677 | 2.0548 | 1.499 | 7.4945 | 9.2315 | 1.4974 | 1.0924 | 6.1795 | 6.2659 | 1.0164 | 0.74145 | 4.799 | 3.3041 | 0.53596 | 0.39097 | 3.3041 | 2.6914 | 0.43658 | 0.31848 | -0.42729 | 2.6914 | 0.43658 | 0.31848 | -4.0915 | 2.6914 | 0.43658 | 0.31848 | -7.0693 | 26.586 | 6.856 | 5.0013 | -8.905 | 26.4771 | 6.6499 | 4.851 | -7.5687 | 22.6838 | 3.6848 | 2.688 | 9.176 | 22.6339 | 3.6714 | 2.6783 | 8.7357 | 21.5172 | 3.4903 | 2.5461 | 8.4893 | 20.2546 | 3.2855 | 2.3967 | 8.3491 | 19.3989 | 3.1467 | 2.2955 | 8.2021 | 17.8504 | 2.8955 | 2.1122 | 8.0555 | 15.7703 | 2.5581 | 1.8661 | 7.9121 | 13.9218 | 2.2583 | 1.6474 | 7.7431 | 12.5735 | 2.0395 | 1.4878 | 7.4558 | 11.176 | 1.8129 | 1.3225 | 7.1685 | 7.557 | 1.2258 | 0.89422 | 6.1465 | 4.8429 | 0.78556 | 0.57306 | 4.8429 | 3.8745 | 0.62848 | 0.45847 | 3.8745 | 26.401 | 5.0741 | 3.7015 | 3.4531 | 26.4862 | 9.6473 | 7.0376 | 3.1758 | 22.6838 | 3.6848 | 2.688 | 9.176 | 22.5964 | 3.6654 | 2.6738 | 8.7322 | 21.3515 | 3.4634 | 2.5265 | 8.4338 | 19.5942 | 3.1784 | 2.3186 | 8.1745 | 18.4456 | 2.9921 | 2.1827 | 7.8012 | 15.6544 | 2.5393 | 1.8524 | 7.4235 | 11.7456 | 1.9052 | 1.3899 | 6.833 | 8.263 | 1.3403 | 0.97776 | 5.4261 | 5.2174 | 0.84631 | 0.61737 | 3.996 | 2.2535 | 0.36554 | 0.26665 | 2.2535 | 2.6914 | 0.43658 | 0.31848 | -1.5019 | 2.6914 | 0.43658 | 0.31848 | -5.4225 | 2.6914 | 0.43658 | 0.31848 | -8.6355 | 26.7887 | 6.4434 | 4.7004 | -10.7591 | 26.6992 | 6.1679 | 4.4994 | -9.7594
COX GREEN | BOLTON | KEARSLEY | 371893 | 413641 | 23.2924 | 13.9594 | 10.0329 | 9.7466 | 23.3655 | 13.9126 | 9.9992 | 9.4266 | 23.4769 | 13.7702 | 9.8969 | 9.3182 | 23.6024 | 13.6264 | 9.7935 | 9.2767 | 23.7351 | 13.3982 | 9.6295 | 9.1713 | 23.8859 | 13.1475 | 9.4494 | 9.0669 | 24.0536 | 12.9763 | 9.3263 | 8.9895 | 24.2053 | 12.8689 | 9.2491 | 8.9164 | 24.3038 | 12.7592 | 9.1703 | 8.7791 | 24.3958 | 12.6586 | 9.098 | 8.6639 | 24.7144 | 12.1275 | 8.7163 | 7.3639 | 25.0929 | 11.5903 | 8.3301 | 4.7866 | 25.3804 | 11.1312 | 8.0002 | 2.573 | 25.6487 | 10.7888 | 7.7541 | 0.16331 | 25.8308 | 10.3722 | 7.4547 | -1.7885 | 23.2609 | 13.9594 | 10.0329 | 9.7466 | 23.3109 | 13.9672 | 10.0385 | 9.6359 | 23.3632 | 13.9193 | 10.0041 | 9.5672 | 23.4377 | 13.8381 | 9.9458 | 9.4983 | 23.5405 | 13.7529 | 9.8845 | 9.3794 | 23.6326 | 13.6029 | 9.7767 | 9.235 | 23.7458 | 13.4037 | 9.6335 | 9.0395 | 23.8763 | 13.3203 | 9.5735 | 8.7983 | 23.9624 | 13.2412 | 9.5167 | 8.5744 | 24.0515 | 13.1428 | 9.446 | 8.3463 | 24.3222 | 12.8561 | 9.24 | 7.6745 | 24.5734 | 12.6471 | 9.0897 | 7.0391 | 24.7697 | 12.3583 | 8.8822 | 6.4549 | 24.9564 | 12.1387 | 8.7243 | 5.8529 | 25.0522 | 11.9365 | 8.579 | 5.4603 | 23.3057 | 13.9594 | 10.0329 | 9.7466 | 23.3898 | 13.882 | 9.9773 | 9.4038 | 23.5199 | 13.6698 | 9.8247 | 9.3141 | 23.648 | 13.4403 | 9.6598 | 9.3178 | 23.8032 | 13.2117 | 9.4955 | 9.2617 | 23.9811 | 12.9319 | 9.2944 | 9.2149 | 24.1448 | 12.7869 | 9.1902 | 9.2168 | 24.2875 | 12.6248 | 9.0737 | 9.2307 | 24.3956 | 12.4131 | 8.9215 | 9.1858 | 24.4963 | 12.3556 | 8.8802 | 9.149 | 24.8401 | 12.0948 | 8.6928 | 8.093 | 25.2375 | 11.4675 | 8.2419 | 5.7333 | 25.5343 | 10.833 | 7.7859 | 3.7064 | 25.803 | 10.715 | 7.7011 | 1.5041 | 25.9743 | 10.1375 | 7.286 | -0.22927 | 23.3057 | 13.9594 | 10.0329 | 9.7466 | 23.2954 | 13.9602 | 10.0335 | 9.7578 | 23.3464 | 13.77 | 9.8967 | 9.7681 | 23.4282 | 13.5218 | 9.7184 | 9.8034 | 23.547 | 13.232 | 9.5101 | 9.7536 | 23.7013 | 12.9856 | 9.333 | 9.6829 | 23.864 | 12.6338 | 9.0802 | 9.4759 | 24.0367 | 12.5895 | 9.0483 | 8.73 | 24.17 | 12.3996 | 8.9118 | 7.9327 | 24.2891 | 12.1324 | 8.7198 | 7.1395 | 24.6496 | 11.8965 | 8.5502 | 4.846 | 25.0284 | 11.2914 | 8.1154 | 2.6173 | 25.3078 | 10.7536 | 7.7289 | 0.77168 | 25.5181 | 10.3152 | 7.4137 | -0.42424 | 25.5155 | 10.313 | 7.4121 | 0.63651 | 23.2924 | 13.9594 | 10.0329 | 9.7466 | 23.3524 | 13.9509 | 10.0268 | 9.614 | 23.4224 | 13.8391 | 9.9464 | 9.5856 | 23.5077 | 13.7109 | 9.8543 | 9.6121 | 23.5934 | 13.5146 | 9.7132 | 9.6172 | 23.7193 | 13.2917 | 9.553 | 9.5897 | 23.886 | 13.1107 | 9.4229 | 9.5369 | 24.0508 | 13.0134 | 9.353 | 9.4801 | 24.161 | 12.9076 | 9.277 | 9.3467 | 24.2667 | 12.8066 | 9.2044 | 9.2193 | 24.5411 | 12.4119 | 8.9207 | 8.742 | 24.8373 | 12.2426 | 8.799 | 8.1421 | 25.0534 | 12.0639 | 8.6705 | 7.5504 | 25.2482 | 12.1273 | 8.7162 | 6.981 | 25.3428 | 12.0017 | 8.6259 | 6.7554 | 23.2924 | 13.9594 | 10.0329 | 9.7466 | 23.3171 | 13.9098 | 9.9972 | 9.559 | 23.4219 | 13.7184 | 9.8597 | 9.4551 | 23.5515 | 13.4247 | 9.6486 | 9.3929 | 23.6892 | 13.1235 | 9.4322 | 9.2557 | 23.843 | 12.869 | 9.2492 | 9.1282 | 24.0015 | 12.5034 | 8.9864 | 8.8501 | 24.1911 | 12.4387 | 8.9399 | 8.0021 | 24.3267 | 12.2348 | 8.7934 | 7.1221 | 24.4571 | 11.9555 | 8.5927 | 6.2473 | 24.8292 | 11.6561 | 8.3775 | 3.7137 | 25.1827 | 11.0141 | 7.916 | 1.2856 | 25.4436 | 10.4288 | 7.4954 | -0.75383 | 25.6309 | 9.9565 | 7.1559 | -2.1966 | 25.6334 | 9.9068 | 7.1202 | -1.4148
CRAGGS ROW & BUSHELL ST | RIBBLE | PENWORTHAM EAST / ROCHDALE | 353740 | 430080 | 32.3756 | 12.4245 | 9.0635 | 10.2347 | 32.4289 | 11.9479 | 8.7158 | 7.6468 | 32.5293 | 11.7456 | 8.5683 | 7.0159 | 32.6126 | 11.6123 | 8.471 | 6.8463 | 32.6953 | 11.5102 | 8.3965 | 6.6279 | 32.7879 | 11.3291 | 8.2644 | 6.4062 | 32.8948 | 11.1438 | 8.1292 | 6.2189 | 33.0218 | 11.0084 | 8.0305 | 6.0586 | 33.1235 | 10.8482 | 7.9136 | 5.8232 | 33.2162 | 10.6405 | 7.7621 | 5.6218 | 33.512 | 10.2611 | 7.4854 | 4.0183 | 33.8347 | 9.6088 | 7.0095 | 1.0623 | 34.0591 | 8.9866 | 6.5556 | -1.3611 | 34.2422 | 8.3208 | 6.0699 | -3.9052 | 34.3205 | 7.681 | 5.6032 | -6.0183 | 32.3652 | 12.4245 | 9.0635 | 10.2347 | 32.4478 | 12.2851 | 8.9618 | 9.4258 | 32.5732 | 12.1658 | 8.8748 | 9.0737 | 32.7013 | 12.0199 | 8.7683 | 8.8513 | 32.8475 | 11.9292 | 8.7022 | 8.609 | 33.0252 | 11.8369 | 8.6349 | 8.3639 | 33.1975 | 11.5914 | 8.4557 | 8.0524 | 33.3268 | 11.4304 | 8.3383 | 7.6659 | 33.4198 | 11.2872 | 8.2338 | 7.3528 | 33.5114 | 11.1915 | 8.164 | 7.0447 | 33.7722 | 10.8191 | 7.8924 | 6.1703 | 34.0061 | 10.5172 | 7.6721 | 5.3514 | 34.1982 | 10.2687 | 7.4909 | 4.6726 | 34.3826 | 10.0302 | 7.3169 | 3.9915 | 34.4998 | 9.7647 | 7.1232 | 3.5431 | 32.38 | 12.4245 | 9.0635 | 10.2347 | 32.439 | 11.8546 | 8.6478 | 7.2637 | 32.5449 | 11.5663 | 8.4375 | 6.5832 | 32.6344 | 11.449 | 8.3519 | 6.4546 | 32.7269 | 11.2828 | 8.2307 | 6.27 | 32.8312 | 11.0926 | 8.0919 | 6.085 | 32.9534 | 10.884 | 7.9397 | 5.9533 | 33.0981 | 10.6798 | 7.7908 | 5.8488 | 33.1933 | 10.5199 | 7.6741 | 5.7268 | 33.2762 | 10.4953 | 7.6562 | 5.607 | 33.5685 | 9.9762 | 7.2775 | 4.2653 | 33.8691 | 9.1959 | 6.7083 | 1.5633 | 34.0617 | 8.5412 | 6.2307 | -0.61041 | 34.1906 | 7.8173 | 5.7026 | -2.8299 | 34.19 | 7.2087 | 5.2587 | -4.5459 | 32.38 | 12.4245 | 9.0635 | 10.2347 | 32.3494 | 12.0537 | 8.793 | 8.3274 | 32.396 | 11.9053 | 8.6848 | 7.8792 | 32.4273 | 11.7524 | 8.5732 | 7.8065 | 32.4632 | 11.6388 | 8.4904 | 7.657 | 32.5266 | 11.4663 | 8.3645 | 7.4837 | 32.6158 | 11.2922 | 8.2375 | 7.161 | 32.732 | 10.9951 | 8.0208 | 6.2472 | 32.8396 | 10.6906 | 7.7987 | 5.2811 | 32.9396 | 10.3988 | 7.5858 | 4.3175 | 33.2272 | 9.6977 | 7.0743 | 1.6137 | 33.509 | 8.946 | 6.526 | -0.94309 | 33.6851 | 8.2722 | 6.0345 | -2.9318 | 33.7665 | 7.7449 | 5.6498 | -4.0561 | 33.6276 | 7.6378 | 5.5717 | -2.7695 | 32.3756 | 12.4245 | 9.0635 | 10.2347 | 32.4222 | 12.1679 | 8.8763 | 8.8576 | 32.5019 | 12.0129 | 8.7632 | 8.4701 | 32.5623 | 11.9018 | 8.6822 | 8.3667 | 32.6168 | 11.8219 | 8.6239 | 8.2742 | 32.698 | 11.668 | 8.5116 | 8.1761 | 32.8055 | 11.494 | 8.3847 | 8.0632 | 32.9228 | 11.366 | 8.2913 | 7.9227 | 33.0161 | 11.2056 | 8.1743 | 7.664 | 33.1054 | 11.0002 | 8.0245 | 7.4107 | 33.3738 | 10.7413 | 7.8356 | 6.581 | 33.64 | 10.4918 | 7.6536 | 5.7055 | 33.8193 | 10.2169 | 7.4531 | 5.1504 | 33.9599 | 9.9351 | 7.2475 | 4.6638 | 33.9763 | 9.724 | 7.0935 | 4.7022 | 32.3756 | 12.4245 | 9.0635 | 10.2347 | 32.3804 | 11.8116 | 8.6164 | 7.0474 | 32.4736 | 11.603 | 8.4642 | 6.3018 | 32.5529 | 11.4443 | 8.3485 | 6.1318 | 32.6363 | 11.2972 | 8.2411 | 5.8919 | 32.7275 | 11.1119 | 8.106 | 5.6552 | 32.8396 | 10.9273 | 7.9713 | 5.2573 | 32.9982 | 10.6108 | 7.7404 | 4.241 | 33.1179 | 10.2942 | 7.5095 | 3.2123 | 33.2277 | 9.992 | 7.289 | 2.1862 | 33.5254 | 9.2402 | 6.7406 | -0.70269 | 33.7871 | 8.4535 | 6.1667 | -3.4055 | 33.9494 | 7.7498 | 5.6534 | -5.5519 | 34.0149 | 7.1712 | 5.2313 | -6.8962 | 33.8859 | 7.0172 | 5.119 | -5.8837
CROWN LANE | WESTHOUGHTON | KEARSLEY | 362706 | 410859 | 31.7721 | 8.271 | 5.9445 | 11.379 | 32.2113 | 7.8784 | 5.6624 | 10.1042 | 32.6196 | 6.9186 | 4.9725 | 8.9221 | 32.93 | 5.9228 | 4.2568 | 7.8963 | 30.4816 | 5.0186 | 3.6069 | 6.7196 | 23.8808 | 3.9318 | 2.8259 | 5.4724 | 18.0289 | 2.9683 | 2.1334 | 4.1871 | 15.5577 | 2.5615 | 1.841 | 2.8121 | 13.065 | 2.151 | 1.546 | 1.2626 | 10.536 | 1.7347 | 1.2467 | -0.34677 | 4.2058 | 0.69245 | 0.49768 | -6.5439 | 2.0588 | 0.33896 | 0.24362 | -12.5174 | 9.4247 | 1.5517 | 1.1152 | -16.5267 | 28.2867 | 4.6572 | 3.3472 | -19.952 | 35.3917 | 5.827 | 4.188 | -22.1289 | 31.7221 | 8.271 | 5.9445 | 11.379 | 31.9893 | 8.0696 | 5.7998 | 10.9979 | 32.2497 | 7.3342 | 5.2712 | 10.68 | 32.5943 | 6.5491 | 4.7069 | 10.3706 | 32.8204 | 5.5987 | 4.0239 | 9.9857 | 30.0718 | 4.9511 | 3.5584 | 9.5497 | 24.7687 | 4.078 | 2.9309 | 8.9991 | 23.4989 | 3.8689 | 2.7807 | 8.3022 | 22.5584 | 3.7141 | 2.6694 | 7.6747 | 21.3207 | 3.5103 | 2.5229 | 6.9821 | 17.02 | 2.8022 | 2.014 | 4.6109 | 12.8334 | 2.1129 | 1.5186 | 1.9009 | 16.5903 | 2.7315 | 1.9632 | -0.81023 | 29.7959 | 4.9057 | 3.5258 | -4.4657 | 36.6328 | 6.0313 | 4.3348 | -6.8187 | 31.7966 | 8.271 | 5.9445 | 11.379 | 32.2189 | 7.7792 | 5.5911 | 9.8573 | 32.674 | 6.747 | 4.8492 | 8.5362 | 32.9895 | 5.7272 | 4.1163 | 7.4195 | 28.3218 | 4.663 | 3.3514 | 6.1537 | 21.5454 | 3.5473 | 2.5495 | 4.8303 | 15.1396 | 2.4926 | 1.7915 | 3.5021 | 12.7121 | 2.0929 | 1.5042 | 2.1018 | 10.2418 | 1.6862 | 1.2119 | 0.56963 | 8.3079 | 1.3678 | 0.98308 | -1.08 | 0.054061 | 0.0089007 | 0.0063971 | -7.5807 | 2.6844 | 0.44197 | 0.31765 | -13.6537 | 3.4668 | 0.57078 | 0.41023 | -17.4522 | 22.3652 | 3.6823 | 2.6465 | -20.4381 | 29.7604 | 4.8998 | 3.5216 | -21.5831 | 31.797 | 8.271 | 5.9445 | 11.379 | 32.0871 | 7.919 | 5.6915 | 10.4462 | 32.4742 | 7.3469 | 5.2804 | 9.2933 | 32.79 | 6.8377 | 4.9144 | 8.2098 | 33.1138 | 6.0944 | 4.3802 | 6.9407 | 32.544 | 5.3581 | 3.851 | 5.5524 | 28.7135 | 4.7275 | 3.3977 | 3.8872 | 27.2392 | 4.4847 | 3.2233 | 1.43 | 24.244 | 3.9916 | 2.8688 | -1.1257 | 25.3284 | 4.1701 | 2.9972 | -3.7232 | 39.4866 | 8.3741 | 6.0186 | -11.2773 | 41.4355 | 7.0448 | 5.0632 | -16.4348 | 37.1165 | 6.1109 | 4.3921 | -19.273 | 32.8147 | 5.4027 | 3.883 | -20.4297 | 31.2648 | 5.1475 | 3.6996 | -19.5962 | 31.7717 | 8.271 | 5.9445 | 11.379 | 32.1178 | 8.018 | 5.7627 | 10.7993 | 32.4932 | 7.0918 | 5.097 | 9.8253 | 32.7508 | 6.1227 | 4.4005 | 8.9295 | 32.0759 | 5.2811 | 3.7956 | 7.9813 | 25.7719 | 4.2431 | 3.0496 | 6.9397 | 20.1271 | 3.3138 | 2.3817 | 5.8012 | 17.7337 | 2.9197 | 2.0985 | 4.5503 | 15.3654 | 2.5298 | 1.8182 | 3.1023 | 12.924 | 2.1278 | 1.5293 | 1.5661 | 8.0041 | 1.3178 | 0.94713 | -3.483 | 8.511 | 1.4013 | 1.0071 | -7.2359 | 17.4532 | 2.8735 | 2.0653 | -9.7804 | 37.5798 | 6.1872 | 4.4469 | -11.8824 | 42.5939 | 7.7117 | 5.5425 | -12.8332 | 31.7717 | 8.271 | 5.9445 | 11.379 | 32.1131 | 7.7901 | 5.5989 | 9.903 | 32.5782 | 7.2003 | 5.175 | 8.5337 | 32.8899 | 6.6493 | 4.779 | 7.317 | 33.2313 | 5.8779 | 4.2246 | 5.9402 | 31.2054 | 5.1377 | 3.6926 | 4.5079 | 27.3505 | 4.5031 | 3.2364 | 2.8088 | 25.7971 | 4.2473 | 3.0526 | 0.29313 | 22.51 | 3.7061 | 2.6636 | -2.2616 | 23.8206 | 3.9219 | 2.8187 | -4.8674 | 39.3844 | 8.0442 | 5.7815 | -12.6975 | 40.1097 | 6.6038 | 4.7462 | -18.4088 | 33.7645 | 5.5591 | 3.9954 | -21.8094 | 28.874 | 4.7539 | 3.4167 | -23.4661 | 27.2355 | 4.4841 | 3.2228 | -22.7039
CULCHETH | GOLBORNE | BOLD | 365430 | 395366 | 13.5138 | 13.5138 | 13.5138 | 9.3091 | 13.5409 | 13.5409 | 13.5409 | 9.0596 | 13.5882 | 13.5882 | 13.5882 | 8.9358 | 13.6337 | 13.6337 | 13.6337 | 8.8772 | 13.6797 | 13.6797 | 13.6797 | 8.7851 | 13.7359 | 13.7359 | 13.7359 | 8.6871 | 13.806 | 13.806 | 13.806 | 8.5981 | 13.896 | 13.896 | 13.896 | 8.5027 | 13.9881 | 13.9881 | 13.9881 | 8.3643 | 14.0815 | 14.0815 | 14.0815 | 8.2355 | 14.3854 | 14.3854 | 14.3854 | 7.5556 | 14.708 | 14.708 | 14.708 | 6.482 | 14.9388 | 14.9388 | 14.9388 | 5.6153 | 15.1382 | 15.1382 | 15.1382 | 4.7659 | 15.2802 | 15.2802 | 15.2802 | 3.8393 | 13.4983 | 13.4983 | 13.4983 | 9.3091 | 13.5276 | 13.5276 | 13.5276 | 9.2628 | 13.5621 | 13.5621 | 13.5621 | 9.1903 | 13.6001 | 13.6001 | 13.6001 | 9.144 | 13.6498 | 13.6498 | 13.6498 | 9.0995 | 13.7072 | 13.7072 | 13.7072 | 9.0559 | 13.7698 | 13.7698 | 13.7698 | 8.9893 | 13.8437 | 13.8437 | 13.8437 | 8.8947 | 13.8985 | 13.8985 | 13.8985 | 8.7557 | 13.9569 | 13.9569 | 13.9569 | 8.6154 | 14.1532 | 14.1532 | 14.1532 | 8.1859 | 14.369 | 14.369 | 14.369 | 7.7444 | 14.5739 | 14.5739 | 14.5739 | 7.2688 | 14.7812 | 14.7812 | 14.7812 | 6.6723 | 14.918 | 14.918 | 14.918 | 6.2348 | 13.518 | 13.518 | 13.518 | 9.3091 | 13.5485 | 13.5485 | 13.5485 | 9.022 | 13.6012 | 13.6012 | 13.6012 | 8.8905 | 13.6434 | 13.6434 | 13.6434 | 8.831 | 13.693 | 13.693 | 13.693 | 8.2559 | 13.7526 | 13.7526 | 13.7526 | 7.6757 | 13.8264 | 13.8264 | 13.8264 | 7.1039 | 13.9192 | 13.9192 | 13.9192 | 6.528 | 14.003 | 14.003 | 14.003 | 5.9332 | 14.0845 | 14.0845 | 14.0845 | 5.6522 | 14.383 | 14.383 | 14.383 | 5.0525 | 14.7165 | 14.7165 | 14.7165 | 4.0561 | 14.956 | 14.956 | 14.956 | 3.2698 | 15.1485 | 15.1485 | 15.1485 | 2.54 | 15.2654 | 15.2654 | 15.2654 | 1.9404 | 13.518 | 13.518 | 13.518 | 9.3091 | 13.4976 | 13.4976 | 13.4976 | 9.2118 | 13.5182 | 13.5182 | 13.5182 | 9.1345 | 13.5455 | 13.5455 | 13.5455 | 9.0942 | 13.5761 | 13.5761 | 13.5761 | 8.5399 | 13.6266 | 13.6266 | 13.6266 | 7.9668 | 13.7009 | 13.7009 | 13.7009 | 7.3381 | 13.8062 | 13.8062 | 13.8062 | 6.5311 | 13.9075 | 13.9075 | 13.9075 | 5.7046 | 14.0122 | 14.0122 | 14.0122 | 5.1905 | 14.3352 | 14.3352 | 14.3352 | 4.2228 | 14.64 | 14.64 | 14.64 | 3.2841 | 14.849 | 14.849 | 14.849 | 2.5793 | 14.9891 | 14.9891 | 14.9891 | 2.177 | 14.9824 | 14.9824 | 14.9824 | 2.5117 | 13.5138 | 13.5138 | 13.5138 | 9.3091 | 13.5355 | 13.5355 | 13.5355 | 9.2475 | 13.5673 | 13.5673 | 13.5673 | 9.1767 | 13.5987 | 13.5987 | 13.5987 | 9.1463 | 13.6263 | 13.6263 | 13.6263 | 9.117 | 13.672 | 13.672 | 13.672 | 9.0745 | 13.7403 | 13.7403 | 13.7403 | 9.0017 | 13.8266 | 13.8266 | 13.8266 | 8.8842 | 13.9152 | 13.9152 | 13.9152 | 8.7034 | 14.0089 | 14.0089 | 14.0089 | 8.5182 | 14.3137 | 14.3137 | 14.3137 | 7.9018 | 14.6157 | 14.6157 | 14.6157 | 7.2298 | 14.8345 | 14.8345 | 14.8345 | 6.736 | 15.0106 | 15.0106 | 15.0106 | 6.2939 | 15.0681 | 15.0681 | 15.0681 | 6.195 | 13.5138 | 13.5138 | 13.5138 | 9.3091 | 13.5087 | 13.5087 | 13.5087 | 9.0816 | 13.5512 | 13.5512 | 13.5512 | 8.9517 | 13.5942 | 13.5942 | 13.5942 | 8.8764 | 13.6389 | 13.6389 | 13.6389 | 8.2928 | 13.6911 | 13.6911 | 13.6911 | 7.7109 | 13.7616 | 13.7616 | 13.7616 | 7.0787 | 13.8723 | 13.8723 | 13.8723 | 6.2509 | 13.9794 | 13.9794 | 13.9794 | 5.4083 | 14.087 | 14.087 | 14.087 | 4.8801 | 14.4168 | 14.4168 | 14.4168 | 3.876 | 14.7306 | 14.7306 | 14.7306 | 2.9096 | 14.9524 | 14.9524 | 14.9524 | 2.1709 | 15.0955 | 15.0955 | 15.0955 | 1.7296 | 15.0966 | 15.0966 | 15.0966 | 2.0045
CUTACRE | KEARSLEY LOCAL | KEARSLEY | 369848 | 404515 | 26.5999 | 15.8067 | 11.3606 | 22.0791 | 26.6055 | 14.9547 | 10.7482 | 16.6394 | 26.6295 | 14.7498 | 10.601 | 15.4849 | 26.6469 | 14.6818 | 10.5521 | 15.4669 | 26.6643 | 14.5636 | 10.4672 | 15.4666 | 26.6902 | 14.4999 | 10.4213 | 15.4654 | 26.7268 | 14.4406 | 10.3787 | 15.4639 | 26.7788 | 14.3827 | 10.3371 | 15.4562 | 26.8622 | 14.2821 | 10.2648 | 15.3903 | 26.948 | 14.1496 | 10.1696 | 15.3201 | 27.1451 | 14.0038 | 10.0648 | 15.0447 | 27.3178 | 13.6825 | 9.8339 | 14.7318 | 27.4226 | 13.5196 | 9.7168 | 14.5126 | 27.4841 | 13.2686 | 9.5364 | 14.3369 | 27.4964 | 13.1188 | 9.4288 | 14.2454 | 26.5995 | 15.8067 | 11.3606 | 22.0791 | 26.603 | 15.5914 | 11.2058 | 20.4768 | 26.6236 | 15.5511 | 11.1769 | 20.1047 | 26.6338 | 15.5668 | 11.1882 | 20.0925 | 26.6377 | 15.5871 | 11.2028 | 20.1041 | 26.6436 | 15.6139 | 11.222 | 20.1174 | 26.652 | 15.5355 | 11.1657 | 20.1319 | 26.6642 | 15.5787 | 11.1967 | 20.1469 | 26.7052 | 15.5879 | 11.2033 | 20.0888 | 26.7521 | 15.5925 | 11.2066 | 20.0283 | 26.93 | 15.5785 | 11.1966 | 19.8337 | 27.14 | 15.5564 | 11.1807 | 19.6215 | 27.2923 | 15.552 | 11.1776 | 19.4214 | 27.4516 | 15.4821 | 11.1273 | 19.2122 | 27.5512 | 15.2728 | 10.9768 | 19.0732 | 26.6 | 15.8067 | 11.3606 | 22.0791 | 26.6062 | 14.8147 | 10.6476 | 15.7318 | 26.63 | 14.5713 | 10.4727 | 14.3932 | 26.6469 | 14.5368 | 10.4479 | 14.3747 | 26.6618 | 14.4189 | 10.3632 | 14.3759 | 26.6829 | 14.357 | 10.3187 | 14.3777 | 26.7117 | 14.1758 | 10.1884 | 14.3809 | 26.7522 | 14.0504 | 10.0983 | 14.3802 | 26.8148 | 13.9735 | 10.043 | 14.3428 | 26.8868 | 13.9104 | 9.9977 | 14.3039 | 27.0644 | 13.6393 | 9.8029 | 14.1065 | 27.2307 | 13.4274 | 9.6506 | 13.8497 | 27.33 | 13.1921 | 9.4814 | 13.6894 | 27.3646 | 12.965 | 9.3182 | 13.6168 | 27.3258 | 12.8518 | 9.2369 | 13.6764 | 26.6 | 15.8067 | 11.3606 | 22.0791 | 26.605 | 15.1391 | 10.8808 | 17.5467 | 26.6278 | 14.9574 | 10.7502 | 16.5781 | 26.6455 | 14.9357 | 10.7346 | 16.5589 | 26.6625 | 14.8221 | 10.6529 | 16.5588 | 26.6891 | 14.7023 | 10.5668 | 16.5566 | 26.7338 | 14.339 | 10.3057 | 16.5392 | 26.812 | 14.2363 | 10.2319 | 16.4774 | 26.886 | 14.1238 | 10.1511 | 16.3761 | 26.9467 | 13.993 | 10.057 | 16.2737 | 27.1312 | 13.6799 | 9.832 | 15.982 | 27.2744 | 13.5054 | 9.7066 | 15.7518 | 27.3484 | 13.3649 | 9.6056 | 15.6223 | 27.3563 | 13.2436 | 9.5184 | 15.6309 | 27.2795 | 13.2041 | 9.49 | 15.8727 | 26.5999 | 15.8067 | 11.3606 | 22.0791 | 26.6039 | 15.3498 | 11.0322 | 18.8718 | 26.6259 | 15.2284 | 10.9449 | 18.173 | 26.6389 | 15.1828 | 10.9122 | 18.16 | 26.6482 | 15.0929 | 10.8475 | 18.1702 | 26.6646 | 14.9844 | 10.7696 | 18.1793 | 26.6912 | 14.9582 | 10.7507 | 18.1846 | 26.7301 | 14.9075 | 10.7143 | 18.1833 | 26.7975 | 14.8355 | 10.6626 | 18.1251 | 26.8749 | 14.7158 | 10.5765 | 18.0618 | 27.0658 | 14.5529 | 10.4594 | 17.8507 | 27.2248 | 14.3282 | 10.298 | 17.6565 | 27.3237 | 14.2072 | 10.211 | 17.5432 | 27.3712 | 13.9738 | 10.0433 | 17.4975 | 27.3514 | 13.893 | 9.9852 | 17.5784 | 26.5999 | 15.8067 | 11.3606 | 22.0791 | 26.6057 | 14.6512 | 10.5301 | 14.8257 | 26.6297 | 14.3594 | 10.3204 | 13.302 | 26.6478 | 14.3249 | 10.2956 | 13.2803 | 26.6635 | 14.208 | 10.2115 | 13.2789 | 26.6849 | 14.0814 | 10.1206 | 13.2787 | 26.7207 | 13.7206 | 9.8613 | 13.2659 | 26.7875 | 13.4939 | 9.6983 | 12.6073 | 26.8769 | 13.2767 | 9.5422 | 11.9115 | 26.9364 | 13.037 | 9.37 | 11.2146 | 27.1198 | 12.3854 | 8.9016 | 9.1177 | 27.2855 | 11.9831 | 8.6125 | 7.659 | 27.3838 | 11.8387 | 8.5087 | 7.504 | 27.4055 | 11.7146 | 8.4195 | 7.4978 | 27.3318 | 11.6563 | 8.3776 | 7.736
ASKAM & DALTON | ULVERSTON | HARKER / HUTTON | 323582 | 474255 | 29.5325 | 9.8335 | 7.0675 | 11.1149 | 29.671 | 9.7429 | 7.0024 | 10.9654 | 29.7909 | 9.1903 | 6.6053 | 10.7171 | 29.9444 | 8.634 | 6.2054 | 10.5439 | 30.1704 | 8.0249 | 5.7677 | 10.3698 | 30.4078 | 7.3982 | 5.3173 | 10.1925 | 30.6322 | 6.8039 | 4.8901 | 10.0349 | 30.8761 | 6.5694 | 4.7215 | 9.8639 | 31.0814 | 6.3715 | 4.5793 | 9.642 | 31.2709 | 6.2339 | 4.4805 | 9.4442 | 32.3467 | 5.3757 | 3.8636 | 7.6361 | 25.395 | 4.1811 | 3.005 | 3.5758 | 17.6625 | 2.908 | 2.09 | 0.13991 | 11.1801 | 1.8407 | 1.323 | -3.2687 | 2.2279 | 0.36681 | 0.26363 | -5.9932 | 29.5343 | 9.8335 | 7.0675 | 11.1149 | 29.6836 | 9.7574 | 7.0128 | 10.949 | 29.804 | 9.6415 | 6.9295 | 10.6537 | 29.965 | 9.509 | 6.8343 | 10.4071 | 30.1814 | 9.3449 | 6.7164 | 10.1625 | 30.4304 | 9.1679 | 6.5891 | 9.8746 | 30.725 | 8.942 | 6.4268 | 9.5264 | 31.0593 | 8.7529 | 6.2909 | 9.1214 | 31.2217 | 8.6094 | 6.1877 | 8.8801 | 31.3875 | 8.4638 | 6.0831 | 8.6412 | 31.8776 | 8.0433 | 5.7809 | 7.9673 | 32.3314 | 7.6411 | 5.4918 | 7.3753 | 32.7107 | 7.2529 | 5.2128 | 6.6765 | 33.0998 | 6.9107 | 4.9668 | 5.8409 | 33.4493 | 6.3591 | 4.5704 | 5.1433 | 29.5318 | 9.8335 | 7.0675 | 11.1149 | 29.6721 | 9.7157 | 6.9829 | 10.9569 | 29.7915 | 9.1058 | 6.5445 | 10.7079 | 29.9456 | 8.4919 | 6.1033 | 10.5344 | 30.1701 | 7.7674 | 5.5826 | 10.3621 | 30.405 | 7.1747 | 5.1566 | 10.1875 | 30.6273 | 6.5132 | 4.6812 | 10.032 | 30.8673 | 6.0389 | 4.3402 | 9.8654 | 31.0718 | 6.0336 | 4.3365 | 9.7014 | 31.2564 | 5.8176 | 4.1812 | 9.566 | 29.8506 | 4.9147 | 3.5323 | 8.6282 | 19.7774 | 3.2562 | 2.3403 | 4.9085 | 13.1195 | 2.16 | 1.5524 | 1.7874 | 3.9627 | 0.65244 | 0.46892 | -1.2369 | 2.6844 | 0.44197 | 0.31765 | -3.5176 | 29.5318 | 9.8335 | 7.0675 | 11.1149 | 29.5475 | 9.7506 | 7.008 | 11.14 | 29.594 | 9.1957 | 6.6091 | 10.9942 | 29.7641 | 8.544 | 6.1407 | 10.8314 | 29.9289 | 7.9193 | 5.6918 | 10.747 | 30.1356 | 7.2249 | 5.1927 | 10.628 | 30.4415 | 5.2627 | 3.7824 | 10.4162 | 29.0069 | 4.7758 | 3.4324 | 9.2174 | 22.9157 | 3.7729 | 2.7117 | 7.8731 | 17.041 | 2.8057 | 2.0165 | 6.5363 | 9.5707 | 1.5757 | 1.1325 | 2.7555 | 3.1622 | 0.52063 | 0.37418 | -0.75685 | 2.6844 | 0.44197 | 0.31765 | -3.5468 | 2.6844 | 0.44197 | 0.31765 | -5.0076 | 2.6844 | 0.44197 | 0.31765 | -2.8804 | 29.5325 | 9.8335 | 7.0675 | 11.1149 | 29.6522 | 9.7606 | 7.0151 | 11.0153 | 29.7361 | 9.2211 | 6.6274 | 10.8113 | 29.8329 | 8.6817 | 6.2397 | 10.6996 | 29.9619 | 8.1004 | 5.8219 | 10.6279 | 30.128 | 7.4845 | 5.3792 | 10.524 | 30.3381 | 6.9021 | 4.9607 | 10.3802 | 30.5893 | 6.6675 | 4.7921 | 10.2028 | 30.8153 | 6.4651 | 4.6466 | 9.9615 | 31.0444 | 6.323 | 4.5445 | 9.7243 | 31.8092 | 5.6884 | 4.0884 | 8.9723 | 30.7501 | 5.0628 | 3.6387 | 7.82 | 25.0146 | 4.1185 | 2.96 | 6.9653 | 23.0465 | 3.7944 | 2.7271 | 6.203 | 19.3339 | 3.1832 | 2.2878 | 6.2094 | 29.5325 | 9.8335 | 7.0675 | 11.1149 | 29.5994 | 9.7272 | 6.9911 | 11.0465 | 29.7182 | 9.1487 | 6.5754 | 10.8001 | 29.9723 | 8.4596 | 6.0801 | 10.526 | 30.212 | 7.8252 | 5.6242 | 10.3385 | 30.4552 | 7.118 | 5.1159 | 10.1564 | 30.7914 | 5.2117 | 3.7458 | 9.8745 | 27.8662 | 4.588 | 3.2975 | 8.455 | 21.7504 | 3.581 | 2.5738 | 7.0158 | 15.7952 | 2.6006 | 1.8691 | 5.5854 | 7.7561 | 1.277 | 0.9178 | 1.5265 | 1.0054 | 0.16552 | 0.11897 | -2.2412 | 2.6844 | 0.44197 | 0.31765 | -5.2953 | 2.6844 | 0.44197 | 0.31765 | -7.1093 | 2.6844 | 0.44197 | 0.31765 | -5.382
DEANSGATE | BLOOM ST | SOUTH MANCHESTER | 383463 | 398149 | 29.5154 | 12.6772 | 9.2479 | 16.023 | 29.5397 | 12.245 | 8.9325 | 13.5469 | 29.5863 | 11.6683 | 8.5119 | 12.8818 | 29.621 | 11.6575 | 8.504 | 12.7785 | 29.6453 | 11.6307 | 8.4844 | 12.7231 | 29.6695 | 11.5949 | 8.4583 | 12.6772 | 29.6947 | 11.5778 | 8.4459 | 12.6456 | 29.722 | 11.516 | 8.4007 | 12.6173 | 29.7415 | 11.4253 | 8.3346 | 12.5132 | 29.7593 | 11.3232 | 8.2601 | 12.4186 | 29.7991 | 11.0724 | 8.0772 | 12.0346 | 29.8215 | 10.8479 | 7.9134 | 11.5102 | 29.8292 | 10.645 | 7.7654 | 11.111 | 29.8223 | 10.4605 | 7.6308 | 10.7326 | 29.7926 | 10.2934 | 7.5089 | 10.485 | 29.5149 | 12.6772 | 9.2479 | 16.023 | 29.5714 | 12.5833 | 9.1794 | 15.2679 | 29.6443 | 12.5308 | 9.141 | 14.9113 | 29.7154 | 12.4844 | 9.1072 | 14.7466 | 29.7892 | 12.4352 | 9.0713 | 14.6199 | 29.876 | 12.3287 | 8.9936 | 14.4793 | 29.9775 | 12.0391 | 8.7823 | 14.3201 | 30.0969 | 11.9468 | 8.715 | 14.1363 | 30.1214 | 11.8582 | 8.6504 | 13.9872 | 30.1453 | 11.7734 | 8.5885 | 13.8426 | 30.2102 | 11.5406 | 8.4187 | 13.4516 | 30.264 | 11.3889 | 8.308 | 13.1154 | 30.3061 | 11.2262 | 8.1894 | 12.8581 | 30.346 | 11.0375 | 8.0517 | 12.6061 | 30.3744 | 10.8787 | 7.9358 | 12.4069 | 29.5155 | 12.6772 | 9.2479 | 16.023 | 29.5419 | 12.1523 | 8.8649 | 13.1391 | 29.5894 | 11.5032 | 8.3914 | 12.3918 | 29.6263 | 11.4799 | 8.3744 | 12.2859 | 29.6521 | 11.46 | 8.3599 | 12.2291 | 29.6779 | 11.4382 | 8.344 | 12.1821 | 29.7051 | 11.3917 | 8.3101 | 12.1486 | 29.7348 | 11.3106 | 8.2509 | 12.1185 | 29.7503 | 11.206 | 8.1747 | 12.0596 | 29.7611 | 11.0926 | 8.0919 | 12.0163 | 29.7744 | 10.7922 | 7.8728 | 11.7945 | 29.7723 | 10.5378 | 7.6872 | 11.4508 | 29.7535 | 10.3086 | 7.52 | 11.2453 | 29.7094 | 10.1071 | 7.373 | 11.1401 | 29.631 | 9.9408 | 7.2517 | 11.2492 | 29.5155 | 12.6772 | 9.2479 | 16.023 | 29.5226 | 12.3012 | 8.9735 | 13.9705 | 29.5484 | 11.7773 | 8.5913 | 13.4149 | 29.565 | 11.7701 | 8.5861 | 13.3349 | 29.5726 | 11.7476 | 8.5697 | 13.3062 | 29.5803 | 11.6231 | 8.4789 | 13.2842 | 29.5878 | 11.6693 | 8.5126 | 13.2457 | 29.5945 | 11.5999 | 8.462 | 13.1272 | 29.605 | 11.499 | 8.3884 | 12.9436 | 29.6111 | 11.3552 | 8.2834 | 12.7749 | 29.6213 | 11.0037 | 8.0271 | 12.3423 | 29.6207 | 10.7247 | 7.8235 | 11.9984 | 29.6017 | 10.483 | 7.6472 | 11.8002 | 29.5579 | 10.3371 | 7.5408 | 11.8456 | 29.4785 | 10.1896 | 7.4332 | 12.3783 | 29.5154 | 12.6772 | 9.2479 | 16.023 | 29.5391 | 12.4538 | 9.0848 | 14.6475 | 29.584 | 11.918 | 8.694 | 14.211 | 29.6158 | 11.9004 | 8.6812 | 14.1181 | 29.6374 | 11.8889 | 8.6728 | 14.0827 | 29.661 | 11.8386 | 8.6361 | 14.0528 | 29.6866 | 11.8368 | 8.6348 | 14.0246 | 29.713 | 11.7763 | 8.5906 | 13.9932 | 29.7314 | 11.6863 | 8.525 | 13.8839 | 29.7484 | 11.5833 | 8.4499 | 13.7805 | 29.7919 | 11.359 | 8.2862 | 13.5022 | 29.816 | 11.2049 | 8.1738 | 13.2732 | 29.8254 | 11.0606 | 8.0686 | 13.1567 | 29.8209 | 10.9479 | 7.9863 | 13.1059 | 29.7922 | 10.8686 | 7.9285 | 13.2697 | 29.5154 | 12.6772 | 9.2479 | 16.023 | 29.5408 | 12.0649 | 8.8012 | 12.7387 | 29.5878 | 11.5192 | 8.4031 | 11.908 | 29.6238 | 11.4962 | 8.3863 | 11.795 | 29.6487 | 11.4485 | 8.3515 | 11.7328 | 29.6733 | 11.3109 | 8.2512 | 11.6814 | 29.6992 | 11.3604 | 8.2872 | 11.6124 | 29.7272 | 11.2789 | 8.2278 | 11.4565 | 29.7415 | 11.1732 | 8.1507 | 11.2694 | 29.7512 | 11.026 | 8.0433 | 11.0979 | 29.7675 | 10.6674 | 7.7817 | 10.6609 | 29.7637 | 10.3808 | 7.5726 | 10.3201 | 29.7439 | 10.1337 | 7.3924 | 10.1238 | 29.6987 | 9.9826 | 7.2822 | 10.1713 | 29.6194 | 9.8327 | 7.1728 | 10.6995
DENTON EAST | DROYLSDEN | STALYBRIDGE | 392394 | 395626 | 28.7318 | 15.5943 | 11.3759 | 15.5417 | 28.828 | 15.4005 | 11.2345 | 15.185 | 28.9564 | 15.1681 | 11.065 | 14.9814 | 29.1199 | 14.9054 | 10.8732 | 14.7756 | 29.3213 | 14.6658 | 10.6985 | 14.4483 | 29.5457 | 14.3918 | 10.4986 | 14.1066 | 29.6883 | 14.2088 | 10.3651 | 13.7973 | 29.8567 | 14.0662 | 10.2611 | 13.5415 | 29.9755 | 13.9315 | 10.1628 | 13.2748 | 30.0874 | 13.804 | 10.0698 | 13.034 | 30.4592 | 13.3107 | 9.71 | 11.3253 | 30.8671 | 12.703 | 9.2666 | 8.4959 | 31.166 | 12.2078 | 8.9054 | 6.3004 | 31.4268 | 12.0328 | 8.7778 | 4.339 | 31.606 | 11.669 | 8.5124 | 2.8962 | 28.7095 | 15.5943 | 11.3759 | 15.5417 | 28.7861 | 15.4653 | 11.2817 | 15.3506 | 28.8632 | 15.2966 | 11.1586 | 15.2177 | 28.9619 | 15.1425 | 11.0463 | 15.0857 | 29.0972 | 14.9651 | 10.9168 | 14.9012 | 29.2195 | 14.7851 | 10.7855 | 14.6921 | 29.3485 | 14.5813 | 10.6369 | 14.4202 | 29.5018 | 14.4522 | 10.5427 | 14.093 | 29.5738 | 14.3466 | 10.4657 | 13.8735 | 29.6516 | 14.2296 | 10.3803 | 13.6256 | 29.8926 | 13.9601 | 10.1837 | 12.886 | 30.1329 | 13.7453 | 10.027 | 12.1774 | 30.3899 | 13.525 | 9.8663 | 11.4801 | 30.6823 | 13.5217 | 9.8639 | 10.7372 | 30.9302 | 13.5086 | 9.8543 | 10.1698 | 28.7412 | 15.5943 | 11.3759 | 15.5417 | 28.8642 | 15.3549 | 11.2012 | 15.0739 | 29.0278 | 15.0827 | 11.0026 | 14.7792 | 29.2371 | 14.8112 | 10.8045 | 14.491 | 29.4927 | 14.5 | 10.5775 | 14.0783 | 29.6792 | 14.2097 | 10.3658 | 13.6501 | 29.8618 | 13.9844 | 10.2014 | 13.2637 | 30.0756 | 13.7888 | 10.0587 | 12.9194 | 30.23 | 13.6521 | 9.959 | 12.5715 | 30.3772 | 13.4927 | 9.8428 | 12.2184 | 30.8601 | 12.8522 | 9.3755 | 10.0798 | 31.349 | 12.1831 | 8.8874 | 7.3407 | 31.695 | 11.6665 | 8.5105 | 5.4857 | 31.9914 | 11.5392 | 8.4177 | 4.106 | 32.1386 | 11.2795 | 8.2282 | 3.6106 | 28.7412 | 15.5943 | 11.3759 | 15.5417 | 28.7634 | 15.4311 | 11.2568 | 15.4263 | 28.8474 | 15.2093 | 11.095 | 15.2154 | 28.9631 | 14.9571 | 10.911 | 14.9539 | 29.1306 | 14.6498 | 10.6868 | 14.5427 | 29.375 | 14.3448 | 10.4643 | 14.0888 | 29.5368 | 14.0974 | 10.2839 | 13.5125 | 29.7247 | 13.8164 | 10.0789 | 12.4725 | 29.8793 | 13.5523 | 9.8862 | 11.442 | 30.03 | 13.2982 | 9.7009 | 10.449 | 30.4909 | 12.8511 | 9.3747 | 7.7138 | 30.9437 | 12.223 | 8.9165 | 5.5253 | 31.257 | 11.7143 | 8.5454 | 4.244 | 31.5025 | 11.5871 | 8.4526 | 3.9165 | 31.5996 | 11.5136 | 8.399 | 4.7569 | 28.7318 | 15.5943 | 11.3759 | 15.5417 | 28.8169 | 15.4385 | 11.2622 | 15.278 | 28.9077 | 15.2213 | 11.1037 | 15.139 | 29.0107 | 14.9881 | 10.9336 | 15.0333 | 29.1451 | 14.7822 | 10.7834 | 14.9025 | 29.346 | 14.5419 | 10.6081 | 14.7367 | 29.5697 | 14.3818 | 10.4913 | 14.5429 | 29.7235 | 14.251 | 10.3959 | 14.3385 | 29.8298 | 14.1109 | 10.2937 | 14.0748 | 29.935 | 13.991 | 10.2062 | 13.8094 | 30.2706 | 13.6361 | 9.9474 | 12.8779 | 30.622 | 13.3305 | 9.7244 | 11.705 | 30.8828 | 13.0865 | 9.5464 | 10.8639 | 31.129 | 13.1548 | 9.5962 | 10.0535 | 31.2814 | 12.954 | 9.4497 | 9.5666 | 28.7318 | 15.5943 | 11.3759 | 15.5417 | 28.7887 | 15.3876 | 11.2251 | 15.2754 | 28.9276 | 15.128 | 11.0357 | 14.9501 | 29.1112 | 14.8671 | 10.8454 | 14.5839 | 29.3369 | 14.5425 | 10.6085 | 14.0771 | 29.558 | 14.2187 | 10.3723 | 13.5589 | 29.7262 | 13.9632 | 10.186 | 12.9054 | 29.9478 | 13.6646 | 9.9681 | 11.7569 | 30.116 | 13.3841 | 9.7635 | 10.6472 | 30.2776 | 13.1178 | 9.5692 | 9.576 | 30.7478 | 12.6228 | 9.2082 | 6.6147 | 31.1711 | 11.9698 | 8.7318 | 4.2514 | 31.463 | 11.4328 | 8.3401 | 2.8089 | 31.6831 | 11.263 | 8.2162 | 2.3924 | 31.7899 | 11.1606 | 8.1415 | 3.0682
DENTON WEST | DROYLSDEN | STALYBRIDGE | 390380 | 395565 | 30.513 | 11.4849 | 8.3781 | 14.9405 | 30.5904 | 10.9373 | 7.9786 | 12.3586 | 30.7034 | 10.6988 | 7.8046 | 11.7833 | 30.8499 | 10.4476 | 7.6214 | 11.3645 | 31.3306 | 10.1549 | 7.4078 | 10.7337 | 31.5374 | 9.9412 | 7.2519 | 10.3969 | 31.7873 | 9.8636 | 7.1954 | 10.0693 | 32.1066 | 9.7595 | 7.1195 | 9.7369 | 32.3132 | 9.6308 | 7.0255 | 9.3404 | 32.5031 | 9.5435 | 6.9618 | 9.1158 | 33.1464 | 9.076 | 6.6208 | 7.3941 | 33.8215 | 8.4191 | 6.1416 | 4.3294 | 34.2983 | 7.8913 | 5.7566 | 1.8047 | 34.6964 | 7.7077 | 5.6227 | -0.83591 | 34.9868 | 7.1702 | 5.2306 | -3.1627 | 30.4766 | 11.4849 | 8.3781 | 14.9405 | 30.5396 | 11.2842 | 8.2316 | 14.4621 | 30.5943 | 11.1193 | 8.1114 | 14.3011 | 30.6633 | 10.9525 | 7.9897 | 14.2101 | 30.7634 | 10.766 | 7.8536 | 14.0434 | 30.8946 | 10.5676 | 7.7089 | 13.8515 | 31.0553 | 10.3693 | 7.5642 | 13.5957 | 31.24 | 10.2618 | 7.4858 | 13.27 | 31.3702 | 10.1563 | 7.4089 | 12.97 | 31.5086 | 10.0687 | 7.345 | 12.6653 | 31.959 | 9.8114 | 7.1573 | 11.7474 | 32.4288 | 9.5923 | 6.9975 | 10.8377 | 32.8641 | 9.3646 | 6.8314 | 10.0067 | 33.2572 | 9.4254 | 6.8757 | 9.1541 | 33.5165 | 9.5515 | 6.9677 | 8.616 | 30.5239 | 11.4849 | 8.3781 | 14.9405 | 30.6122 | 10.861 | 7.9229 | 11.9609 | 30.7433 | 10.5889 | 7.7245 | 11.3293 | 30.9159 | 10.3314 | 7.5366 | 10.949 | 31.4115 | 9.9332 | 7.2462 | 10.3748 | 31.6528 | 9.8447 | 7.1816 | 10.0869 | 31.9438 | 9.7346 | 7.1013 | 9.8295 | 32.2435 | 9.63 | 7.025 | 9.5697 | 32.4431 | 9.5118 | 6.9387 | 9.2669 | 32.6395 | 9.3979 | 6.8556 | 9.1192 | 33.3322 | 8.8961 | 6.4896 | 7.6092 | 34.0789 | 8.2238 | 5.9991 | 4.7069 | 34.6115 | 7.6569 | 5.5856 | 2.3233 | 34.9555 | 7.4723 | 5.4509 | -0.13831 | 35.1259 | 6.9346 | 5.0587 | -2.2297 | 30.5239 | 11.4849 | 8.3781 | 14.9405 | 30.5067 | 11.0648 | 8.0716 | 13.1015 | 30.5607 | 10.8677 | 7.9278 | 12.7072 | 30.6427 | 10.571 | 7.7114 | 12.3841 | 31.0502 | 10.3709 | 7.5654 | 11.8404 | 31.2543 | 10.2006 | 7.4412 | 11.5375 | 31.5293 | 10.0596 | 7.3384 | 11.0595 | 31.8735 | 9.7731 | 7.1293 | 9.9764 | 32.1279 | 9.5192 | 6.9441 | 8.8526 | 32.3441 | 9.2737 | 6.765 | 7.8868 | 33.0443 | 8.9647 | 6.5397 | 5.0544 | 33.7396 | 8.2535 | 6.0208 | 2.2371 | 34.2211 | 7.6196 | 5.5584 | -0.029517 | 34.6028 | 7.1557 | 5.22 | -1.4901 | 34.6207 | 7.1983 | 5.2511 | -0.30708 | 30.513 | 11.4849 | 8.3781 | 14.9405 | 30.5781 | 11.238 | 8.198 | 14.1255 | 30.6509 | 11.0687 | 8.0745 | 13.9475 | 30.7341 | 10.8316 | 7.9015 | 13.6117 | 31.1468 | 10.5682 | 7.7094 | 13.1062 | 31.3252 | 10.3827 | 7.5741 | 12.866 | 31.5721 | 10.3168 | 7.5259 | 12.5887 | 31.8546 | 10.2212 | 7.4562 | 12.287 | 32.0797 | 10.086 | 7.3576 | 11.8928 | 32.2701 | 10.0036 | 7.2975 | 11.6449 | 32.8505 | 9.6957 | 7.0728 | 10.7382 | 33.4586 | 9.4204 | 6.872 | 9.7164 | 33.8907 | 9.2329 | 6.7353 | 9.0289 | 34.2419 | 9.4585 | 6.8998 | 8.4448 | 34.4477 | 9.2897 | 6.7767 | 8.2673 | 30.513 | 11.4849 | 8.3781 | 14.9405 | 30.5255 | 10.8379 | 7.9061 | 11.8053 | 30.6288 | 10.5785 | 7.7168 | 11.061 | 30.7718 | 10.2734 | 7.4943 | 10.6316 | 31.2279 | 10.0399 | 7.324 | 9.9953 | 31.4253 | 9.8596 | 7.1924 | 9.6426 | 31.673 | 9.7041 | 7.079 | 9.1066 | 32.0254 | 9.4035 | 6.8597 | 7.9317 | 32.2739 | 9.1364 | 6.6649 | 6.7361 | 32.4913 | 8.8882 | 6.4838 | 5.6993 | 33.1863 | 8.5185 | 6.2142 | 2.6656 | 33.8515 | 7.7769 | 5.6731 | -0.28498 | 34.3208 | 7.0747 | 5.1609 | -2.7712 | 34.6745 | 6.5926 | 4.8092 | -4.5287 | 34.7223 | 6.5376 | 4.7691 | -3.6898
DICKINSON ST T11 & T12 | BLOOM ST | SOUTH MANCHESTER | 384109 | 397722 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
DICKINSON ST T13 | STUART ST | STALYBRIDGE | 384109 | 397722 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 384792 | 391153 | 30.1996 | 13.3093 | 9.7089 | 12.6879 | 30.2848 | 13.1754 | 9.6113 | 12.3972 | 30.3975 | 13.126 | 9.5752 | 12.2459 | 30.5498 | 13.0088 | 9.4897 | 12.1068 | 30.7408 | 12.8887 | 9.4021 | 11.8651 | 30.9606 | 12.7669 | 9.3133 | 11.6115 | 31.2142 | 12.5728 | 9.1717 | 11.3812 | 31.524 | 12.4417 | 9.076 | 11.18 | 31.7314 | 12.288 | 8.964 | 10.9494 | 31.9255 | 12.1159 | 8.8383 | 10.7637 | 32.4598 | 11.6051 | 8.4657 | 9.18 | 33.038 | 10.9131 | 7.961 | 6.2203 | 33.4661 | 10.3548 | 7.5537 | 3.8233 | 33.8521 | 9.7573 | 7.1179 | 1.2829 | 34.1171 | 9.261 | 6.7558 | -1.0196 | 30.1671 | 13.3093 | 9.7089 | 12.6879 | 30.252 | 13.1441 | 9.5884 | 12.4973 | 30.336 | 13.1491 | 9.5921 | 12.3452 | 30.4543 | 13.0487 | 9.5189 | 12.183 | 30.6204 | 12.9295 | 9.4319 | 11.9558 | 30.8286 | 12.8282 | 9.358 | 11.7014 | 31.0802 | 12.6189 | 9.2053 | 11.3747 | 31.371 | 12.4887 | 9.1104 | 10.99 | 31.4701 | 12.3749 | 9.0273 | 10.6942 | 31.5732 | 12.2487 | 8.9353 | 10.3974 | 31.8895 | 11.8688 | 8.6581 | 9.5397 | 32.1922 | 11.7034 | 8.5374 | 8.762 | 32.4535 | 11.5051 | 8.3928 | 8.0967 | 32.7112 | 11.2747 | 8.2247 | 7.4567 | 32.9035 | 11.0208 | 8.0395 | 7.0783 | 30.2133 | 13.3093 | 9.7089 | 12.6879 | 30.3102 | 13.172 | 9.6088 | 12.3935 | 30.4418 | 13.0896 | 9.5487 | 12.2671 | 30.622 | 12.9594 | 9.4537 | 12.1682 | 30.8473 | 12.8201 | 9.3521 | 11.9736 | 31.108 | 12.6705 | 9.243 | 11.7736 | 31.4115 | 12.4776 | 9.1023 | 11.6208 | 31.782 | 12.3335 | 8.9971 | 11.4997 | 32.0162 | 12.1644 | 8.8738 | 11.3644 | 32.213 | 11.9974 | 8.7519 | 11.2565 | 32.8303 | 11.3732 | 8.2966 | 9.9178 | 33.4888 | 10.7504 | 7.8422 | 7.171 | 33.9755 | 10.1214 | 7.3834 | 4.9633 | 34.4119 | 9.5758 | 6.9854 | 2.7272 | 34.7125 | 9.0358 | 6.5915 | 0.7539 | 30.2133 | 13.3093 | 9.7089 | 12.6879 | 30.1837 | 13.2685 | 9.6792 | 12.7942 | 30.2201 | 13.2514 | 9.6667 | 12.7888 | 30.2916 | 13.1597 | 9.5998 | 12.7722 | 30.417 | 13.054 | 9.5227 | 12.6283 | 30.6236 | 12.9065 | 9.4151 | 12.4121 | 30.8878 | 12.7476 | 9.2992 | 12.0579 | 31.1973 | 12.4739 | 9.0996 | 11.1652 | 31.425 | 12.1919 | 8.8938 | 10.2205 | 31.6458 | 11.914 | 8.6911 | 9.2513 | 32.2518 | 11.0762 | 8.0799 | 6.4655 | 32.8863 | 10.3819 | 7.5734 | 3.7867 | 33.3524 | 9.7532 | 7.1148 | 1.6909 | 33.7378 | 9.3631 | 6.8303 | 0.5084 | 33.8561 | 9.3526 | 6.8226 | 1.809 | 30.1996 | 13.3093 | 9.7089 | 12.6879 | 30.2714 | 13.2004 | 9.6295 | 12.4969 | 30.3411 | 13.176 | 9.6117 | 12.4167 | 30.4284 | 13.0767 | 9.5393 | 12.3939 | 30.5532 | 12.9975 | 9.4815 | 12.3241 | 30.7486 | 12.9112 | 9.4186 | 12.2114 | 31.0046 | 12.7439 | 9.2965 | 12.0838 | 31.2851 | 12.6211 | 9.2069 | 11.9543 | 31.4668 | 12.476 | 9.1011 | 11.7514 | 31.6452 | 12.3011 | 8.9735 | 11.5604 | 32.1716 | 11.949 | 8.7166 | 10.88 | 32.6943 | 11.6632 | 8.5082 | 10.0857 | 33.085 | 11.4048 | 8.3196 | 9.5692 | 33.4499 | 11.2115 | 8.1787 | 9.11 | 33.6157 | 11.0897 | 8.0898 | 8.9963 | 30.1996 | 13.3093 | 9.7089 | 12.6879 | 30.2172 | 13.2298 | 9.651 | 12.6276 | 30.3207 | 13.1829 | 9.6167 | 12.4953 | 30.4714 | 13.0577 | 9.5254 | 12.3246 | 30.6639 | 12.9287 | 9.4313 | 12.0441 | 30.8829 | 12.7674 | 9.3136 | 11.7603 | 31.1429 | 12.5891 | 9.1836 | 11.3255 | 31.4902 | 12.2928 | 8.9675 | 10.3066 | 31.7371 | 11.9917 | 8.7478 | 9.2667 | 31.9718 | 11.7041 | 8.538 | 8.2397 | 32.5608 | 10.8278 | 7.8988 | 5.2265 | 33.1226 | 10.085 | 7.3568 | 2.3446 | 33.5339 | 9.3948 | 6.8534 | 0.047722 | 33.855 | 8.9763 | 6.5481 | -1.3912 | 33.965 | 8.9179 | 6.5055 | -0.39501
DODGSON RD | PRESTON EAST | PENWORTHAM EAST / ROCHDALE | 355190 | 430397 | 28.6931 | 11.5111 | 8.3972 | 19.9123 | 28.7465 | 11.4208 | 8.3313 | 19.7478 | 28.7758 | 11.3682 | 8.293 | 19.7637 | 28.8165 | 11.2979 | 8.2416 | 19.7019 | 28.8852 | 11.1967 | 8.1678 | 19.5492 | 28.9707 | 11.0598 | 8.0679 | 19.3693 | 29.0746 | 10.9389 | 7.9798 | 19.1871 | 29.1989 | 10.8471 | 7.9128 | 19.0155 | 29.3267 | 10.7527 | 7.844 | 18.8102 | 29.4569 | 10.6217 | 7.7484 | 18.3738 | 29.9852 | 10.0015 | 7.2959 | 15.917 | 30.6368 | 9.4541 | 6.8966 | 13.1117 | 31.1367 | 9.1612 | 6.683 | 10.9931 | 31.6059 | 8.9761 | 6.5479 | 9.1536 | 31.9354 | 8.9002 | 6.4926 | 7.9142 | 28.6919 | 11.5111 | 8.3972 | 19.9123 | 28.7354 | 11.4602 | 8.36 | 19.744 | 28.759 | 11.4397 | 8.3451 | 19.7332 | 28.7923 | 11.4135 | 8.326 | 19.6481 | 28.8435 | 11.333 | 8.2672 | 19.5303 | 28.9087 | 11.2205 | 8.1852 | 19.3967 | 28.9928 | 11.0478 | 8.0592 | 19.2126 | 29.093 | 10.953 | 7.9901 | 18.9734 | 29.1689 | 10.8974 | 7.9495 | 18.8096 | 29.2515 | 10.8323 | 7.902 | 18.6386 | 29.55 | 10.5837 | 7.7206 | 18.0278 | 29.896 | 10.2346 | 7.466 | 16.4532 | 30.207 | 9.9098 | 7.2291 | 14.7999 | 30.5093 | 9.7232 | 7.0929 | 13.2386 | 30.7007 | 9.5146 | 6.9408 | 12.3223 | 28.6935 | 11.5111 | 8.3972 | 19.9123 | 28.742 | 11.4 | 8.3161 | 19.7659 | 28.768 | 11.324 | 8.2607 | 19.7986 | 28.8048 | 11.2205 | 8.1852 | 19.7619 | 28.8674 | 11.1005 | 8.0977 | 19.6365 | 28.9443 | 10.9681 | 8.0011 | 19.4897 | 29.0376 | 10.8407 | 7.9082 | 19.3574 | 29.1478 | 10.7484 | 7.8408 | 19.2364 | 29.2593 | 10.6368 | 7.7594 | 19.1145 | 29.3765 | 10.5109 | 7.6675 | 18.9901 | 29.9066 | 9.9388 | 7.2502 | 16.7705 | 30.5952 | 9.3496 | 6.8204 | 13.7206 | 31.1324 | 8.8635 | 6.4658 | 11.2297 | 31.5539 | 8.5949 | 6.2699 | 9.0637 | 31.8481 | 8.422 | 6.1438 | 7.6741 | 28.6936 | 11.5111 | 8.3972 | 19.9123 | 28.6751 | 11.4516 | 8.3538 | 19.9625 | 28.6792 | 11.4184 | 8.3295 | 20.0409 | 28.7007 | 11.3181 | 8.2564 | 20.0136 | 28.7554 | 11.2019 | 8.1716 | 19.8805 | 28.8357 | 11.0703 | 8.0756 | 19.7153 | 28.9609 | 10.9491 | 7.9872 | 19.4165 | 29.1739 | 10.738 | 7.8332 | 18.6638 | 29.3954 | 10.5241 | 7.6772 | 17.8719 | 29.6226 | 10.273 | 7.494 | 17.0608 | 30.3045 | 10.1275 | 7.3879 | 14.2472 | 30.9261 | 9.5123 | 6.9391 | 11.6316 | 31.3556 | 9.0107 | 6.5732 | 9.6698 | 31.6029 | 8.8167 | 6.4316 | 8.4723 | 31.5148 | 8.6783 | 6.3307 | 8.6999 | 28.6931 | 11.5111 | 8.3972 | 19.9123 | 28.7348 | 11.4509 | 8.3533 | 19.7717 | 28.7482 | 11.4074 | 8.3215 | 19.8124 | 28.764 | 11.3528 | 8.2817 | 19.8033 | 28.7968 | 11.2787 | 8.2276 | 19.7692 | 28.8515 | 11.1599 | 8.141 | 19.7164 | 28.9338 | 11.0572 | 8.0661 | 19.6299 | 29.0372 | 10.9733 | 8.0049 | 19.5073 | 29.1472 | 10.8834 | 7.9393 | 19.3355 | 29.2676 | 10.7934 | 7.8737 | 19.1523 | 29.6949 | 10.3433 | 7.5453 | 17.7078 | 30.1286 | 9.985 | 7.2839 | 15.8068 | 30.4408 | 9.834 | 7.1738 | 14.3538 | 30.7034 | 9.8387 | 7.1772 | 13.136 | 30.7972 | 9.838 | 7.1767 | 12.63 | 28.6931 | 11.5111 | 8.3972 | 19.9123 | 28.6802 | 11.4208 | 8.3313 | 19.9403 | 28.6974 | 11.3791 | 8.3009 | 19.9835 | 28.7335 | 11.2716 | 8.2225 | 19.9179 | 28.7979 | 11.1431 | 8.1287 | 19.7519 | 28.8737 | 11.0099 | 8.0316 | 19.569 | 28.9874 | 10.8821 | 7.9383 | 19.248 | 29.1967 | 10.6687 | 7.7826 | 18.467 | 29.4104 | 10.4552 | 7.6269 | 17.6832 | 29.6324 | 10.1934 | 7.4359 | 16.8947 | 30.3305 | 10.0995 | 7.3675 | 14.3555 | 30.9986 | 9.4141 | 6.8675 | 11.4644 | 31.5155 | 8.8506 | 6.4564 | 9.1632 | 31.8167 | 8.5651 | 6.2482 | 7.5803 | 31.7606 | 8.4054 | 6.1316 | 7.7017
DOUGLAS ST | RIBBLE | PENWORTHAM EAST / ROCHDALE | 352220 | 429932 | 27.7341 | 7.745 | 5.6499 | 15.5396 | 27.7701 | 7.4187 | 5.4119 | 14.8028 | 27.8458 | 7.4777 | 5.4549 | 14.5704 | 27.914 | 7.5002 | 5.4713 | 14.4568 | 27.9974 | 7.4646 | 5.4453 | 14.3476 | 28.1036 | 7.38 | 5.3836 | 14.2295 | 28.2394 | 7.2115 | 5.2607 | 14.1043 | 28.4141 | 7.1404 | 5.2088 | 13.9594 | 28.6042 | 7.0443 | 5.1388 | 13.7561 | 28.8072 | 6.9484 | 5.0688 | 13.5603 | 29.4964 | 6.5905 | 4.8077 | 12.7045 | 30.1458 | 6.1938 | 4.5183 | 11.5045 | 30.5049 | 5.9569 | 4.3455 | 10.3584 | 30.72 | 6.7167 | 4.8997 | 9.1636 | 30.796 | 6.5017 | 4.7429 | 8.2402 | 27.7213 | 7.745 | 5.6499 | 15.5396 | 27.7599 | 7.618 | 5.5573 | 15.2523 | 27.8266 | 7.8418 | 5.7205 | 15.0734 | 27.8941 | 7.8625 | 5.7356 | 14.9199 | 27.9735 | 7.7698 | 5.6679 | 14.7673 | 28.0748 | 7.6514 | 5.5816 | 14.5872 | 28.1805 | 7.3859 | 5.3879 | 14.3674 | 28.2845 | 7.2439 | 5.2843 | 14.1086 | 28.3805 | 7.114 | 5.1895 | 13.9172 | 28.4864 | 6.9898 | 5.099 | 13.7253 | 28.866 | 6.5216 | 4.7574 | 13.1522 | 29.3127 | 6.5264 | 4.7609 | 12.5934 | 29.7626 | 6.5012 | 4.7426 | 12.1058 | 30.2383 | 7.061 | 5.1509 | 11.6234 | 30.5412 | 7.545 | 5.504 | 11.3232 | 27.7388 | 7.745 | 5.6499 | 15.5396 | 27.779 | 7.449 | 5.4339 | 14.6949 | 27.8537 | 7.4996 | 5.4709 | 14.4443 | 27.9253 | 7.4448 | 5.4309 | 14.3304 | 28.0106 | 7.3723 | 5.378 | 14.2234 | 28.1162 | 7.2372 | 5.2794 | 14.1099 | 28.2483 | 7.0932 | 5.1744 | 13.9904 | 28.415 | 6.9842 | 5.0949 | 13.8556 | 28.5797 | 6.8622 | 5.0059 | 13.7017 | 28.7568 | 6.7597 | 4.9311 | 13.559 | 29.4248 | 6.3146 | 4.6064 | 12.8442 | 30.1197 | 5.9273 | 4.3239 | 11.7671 | 30.5247 | 5.7059 | 4.1623 | 10.7291 | 30.7437 | 6.3638 | 4.6423 | 9.7319 | 30.7703 | 6.1344 | 4.4749 | 9.0871 | 27.7388 | 7.745 | 5.6499 | 15.5396 | 27.7274 | 7.5349 | 5.4966 | 15.0339 | 27.7725 | 7.52 | 5.4858 | 14.8853 | 27.8136 | 7.5499 | 5.5076 | 14.8265 | 27.8739 | 7.5673 | 5.5203 | 14.7646 | 27.971 | 7.4868 | 5.4615 | 14.6722 | 28.114 | 7.3544 | 5.3649 | 14.505 | 28.3241 | 7.2217 | 5.2681 | 14.1585 | 28.5521 | 7.1314 | 5.2023 | 13.7559 | 28.7932 | 7.021 | 5.1217 | 13.362 | 29.4526 | 7.4141 | 5.4085 | 12.0143 | 29.9775 | 6.9304 | 5.0557 | 10.6789 | 30.2846 | 6.5146 | 4.7523 | 9.7002 | 30.4378 | 6.4974 | 4.7398 | 9.1853 | 30.3823 | 6.3671 | 4.6447 | 9.821 | 27.7341 | 7.745 | 5.6499 | 15.5396 | 27.7639 | 7.4494 | 5.4342 | 15.1373 | 27.8237 | 7.5395 | 5.5 | 14.987 | 27.8718 | 7.5967 | 5.5417 | 14.9152 | 27.9256 | 7.581 | 5.5302 | 14.8641 | 28.0094 | 7.5283 | 5.4918 | 14.7863 | 28.1256 | 7.3749 | 5.3799 | 14.6782 | 28.2668 | 7.2965 | 5.3227 | 14.5522 | 28.4208 | 7.2026 | 5.2542 | 14.3645 | 28.5896 | 7.1093 | 5.1861 | 14.1752 | 29.1721 | 6.8162 | 4.9723 | 13.5699 | 29.7357 | 6.5758 | 4.7969 | 12.9731 | 30.1092 | 6.501 | 4.7424 | 12.585 | 30.352 | 7.4802 | 5.4567 | 12.32 | 30.4185 | 7.4799 | 5.4565 | 12.3896 | 27.7341 | 7.745 | 5.6499 | 15.5396 | 27.7419 | 7.4784 | 5.4554 | 14.674 | 27.811 | 7.44 | 5.4274 | 14.4139 | 27.8779 | 7.4212 | 5.4137 | 14.2919 | 27.9585 | 7.4138 | 5.4082 | 14.1736 | 28.057 | 7.3224 | 5.3416 | 14.0524 | 28.1914 | 7.1851 | 5.2414 | 13.8706 | 28.3997 | 7.0477 | 5.1412 | 13.4934 | 28.6105 | 6.961 | 5.078 | 13.095 | 28.8326 | 6.845 | 4.9933 | 12.6973 | 29.4865 | 7.2312 | 5.2751 | 11.3762 | 30.0576 | 6.7327 | 4.9114 | 9.988 | 30.4219 | 6.3095 | 4.6027 | 8.947 | 30.6017 | 6.272 | 4.5753 | 8.3711 | 30.5563 | 6.1247 | 4.4679 | 8.9288
DROYLSDEN EAST | DROYLSDEN | STALYBRIDGE | 390532 | 398053 | 30.7161 | 6.1951 | 4.5192 | 13.0349 | 30.9099 | 5.8505 | 4.2679 | 12.6819 | 31.1836 | 5.5457 | 4.0455 | 12.47 | 31.3408 | 5.0838 | 3.7086 | 12.2749 | 30.4132 | 4.9333 | 3.5988 | 11.9626 | 27.9976 | 4.5415 | 3.313 | 11.6287 | 26.6051 | 4.3156 | 3.1482 | 11.2991 | 25.6546 | 4.1614 | 3.0357 | 10.9878 | 24.2686 | 3.9366 | 2.8717 | 10.5824 | 23.842 | 3.8674 | 2.8212 | 10.1602 | 20.6385 | 3.3478 | 2.4422 | 7.8378 | 16.3926 | 2.659 | 1.9397 | 4.3055 | 12.9879 | 2.1068 | 1.5369 | 1.6013 | 12.0281 | 1.9511 | 1.4233 | -1.0032 | 8.6322 | 1.4002 | 1.0215 | -2.9348 | 30.6832 | 6.1951 | 4.5192 | 13.0349 | 30.7995 | 5.9553 | 4.3443 | 12.8315 | 30.9019 | 5.7332 | 4.1823 | 12.7017 | 31.0458 | 5.4942 | 4.0079 | 12.5677 | 31.2597 | 5.236 | 3.8196 | 12.369 | 30.7012 | 4.98 | 3.6329 | 12.15 | 29.0743 | 4.7161 | 3.4404 | 11.8467 | 28.0939 | 4.5571 | 3.3243 | 11.4425 | 27.2655 | 4.4227 | 3.2263 | 11.1292 | 26.5641 | 4.309 | 3.1433 | 10.806 | 24.2127 | 3.9275 | 2.8651 | 9.7432 | 21.9645 | 3.5629 | 2.5991 | 8.5173 | 20.3262 | 3.2971 | 2.4052 | 7.3057 | 18.6321 | 3.0223 | 2.2047 | 5.9722 | 18.393 | 2.9835 | 2.1764 | 4.9874 | 30.7327 | 6.1951 | 4.5192 | 13.0349 | 30.9584 | 5.8126 | 4.2402 | 12.5799 | 31.2779 | 5.442 | 3.9699 | 12.2766 | 31.3857 | 5.0911 | 3.7139 | 11.9972 | 29.2628 | 4.7467 | 3.4627 | 11.5962 | 26.2068 | 4.251 | 3.101 | 11.1708 | 25.242 | 4.0945 | 2.9869 | 10.7631 | 23.8589 | 3.8701 | 2.8232 | 10.2976 | 23.203 | 3.7638 | 2.7456 | 9.7448 | 22.3213 | 3.6207 | 2.6413 | 9.1876 | 18.0209 | 2.9232 | 2.1324 | 6.5094 | 13.2049 | 2.142 | 1.5625 | 3.02 | 9.6608 | 1.5671 | 1.1432 | 0.63236 | 8.9441 | 1.4508 | 1.0584 | -1.344 | 6.3785 | 1.0347 | 0.75477 | -2.316 | 30.7327 | 6.1951 | 4.5192 | 13.0349 | 30.791 | 5.908 | 4.3098 | 13.0077 | 30.9575 | 5.5651 | 4.0596 | 12.8083 | 31.1836 | 5.2479 | 3.8283 | 12.5413 | 28.9314 | 4.693 | 3.4234 | 12.1231 | 27.1115 | 4.3978 | 3.2081 | 11.6613 | 26.8157 | 4.3498 | 3.1731 | 11.0227 | 25.1736 | 4.0834 | 2.9788 | 9.798 | 23.5005 | 3.812 | 2.7808 | 8.5819 | 21.8987 | 3.5522 | 2.5913 | 7.3963 | 19.7052 | 3.1964 | 2.3317 | 3.9492 | 14.9789 | 2.4297 | 1.7725 | 0.99757 | 11.2336 | 1.8222 | 1.3293 | -0.8295 | 8.372 | 1.358 | 0.99065 | -1.6703 | 7.7185 | 1.252 | 0.91333 | -0.98283 | 30.7161 | 6.1951 | 4.5192 | 13.0349 | 30.8815 | 5.895 | 4.3003 | 12.7639 | 31.0629 | 5.6069 | 4.0902 | 12.6069 | 31.2694 | 5.1704 | 3.7717 | 12.4928 | 31.1076 | 5.046 | 3.681 | 12.3312 | 28.9129 | 4.69 | 3.4213 | 12.1287 | 27.4917 | 4.4594 | 3.2531 | 11.8875 | 26.6713 | 4.3263 | 3.156 | 11.625 | 25.411 | 4.1219 | 3.0069 | 11.2864 | 24.8766 | 4.0352 | 2.9436 | 10.8639 | 22.7356 | 3.6879 | 2.6903 | 9.3923 | 20.7191 | 3.3608 | 2.4517 | 7.7807 | 19.1809 | 3.1113 | 2.2697 | 6.6306 | 20.1406 | 3.267 | 2.3832 | 5.4783 | 18.0917 | 2.9347 | 2.1408 | 4.6129 | 30.7161 | 6.1951 | 4.5192 | 13.0349 | 30.8395 | 5.8647 | 4.2782 | 12.8764 | 31.1173 | 5.4993 | 4.0117 | 12.5725 | 31.4345 | 5.1622 | 3.7658 | 12.2026 | 28.2532 | 4.583 | 3.3432 | 11.6895 | 26.3166 | 4.2688 | 3.114 | 11.1606 | 25.9529 | 4.2098 | 3.071 | 10.436 | 24.1595 | 3.9189 | 2.8588 | 9.0763 | 22.3401 | 3.6238 | 2.6435 | 7.7266 | 20.589 | 3.3397 | 2.4363 | 6.4154 | 18.0378 | 2.9259 | 2.1344 | 2.7 | 13.0392 | 2.1151 | 1.5429 | -0.44857 | 9.1096 | 1.4777 | 1.0779 | -2.457 | 5.9768 | 0.9695 | 0.70723 | -3.4972 | 5.0411 | 0.81772 | 0.59652 | -3.0586
DUKINFIELD | HYDE | STALYBRIDGE | 394372 | 396438 | 21.2983 | 3.886 | 2.8348 | 16.9484 | 21.3635 | 3.5902 | 2.619 | 16.3678 | 21.1306 | 3.4276 | 2.5004 | 16.1064 | 19.3341 | 3.1362 | 2.2878 | 15.9947 | 19.8055 | 3.2126 | 2.3436 | 15.8014 | 18.9512 | 3.0741 | 2.2425 | 15.6103 | 18.515 | 3.0033 | 2.1909 | 15.4402 | 18.0642 | 2.9302 | 2.1375 | 15.2798 | 17.5168 | 2.8414 | 2.0728 | 15.026 | 17.4643 | 2.8329 | 2.0665 | 14.7791 | 17.0237 | 2.7614 | 2.0144 | 13.5731 | 20.5649 | 3.3358 | 2.4334 | 11.7301 | 23.7493 | 5.3584 | 3.9089 | 10.2149 | 24.2086 | 7.9651 | 5.8104 | 8.8378 | 24.6157 | 8.5927 | 6.2683 | 7.6786 | 21.2996 | 3.886 | 2.8348 | 16.9484 | 21.3654 | 3.8398 | 2.8011 | 16.7805 | 21.4232 | 3.7953 | 2.7686 | 16.653 | 21.4991 | 3.7535 | 2.7381 | 16.6113 | 21.5983 | 3.6883 | 2.6906 | 16.5277 | 21.7147 | 3.6304 | 2.6483 | 16.4566 | 21.5194 | 3.4907 | 2.5464 | 16.3688 | 20.9822 | 3.4035 | 2.4828 | 16.2324 | 20.5566 | 3.3345 | 2.4325 | 15.9658 | 20.0373 | 3.2502 | 2.371 | 15.6978 | 17.9663 | 2.9143 | 2.1259 | 14.887 | 17.2769 | 2.8025 | 2.0444 | 13.9787 | 22.9941 | 3.9612 | 2.8896 | 13.0698 | 23.2553 | 5.8614 | 4.2758 | 12.2245 | 23.4269 | 6.4201 | 4.6834 | 11.714 | 21.2978 | 3.886 | 2.8348 | 16.9484 | 21.364 | 3.5362 | 2.5796 | 16.2741 | 20.6724 | 3.3533 | 2.4462 | 15.9937 | 19.4957 | 3.1624 | 2.3069 | 15.8799 | 19.3381 | 3.1368 | 2.2883 | 15.6867 | 18.4663 | 2.9954 | 2.1851 | 15.4968 | 17.9651 | 2.9141 | 2.1258 | 15.3284 | 17.4348 | 2.8281 | 2.0631 | 15.1714 | 16.8353 | 2.7308 | 1.9921 | 14.9629 | 16.7878 | 2.7231 | 1.9865 | 14.7668 | 16.271 | 2.6393 | 1.9253 | 13.7073 | 19.8432 | 3.2188 | 2.348 | 12.0082 | 23.7292 | 5.2583 | 3.8358 | 10.6453 | 24.1882 | 7.8802 | 5.7485 | 9.4941 | 24.5862 | 8.5551 | 6.2409 | 8.6786 | 21.2978 | 3.886 | 2.8348 | 16.9484 | 21.335 | 3.591 | 2.6196 | 16.4832 | 20.9566 | 3.3994 | 2.4798 | 16.2565 | 20.4892 | 3.3236 | 2.4245 | 16.1477 | 19.9099 | 3.2296 | 2.3559 | 15.9564 | 18.9766 | 3.0782 | 2.2455 | 15.7563 | 18.2628 | 2.9624 | 2.161 | 15.4813 | 20.5295 | 3.3301 | 2.4292 | 14.9352 | 21.6073 | 3.5049 | 2.5568 | 14.3296 | 22.3589 | 3.9604 | 2.8891 | 13.7396 | 22.9543 | 9.7008 | 7.0766 | 12.0398 | 23.5326 | 9.2471 | 6.7456 | 10.4067 | 23.9746 | 8.8549 | 6.4595 | 9.1291 | 24.3097 | 8.6036 | 6.2762 | 8.468 | 24.3595 | 8.5977 | 6.2719 | 9.0505 | 21.2983 | 3.886 | 2.8348 | 16.9484 | 21.3554 | 3.649 | 2.6619 | 16.607 | 21.4101 | 3.4964 | 2.5506 | 16.4044 | 19.6227 | 3.183 | 2.322 | 16.3212 | 20.3778 | 3.3055 | 2.4113 | 16.1951 | 19.6223 | 3.1829 | 2.3219 | 16.0686 | 19.2375 | 3.1205 | 2.2764 | 15.9435 | 18.837 | 3.0556 | 2.229 | 15.807 | 18.2878 | 2.9665 | 2.164 | 15.5507 | 18.2292 | 2.957 | 2.1571 | 15.2905 | 18.276 | 2.9645 | 2.1626 | 14.4691 | 22.8252 | 3.7352 | 2.7248 | 13.5982 | 23.0936 | 5.9438 | 4.3359 | 12.9648 | 23.3335 | 8.7933 | 6.4146 | 12.5728 | 23.4711 | 9.6686 | 7.0531 | 12.5125 | 21.2983 | 3.886 | 2.8348 | 16.9484 | 21.3566 | 3.5218 | 2.5691 | 16.1977 | 20.4608 | 3.3189 | 2.4211 | 15.8967 | 20.005 | 3.245 | 2.3672 | 15.7662 | 19.3487 | 3.1385 | 2.2895 | 15.557 | 18.4053 | 2.9855 | 2.1779 | 15.3525 | 17.6806 | 2.868 | 2.0921 | 15.0765 | 19.924 | 3.2319 | 2.3576 | 14.5194 | 20.9768 | 3.4026 | 2.4822 | 13.9058 | 22.5473 | 3.8553 | 2.8124 | 13.3083 | 23.1744 | 9.5732 | 6.9835 | 11.5795 | 23.7776 | 9.1096 | 6.6453 | 9.9091 | 24.2442 | 8.7043 | 6.3497 | 8.5813 | 24.5962 | 8.4308 | 6.1502 | 7.8086 | 24.6687 | 8.4013 | 6.1286 | 8.2892
DUMERS LANE | BURY | KEARSLEY | 380057 | 408141 | 27.2196 | 10.8422 | 7.7925 | 16.6562 | 27.2784 | 10.6115 | 7.6267 | 14.9838 | 27.3577 | 10.3411 | 7.4323 | 14.2375 | 27.4532 | 10.44 | 7.5035 | 13.8718 | 27.5876 | 10.3689 | 7.4524 | 13.2389 | 27.7527 | 10.1996 | 7.3306 | 12.5871 | 27.9514 | 10.1057 | 7.2632 | 12.0798 | 28.1941 | 9.9673 | 7.1637 | 11.5499 | 28.4575 | 9.8404 | 7.0725 | 10.9956 | 28.7396 | 9.7158 | 6.983 | 10.436 | 29.8317 | 9.2365 | 6.6385 | 8.2051 | 30.9944 | 8.7732 | 6.3055 | 5.3581 | 31.4952 | 8.6679 | 6.2298 | 3.6858 | 31.9515 | 8.6085 | 6.1871 | 1.9923 | 32.3024 | 8.3122 | 5.9742 | 0.56416 | 27.2105 | 10.8422 | 7.7925 | 16.6562 | 27.2521 | 10.8007 | 7.7627 | 16.2185 | 27.2999 | 10.7779 | 7.7463 | 16.0101 | 27.35 | 10.7253 | 7.7085 | 15.8938 | 27.4132 | 10.6022 | 7.62 | 15.7708 | 27.4861 | 10.5386 | 7.5743 | 15.6315 | 27.5843 | 10.347 | 7.4366 | 15.4517 | 27.7199 | 10.36 | 7.4459 | 15.2212 | 27.8536 | 10.3332 | 7.4266 | 14.9386 | 28.0034 | 10.3022 | 7.4044 | 14.643 | 28.5605 | 10.1299 | 7.2806 | 13.6761 | 29.2513 | 9.9407 | 7.1446 | 12.6093 | 29.9318 | 9.9231 | 7.132 | 11.5655 | 30.5875 | 9.9818 | 7.1741 | 10.4455 | 31.0635 | 9.8473 | 7.0775 | 9.6844 | 27.2222 | 10.8422 | 7.7925 | 16.6562 | 27.2815 | 10.5736 | 7.5995 | 14.7704 | 27.3617 | 10.3889 | 7.4667 | 13.9959 | 27.458 | 10.4236 | 7.4916 | 13.6671 | 27.5906 | 10.3025 | 7.4046 | 13.0707 | 27.7497 | 10.1523 | 7.2967 | 12.4631 | 27.9371 | 10.0112 | 7.1952 | 12.0195 | 28.1624 | 9.8861 | 7.1053 | 11.5634 | 28.3944 | 9.7495 | 7.0071 | 11.1221 | 28.6467 | 9.6243 | 6.9172 | 10.6507 | 29.7461 | 9.0711 | 6.5196 | 8.625 | 30.871 | 8.6668 | 6.229 | 5.8904 | 31.3663 | 8.5328 | 6.1327 | 4.3155 | 31.778 | 8.4376 | 6.0643 | 2.7954 | 32.0391 | 8.1159 | 5.8331 | 1.6273 | 27.2222 | 10.8422 | 7.7925 | 16.6562 | 27.2278 | 10.6733 | 7.6711 | 15.3806 | 27.2844 | 10.5411 | 7.5761 | 14.7501 | 27.3645 | 10.5796 | 7.6038 | 14.4436 | 27.489 | 10.48 | 7.5321 | 13.8502 | 27.6585 | 10.3298 | 7.4242 | 13.2217 | 27.9097 | 10.1335 | 7.2831 | 12.6477 | 28.3324 | 9.954 | 7.1542 | 11.7536 | 28.774 | 9.8214 | 7.0588 | 10.8688 | 29.2337 | 9.6492 | 6.9351 | 9.9539 | 30.3781 | 9.8367 | 7.0699 | 7.2361 | 31.0034 | 9.1547 | 6.5797 | 4.6398 | 31.4383 | 8.6601 | 6.2242 | 3.2328 | 31.7203 | 8.4112 | 6.0453 | 2.3265 | 31.6943 | 8.3639 | 6.0113 | 2.7187 | 27.2195 | 10.8422 | 7.7925 | 16.6562 | 27.2667 | 10.7427 | 7.721 | 15.7487 | 27.329 | 10.489 | 7.5387 | 15.1854 | 27.3949 | 10.6079 | 7.6241 | 14.87 | 27.4815 | 10.561 | 7.5904 | 14.3175 | 27.6026 | 10.4276 | 7.4945 | 13.7312 | 27.7621 | 10.3245 | 7.4204 | 13.2668 | 27.9565 | 10.1976 | 7.3292 | 12.7773 | 28.1744 | 10.074 | 7.2404 | 12.2546 | 28.416 | 9.9557 | 7.1554 | 11.7155 | 29.2361 | 9.5668 | 6.8759 | 9.9566 | 30.0079 | 9.3159 | 6.6955 | 8.144 | 30.5528 | 9.3992 | 6.7554 | 7.4002 | 31.0366 | 9.5974 | 6.8978 | 6.7878 | 31.3213 | 9.5209 | 6.8429 | 6.5156 | 27.2195 | 10.8422 | 7.7925 | 16.6562 | 27.2339 | 10.551 | 7.5832 | 14.6403 | 27.3057 | 10.3926 | 7.4693 | 13.8167 | 27.402 | 10.4084 | 7.4807 | 13.456 | 27.5352 | 10.2901 | 7.3957 | 12.818 | 27.6918 | 10.1365 | 7.2853 | 12.1695 | 27.9173 | 9.9387 | 7.1432 | 11.5754 | 28.3188 | 9.7643 | 7.0178 | 10.6491 | 28.7327 | 9.607 | 6.9047 | 9.7489 | 29.167 | 9.426 | 6.7746 | 8.8167 | 30.4881 | 9.584 | 6.8882 | 5.9851 | 31.1548 | 8.8768 | 6.3799 | 3.2175 | 31.6343 | 8.373 | 6.0178 | 1.638 | 31.939 | 8.0493 | 5.7852 | 0.56724 | 31.9294 | 7.9794 | 5.7349 | 0.81494
DUMPLINGTON | BARTON | CARRINGTON | 376770 | 397157 | 25.8262 | 4.2521 | 3.0561 | 18.5342 | 17.2252 | 2.836 | 2.0383 | 10.546 | 12.4638 | 2.0521 | 1.4749 | 7.4166 | 9.982 | 1.6435 | 1.1812 | 5.5981 | 6.9652 | 1.1468 | 0.82421 | 3.2571 | 5.7092 | 0.93998 | 0.67558 | 2.7299 | 4.3534 | 0.71676 | 0.51515 | 2.2171 | 3.5062 | 0.57727 | 0.4149 | 1.7045 | 2.3789 | 0.39166 | 0.28149 | 1.0378 | 1.4819 | 0.24399 | 0.17536 | 0.37424 | 2.6844 | 0.44197 | 0.31765 | -1.7381 | 2.6844 | 0.44197 | 0.31765 | -3.9946 | 2.6844 | 0.44197 | 0.31765 | -6.0502 | 2.6844 | 0.44197 | 0.31765 | -8.5172 | 2.6844 | 0.44197 | 0.31765 | -11.2405 | 25.8262 | 4.2521 | 3.0561 | 18.5342 | 23.5195 | 3.8723 | 2.7831 | 16.4007 | 21.5565 | 3.5491 | 2.5508 | 15.3683 | 20.1536 | 3.3181 | 2.3848 | 14.8222 | 18.541 | 3.0526 | 2.194 | 14.1515 | 17.361 | 2.8584 | 2.0544 | 14.037 | 15.3378 | 2.5252 | 1.8149 | 13.8915 | 14.7405 | 2.4269 | 1.7443 | 13.7291 | 14.1833 | 2.3352 | 1.6783 | 13.5123 | 14.0993 | 2.3213 | 1.6684 | 13.2943 | 13.2012 | 2.1735 | 1.5621 | 12.6641 | 12.2792 | 2.0217 | 1.453 | 12.0652 | 12.3879 | 2.0396 | 1.4659 | 11.5392 | 13.6012 | 2.2393 | 1.6094 | 10.9996 | 14.0789 | 2.318 | 1.666 | 10.5952 | 25.8262 | 4.2521 | 3.0561 | 18.5342 | 15.8629 | 2.6117 | 1.8771 | 9.3614 | 10.9749 | 1.8069 | 1.2987 | 5.9913 | 8.1993 | 1.3499 | 0.97023 | 4.1686 | 5.366 | 0.88347 | 0.63496 | 1.8282 | 3.8801 | 0.63883 | 0.45914 | 1.3037 | 2.4069 | 0.39627 | 0.28481 | 0.79457 | 1.4646 | 0.24113 | 0.17331 | 0.28836 | 0.51042 | 0.084037 | 0.060399 | -0.30273 | 2.6844 | 0.44197 | 0.31765 | -0.87882 | 2.6844 | 0.44197 | 0.31765 | -2.7339 | 2.6844 | 0.44197 | 0.31765 | -4.7337 | 2.6844 | 0.44197 | 0.31765 | -6.5168 | 2.6844 | 0.44197 | 0.31765 | -8.5821 | 2.6844 | 0.44197 | 0.31765 | -10.7649 | 25.8262 | 4.2521 | 3.0561 | 18.5342 | 18.3113 | 3.0148 | 2.1668 | 11.7469 | 14.7833 | 2.434 | 1.7493 | 8.8863 | 12.9917 | 2.139 | 1.5373 | 7.0904 | 10.3132 | 1.698 | 1.2204 | 4.7747 | 9.188 | 1.5127 | 1.0872 | 4.2614 | 8.2317 | 1.3553 | 0.97407 | 3.7233 | 6.579 | 1.0832 | 0.7785 | 3.0934 | 5.0581 | 0.83279 | 0.59854 | 2.3576 | 4.5099 | 0.74252 | 0.53367 | 1.6357 | 1.8137 | 0.29861 | 0.21461 | -0.45201 | 2.6844 | 0.44197 | 0.31765 | -2.4286 | 2.6844 | 0.44197 | 0.31765 | -4.1826 | 2.6844 | 0.44197 | 0.31765 | -6.066 | 2.6844 | 0.44197 | 0.31765 | -7.752 | 25.8262 | 4.2521 | 3.0561 | 18.5342 | 20.7829 | 3.4217 | 2.4593 | 13.9174 | 16.9287 | 2.7872 | 2.0032 | 11.4868 | 14.2806 | 2.3512 | 1.6899 | 9.6928 | 11.2424 | 1.851 | 1.3303 | 7.3873 | 10.1167 | 1.6656 | 1.1971 | 6.8831 | 8.7784 | 1.4453 | 1.0388 | 6.3758 | 7.9705 | 1.3123 | 0.94317 | 5.8693 | 6.7529 | 1.1118 | 0.79909 | 5.2098 | 5.9475 | 0.97921 | 0.70378 | 4.5485 | 2.9635 | 0.48791 | 0.35067 | 2.5746 | 0.070572 | 0.011619 | 0.0083509 | 0.070572 | 2.6844 | 0.44197 | 0.31765 | -1.1024 | 2.6844 | 0.44197 | 0.31765 | -3.2016 | 2.6844 | 0.44197 | 0.31765 | -5.4333 | 25.8262 | 4.2521 | 3.0561 | 18.5342 | 14.5611 | 2.3974 | 1.723 | 8.1806 | 10.2652 | 1.6901 | 1.2147 | 4.5678 | 8.4114 | 1.3849 | 0.99533 | 2.7358 | 5.6408 | 0.92871 | 0.66748 | 0.38787 | 4.4844 | 0.73832 | 0.53064 | -0.14296 | 3.4971 | 0.57576 | 0.41381 | -0.69558 | 1.8218 | 0.29995 | 0.21558 | -1.3511 | 0.3388 | 0.055781 | 0.040091 | -2.093 | 2.6844 | 0.44197 | 0.31765 | -2.8199 | 2.6844 | 0.44197 | 0.31765 | -4.9289 | 2.6844 | 0.44197 | 0.31765 | -6.9297 | 2.6844 | 0.44197 | 0.31765 | -8.7071 | 2.6844 | 0.44197 | 0.31765 | -10.5985 | 2.6844 | 0.44197 | 0.31765 | -12.2901
EASTLANDS | STUART ST | STALYBRIDGE | 386458 | 398693 | 30.2898 | 10.5158 | 7.6712 | 15.8806 | 30.3464 | 9.7287 | 7.097 | 11.7021 | 30.4207 | 9.4262 | 6.8763 | 10.1217 | 30.4944 | 9.2738 | 6.7651 | 9.1316 | 30.5684 | 9.0246 | 6.5833 | 8.1512 | 30.6497 | 8.7721 | 6.3991 | 7.1616 | 30.7387 | 8.5457 | 6.234 | 6.1807 | 30.8419 | 8.3491 | 6.0906 | 5.1944 | 30.9436 | 8.1366 | 5.9355 | 4.1387 | 31.0453 | 7.9238 | 5.7803 | 3.0875 | 31.3417 | 7.2597 | 5.2958 | -0.18934 | 31.6234 | 6.5893 | 4.8068 | -3.6249 | 31.8269 | 5.9971 | 4.3748 | -6.765 | 32.0249 | 5.3944 | 3.9351 | -10.7136 | 31.2175 | 5.0638 | 3.694 | -12.6862 | 30.2848 | 10.5158 | 7.6712 | 15.8806 | 30.3398 | 10.1435 | 7.3995 | 13.7576 | 30.409 | 9.909 | 7.2285 | 12.6177 | 30.4777 | 9.6941 | 7.0717 | 11.6498 | 30.5475 | 9.4684 | 6.9071 | 10.7001 | 30.6271 | 9.2216 | 6.727 | 9.7435 | 30.7156 | 8.9301 | 6.5143 | 8.7685 | 30.8166 | 8.6961 | 6.3437 | 7.7484 | 30.8971 | 8.4831 | 6.1883 | 6.6786 | 30.9803 | 8.2359 | 6.008 | 5.5997 | 31.2232 | 7.7222 | 5.6333 | 2.4217 | 31.4622 | 7.2213 | 5.2679 | -0.72694 | 31.6652 | 6.7251 | 4.9058 | -3.7439 | 31.8873 | 6.1506 | 4.4868 | -7.5982 | 32.1062 | 5.8523 | 4.2692 | -9.5311 | 30.2918 | 10.5158 | 7.6712 | 15.8806 | 30.3573 | 9.6089 | 7.0096 | 11.2164 | 30.441 | 9.2236 | 6.7285 | 8.9115 | 30.5272 | 8.938 | 6.5201 | 7.2959 | 30.6149 | 8.575 | 6.2553 | 5.6795 | 30.7118 | 8.2106 | 5.9895 | 4.0494 | 30.8194 | 7.8742 | 5.7441 | 2.437 | 30.9428 | 7.5571 | 5.5128 | 0.80645 | 31.0567 | 7.2286 | 5.2732 | -0.85711 | 31.1695 | 6.9029 | 5.0356 | -2.5404 | 31.511 | 5.8793 | 4.2888 | -7.7256 | 29.9403 | 4.8566 | 3.5428 | -13.0364 | 25.0274 | 4.0597 | 2.9615 | -17.3681 | 21.1697 | 3.4339 | 2.505 | -21.217 | 19.2563 | 3.1236 | 2.2786 | -22.9967 | 30.2918 | 10.5158 | 7.6712 | 15.8806 | 30.3219 | 9.822 | 7.165 | 12.2521 | 30.3857 | 9.5087 | 6.9365 | 10.1704 | 30.4503 | 9.2709 | 6.763 | 8.5786 | 30.5185 | 8.9273 | 6.5123 | 6.9772 | 30.6033 | 8.5913 | 6.2672 | 5.355 | 30.701 | 8.2587 | 6.0246 | 3.721 | 30.8105 | 7.8976 | 5.7612 | 1.9797 | 30.9185 | 7.5297 | 5.4928 | 0.20697 | 31.0271 | 7.1666 | 5.2279 | -1.5808 | 31.3496 | 6.2087 | 4.5292 | -6.8708 | 31.6551 | 5.2011 | 3.7942 | -12.0677 | 26.904 | 4.3641 | 3.1835 | -16.284 | 23.0849 | 3.7446 | 2.7316 | -19.9129 | 20.961 | 3.4001 | 2.4803 | -21.3927 | 30.2898 | 10.5158 | 7.6712 | 15.8806 | 30.3442 | 9.9822 | 7.2818 | 13.0028 | 30.4113 | 9.6892 | 7.0681 | 11.697 | 30.4737 | 9.5725 | 6.983 | 10.7285 | 30.5352 | 9.3523 | 6.8224 | 9.7855 | 30.6112 | 9.1017 | 6.6396 | 8.8297 | 30.6994 | 8.8806 | 6.4783 | 7.8733 | 30.7963 | 8.6906 | 6.3397 | 6.8996 | 30.892 | 8.479 | 6.1853 | 5.8411 | 30.9895 | 8.2657 | 6.0297 | 4.7804 | 31.2785 | 7.6376 | 5.5716 | 1.6183 | 31.5595 | 7.0437 | 5.1383 | -1.5195 | 31.7669 | 6.5137 | 4.7517 | -4.4019 | 31.9741 | 5.9887 | 4.3686 | -8.0736 | 32.1572 | 5.7309 | 4.1806 | -9.7618 | 30.2898 | 10.5158 | 7.6712 | 15.8806 | 30.3288 | 9.5229 | 6.9468 | 10.8487 | 30.4052 | 9.211 | 6.7193 | 8.4582 | 30.4847 | 8.9308 | 6.5149 | 6.8356 | 30.5659 | 8.579 | 6.2583 | 5.206 | 30.654 | 8.239 | 6.0102 | 3.5655 | 30.751 | 7.8976 | 5.7612 | 1.9032 | 30.8675 | 7.5282 | 5.4918 | 0.13096 | 30.9772 | 7.1546 | 5.2192 | -1.663 | 31.0865 | 6.7883 | 4.952 | -3.4742 | 31.4063 | 5.8128 | 4.2404 | -8.8451 | 29.5705 | 4.7966 | 3.4991 | -14.0887 | 24.3253 | 3.9458 | 2.8784 | -18.3509 | 20.4135 | 3.3113 | 2.4155 | -22.0386 | 18.1702 | 2.9474 | 2.1501 | -23.6074
EASTON | - | HARKER / HUTTON | 343201 | 571738 | 2.4996 | 2.4996 | 2.4996 | 0.41896 | 2.5096 | 2.5096 | 2.5096 | 0.33828 | 2.5261 | 2.5261 | 2.5261 | 0.3068 | 2.5454 | 2.5454 | 2.5454 | 0.28851 | 2.5682 | 2.5682 | 2.5682 | 0.25581 | 2.5949 | 2.5949 | 2.5949 | 0.21939 | 2.6254 | 2.6254 | 2.6254 | 0.187 | 2.6619 | 2.6619 | 2.6619 | 0.16004 | 2.6874 | 2.6874 | 2.6874 | 0.13499 | 2.7084 | 2.7084 | 2.7084 | 0.11649 | 2.7805 | 2.7805 | 2.7805 | -0.0034793 | 2.8491 | 2.8491 | 2.8491 | -0.21409 | 2.8891 | 2.8891 | 2.8891 | -0.3806 | 2.9142 | 2.9142 | 2.9142 | -0.50375 | 2.9284 | 2.9284 | 2.9284 | -0.64072 | 2.4976 | 2.4976 | 2.4976 | 0.41896 | 2.5112 | 2.5112 | 2.5112 | 0.36605 | 2.526 | 2.526 | 2.526 | 0.32562 | 2.5448 | 2.5448 | 2.5448 | 0.28616 | 2.5627 | 2.5627 | 2.5627 | 0.24074 | 2.5788 | 2.5788 | 2.5788 | 0.20048 | 2.5981 | 2.5981 | 2.5981 | 0.15192 | 2.6205 | 2.6205 | 2.6205 | 0.09519 | 2.6347 | 2.6347 | 2.6347 | 0.06427 | 2.6493 | 2.6493 | 2.6493 | 0.033184 | 2.6914 | 2.6914 | 2.6914 | -0.055338 | 2.7254 | 2.7254 | 2.7254 | -0.13175 | 2.7605 | 2.7605 | 2.7605 | -0.21749 | 2.8076 | 2.8076 | 2.8076 | -0.34803 | 2.8529 | 2.8529 | 2.8529 | -0.48283 | 2.5005 | 2.5005 | 2.5005 | 0.41896 | 2.5114 | 2.5114 | 2.5114 | 0.3302 | 2.5294 | 2.5294 | 2.5294 | 0.29971 | 2.5513 | 2.5513 | 2.5513 | 0.2868 | 2.5773 | 2.5773 | 2.5773 | 0.25965 | 2.6081 | 2.6081 | 2.6081 | 0.22991 | 2.6436 | 2.6436 | 2.6436 | 0.20689 | 2.6601 | 2.6601 | 2.6601 | 0.19045 | 2.6723 | 2.6723 | 2.6723 | 0.17925 | 2.6802 | 2.6802 | 2.6802 | 0.17189 | 2.7561 | 2.7561 | 2.7561 | 0.086756 | 2.8443 | 2.8443 | 2.8443 | -0.091582 | 2.8761 | 2.8761 | 2.8761 | -0.23021 | 2.8928 | 2.8928 | 2.8928 | -0.32217 | 2.8992 | 2.8992 | 2.8992 | -0.42533 | 2.5005 | 2.5005 | 2.5005 | 0.41896 | 2.5011 | 2.5011 | 2.5011 | 0.37546 | 2.5095 | 2.5095 | 2.5095 | 0.3541 | 2.5204 | 2.5204 | 2.5204 | 0.32739 | 2.5346 | 2.5346 | 2.5346 | 0.29834 | 2.5567 | 2.5567 | 2.5567 | 0.26723 | 2.5844 | 2.5844 | 2.5844 | 0.23251 | 2.6154 | 2.6154 | 2.6154 | 0.17559 | 2.6396 | 2.6396 | 2.6396 | 0.11194 | 2.663 | 2.663 | 2.663 | 0.047542 | 2.7335 | 2.7335 | 2.7335 | -0.13462 | 2.8054 | 2.8054 | 2.8054 | -0.3056 | 2.8505 | 2.8505 | 2.8505 | -0.41162 | 2.8596 | 2.8596 | 2.8596 | -0.42117 | 2.84 | 2.84 | 2.84 | -0.31385 | 2.4996 | 2.4996 | 2.4996 | 0.41896 | 2.5087 | 2.5087 | 2.5087 | 0.35079 | 2.522 | 2.522 | 2.522 | 0.32086 | 2.5362 | 2.5362 | 2.5362 | 0.30167 | 2.5529 | 2.5529 | 2.5529 | 0.27989 | 2.5762 | 2.5762 | 2.5762 | 0.26428 | 2.6058 | 2.6058 | 2.6058 | 0.25091 | 2.636 | 2.636 | 2.636 | 0.23774 | 2.6553 | 2.6553 | 2.6553 | 0.21828 | 2.6733 | 2.6733 | 2.6733 | 0.19978 | 2.7412 | 2.7412 | 2.7412 | 0.10944 | 2.8184 | 2.8184 | 2.8184 | -0.025923 | 2.8458 | 2.8458 | 2.8458 | -0.11146 | 2.8681 | 2.8681 | 2.8681 | -0.20349 | 2.8735 | 2.8735 | 2.8735 | -0.26577 | 2.4996 | 2.4996 | 2.4996 | 0.41896 | 2.5061 | 2.5061 | 2.5061 | 0.33394 | 2.5224 | 2.5224 | 2.5224 | 0.29514 | 2.5428 | 2.5428 | 2.5428 | 0.25464 | 2.5661 | 2.5661 | 2.5661 | 0.21192 | 2.593 | 2.593 | 2.593 | 0.16953 | 2.6239 | 2.6239 | 2.6239 | 0.12164 | 2.6621 | 2.6621 | 2.6621 | 0.047755 | 2.6885 | 2.6885 | 2.6885 | -0.025882 | 2.7135 | 2.7135 | 2.7135 | -0.10009 | 2.7839 | 2.7839 | 2.7839 | -0.31033 | 2.8463 | 2.8463 | 2.8463 | -0.50252 | 2.8839 | 2.8839 | 2.8839 | -0.62542 | 2.901 | 2.901 | 2.901 | -0.65137 | 2.8784 | 2.8784 | 2.8784 | -0.56127
EGREMONT | EGREMONT | HARKER / HUTTON | 301070 | 513074 | 19.7106 | 18.2991 | 13.1519 | 6.1454 | 19.9448 | 18.0953 | 13.0055 | 5.4222 | 20.197 | 17.8397 | 12.8218 | 5.0815 | 20.4573 | 17.5448 | 12.6098 | 4.8563 | 20.74 | 17.0436 | 12.2496 | 4.5179 | 21.0663 | 16.9337 | 12.1706 | 4.1808 | 21.4414 | 16.9357 | 12.172 | 3.9228 | 21.6464 | 16.8815 | 12.1331 | 3.7459 | 21.8066 | 16.7857 | 12.0642 | 3.5152 | 21.9605 | 16.6195 | 11.9448 | 3.3203 | 22.5085 | 16.1391 | 11.5995 | 1.6345 | 23.1459 | 15.5008 | 11.1408 | -1.5004 | 23.6214 | 15.0064 | 10.7854 | -4.0939 | 24.0361 | 15.3607 | 11.04 | -6.6261 | 24.2964 | 14.7876 | 10.6281 | -8.6332 | 19.6778 | 18.2991 | 13.1519 | 6.1454 | 19.8095 | 18.1973 | 13.0788 | 5.9579 | 19.914 | 18.1104 | 13.0163 | 5.7776 | 20.0522 | 17.8224 | 12.8093 | 5.5998 | 20.2396 | 17.5034 | 12.58 | 5.3811 | 20.462 | 17.1983 | 12.3607 | 5.1552 | 20.7052 | 17.7157 | 12.7326 | 4.8647 | 20.9851 | 17.5246 | 12.5952 | 4.4984 | 21.2314 | 17.4289 | 12.5265 | 4.2157 | 21.4996 | 17.2853 | 12.4233 | 3.9336 | 22.0996 | 16.3839 | 11.7754 | 3.098 | 22.4517 | 16.7826 | 12.062 | 2.3004 | 22.7423 | 16.6074 | 11.936 | 1.4581 | 23 | 16.7598 | 12.0456 | 0.62502 | 23.14 | 16.7602 | 12.0459 | 0.14797 | 19.7245 | 18.2991 | 13.1519 | 6.1454 | 19.9443 | 18.0666 | 12.9848 | 5.3517 | 20.2033 | 17.784 | 12.7817 | 5.0266 | 20.4707 | 17.3871 | 12.4965 | 4.853 | 20.7657 | 16.7211 | 12.0178 | 4.5693 | 21.105 | 16.903 | 12.1485 | 4.2965 | 21.4881 | 16.8733 | 12.1272 | 4.124 | 21.6682 | 16.7438 | 12.0341 | 4.0436 | 21.8215 | 16.55 | 11.8948 | 3.9286 | 21.9702 | 16.4233 | 11.8038 | 3.825 | 22.5286 | 15.9084 | 11.4337 | 2.3927 | 23.1931 | 15.2025 | 10.9263 | -0.62877 | 23.6871 | 14.5807 | 10.4795 | -3.4348 | 24.1055 | 14.8662 | 10.6847 | -5.9421 | 24.3399 | 14.2927 | 10.2724 | -7.702 | 19.7248 | 18.2991 | 13.1519 | 6.1454 | 19.8788 | 18.1286 | 13.0294 | 5.7547 | 20.0642 | 17.8224 | 12.8093 | 5.5353 | 20.2507 | 17.2154 | 12.373 | 5.3664 | 20.4671 | 17.2302 | 12.3837 | 5.1014 | 20.7771 | 17.1834 | 12.35 | 4.8198 | 21.1631 | 16.6186 | 11.9441 | 4.398 | 21.5363 | 16.0887 | 11.5633 | 3.3834 | 21.7601 | 15.5984 | 11.2109 | 2.3297 | 21.98 | 15.4367 | 11.0946 | 1.2964 | 22.626 | 15.7065 | 11.2886 | -1.6225 | 23.2415 | 15.0431 | 10.8117 | -4.3515 | 23.6833 | 14.4376 | 10.3766 | -6.4788 | 23.9692 | 13.9553 | 10.03 | -7.6012 | 23.8713 | 13.9878 | 10.0533 | -6.06 | 19.7104 | 18.2991 | 13.1519 | 6.1454 | 19.8946 | 18.187 | 13.0714 | 5.9532 | 20.072 | 17.9053 | 12.8689 | 5.7405 | 20.2821 | 17.6712 | 12.7006 | 5.5837 | 20.4778 | 17.1966 | 12.3596 | 5.4199 | 20.7428 | 17.1363 | 12.3162 | 5.2521 | 21.0795 | 17.149 | 12.3253 | 5.06 | 21.4619 | 17.0938 | 12.2856 | 4.8533 | 21.6131 | 16.9934 | 12.2135 | 4.5438 | 21.7677 | 16.8146 | 12.085 | 4.2322 | 22.2724 | 16.4424 | 11.8175 | 3.1481 | 22.7874 | 16.1268 | 11.5907 | 1.8138 | 23.1609 | 15.89 | 11.4204 | 0.70308 | 23.4683 | 16.4502 | 11.823 | -0.71004 | 23.5311 | 16.1264 | 11.5904 | -1.3305 | 19.7104 | 18.2991 | 13.1519 | 6.1454 | 19.8698 | 18.0691 | 12.9866 | 5.3922 | 20.1004 | 17.7451 | 12.7537 | 5.0256 | 20.3696 | 17.1304 | 12.312 | 4.7482 | 20.6319 | 17.086 | 12.28 | 4.3853 | 20.9295 | 17.0179 | 12.2311 | 4.041 | 21.2787 | 16.4509 | 11.8236 | 3.5487 | 21.6653 | 15.9058 | 11.4318 | 2.4267 | 21.8932 | 15.42 | 11.0826 | 1.2982 | 22.1182 | 15.2258 | 10.9431 | 0.1883 | 22.785 | 15.4454 | 11.1009 | -2.9773 | 23.4048 | 14.735 | 10.5903 | -5.9402 | 23.8593 | 14.0859 | 10.1238 | -8.3041 | 24.1553 | 13.5504 | 9.7389 | -9.7271 | 24.0852 | 13.5292 | 9.7237 | -8.5134
EMBLETON | STAINBURN & SIDDICK | HARKER / HUTTON | 315767 | 529389 | 29.2468 | 18.678 | 13.4242 | 16.1373 | 29.355 | 18.4855 | 13.2859 | 15.3205 | 29.4422 | 18.3486 | 13.1875 | 15.0406 | 29.5386 | 18.223 | 13.0973 | 14.8938 | 29.6593 | 18.0654 | 12.984 | 14.6936 | 29.8069 | 17.9046 | 12.8684 | 14.4781 | 29.9856 | 17.7496 | 12.757 | 14.2759 | 30.2116 | 17.6193 | 12.6633 | 14.0618 | 30.4159 | 17.4853 | 12.5671 | 13.8233 | 30.6218 | 17.3638 | 12.4797 | 13.607 | 31.2695 | 16.9063 | 12.1509 | 12.5509 | 31.8741 | 16.3939 | 11.7826 | 10.8138 | 32.2733 | 15.9339 | 11.452 | 9.2095 | 32.5622 | 16.2075 | 11.6487 | 7.6696 | 32.7216 | 15.474 | 11.1215 | 6.2905 | 29.2192 | 18.678 | 13.4242 | 16.1373 | 29.2861 | 18.5675 | 13.3448 | 15.6701 | 29.364 | 18.4599 | 13.2675 | 15.4022 | 29.4597 | 18.3332 | 13.1765 | 15.1637 | 29.5732 | 18.1785 | 13.0653 | 14.8684 | 29.6881 | 18.0123 | 12.9458 | 14.5274 | 29.8275 | 17.8306 | 12.8152 | 14.1088 | 29.9922 | 17.6489 | 12.6846 | 13.597 | 30.0919 | 17.5225 | 12.5938 | 13.3333 | 30.1984 | 17.3917 | 12.4998 | 13.0706 | 30.5617 | 17.0067 | 12.2231 | 12.2669 | 30.9581 | 16.6453 | 11.9633 | 11.4859 | 31.335 | 16.3315 | 11.7378 | 10.7968 | 31.7231 | 16.5656 | 11.9061 | 10.0886 | 31.9806 | 16.748 | 12.0371 | 9.6499 | 29.2602 | 18.678 | 13.4242 | 16.1373 | 29.3689 | 18.4349 | 13.2495 | 15.2234 | 29.4633 | 18.2201 | 13.0951 | 14.9408 | 29.5737 | 18.0275 | 12.9567 | 14.8285 | 29.7105 | 17.8261 | 12.812 | 14.6636 | 29.8761 | 17.6351 | 12.6747 | 14.4901 | 30.0755 | 17.4504 | 12.542 | 14.349 | 30.325 | 17.2825 | 12.4213 | 14.2024 | 30.5326 | 17.1114 | 12.2983 | 14.0551 | 30.7398 | 16.9482 | 12.181 | 13.9119 | 31.4189 | 16.339 | 11.7432 | 13.0562 | 32.0899 | 15.6498 | 11.2478 | 11.4892 | 32.5509 | 14.9866 | 10.7712 | 10.0247 | 32.8726 | 14.9892 | 10.773 | 8.6667 | 33.0169 | 14.0252 | 10.0802 | 7.5099 | 29.2602 | 18.678 | 13.4242 | 16.1373 | 29.2872 | 18.5213 | 13.3116 | 15.6768 | 29.342 | 18.3845 | 13.2133 | 15.5345 | 29.4015 | 18.2211 | 13.0959 | 15.4846 | 29.4863 | 18.0509 | 12.9735 | 15.3817 | 29.625 | 17.8872 | 12.8559 | 15.2446 | 29.8097 | 17.6716 | 12.7009 | 15.0593 | 30.0375 | 17.3996 | 12.5055 | 14.5474 | 30.2458 | 17.1471 | 12.3239 | 13.9157 | 30.4586 | 16.895 | 12.1427 | 13.2881 | 31.1197 | 16.987 | 12.2089 | 11.4641 | 31.742 | 16.1225 | 11.5876 | 9.7161 | 32.1442 | 15.3635 | 11.0421 | 8.4343 | 32.4074 | 14.3608 | 10.3214 | 7.7685 | 32.4383 | 13.4491 | 9.6661 | 8.4828 | 29.2468 | 18.678 | 13.4242 | 16.1373 | 29.339 | 18.5173 | 13.3087 | 15.4661 | 29.4131 | 18.3935 | 13.2197 | 15.2426 | 29.4742 | 18.2802 | 13.1383 | 15.1466 | 29.5532 | 18.1437 | 13.0402 | 15.0353 | 29.6784 | 18.0006 | 12.9374 | 14.892 | 29.8484 | 17.8531 | 12.8314 | 14.7185 | 30.0478 | 17.7242 | 12.7387 | 14.5052 | 30.225 | 17.5867 | 12.6399 | 14.2472 | 30.4093 | 17.4576 | 12.5471 | 13.992 | 31.0229 | 17.039 | 12.2463 | 13.0999 | 31.6387 | 16.6876 | 11.9937 | 12.1267 | 32.0367 | 16.4221 | 11.8029 | 11.4788 | 32.3276 | 16.8924 | 12.1409 | 10.9525 | 32.4305 | 16.4014 | 11.788 | 10.8698 | 29.2468 | 18.678 | 13.4242 | 16.1373 | 29.3073 | 18.4429 | 13.2553 | 15.2614 | 29.3951 | 18.2724 | 13.1327 | 14.9513 | 29.4911 | 18.0852 | 12.9982 | 14.7874 | 29.6094 | 17.8928 | 12.8599 | 14.5779 | 29.7503 | 17.713 | 12.7307 | 14.3651 | 29.9237 | 17.4804 | 12.5635 | 14.0965 | 30.1591 | 17.2047 | 12.3654 | 13.5793 | 30.3642 | 16.9568 | 12.1872 | 12.9809 | 30.5716 | 16.7146 | 12.0131 | 12.3064 | 31.2224 | 16.7521 | 12.0401 | 10.3225 | 31.8307 | 15.8613 | 11.3999 | 8.4209 | 32.2344 | 15.0486 | 10.8157 | 6.9919 | 32.477 | 14.1457 | 10.1668 | 6.1641 | 32.5062 | 13.1816 | 9.4739 | 6.7096
EXCHANGE ST | LOWER DARWEN | ROCHDALE | 369100 | 423028 | 23.5475 | 15.8664 | 11.5743 | 11.424 | 23.6118 | 15.4403 | 11.2635 | 8.9864 | 23.7178 | 15.2736 | 11.1419 | 8.5273 | 23.8618 | 15.174 | 11.0693 | 8.2951 | 24.0471 | 15.0727 | 10.9953 | 7.9633 | 24.2905 | 14.8787 | 10.8538 | 7.5935 | 24.6145 | 14.6791 | 10.7082 | 7.2075 | 25.0024 | 14.4014 | 10.5056 | 6.7874 | 25.3488 | 14.1788 | 10.3432 | 6.0836 | 25.735 | 14.0212 | 10.2283 | 5.3044 | 26.9955 | 13.2649 | 9.6765 | 2.1532 | 28.0824 | 12.5839 | 9.1798 | -1.1723 | 28.7585 | 12.1493 | 8.8627 | -3.6357 | 29.2059 | 11.7939 | 8.6035 | -5.8658 | 29.427 | 11.412 | 8.3249 | -7.4921 | 23.5228 | 15.8664 | 11.5743 | 11.424 | 23.5899 | 15.6868 | 11.4433 | 10.5591 | 23.6705 | 15.683 | 11.4405 | 10.4725 | 23.7673 | 15.6407 | 11.4097 | 10.3568 | 23.8979 | 15.5399 | 11.3361 | 10.1925 | 24.0672 | 15.3564 | 11.2023 | 10.0015 | 24.2795 | 15.1689 | 11.0655 | 9.7419 | 24.5271 | 15.0092 | 10.949 | 9.4018 | 24.6998 | 14.9276 | 10.8895 | 9.1606 | 24.9034 | 14.8433 | 10.828 | 8.8974 | 25.7016 | 14.4635 | 10.5509 | 7.9607 | 26.5483 | 14.1852 | 10.3479 | 6.402 | 27.4312 | 14.0927 | 10.2804 | 4.7962 | 28.3632 | 13.8852 | 10.129 | 3.0649 | 28.8797 | 13.5389 | 9.8765 | 1.9566 | 23.5552 | 15.8664 | 11.5743 | 11.424 | 23.6246 | 15.361 | 11.2056 | 8.6267 | 23.7394 | 15.0772 | 10.9986 | 8.0706 | 23.8918 | 15.0436 | 10.9741 | 7.8148 | 24.079 | 14.7968 | 10.7941 | 7.4646 | 24.3214 | 14.645 | 10.6833 | 7.0875 | 24.6349 | 14.2877 | 10.4227 | 6.7192 | 24.9432 | 14.1622 | 10.3311 | 6.2819 | 25.2363 | 13.9467 | 10.1739 | 5.6245 | 25.5711 | 13.7073 | 9.9993 | 4.9047 | 26.8107 | 12.7914 | 9.3311 | 1.7439 | 28.0525 | 11.9839 | 8.7421 | -1.8167 | 28.8636 | 11.4732 | 8.3696 | -4.4481 | 29.4144 | 11.021 | 8.0397 | -6.7081 | 29.6421 | 10.6801 | 7.791 | -8.1974 | 23.5552 | 15.8664 | 11.5743 | 11.424 | 23.548 | 15.5186 | 11.3206 | 9.5519 | 23.6065 | 15.3128 | 11.1705 | 9.1853 | 23.6987 | 15.313 | 11.1707 | 8.9608 | 23.8521 | 15.0905 | 11.0083 | 8.6193 | 24.0853 | 14.8595 | 10.8398 | 8.2295 | 24.4177 | 14.6857 | 10.713 | 7.648 | 24.8358 | 14.3883 | 10.4961 | 6.4485 | 25.2017 | 14.0385 | 10.2409 | 5.1777 | 25.6092 | 13.5919 | 9.9151 | 3.7976 | 26.8984 | 13.1184 | 9.5697 | -0.3293 | 27.9747 | 12.2589 | 8.9427 | -3.5402 | 28.6331 | 11.5642 | 8.4359 | -5.7719 | 29.0178 | 11.203 | 8.1724 | -7.1103 | 29.0685 | 11.0566 | 8.0656 | -6.4918 | 23.5475 | 15.8664 | 11.5743 | 11.424 | 23.6016 | 15.5796 | 11.3651 | 9.8357 | 23.6777 | 15.4569 | 11.2756 | 9.5502 | 23.771 | 15.343 | 11.1925 | 9.3736 | 23.9074 | 15.2928 | 11.1559 | 9.1593 | 24.1087 | 15.1091 | 11.0218 | 8.905 | 24.3919 | 14.9471 | 10.9037 | 8.5974 | 24.7429 | 14.6709 | 10.7022 | 8.2335 | 25.0503 | 14.4893 | 10.5698 | 7.6313 | 25.3622 | 14.3341 | 10.4565 | 6.943 | 26.4763 | 13.731 | 10.0166 | 4.5539 | 27.5498 | 13.3182 | 9.7155 | 2.6098 | 28.2217 | 13.1249 | 9.5744 | 1.3199 | 28.6258 | 12.8587 | 9.3802 | 0.44304 | 28.7453 | 12.9787 | 9.4678 | 0.19772 | 23.5475 | 15.8664 | 11.5743 | 11.424 | 23.5666 | 15.3384 | 11.1891 | 8.4757 | 23.6632 | 15.0742 | 10.9964 | 7.8679 | 23.7973 | 15.0768 | 10.9983 | 7.5759 | 23.9694 | 14.8463 | 10.8301 | 7.1759 | 24.1864 | 14.5575 | 10.6195 | 6.7524 | 24.4775 | 14.4072 | 10.5098 | 6.1355 | 24.8571 | 14.0955 | 10.2825 | 4.8924 | 25.1734 | 13.7426 | 10.0251 | 3.6248 | 25.5331 | 13.3239 | 9.7196 | 2.3284 | 26.796 | 12.8684 | 9.3873 | -1.5676 | 27.9999 | 11.976 | 8.7363 | -4.9497 | 28.808 | 11.251 | 8.2075 | -7.5197 | 29.2786 | 10.78 | 7.8639 | -9.1444 | 29.3587 | 10.5947 | 7.7287 | -8.7364
FAILSWORTH | CHADDERTON | WHITEGATE | 389631 | 401496 | 27.9496 | 9.9867 | 7.2851 | 14.9993 | 28.0187 | 9.7028 | 7.078 | 13.8683 | 28.1088 | 9.5277 | 6.9503 | 13.56 | 28.2228 | 9.3566 | 6.8255 | 13.4597 | 28.3692 | 9.172 | 6.6909 | 13.2575 | 28.5109 | 8.9532 | 6.5312 | 13.03 | 28.6191 | 8.7793 | 6.4044 | 12.8137 | 28.7519 | 8.67 | 6.3246 | 12.6132 | 28.8657 | 8.5617 | 6.2457 | 12.3814 | 28.9776 | 8.4647 | 6.1749 | 12.1775 | 29.3961 | 8.0041 | 5.8389 | 10.4618 | 29.8946 | 7.4023 | 5.3998 | 7.2728 | 30.2782 | 7.0156 | 5.1178 | 4.5372 | 30.6515 | 6.5997 | 4.8144 | 1.5777 | 30.9606 | 6.0736 | 4.4306 | -1.1185 | 27.9308 | 9.9867 | 7.2851 | 14.9993 | 27.9929 | 9.8696 | 7.1997 | 14.6871 | 28.0516 | 9.7455 | 7.1092 | 14.5199 | 28.1231 | 9.5998 | 7.0029 | 14.3907 | 28.2222 | 9.4435 | 6.8889 | 14.2191 | 28.3489 | 9.2889 | 6.7761 | 14.0219 | 28.503 | 9.0166 | 6.5775 | 13.759 | 28.6814 | 8.901 | 6.4932 | 13.411 | 28.7885 | 8.8027 | 6.4215 | 13.1347 | 28.9021 | 8.7046 | 6.3499 | 12.8532 | 29.2686 | 8.4044 | 6.1309 | 11.9919 | 29.5437 | 8.1505 | 5.9457 | 11.0823 | 29.7922 | 8.0445 | 5.8684 | 10.1919 | 30.0508 | 7.9743 | 5.8172 | 9.1814 | 30.2433 | 7.6846 | 5.6058 | 8.3996 | 27.9569 | 9.9867 | 7.2851 | 14.9993 | 28.0347 | 9.6599 | 7.0468 | 13.7159 | 28.1385 | 9.4311 | 6.8798 | 13.3881 | 28.2722 | 9.2218 | 6.7272 | 13.3144 | 28.4423 | 8.9922 | 6.5597 | 13.1385 | 28.5385 | 8.7787 | 6.404 | 12.9419 | 28.6537 | 8.5808 | 6.2596 | 12.7873 | 28.7931 | 8.4616 | 6.1726 | 12.6482 | 28.9061 | 8.3466 | 6.0887 | 12.4975 | 29.017 | 8.2368 | 6.0087 | 12.355 | 29.4461 | 7.6988 | 5.6162 | 10.8277 | 29.9663 | 7.0194 | 5.1205 | 7.7905 | 30.3661 | 6.539 | 4.7701 | 5.1963 | 30.74 | 6.187 | 4.5133 | 2.4203 | 31.0303 | 5.5788 | 4.0697 | -0.051168 | 27.9569 | 9.9867 | 7.2851 | 14.9993 | 27.9415 | 9.7851 | 7.1381 | 14.3502 | 27.984 | 9.7009 | 7.0767 | 14.1701 | 28.048 | 9.5636 | 6.9765 | 14.1223 | 28.1546 | 9.4042 | 6.8603 | 13.9482 | 28.3101 | 9.23 | 6.7331 | 13.7367 | 28.4216 | 9.0328 | 6.5893 | 13.3692 | 28.5895 | 8.773 | 6.3998 | 12.399 | 28.749 | 8.4941 | 6.1963 | 11.3942 | 28.9106 | 8.2238 | 5.9992 | 10.3931 | 29.4042 | 8.061 | 5.8804 | 7.4723 | 29.8865 | 7.2614 | 5.2971 | 4.5964 | 30.246 | 6.5538 | 4.7809 | 2.2183 | 30.5146 | 5.9509 | 4.3411 | 0.61428 | 30.5533 | 5.7846 | 4.2198 | 1.3062 | 27.9496 | 9.9867 | 7.2851 | 14.9993 | 28.0097 | 9.8366 | 7.1757 | 14.5739 | 28.0707 | 9.7064 | 7.0807 | 14.4373 | 28.1378 | 9.5536 | 6.9692 | 14.4035 | 28.2322 | 9.4027 | 6.8591 | 14.3395 | 28.3824 | 9.2131 | 6.7208 | 14.2407 | 28.522 | 9.048 | 6.6004 | 14.1064 | 28.6415 | 8.9485 | 6.5278 | 13.9435 | 28.742 | 8.8417 | 6.4499 | 13.7093 | 28.8447 | 8.7421 | 6.3773 | 13.4823 | 29.1917 | 8.4403 | 6.1571 | 12.6492 | 29.5568 | 8.239 | 6.0102 | 11.653 | 29.8235 | 8.2181 | 5.995 | 10.9316 | 30.0652 | 8.2694 | 6.0324 | 10.1904 | 30.2067 | 8.1519 | 5.9467 | 9.7305 | 27.9496 | 9.9867 | 7.2851 | 14.9993 | 27.9593 | 9.6759 | 7.0584 | 13.804 | 28.0415 | 9.5463 | 6.9639 | 13.4543 | 28.1543 | 9.3857 | 6.8467 | 13.3287 | 28.3016 | 9.2132 | 6.7209 | 13.0829 | 28.4309 | 9.0339 | 6.5901 | 12.8218 | 28.5474 | 8.8257 | 6.4382 | 12.3919 | 28.7346 | 8.5518 | 6.2384 | 11.341 | 28.8992 | 8.2665 | 6.0303 | 10.2833 | 29.0641 | 7.9669 | 5.8117 | 9.2279 | 29.5657 | 7.766 | 5.6652 | 6.1309 | 30.051 | 6.9353 | 5.0592 | 3.1042 | 30.4197 | 6.1944 | 4.5187 | 0.56311 | 30.6889 | 5.5532 | 4.051 | -1.2587 | 30.741 | 5.339 | 3.8947 | -0.8266
FALLOWFIELD | WEST DIDSBURY | SOUTH MANCHESTER | 385608 | 393881 | 31.3639 | 12.2677 | 8.9491 | 12.0579 | 31.4787 | 11.9598 | 8.7245 | 10.4486 | 31.6309 | 11.7729 | 8.5881 | 9.7314 | 31.8066 | 11.5991 | 8.4613 | 9.238 | 32.0102 | 11.4138 | 8.3262 | 8.6524 | 32.2377 | 11.1888 | 8.1621 | 8.0467 | 32.4876 | 10.9418 | 7.9819 | 7.4563 | 32.7135 | 10.7218 | 7.8214 | 6.8871 | 32.8758 | 10.4839 | 7.6478 | 6.3244 | 32.9928 | 10.2728 | 7.4939 | 5.9966 | 33.3652 | 9.7137 | 7.086 | 4.3724 | 33.7349 | 9.1376 | 6.6658 | 2.1306 | 33.9774 | 8.7173 | 6.3591 | 0.6574 | 34.178 | 8.3869 | 6.1181 | -0.52624 | 34.284 | 8.1195 | 5.9231 | -1.1167 | 31.3445 | 12.2677 | 8.9491 | 12.0579 | 31.447 | 12.1784 | 8.884 | 11.5855 | 31.5667 | 12.0509 | 8.791 | 11.2086 | 31.708 | 11.8382 | 8.6358 | 10.8321 | 31.8842 | 11.671 | 8.5138 | 10.383 | 32.0962 | 11.4091 | 8.3228 | 9.9182 | 32.3474 | 11.1191 | 8.1112 | 9.3654 | 32.636 | 11.0538 | 8.0636 | 8.7183 | 32.7667 | 10.9354 | 7.9772 | 8.2371 | 32.9125 | 10.778 | 7.8624 | 7.6814 | 33.2947 | 10.4041 | 7.5896 | 6.3978 | 33.5794 | 10.1021 | 7.3693 | 5.3833 | 33.7896 | 9.8048 | 7.1525 | 4.5258 | 33.9776 | 9.523 | 6.9469 | 3.7736 | 34.103 | 9.2807 | 6.7701 | 3.3243 | 31.3721 | 12.2677 | 8.9491 | 12.0579 | 31.5334 | 11.883 | 8.6685 | 10.0357 | 31.7423 | 11.598 | 8.4606 | 9.0361 | 31.986 | 11.349 | 8.279 | 8.2876 | 32.2641 | 11.1003 | 8.0975 | 7.4284 | 32.5652 | 10.7594 | 7.8489 | 6.5293 | 32.8364 | 10.5506 | 7.6965 | 6.0238 | 33.0481 | 10.3147 | 7.5244 | 5.5189 | 33.2108 | 10.0511 | 7.3321 | 4.9752 | 33.3704 | 9.6932 | 7.071 | 4.4188 | 33.8957 | 9.0451 | 6.5983 | 2.1365 | 34.3798 | 8.3989 | 6.1269 | -0.27684 | 34.6881 | 7.9491 | 5.7987 | -1.6047 | 34.939 | 7.5518 | 5.5089 | -2.3961 | 35.055 | 7.3402 | 5.3546 | -2.1973 | 31.3721 | 12.2677 | 8.9491 | 12.0579 | 31.4213 | 12.0319 | 8.7771 | 10.7849 | 31.5564 | 11.8351 | 8.6335 | 9.9792 | 31.7158 | 11.6077 | 8.4677 | 9.3028 | 31.9049 | 11.412 | 8.3249 | 8.4905 | 32.1533 | 11.1514 | 8.1348 | 7.6142 | 32.3827 | 10.9045 | 7.9547 | 7.0111 | 32.6444 | 10.6392 | 7.7611 | 6.0653 | 32.8526 | 10.3678 | 7.5632 | 5.1465 | 33.0259 | 10.0628 | 7.3407 | 4.2237 | 33.5237 | 9.1964 | 6.7087 | 1.6181 | 33.9659 | 8.5646 | 6.2477 | -0.36445 | 34.2353 | 8.2016 | 5.9829 | -1.2701 | 34.4359 | 7.9128 | 5.7722 | -1.3807 | 34.4972 | 7.8001 | 5.6901 | -0.52968 | 31.3639 | 12.2677 | 8.9491 | 12.0579 | 31.4695 | 12.1135 | 8.8367 | 11.3265 | 31.592 | 11.9733 | 8.7343 | 10.8274 | 31.7214 | 11.8179 | 8.621 | 10.4144 | 31.8756 | 11.6593 | 8.5053 | 9.9641 | 32.0825 | 11.47 | 8.3672 | 9.4852 | 32.3368 | 11.2384 | 8.1983 | 8.9774 | 32.6109 | 11.0316 | 8.0474 | 8.4422 | 32.7635 | 10.7913 | 7.8721 | 7.8682 | 32.8746 | 10.5753 | 7.7145 | 7.519 | 33.2182 | 10.1093 | 7.3746 | 6.3587 | 33.5477 | 9.7346 | 7.1013 | 5.2485 | 33.7702 | 9.4557 | 6.8978 | 4.5939 | 33.9708 | 9.3085 | 6.7904 | 4.0185 | 34.0845 | 9.1235 | 6.6555 | 3.7466 | 31.3639 | 12.2677 | 8.9491 | 12.0579 | 31.449 | 11.9104 | 8.6885 | 10.1159 | 31.6354 | 11.6677 | 8.5114 | 9.092 | 31.8574 | 11.4178 | 8.3291 | 8.3073 | 32.115 | 11.1989 | 8.1694 | 7.3968 | 32.3891 | 10.9253 | 7.9698 | 6.4572 | 32.6335 | 10.6609 | 7.777 | 5.7764 | 32.9076 | 10.3749 | 7.5684 | 4.7251 | 33.0791 | 10.0924 | 7.3623 | 3.7548 | 33.2479 | 9.7801 | 7.1345 | 2.7907 | 33.7557 | 8.8765 | 6.4753 | -0.012775 | 34.1878 | 8.2273 | 6.0017 | -2.1228 | 34.4553 | 7.8121 | 5.6988 | -3.1561 | 34.6556 | 7.4953 | 5.4677 | -3.4247 | 34.751 | 7.338 | 5.353 | -2.8096
FARNWORTH | KEARSLEY LOCAL | KEARSLEY | 373726 | 405532 | 29.6591 | 12.7443 | 9.1596 | 14.0881 | 29.7923 | 12.5623 | 9.0288 | 13.3771 | 29.9262 | 12.4681 | 8.961 | 13.1401 | 30.0963 | 12.3599 | 8.8833 | 12.936 | 30.3153 | 12.2208 | 8.7833 | 12.5964 | 30.5799 | 12.0575 | 8.666 | 12.2247 | 30.9006 | 11.8583 | 8.5228 | 11.8583 | 31.294 | 11.6535 | 8.3756 | 11.5117 | 31.6572 | 11.5821 | 8.3243 | 11.1019 | 31.9642 | 11.4798 | 8.2508 | 10.6855 | 32.8381 | 10.9214 | 7.8494 | 8.4954 | 33.6446 | 10.1917 | 7.325 | 5.3162 | 34.1897 | 9.6163 | 6.9114 | 2.922 | 34.611 | 9.1249 | 6.5583 | 0.78743 | 34.8603 | 8.7287 | 6.2735 | -0.74267 | 29.6395 | 12.7443 | 9.1596 | 14.0881 | 29.7447 | 12.6807 | 9.1138 | 13.7703 | 29.8326 | 12.6313 | 9.0784 | 13.6536 | 29.943 | 12.5519 | 9.0213 | 13.5102 | 30.0915 | 12.4541 | 8.951 | 13.3049 | 30.2776 | 12.3446 | 8.8723 | 13.0711 | 30.5043 | 12.2116 | 8.7767 | 12.7618 | 30.7704 | 12.084 | 8.685 | 12.3675 | 30.933 | 11.9732 | 8.6054 | 12.0915 | 31.1173 | 11.8471 | 8.5148 | 11.7931 | 31.8023 | 11.518 | 8.2782 | 10.7802 | 32.5537 | 11.1302 | 7.9995 | 9.5903 | 33.121 | 10.7988 | 7.7613 | 8.4498 | 33.6887 | 10.5192 | 7.5603 | 7.2501 | 34.0561 | 10.3292 | 7.4238 | 6.4115 | 29.6651 | 12.7443 | 9.1596 | 14.0881 | 29.8061 | 12.5038 | 8.9867 | 13.2252 | 29.958 | 12.3432 | 8.8713 | 12.8893 | 30.1503 | 12.2069 | 8.7733 | 12.6034 | 30.3925 | 12.013 | 8.634 | 12.1798 | 30.6792 | 11.7973 | 8.479 | 11.7239 | 31.0205 | 11.5956 | 8.334 | 11.2875 | 31.4359 | 11.4801 | 8.251 | 10.858 | 31.8054 | 11.3367 | 8.1479 | 10.4262 | 32.1239 | 11.1673 | 8.0262 | 9.9194 | 33.1229 | 10.4395 | 7.5031 | 7.4498 | 34.107 | 9.6363 | 6.9258 | 4.2966 | 34.7996 | 8.9808 | 6.4546 | 2.0631 | 35.3435 | 8.4225 | 6.0534 | 0.28783 | 35.6522 | 8.0765 | 5.8047 | -0.49955 | 29.6652 | 12.7443 | 9.1596 | 14.0881 | 29.7235 | 12.6066 | 9.0606 | 13.7064 | 29.8215 | 12.497 | 8.9818 | 13.4925 | 29.9551 | 12.3613 | 8.8843 | 13.2428 | 30.1489 | 12.1759 | 8.7511 | 12.8281 | 30.4235 | 11.992 | 8.6189 | 12.3589 | 30.7745 | 11.8135 | 8.4906 | 11.7417 | 31.2005 | 11.5214 | 8.2807 | 10.6257 | 31.6045 | 11.2122 | 8.0584 | 9.4777 | 31.975 | 10.8986 | 7.833 | 8.3472 | 32.9564 | 10.0601 | 7.2304 | 5.1732 | 33.8246 | 9.3179 | 6.697 | 2.5531 | 34.3979 | 8.7787 | 6.3094 | 0.97297 | 34.8199 | 8.5569 | 6.15 | 0.40886 | 35.0088 | 8.3524 | 6.003 | 0.90453 | 29.6589 | 12.7443 | 9.1596 | 14.0881 | 29.7692 | 12.6282 | 9.0762 | 13.6321 | 29.8645 | 12.552 | 9.0214 | 13.4839 | 29.9749 | 12.4582 | 8.954 | 13.3688 | 30.1228 | 12.3645 | 8.8866 | 13.2076 | 30.3359 | 12.2354 | 8.7938 | 13.0045 | 30.6151 | 12.0675 | 8.6731 | 12.7535 | 30.9393 | 11.8718 | 8.5325 | 12.4586 | 31.2322 | 11.7889 | 8.4729 | 12.1043 | 31.55 | 11.69 | 8.4018 | 11.6793 | 32.4257 | 11.2848 | 8.1106 | 10.202 | 33.2113 | 10.8688 | 7.8116 | 8.6729 | 33.7733 | 10.5318 | 7.5694 | 7.4278 | 34.2259 | 10.2338 | 7.3553 | 6.2599 | 34.4694 | 10.0196 | 7.2013 | 5.5971 | 29.6589 | 12.7443 | 9.1596 | 14.0881 | 29.7315 | 12.5388 | 9.0119 | 13.4277 | 29.8633 | 12.4073 | 8.9174 | 13.0876 | 30.0367 | 12.2445 | 8.8004 | 12.7466 | 30.2585 | 12.0423 | 8.655 | 12.2494 | 30.5179 | 11.8517 | 8.518 | 11.7271 | 30.8326 | 11.6496 | 8.3728 | 11.045 | 31.2422 | 11.335 | 8.1467 | 9.8435 | 31.617 | 11.0212 | 7.9211 | 8.6622 | 32.0145 | 10.6919 | 7.6845 | 7.4761 | 33.0028 | 9.8079 | 7.0491 | 4.079 | 33.9239 | 9.0151 | 6.4793 | 1.2243 | 34.5652 | 8.4305 | 6.0592 | -0.5863 | 35.0366 | 8.1631 | 5.867 | -1.3922 | 35.274 | 7.9385 | 5.7056 | -1.0985
FENISCOWLES | LOWER DARWEN | ROCHDALE | 364660 | 425120 | 18.5867 | 18.5867 | 18.5867 | 15.3003 | 18.596 | 18.596 | 18.596 | 14.9566 | 18.6078 | 18.6078 | 18.6078 | 14.8404 | 18.6219 | 18.6219 | 18.6219 | 14.78 | 18.6405 | 18.6405 | 18.6405 | 14.7069 | 18.6622 | 18.6622 | 18.6622 | 14.6345 | 18.6884 | 18.6884 | 18.6884 | 14.5675 | 18.721 | 18.721 | 18.721 | 14.502 | 18.7495 | 18.7495 | 18.7495 | 14.4194 | 18.7776 | 18.7776 | 18.7776 | 14.3402 | 18.8736 | 18.8736 | 18.8736 | 13.872 | 18.9802 | 18.9802 | 18.9802 | 13.0884 | 19.0587 | 19.0587 | 19.0587 | 12.4758 | 19.1306 | 19.1306 | 19.1306 | 11.8406 | 19.1825 | 19.1825 | 19.1825 | 11.3043 | 18.5852 | 18.5852 | 18.5852 | 15.3003 | 18.5939 | 18.5939 | 18.5939 | 15.2485 | 18.6025 | 18.6025 | 18.6025 | 15.2104 | 18.6133 | 18.6133 | 18.6133 | 15.1779 | 18.6295 | 18.6295 | 18.6295 | 15.1361 | 18.6504 | 18.6504 | 18.6504 | 15.0885 | 18.6767 | 18.6767 | 18.6767 | 15.0256 | 18.7077 | 18.7077 | 18.7077 | 14.9408 | 18.7255 | 18.7255 | 18.7255 | 14.8593 | 18.7445 | 18.7445 | 18.7445 | 14.7763 | 18.8042 | 18.8042 | 18.8042 | 14.5327 | 18.8657 | 18.8657 | 18.8657 | 14.2919 | 18.9218 | 18.9218 | 18.9218 | 14.0717 | 18.9783 | 18.9783 | 18.9783 | 13.8422 | 19.0157 | 19.0157 | 19.0157 | 13.6921 | 18.5873 | 18.5873 | 18.5873 | 15.3003 | 18.5974 | 18.5974 | 18.5974 | 14.9132 | 18.6102 | 18.6102 | 18.6102 | 14.7951 | 18.6258 | 18.6258 | 18.6258 | 14.7459 | 18.6461 | 18.6461 | 18.6461 | 14.6843 | 18.6697 | 18.6697 | 18.6697 | 14.6256 | 18.698 | 18.698 | 18.698 | 14.5771 | 18.733 | 18.733 | 18.733 | 14.5324 | 18.762 | 18.762 | 18.762 | 14.4745 | 18.7903 | 18.7903 | 18.7903 | 14.4155 | 18.8896 | 18.8896 | 18.8896 | 14.0069 | 19.0022 | 19.0022 | 19.0022 | 13.2742 | 19.0854 | 19.0854 | 19.0854 | 12.7057 | 19.1591 | 19.1591 | 19.1591 | 12.1227 | 19.2089 | 19.2089 | 19.2089 | 11.6449 | 18.5873 | 18.5873 | 18.5873 | 15.3003 | 18.5787 | 18.5787 | 18.5787 | 15.0645 | 18.5814 | 18.5814 | 18.5814 | 14.9801 | 18.5869 | 18.5869 | 18.5869 | 14.9324 | 18.5986 | 18.5986 | 18.5986 | 14.8655 | 18.6185 | 18.6185 | 18.6185 | 14.7939 | 18.6464 | 18.6464 | 18.6464 | 14.6886 | 18.6842 | 18.6842 | 18.6842 | 14.4557 | 18.7187 | 18.7187 | 18.7187 | 14.21 | 18.7536 | 18.7536 | 18.7536 | 13.9626 | 18.8595 | 18.8595 | 18.8595 | 13.2446 | 18.9646 | 18.9646 | 18.9646 | 12.5439 | 19.0399 | 19.0399 | 19.0399 | 12.0239 | 19.0956 | 19.0956 | 19.0956 | 11.705 | 19.1018 | 19.1018 | 19.1018 | 11.9268 | 18.5867 | 18.5867 | 18.5867 | 15.3003 | 18.5942 | 18.5942 | 18.5942 | 15.2069 | 18.6011 | 18.6011 | 18.6011 | 15.1437 | 18.6079 | 18.6079 | 18.6079 | 15.1003 | 18.6187 | 18.6187 | 18.6187 | 15.0544 | 18.6375 | 18.6375 | 18.6375 | 15.0014 | 18.6639 | 18.6639 | 18.6639 | 14.9449 | 18.6933 | 18.6933 | 18.6933 | 14.8887 | 18.7177 | 18.7177 | 18.7177 | 14.81 | 18.7428 | 18.7428 | 18.7428 | 14.7316 | 18.825 | 18.825 | 18.825 | 14.4723 | 18.9117 | 18.9117 | 18.9117 | 14.1749 | 18.9736 | 18.9736 | 18.9736 | 14.0092 | 19.0267 | 19.0267 | 19.0267 | 13.8859 | 19.0551 | 19.0551 | 19.0551 | 13.8237 | 18.5867 | 18.5867 | 18.5867 | 15.3003 | 18.5832 | 18.5832 | 18.5832 | 14.9037 | 18.5932 | 18.5932 | 18.5932 | 14.7738 | 18.6072 | 18.6072 | 18.6072 | 14.7034 | 18.6262 | 18.6262 | 18.6262 | 14.6165 | 18.6476 | 18.6476 | 18.6476 | 14.532 | 18.6753 | 18.6753 | 18.6753 | 14.4112 | 18.7171 | 18.7171 | 18.7171 | 14.1558 | 18.7539 | 18.7539 | 18.7539 | 13.8927 | 18.7903 | 18.7903 | 18.7903 | 13.6283 | 18.8993 | 18.8993 | 18.8993 | 12.8581 | 19.0036 | 19.0036 | 19.0036 | 12.11 | 19.0794 | 19.0794 | 19.0794 | 11.5441 | 19.1332 | 19.1332 | 19.1332 | 11.1695 | 19.1414 | 19.1414 | 19.1414 | 11.3301
FERODO | NEW MILLS | STALYBRIDGE | 405720 | 381338 | 28.3337 | 17.4865 | 12.5679 | 16.9136 | 28.3904 | 17.3546 | 12.4731 | 16.6719 | 28.4708 | 17.2512 | 12.3988 | 16.4479 | 28.5823 | 17.0263 | 12.2371 | 16.2993 | 28.7273 | 16.7197 | 12.0168 | 16.1373 | 28.9033 | 16.354 | 11.754 | 15.9708 | 29.2725 | 15.9319 | 11.4506 | 15.6619 | 29.501 | 15.5852 | 11.2014 | 15.5147 | 29.7049 | 15.3778 | 11.0524 | 15.2858 | 29.9215 | 15.0383 | 10.8083 | 15.0641 | 30.6182 | 14.3385 | 10.3054 | 14.0098 | 31.2527 | 14.4885 | 10.4132 | 12.4119 | 31.6668 | 14.2149 | 10.2166 | 11.114 | 31.9702 | 13.9308 | 10.0123 | 9.8034 | 32.167 | 13.7341 | 9.871 | 8.6501 | 28.3165 | 17.4865 | 12.5679 | 16.9136 | 28.3613 | 17.4203 | 12.5203 | 16.797 | 28.4078 | 17.3127 | 12.443 | 16.6306 | 28.4725 | 17.2725 | 12.4141 | 16.5221 | 28.5616 | 17.1978 | 12.3604 | 16.4394 | 28.6726 | 17.1085 | 12.2962 | 16.368 | 28.807 | 17.0945 | 12.2861 | 16.2696 | 28.9656 | 17.0286 | 12.2388 | 16.1108 | 29.0725 | 16.9494 | 12.1819 | 15.875 | 29.1917 | 16.8226 | 12.0908 | 15.6384 | 29.7528 | 16.5834 | 11.9188 | 14.7931 | 30.2504 | 16.3796 | 11.7724 | 14.0521 | 30.7023 | 16.1117 | 11.5798 | 13.3469 | 31.1822 | 15.4678 | 11.117 | 12.3062 | 31.5088 | 14.382 | 10.3366 | 11.5596 | 28.3413 | 17.4865 | 12.5679 | 16.9136 | 28.4037 | 17.3607 | 12.4774 | 16.644 | 28.4933 | 17.2138 | 12.3719 | 16.4147 | 28.6175 | 16.9482 | 12.181 | 16.2649 | 28.9423 | 16.5643 | 11.9051 | 15.9378 | 29.1259 | 16.2114 | 11.6514 | 15.7822 | 29.3277 | 15.7974 | 11.3539 | 15.6401 | 29.5463 | 15.1438 | 10.8842 | 15.5004 | 29.7425 | 14.7481 | 10.5998 | 15.3171 | 29.9512 | 14.741 | 10.5946 | 15.1455 | 33.7064 | 14.2622 | 10.2505 | 11.1687 | 34.5241 | 13.84 | 9.9471 | 9.601 | 35.0645 | 13.0267 | 9.3626 | 8.3596 | 35.3903 | 13.3459 | 9.592 | 7.2346 | 35.5348 | 13.0394 | 9.3717 | 6.3467 | 28.3413 | 17.4865 | 12.5679 | 16.9136 | 28.3557 | 17.3788 | 12.4905 | 16.7757 | 28.5848 | 17.2077 | 12.3675 | 16.4016 | 28.6504 | 16.8029 | 12.0766 | 16.2691 | 28.7559 | 16.277 | 11.6986 | 16.1309 | 32.5157 | 14.4065 | 10.3542 | 12.3558 | 32.5663 | 14.451 | 10.3863 | 12.3008 | 32.6379 | 14.2927 | 10.2724 | 11.9992 | 32.7486 | 14.0084 | 10.0681 | 11.5775 | 32.8774 | 14.1607 | 10.1776 | 11.1639 | 33.5982 | 13.9801 | 10.0478 | 9.6252 | 34.3459 | 13.5202 | 9.7172 | 7.9876 | 34.8123 | 13.1193 | 9.4291 | 6.8347 | 35.0885 | 12.8153 | 9.2106 | 6.1963 | 35.1843 | 12.7493 | 9.1632 | 6.6657 | 28.3337 | 17.4865 | 12.5679 | 16.9136 | 28.3819 | 17.3688 | 12.4833 | 16.7498 | 28.4391 | 17.2687 | 12.4114 | 16.549 | 28.5135 | 17.0487 | 12.2533 | 16.4201 | 28.616 | 16.7087 | 12.0089 | 16.3139 | 28.7687 | 16.4147 | 11.7976 | 16.2069 | 29.1255 | 15.9942 | 11.4953 | 15.9338 | 29.3559 | 15.6154 | 11.2231 | 15.7934 | 29.5287 | 15.4022 | 11.0698 | 15.5435 | 29.7157 | 15.0619 | 10.8253 | 15.2896 | 30.3627 | 14.6507 | 10.5298 | 14.443 | 31.0101 | 14.8193 | 10.6509 | 13.5135 | 31.4594 | 14.4114 | 10.3577 | 12.8928 | 31.7905 | 14.6192 | 10.5071 | 12.3634 | 31.9524 | 14.4841 | 10.41 | 12.1572 | 28.3337 | 17.4865 | 12.5679 | 16.9136 | 28.3681 | 17.3664 | 12.4816 | 16.6814 | 28.6264 | 17.1876 | 12.3531 | 16.2671 | 28.7259 | 16.7866 | 12.0649 | 16.1066 | 28.8567 | 16.2625 | 11.6882 | 15.9448 | 32.6082 | 14.2196 | 10.2199 | 12.161 | 32.6353 | 14.462 | 10.3941 | 12.1159 | 32.6985 | 14.2358 | 10.2316 | 11.8185 | 32.7932 | 14.0291 | 10.083 | 11.3936 | 32.9055 | 14.0741 | 10.1153 | 10.9771 | 33.6114 | 13.9255 | 10.0086 | 9.4383 | 34.3815 | 13.4569 | 9.6717 | 7.7754 | 34.8849 | 13.0374 | 9.3702 | 6.5527 | 35.195 | 12.7146 | 9.1382 | 5.8295 | 35.3062 | 12.6379 | 9.0831 | 6.2024
FLAT LANE | PADIHAM | PADIHAM | 383248 | 456995 | 10.9663 | 10.9663 | 10.9663 | 5.9374 | 10.9989 | 10.9989 | 10.9989 | 5.2533 | 11.0481 | 11.0481 | 11.0481 | 5.0882 | 11.1114 | 11.1114 | 11.1114 | 5.0299 | 11.1882 | 11.1882 | 11.1882 | 4.9319 | 11.2557 | 11.2557 | 11.2557 | 4.83 | 11.3248 | 11.3248 | 11.3248 | 4.7492 | 11.4042 | 11.4042 | 11.4042 | 4.6737 | 11.4588 | 11.4588 | 11.4588 | 4.5872 | 11.5095 | 11.5095 | 11.5095 | 4.513 | 11.6882 | 11.6882 | 11.6882 | 4.0025 | 11.9016 | 11.9016 | 11.9016 | 3.0991 | 12.0637 | 12.0637 | 12.0637 | 2.3541 | 12.2151 | 12.2151 | 12.2151 | 1.6116 | 12.3376 | 12.3376 | 12.3376 | 0.94678 | 10.9558 | 10.9558 | 10.9558 | 5.9374 | 10.9892 | 10.9892 | 10.9892 | 5.7276 | 11.0289 | 11.0289 | 11.0289 | 5.6267 | 11.0786 | 11.0786 | 11.0786 | 5.5371 | 11.1423 | 11.1423 | 11.1423 | 5.4283 | 11.221 | 11.221 | 11.221 | 5.312 | 11.3143 | 11.3143 | 11.3143 | 5.1682 | 11.4218 | 11.4218 | 11.4218 | 4.9884 | 11.4682 | 11.4682 | 11.4682 | 4.8828 | 11.5159 | 11.5159 | 11.5159 | 4.763 | 11.6607 | 11.6607 | 11.6607 | 4.4145 | 11.7939 | 11.7939 | 11.7939 | 4.1034 | 11.906 | 11.906 | 11.906 | 3.8455 | 12.0132 | 12.0132 | 12.0132 | 3.5894 | 12.0896 | 12.0896 | 12.0896 | 3.3575 | 10.9707 | 10.9707 | 10.9707 | 5.9374 | 11.007 | 11.007 | 11.007 | 5.1567 | 11.0624 | 11.0624 | 11.0624 | 4.9817 | 11.1303 | 11.1303 | 11.1303 | 4.9375 | 11.1898 | 11.1898 | 11.1898 | 4.8564 | 11.2537 | 11.2537 | 11.2537 | 4.7745 | 11.3222 | 11.3222 | 11.3222 | 4.7197 | 11.4003 | 11.4003 | 11.4003 | 4.6731 | 11.4544 | 11.4544 | 11.4544 | 4.6216 | 11.5042 | 11.5042 | 11.5042 | 4.5762 | 11.68 | 11.68 | 11.68 | 4.1568 | 11.8888 | 11.8888 | 11.8888 | 3.3397 | 12.0463 | 12.0463 | 12.0463 | 2.6713 | 12.1916 | 12.1916 | 12.1916 | 2.0177 | 12.3066 | 12.3066 | 12.3066 | 1.4522 | 10.9707 | 10.9707 | 10.9707 | 5.9374 | 10.9744 | 10.9744 | 10.9744 | 5.4516 | 10.9999 | 10.9999 | 10.9999 | 5.3424 | 11.0192 | 11.0192 | 11.0192 | 5.3048 | 11.0489 | 11.0489 | 11.0489 | 5.2326 | 11.0922 | 11.0922 | 11.0922 | 5.1554 | 11.1469 | 11.1469 | 11.1469 | 5.0483 | 11.2206 | 11.2206 | 11.2206 | 4.7792 | 11.2888 | 11.2888 | 11.2888 | 4.4929 | 11.3549 | 11.3549 | 11.3549 | 4.2093 | 11.552 | 11.552 | 11.552 | 3.3992 | 11.7532 | 11.7532 | 11.7532 | 2.62 | 11.9033 | 11.9033 | 11.9033 | 2.0155 | 12.0149 | 12.0149 | 12.0149 | 1.67 | 12.0311 | 12.0311 | 12.0311 | 1.967 | 10.9663 | 10.9663 | 10.9663 | 5.9374 | 10.9943 | 10.9943 | 10.9943 | 5.6224 | 11.03 | 11.03 | 11.03 | 5.5294 | 11.0718 | 11.0718 | 11.0718 | 5.4875 | 11.1247 | 11.1247 | 11.1247 | 5.4383 | 11.1991 | 11.1991 | 11.1991 | 5.3856 | 11.2705 | 11.2705 | 11.2705 | 5.3261 | 11.3465 | 11.3465 | 11.3465 | 5.257 | 11.3969 | 11.3969 | 11.3969 | 5.1648 | 11.4462 | 11.4462 | 11.4462 | 5.0758 | 11.6029 | 11.6029 | 11.6029 | 4.7687 | 11.7682 | 11.7682 | 11.7682 | 4.4091 | 11.8864 | 11.8864 | 11.8864 | 4.1688 | 11.9931 | 11.9931 | 11.9931 | 3.9353 | 12.0453 | 12.0453 | 12.0453 | 3.8301 | 10.9663 | 10.9663 | 10.9663 | 5.9374 | 10.9857 | 10.9857 | 10.9857 | 5.1152 | 11.0333 | 11.0333 | 11.0333 | 4.919 | 11.0969 | 11.0969 | 11.0969 | 4.8427 | 11.1651 | 11.1651 | 11.1651 | 4.7336 | 11.2295 | 11.2295 | 11.2295 | 4.6281 | 11.3043 | 11.3043 | 11.3043 | 4.4876 | 11.4093 | 11.4093 | 11.4093 | 4.1736 | 11.4899 | 11.4899 | 11.4899 | 3.8592 | 11.567 | 11.567 | 11.567 | 3.5478 | 11.7867 | 11.7867 | 11.7867 | 2.6568 | 11.9926 | 11.9926 | 11.9926 | 1.812 | 12.1451 | 12.1451 | 12.1451 | 1.1473 | 12.2544 | 12.2544 | 12.2544 | 0.72994 | 12.2768 | 12.2768 | 12.2768 | 0.94665
FREDERICK RD | FREDERICK RD | KEARSLEY | 381697 | 399348 | 32.246 | 9.4813 | 6.9165 | 13.4974 | 32.347 | 9.0026 | 6.5673 | 11.2717 | 32.4921 | 8.7349 | 6.372 | 10.2827 | 32.6431 | 8.5243 | 6.2184 | 9.6661 | 32.8135 | 8.2704 | 6.0331 | 8.8074 | 33.0151 | 7.9744 | 5.8172 | 7.9232 | 33.2581 | 7.7026 | 5.619 | 6.9096 | 33.555 | 7.4596 | 5.4417 | 5.8909 | 33.8592 | 7.2106 | 5.2601 | 4.8065 | 34.1775 | 7.0459 | 5.1399 | 4.2097 | 35.1712 | 6.4785 | 4.726 | 1.9411 | 36.0317 | 5.8604 | 4.2751 | -0.90517 | 32.7658 | 5.3149 | 3.8772 | -3.017 | 30.4294 | 4.9359 | 3.6007 | -4.9861 | 28.2204 | 4.5776 | 3.3393 | -6.7103 | 32.2344 | 9.4813 | 6.9165 | 13.4974 | 32.3285 | 9.3376 | 6.8116 | 12.9089 | 32.4502 | 9.2047 | 6.7147 | 12.5447 | 32.5699 | 9.0591 | 6.6085 | 12.2521 | 32.7022 | 8.9182 | 6.5057 | 11.9259 | 32.8507 | 8.7756 | 6.4017 | 11.5975 | 33.0153 | 8.466 | 6.1758 | 11.1916 | 33.2067 | 8.3186 | 6.0683 | 10.651 | 33.3854 | 8.1787 | 5.9662 | 10.1339 | 33.5785 | 8.0339 | 5.8606 | 9.6038 | 34.2201 | 7.6329 | 5.5681 | 7.9776 | 34.9161 | 7.2968 | 5.3229 | 6.2697 | 35.5961 | 6.9709 | 5.0852 | 4.677 | 36.3331 | 6.6361 | 4.8409 | 2.9213 | 36.8929 | 6.3203 | 4.6106 | 1.6173 | 32.251 | 9.4813 | 6.9165 | 13.4974 | 32.3687 | 8.914 | 6.5027 | 10.918 | 32.534 | 8.5968 | 6.2712 | 9.8019 | 32.7094 | 8.3561 | 6.0956 | 9.1326 | 32.9057 | 8.0533 | 5.8747 | 8.213 | 33.1336 | 7.7492 | 5.6529 | 7.2611 | 33.4034 | 7.4587 | 5.441 | 6.2027 | 33.7265 | 7.1791 | 5.2371 | 5.1262 | 34.0326 | 6.8966 | 5.031 | 4.0167 | 34.3537 | 6.7032 | 4.8899 | 3.3629 | 35.3859 | 6.0264 | 4.3962 | 0.84875 | 32.6558 | 5.2971 | 3.8642 | -2.199 | 29.2547 | 4.7454 | 3.4617 | -4.2695 | 26.996 | 4.379 | 3.1944 | -6.07 | 24.8033 | 4.0233 | 2.935 | -7.399 | 32.251 | 9.4813 | 6.9165 | 13.4974 | 32.2936 | 9.0909 | 6.6317 | 11.7784 | 32.4118 | 8.8552 | 6.4598 | 10.8694 | 32.5366 | 8.6398 | 6.3026 | 10.2446 | 32.6893 | 8.3447 | 6.0873 | 9.3357 | 32.8981 | 8.0487 | 5.8714 | 8.3811 | 33.1619 | 7.7075 | 5.6225 | 7.2148 | 33.4778 | 7.3249 | 5.3434 | 5.7298 | 33.7998 | 6.9387 | 5.0617 | 4.2134 | 34.1386 | 6.5589 | 4.7846 | 3.1761 | 35.1911 | 6.004 | 4.3798 | 0.18553 | 32.9385 | 5.343 | 3.8976 | -2.4931 | 29.999 | 4.8661 | 3.5498 | -4.1834 | 28.2956 | 4.5898 | 3.3482 | -5.2918 | 26.6923 | 4.3298 | 3.1585 | -5.6846 | 32.246 | 9.4813 | 6.9165 | 13.4974 | 32.3399 | 9.2575 | 6.7532 | 12.5798 | 32.4644 | 9.0411 | 6.5954 | 11.8907 | 32.5814 | 8.8505 | 6.4563 | 11.3482 | 32.7123 | 8.6307 | 6.296 | 10.608 | 32.8885 | 8.3575 | 6.0967 | 9.8418 | 33.1127 | 8.0932 | 5.9039 | 8.9235 | 33.3701 | 7.8652 | 5.7376 | 7.975 | 33.6315 | 7.6188 | 5.5578 | 6.9127 | 33.9105 | 7.4568 | 5.4396 | 6.3174 | 34.8347 | 6.9561 | 5.0743 | 4.409 | 35.7252 | 6.5125 | 4.7508 | 2.464 | 36.2635 | 6.0657 | 4.4249 | 1.1256 | 36.4437 | 5.9115 | 4.3124 | -0.13157 | 35.0723 | 5.6891 | 4.1501 | -1.1436 | 32.246 | 9.4813 | 6.9165 | 13.4974 | 32.3103 | 8.8925 | 6.487 | 10.7951 | 32.4598 | 8.5932 | 6.2687 | 9.6224 | 32.6203 | 8.3602 | 6.0986 | 8.9307 | 32.8009 | 8.0521 | 5.8739 | 7.9705 | 33.0082 | 7.7563 | 5.6581 | 6.9764 | 33.2558 | 7.4079 | 5.404 | 5.7591 | 33.5686 | 7.016 | 5.118 | 4.2121 | 33.8724 | 6.625 | 4.8329 | 2.6601 | 34.1922 | 6.2448 | 4.5555 | 1.5842 | 34.726 | 5.6329 | 4.1091 | -1.5742 | 30.4052 | 4.932 | 3.5978 | -4.4301 | 27.2155 | 4.4146 | 3.2204 | -6.296 | 25.2853 | 4.1015 | 2.992 | -7.585 | 23.4232 | 3.7995 | 2.7717 | -8.1787
FUSEHILL | CARLISLE | HARKER / HUTTON | 341042 | 555452 | 34.9871 | 10.0212 | 7.2024 | 11.2239 | 35.0226 | 9.8032 | 7.0457 | 10.8934 | 35.1299 | 9.5326 | 6.8513 | 10.7307 | 35.2083 | 9.2904 | 6.6772 | 10.6593 | 35.2748 | 8.95 | 6.4326 | 10.5353 | 35.3557 | 8.7636 | 6.2985 | 10.3966 | 35.455 | 8.5668 | 6.1571 | 10.2886 | 35.5791 | 8.4673 | 6.0856 | 10.2133 | 35.7155 | 8.3693 | 6.0152 | 10.0792 | 35.8485 | 8.2675 | 5.942 | 9.9679 | 36.2577 | 7.7788 | 5.5908 | 8.8195 | 36.643 | 7.2986 | 5.2456 | 6.5835 | 36.877 | 6.9767 | 5.0143 | 4.7723 | 36.9992 | 6.6268 | 4.7628 | 2.9711 | 36.9511 | 6.1203 | 4.3988 | 1.5116 | 34.9797 | 10.0212 | 7.2024 | 11.2239 | 35.0357 | 9.8987 | 7.1144 | 11.0434 | 35.1412 | 9.6636 | 6.9454 | 10.8754 | 35.218 | 9.4338 | 6.7803 | 10.7602 | 35.2578 | 9.185 | 6.6015 | 10.644 | 35.2933 | 8.9543 | 6.4356 | 10.5279 | 35.3452 | 8.7038 | 6.2556 | 10.3573 | 35.418 | 8.5778 | 6.165 | 10.1166 | 35.5307 | 8.4635 | 6.0829 | 9.9149 | 35.6456 | 8.3442 | 5.9971 | 9.7162 | 36.0009 | 7.9683 | 5.727 | 9.1486 | 36.36 | 7.7417 | 5.5641 | 8.5955 | 36.6756 | 7.5497 | 5.4261 | 8.1291 | 36.9735 | 7.3851 | 5.3078 | 7.6826 | 37.1215 | 7.3058 | 5.2508 | 7.4735 | 34.9902 | 10.0212 | 7.2024 | 11.2239 | 35.0282 | 9.7644 | 7.0179 | 10.8727 | 35.1398 | 9.4405 | 6.785 | 10.7181 | 35.2263 | 9.1238 | 6.5575 | 10.6795 | 35.3005 | 8.8478 | 6.3591 | 10.5804 | 35.3895 | 8.5972 | 6.179 | 10.4687 | 35.4988 | 8.3573 | 6.0065 | 10.405 | 35.6342 | 8.2198 | 5.9078 | 10.3716 | 35.7502 | 8.0773 | 5.8053 | 10.3363 | 35.8593 | 7.9313 | 5.7004 | 10.2942 | 36.2192 | 7.4284 | 5.3389 | 9.3 | 36.5742 | 6.854 | 4.9261 | 7.2314 | 36.7677 | 6.3558 | 4.568 | 5.5901 | 35.7094 | 5.8793 | 4.2255 | 4.0237 | 32.8305 | 5.4053 | 3.8849 | 2.8636 | 34.9902 | 10.0212 | 7.2024 | 11.2239 | 34.9543 | 9.846 | 7.0765 | 11.1972 | 35.0196 | 9.6285 | 6.9202 | 11.1249 | 35.0561 | 9.5505 | 6.8642 | 11.1176 | 35.0836 | 9.3487 | 6.7191 | 11.0382 | 35.1415 | 9.0321 | 6.4916 | 10.9367 | 35.2293 | 8.9405 | 6.4257 | 10.7265 | 35.3478 | 8.6377 | 6.2081 | 10.051 | 35.4789 | 8.2451 | 5.9259 | 9.3415 | 35.6049 | 8.0626 | 5.7947 | 8.6226 | 35.9671 | 7.4044 | 5.3217 | 6.5807 | 36.279 | 6.7272 | 4.835 | 4.6428 | 36.4294 | 6.0972 | 4.3822 | 3.1693 | 33.8673 | 5.576 | 4.0076 | 2.4726 | 32.768 | 5.395 | 3.8775 | 3.7183 | 34.9871 | 10.0212 | 7.2024 | 11.2239 | 35.0143 | 9.8604 | 7.0868 | 11.0104 | 35.1043 | 9.6004 | 6.9 | 10.8842 | 35.1554 | 9.365 | 6.7308 | 10.8569 | 35.1898 | 9.0196 | 6.4825 | 10.8432 | 35.251 | 8.8803 | 6.3824 | 10.8263 | 35.3396 | 8.7008 | 6.2534 | 10.8008 | 35.4413 | 8.6082 | 6.1869 | 10.7526 | 35.5559 | 8.5069 | 6.1141 | 10.6015 | 35.6724 | 8.3987 | 6.0363 | 10.4535 | 36.0391 | 8.0214 | 5.7652 | 9.9441 | 36.3865 | 7.8402 | 5.6349 | 9.3759 | 36.5991 | 7.7952 | 5.6026 | 9.0586 | 36.7044 | 7.7536 | 5.5727 | 8.8448 | 36.6093 | 7.4926 | 5.3851 | 9.0276 | 34.9871 | 10.0212 | 7.2024 | 11.2239 | 34.9749 | 9.7836 | 7.0317 | 11.0296 | 35.0739 | 9.566 | 6.8753 | 10.8797 | 35.1497 | 9.4518 | 6.7932 | 10.8097 | 35.2128 | 9.2426 | 6.6428 | 10.6708 | 35.2865 | 8.9145 | 6.407 | 10.5255 | 35.3823 | 8.8147 | 6.3353 | 10.2613 | 35.5238 | 8.5027 | 6.1111 | 9.5185 | 35.6528 | 8.1217 | 5.8372 | 8.7726 | 35.7768 | 7.9093 | 5.6846 | 8.0155 | 36.1404 | 7.2288 | 5.1955 | 5.8587 | 36.4511 | 6.53 | 4.6932 | 3.8299 | 35.6933 | 5.8766 | 4.2236 | 2.2442 | 32.3635 | 5.3284 | 3.8296 | 1.388 | 31.0927 | 5.1192 | 3.6792 | 2.4366
GALE | BELFIELD | ROCHDALE | 389570 | 414943 | 29.0285 | 13.1663 | 9.6046 | 18.2367 | 29.0895 | 13.1212 | 9.5717 | 18.1444 | 29.1618 | 13.0099 | 9.4905 | 18.0268 | 29.2603 | 12.8713 | 9.3894 | 17.9237 | 29.4211 | 12.6548 | 9.2315 | 17.7623 | 29.5454 | 12.3555 | 9.0132 | 17.5963 | 29.634 | 12.2644 | 8.9467 | 17.4596 | 29.7183 | 12.1671 | 8.8757 | 17.3433 | 29.7792 | 12.0958 | 8.8237 | 17.1866 | 29.8358 | 12.0597 | 8.7973 | 17.0489 | 30.0573 | 11.7187 | 8.5486 | 15.7076 | 30.3508 | 11.2345 | 8.1954 | 13.1066 | 30.585 | 10.8853 | 7.9406 | 10.8777 | 30.8221 | 10.503 | 7.6618 | 8.452 | 31.0091 | 10.0558 | 7.3356 | 6.3499 | 29.0184 | 13.1663 | 9.6046 | 18.2367 | 29.0604 | 13.1145 | 9.5669 | 18.138 | 29.0918 | 13.0735 | 9.5369 | 18.0185 | 29.132 | 13.0189 | 9.4971 | 17.9128 | 29.189 | 12.9485 | 9.4457 | 17.7914 | 29.2417 | 12.88 | 9.3958 | 17.6661 | 29.3145 | 12.6621 | 9.2368 | 17.5 | 29.4244 | 12.5794 | 9.1765 | 17.2749 | 29.5083 | 12.5037 | 9.1213 | 17.076 | 29.5946 | 12.4467 | 9.0797 | 16.8675 | 29.8623 | 12.2184 | 8.9131 | 16.2472 | 30.1118 | 12.0866 | 8.817 | 15.6207 | 30.2651 | 11.9859 | 8.7435 | 14.9953 | 30.391 | 11.8657 | 8.6559 | 14.2758 | 30.4813 | 11.6415 | 8.4923 | 13.725 | 29.0319 | 13.1663 | 9.6046 | 18.2367 | 29.0983 | 13.1071 | 9.5614 | 18.1585 | 29.1767 | 12.9831 | 9.471 | 18.0561 | 29.2846 | 12.7844 | 9.3261 | 17.9804 | 29.4569 | 12.5563 | 9.1596 | 17.8445 | 29.5796 | 12.2007 | 8.9003 | 17.7074 | 29.6721 | 12.1748 | 8.8813 | 17.6126 | 29.761 | 12.1117 | 8.8353 | 17.5399 | 29.8267 | 12.0498 | 8.7902 | 17.4504 | 29.8865 | 11.9802 | 8.7394 | 17.3641 | 30.1168 | 11.6054 | 8.466 | 16.1852 | 30.4146 | 11.1072 | 8.1026 | 13.7345 | 30.6477 | 10.7346 | 7.8307 | 11.6461 | 30.8771 | 10.3239 | 7.5311 | 9.394 | 31.0525 | 9.8885 | 7.2135 | 7.4965 | 29.0319 | 13.1663 | 9.6046 | 18.2367 | 29.0349 | 13.1587 | 9.5991 | 18.3247 | 29.0882 | 13.0648 | 9.5306 | 18.2698 | 29.1895 | 12.8792 | 9.3952 | 18.1994 | 29.3559 | 12.5318 | 9.1418 | 18.053 | 29.4372 | 12.3639 | 9.0193 | 17.8902 | 29.519 | 12.203 | 8.9019 | 17.5943 | 29.6265 | 11.9829 | 8.7414 | 16.7787 | 29.7232 | 11.7592 | 8.5782 | 15.9364 | 29.8166 | 11.5788 | 8.4466 | 15.099 | 30.0947 | 11.3386 | 8.2714 | 12.6921 | 30.3781 | 10.7988 | 7.8776 | 10.3654 | 30.596 | 10.3251 | 7.5321 | 8.4512 | 30.7603 | 9.9457 | 7.2552 | 7.198 | 30.7568 | 9.9394 | 7.2507 | 8.0223 | 29.0285 | 13.1663 | 9.6046 | 18.2367 | 29.0792 | 13.1419 | 9.5869 | 18.1617 | 29.1353 | 13.0369 | 9.5102 | 18.0696 | 29.1999 | 12.9201 | 9.425 | 18.0137 | 29.2871 | 12.7245 | 9.2823 | 17.9537 | 29.3925 | 12.4371 | 9.0727 | 17.8814 | 29.5158 | 12.359 | 9.0157 | 17.8017 | 29.6194 | 12.2626 | 8.9454 | 17.7125 | 29.6886 | 12.1971 | 8.8976 | 17.5521 | 29.7566 | 12.158 | 8.8691 | 17.394 | 29.9381 | 11.9521 | 8.7189 | 16.8296 | 30.1289 | 11.7856 | 8.5974 | 16.1527 | 30.2706 | 11.7688 | 8.5852 | 15.6763 | 30.4071 | 11.73 | 8.5568 | 15.2007 | 30.4855 | 11.6141 | 8.4723 | 14.948 | 29.0285 | 13.1663 | 9.6046 | 18.2367 | 29.0433 | 13.1328 | 9.5802 | 18.288 | 29.1158 | 13.0227 | 9.4999 | 18.1826 | 29.241 | 12.8227 | 9.354 | 18.0552 | 29.4306 | 12.4763 | 9.1013 | 17.8563 | 29.5237 | 12.2958 | 8.9696 | 17.6574 | 29.6135 | 12.1324 | 8.8504 | 17.317 | 29.738 | 11.8924 | 8.6753 | 16.4399 | 29.8425 | 11.6624 | 8.5075 | 15.5531 | 29.9423 | 11.4733 | 8.3696 | 14.6707 | 30.2281 | 11.2069 | 8.1753 | 12.1257 | 30.5013 | 10.6423 | 7.7634 | 9.676 | 30.713 | 10.1419 | 7.3984 | 7.6251 | 30.866 | 9.7272 | 7.0959 | 6.1757 | 30.876 | 9.6795 | 7.061 | 6.7644
GARSTANG | THORNTON | PENWORTHAM WEST / STANAH | 348319 | 445221 | 14.3184 | 14.3184 | 14.3184 | 2.5219 | 14.437 | 14.437 | 14.437 | 2.0154 | 14.6112 | 14.6112 | 14.6112 | 1.6973 | 14.8308 | 14.8308 | 14.8308 | 1.4288 | 15.0983 | 15.0983 | 15.0983 | 1.0606 | 15.406 | 15.406 | 15.406 | 0.683 | 15.7598 | 15.7598 | 15.7598 | 0.3425 | 16.1942 | 16.1942 | 16.1942 | -0.0033667 | 16.5462 | 16.5462 | 16.5462 | -0.38489 | 16.8937 | 16.8937 | 16.8937 | -0.74271 | 17.764 | 17.764 | 17.764 | -2.4108 | 18.4045 | 18.4045 | 18.4045 | -4.874 | 18.8355 | 18.8355 | 18.8355 | -7.111 | 19.1682 | 19.1682 | 19.1682 | -9.3273 | 19.3873 | 19.3873 | 18.5726 | -11.5387 | 14.2868 | 14.2868 | 14.2868 | 2.5219 | 14.3967 | 14.3967 | 14.3967 | 2.2556 | 14.5216 | 14.5216 | 14.5216 | 1.9967 | 14.6758 | 14.6758 | 14.6758 | 1.7211 | 14.8761 | 14.8761 | 14.8761 | 1.3796 | 15.1218 | 15.1218 | 15.1218 | 1.0118 | 15.4122 | 15.4122 | 15.4122 | 0.5521 | 15.679 | 15.679 | 15.679 | -0.057694 | 15.8595 | 15.8595 | 15.8595 | -0.48917 | 16.0501 | 16.0501 | 16.0501 | -0.92398 | 16.6533 | 16.6533 | 16.6533 | -2.246 | 17.2484 | 17.2484 | 17.2484 | -3.5841 | 17.7984 | 17.7984 | 17.7984 | -4.7982 | 18.3681 | 18.3681 | 18.3681 | -6.1524 | 18.7812 | 18.7812 | 18.7812 | -7.1159 | 14.3317 | 14.3317 | 14.3317 | 2.5219 | 14.4615 | 14.4615 | 14.4615 | 1.9914 | 14.6548 | 14.6548 | 14.6548 | 1.6903 | 14.9024 | 14.9024 | 14.9024 | 1.4647 | 15.2049 | 15.2049 | 15.2049 | 1.1429 | 15.5536 | 15.5536 | 15.5536 | 0.82032 | 15.9552 | 15.9552 | 15.9552 | 0.55669 | 16.4481 | 16.4481 | 16.4481 | 0.29688 | 16.8203 | 16.8203 | 16.8203 | 0.017615 | 17.1214 | 17.1214 | 17.1214 | -0.25459 | 17.8602 | 17.8602 | 17.8602 | -1.6705 | 18.5439 | 18.5439 | 18.5439 | -3.9803 | 19.0067 | 19.0067 | 19.0067 | -6.063 | 19.3389 | 19.3389 | 18.5595 | -8.085 | 19.5184 | 19.5184 | 17.6347 | -10.072 | 14.3317 | 14.3317 | 14.3317 | 2.5219 | 14.3603 | 14.3603 | 14.3603 | 2.3283 | 14.4592 | 14.4592 | 14.4592 | 2.1423 | 14.5944 | 14.5944 | 14.5944 | 1.9698 | 14.7894 | 14.7894 | 14.7894 | 1.6986 | 15.0825 | 15.0825 | 15.0825 | 1.3996 | 15.446 | 15.446 | 15.446 | 1.0424 | 15.8654 | 15.8654 | 15.8654 | 0.35935 | 16.2129 | 16.2129 | 16.2129 | -0.37452 | 16.5629 | 16.5629 | 16.5629 | -1.1114 | 17.4792 | 17.4792 | 17.4792 | -3.3648 | 18.1119 | 18.1119 | 18.1119 | -5.9598 | 18.5233 | 18.5233 | 18.5233 | -7.8494 | 18.8008 | 18.8008 | 18.0594 | -9.0951 | 18.8532 | 18.8532 | 17.5803 | -8.9531 | 14.3184 | 14.3184 | 14.3184 | 2.5219 | 14.421 | 14.421 | 14.421 | 2.283 | 14.5492 | 14.5492 | 14.5492 | 2.0451 | 14.6966 | 14.6966 | 14.6966 | 1.839 | 14.8843 | 14.8843 | 14.8843 | 1.5994 | 15.1574 | 15.1574 | 15.1574 | 1.3334 | 15.5071 | 15.5071 | 15.5071 | 1.0404 | 15.8996 | 15.8996 | 15.8996 | 0.69024 | 16.2095 | 16.2095 | 16.2095 | 0.2602 | 16.5256 | 16.5256 | 16.5256 | -0.17082 | 17.4588 | 17.4588 | 17.4588 | -1.6001 | 18.1653 | 18.1653 | 18.1653 | -3.1735 | 18.6168 | 18.6168 | 18.6168 | -4.2535 | 18.9763 | 18.9763 | 18.9763 | -5.2663 | 19.149 | 19.149 | 19.149 | -5.934 | 14.3184 | 14.3184 | 14.3184 | 2.5219 | 14.3938 | 14.3938 | 14.3938 | 2.1127 | 14.5612 | 14.5612 | 14.5612 | 1.7983 | 14.7787 | 14.7787 | 14.7787 | 1.5078 | 15.0431 | 15.0431 | 15.0431 | 1.1272 | 15.3434 | 15.3434 | 15.3434 | 0.75112 | 15.6917 | 15.6917 | 15.6917 | 0.30564 | 16.1375 | 16.1375 | 16.1375 | -0.49896 | 16.4944 | 16.4944 | 16.4944 | -1.3059 | 16.8485 | 16.8485 | 16.8485 | -2.1141 | 17.7083 | 17.7083 | 17.7083 | -4.5741 | 18.3317 | 18.3317 | 18.3317 | -7.3569 | 18.7453 | 18.7453 | 18.6576 | -9.4168 | 19.0039 | 19.0039 | 17.796 | -10.8424 | 19.058 | 19.058 | 17.2879 | -10.9048
GATLEY | MOSS NOOK | SOUTH MANCHESTER | 384242 | 388388 | 22.6282 | 22.6282 | 18.5583 | 12.0604 | 22.6472 | 22.6472 | 18.5843 | 12.0397 | 22.6689 | 22.6689 | 18.5286 | 12.0197 | 22.7068 | 22.7068 | 18.5303 | 12.005 | 22.791 | 22.791 | 18.5023 | 11.9324 | 22.8881 | 22.8881 | 18.4856 | 11.8473 | 22.9857 | 22.9857 | 18.4433 | 11.7704 | 23.0746 | 23.0746 | 18.4455 | 11.7212 | 23.1417 | 23.1417 | 18.3988 | 11.6409 | 23.2023 | 23.2023 | 18.3492 | 11.5779 | 23.6927 | 23.6927 | 18.1988 | 10.8543 | 24.5882 | 24.5882 | 17.9767 | 9.4241 | 24.8882 | 24.3635 | 17.7729 | 8.1899 | 25.0003 | 24.0673 | 17.5567 | 6.9462 | 25.0587 | 23.7871 | 17.3524 | 5.7467 | 22.6234 | 22.6234 | 18.5583 | 12.0604 | 22.6357 | 22.6357 | 18.6065 | 12.0266 | 22.6455 | 22.6455 | 18.6265 | 11.9863 | 22.6567 | 22.6567 | 18.6257 | 11.9555 | 22.6766 | 22.6766 | 18.6076 | 11.9061 | 22.6971 | 22.6971 | 18.5835 | 11.8443 | 22.7286 | 22.7286 | 18.5313 | 11.7536 | 22.7707 | 22.7707 | 18.494 | 11.6415 | 22.8085 | 22.8085 | 18.4572 | 11.5225 | 22.848 | 22.848 | 18.4237 | 11.4025 | 22.9774 | 22.9774 | 18.3251 | 11.0409 | 23.1188 | 23.1188 | 18.2483 | 10.6866 | 23.2859 | 23.2859 | 18.1476 | 10.3378 | 23.4877 | 23.4877 | 18.051 | 9.9605 | 23.6524 | 23.6524 | 18.0121 | 9.7019 | 22.6303 | 22.6303 | 18.5583 | 12.0604 | 22.6519 | 22.6519 | 18.5731 | 12.0532 | 22.6771 | 22.6771 | 18.4782 | 12.0476 | 22.7201 | 22.7201 | 18.4621 | 12.058 | 22.8101 | 22.8101 | 18.4299 | 12.0102 | 22.9138 | 22.9138 | 18.4689 | 11.9533 | 23.0198 | 23.0198 | 18.4465 | 11.9179 | 23.1177 | 23.1177 | 18.4083 | 11.9118 | 23.1872 | 23.1872 | 18.3655 | 11.8908 | 23.2493 | 23.2493 | 18.3207 | 11.8748 | 23.7507 | 23.7507 | 18.158 | 11.292 | 24.6617 | 24.5746 | 17.9268 | 9.982 | 24.8226 | 24.2863 | 17.7165 | 8.8551 | 24.8913 | 23.9768 | 17.4908 | 7.7454 | 24.8859 | 23.6894 | 17.2811 | 6.7039 | 22.6303 | 22.6303 | 18.5583 | 12.0604 | 22.5936 | 22.5936 | 18.582 | 12.2276 | 22.6003 | 22.6003 | 18.5364 | 12.268 | 22.6386 | 22.6386 | 18.5458 | 12.2894 | 22.7282 | 22.7282 | 18.4836 | 12.235 | 22.8414 | 22.8414 | 18.4695 | 12.1572 | 23.0083 | 23.0083 | 18.4662 | 12.0137 | 23.3299 | 23.3299 | 18.3889 | 11.6116 | 23.6397 | 23.6397 | 18.3104 | 11.1753 | 23.9462 | 23.9462 | 18.228 | 10.7356 | 24.4717 | 24.4717 | 17.9763 | 9.4569 | 24.6268 | 24.3233 | 17.7435 | 8.2186 | 24.7228 | 24.0282 | 17.5283 | 7.1954 | 24.7502 | 23.8331 | 17.3859 | 6.6537 | 24.6452 | 23.815 | 17.3727 | 7.1985 | 22.6282 | 22.6282 | 18.5583 | 12.0604 | 22.6424 | 22.6424 | 18.5902 | 12.0509 | 22.6534 | 22.6534 | 18.538 | 12.055 | 22.6626 | 22.6626 | 18.5484 | 12.092 | 22.6842 | 22.6842 | 18.536 | 12.1211 | 22.7194 | 22.7194 | 18.529 | 12.1305 | 22.7688 | 22.7688 | 18.4925 | 12.1225 | 22.8282 | 22.8282 | 18.5059 | 12.1101 | 22.8848 | 22.8848 | 18.4632 | 12.0413 | 22.9431 | 22.9431 | 18.4066 | 11.976 | 23.1633 | 23.1633 | 18.3182 | 11.7028 | 23.4256 | 23.4256 | 18.2259 | 11.3253 | 23.6232 | 23.6232 | 18.137 | 11.0297 | 23.8165 | 23.8165 | 18.0365 | 10.7423 | 23.9327 | 23.9327 | 17.9534 | 10.6417 | 22.6282 | 22.6282 | 18.5583 | 12.0604 | 22.5995 | 22.5995 | 18.5754 | 12.1955 | 22.6189 | 22.6189 | 18.5194 | 12.1915 | 22.6724 | 22.6724 | 18.5233 | 12.1635 | 22.774 | 22.774 | 18.4627 | 12.0653 | 22.8864 | 22.8864 | 18.4354 | 11.9598 | 23.0475 | 23.0475 | 18.4286 | 11.7811 | 23.3727 | 23.3727 | 18.3478 | 11.3311 | 23.6863 | 23.6863 | 18.2589 | 10.859 | 23.9955 | 23.9955 | 18.1753 | 10.3835 | 24.5517 | 24.5514 | 17.9099 | 8.9949 | 24.7063 | 24.216 | 17.6652 | 7.6665 | 24.8042 | 23.9175 | 17.4475 | 6.5566 | 24.8289 | 23.693 | 17.2837 | 5.9156 | 24.7285 | 23.6467 | 17.2499 | 6.3485
GIDLOW | WIGAN | WASHWAY FARM / KIRKBY | 357620 | 406662 | 30.7016 | 14.3596 | 10.4752 | 13.5443 | 30.8011 | 13.9291 | 10.1611 | 11.5864 | 30.9399 | 13.7019 | 9.9953 | 11.0468 | 31.1139 | 13.5387 | 9.8763 | 10.8529 | 31.3265 | 13.2742 | 9.6834 | 10.5336 | 31.568 | 13.019 | 9.4972 | 10.2031 | 31.8096 | 12.7809 | 9.3235 | 9.9084 | 32.0925 | 12.5827 | 9.1789 | 9.6451 | 32.2999 | 12.3752 | 9.0275 | 9.3475 | 32.4945 | 12.2402 | 8.929 | 9.0875 | 32.9926 | 11.5237 | 8.4064 | 6.9338 | 33.6036 | 10.5958 | 7.7295 | 2.9055 | 34.079 | 9.8552 | 7.1893 | -0.51021 | 34.5413 | 9.2206 | 6.7263 | -4.161 | 34.8575 | 8.4287 | 6.1487 | -7.4158 | 30.6762 | 14.3596 | 10.4752 | 13.5443 | 30.7641 | 14.2086 | 10.365 | 12.8614 | 30.8546 | 14.0927 | 10.2805 | 12.5956 | 30.9657 | 13.9767 | 10.1958 | 12.405 | 31.1132 | 13.8352 | 10.0926 | 12.1354 | 31.3006 | 13.6843 | 9.9825 | 11.83 | 31.5252 | 13.3074 | 9.7076 | 11.4357 | 31.7799 | 13.1438 | 9.5882 | 10.9366 | 31.9295 | 13.0048 | 9.4868 | 10.5511 | 32.0768 | 12.8694 | 9.3881 | 10.163 | 32.4658 | 12.4838 | 9.1068 | 9.0079 | 32.841 | 12.2119 | 8.9084 | 7.8626 | 33.1751 | 11.9723 | 8.7337 | 6.8004 | 33.5156 | 11.7217 | 8.5508 | 5.6703 | 33.7715 | 11.4062 | 8.3207 | 4.875 | 30.7124 | 14.3596 | 10.4752 | 13.5443 | 30.8229 | 13.8548 | 10.1069 | 11.3183 | 30.9803 | 13.5794 | 9.906 | 10.7518 | 31.1816 | 13.3892 | 9.7672 | 10.6087 | 31.4289 | 13.0839 | 9.5445 | 10.2259 | 31.6871 | 12.824 | 9.355 | 9.8416 | 31.9607 | 12.5575 | 9.1605 | 9.5205 | 32.292 | 12.3255 | 8.9913 | 9.2371 | 32.4667 | 12.0955 | 8.8235 | 8.9211 | 32.6151 | 11.948 | 8.7159 | 8.6393 | 33.1394 | 11.1848 | 8.1592 | 6.7686 | 33.7681 | 10.2075 | 7.4462 | 2.9926 | 34.2491 | 9.5138 | 6.9402 | -0.20144 | 34.7037 | 8.7632 | 6.3926 | -3.5976 | 35.0424 | 7.9592 | 5.8061 | -6.5749 | 30.7124 | 14.3596 | 10.4752 | 13.5443 | 30.7055 | 14.0369 | 10.2397 | 12.2758 | 30.7713 | 13.8589 | 10.1099 | 11.9529 | 30.8655 | 13.6938 | 9.9894 | 11.8702 | 31.0135 | 13.4487 | 9.8106 | 11.5085 | 31.2448 | 13.1796 | 9.6143 | 11.1009 | 31.4854 | 12.6148 | 9.2024 | 10.5017 | 31.774 | 12.0236 | 8.7711 | 9.1632 | 32.001 | 11.475 | 8.3709 | 7.7706 | 32.2218 | 11.0307 | 8.0468 | 6.4035 | 32.8939 | 10.2002 | 7.4409 | 2.7582 | 33.523 | 9.4158 | 6.8687 | -0.83552 | 33.9651 | 8.6046 | 6.277 | -3.782 | 34.3017 | 7.9034 | 5.7654 | -5.7283 | 34.3615 | 7.8052 | 5.6938 | -4.6861 | 30.7016 | 14.3596 | 10.4752 | 13.5443 | 30.7872 | 14.1031 | 10.288 | 12.4304 | 30.8816 | 13.92 | 10.1545 | 12.1194 | 30.9858 | 13.7793 | 10.0518 | 12.039 | 31.1235 | 13.553 | 9.8867 | 11.9187 | 31.336 | 13.327 | 9.7219 | 11.7535 | 31.6129 | 13.1077 | 9.5619 | 11.5543 | 31.8732 | 12.9198 | 9.4248 | 11.3458 | 32.0566 | 12.7133 | 9.2742 | 11.0575 | 32.2365 | 12.5722 | 9.1712 | 10.7786 | 32.7274 | 12.0679 | 8.8033 | 9.7919 | 33.1805 | 11.6388 | 8.4904 | 8.6016 | 33.5158 | 11.4072 | 8.3214 | 7.7672 | 33.8323 | 11.3018 | 8.2445 | 6.9378 | 34.0107 | 11.0426 | 8.0554 | 6.4765 | 30.7016 | 14.3596 | 10.4752 | 13.5443 | 30.7356 | 13.8478 | 10.1018 | 11.3099 | 30.8653 | 13.6139 | 9.9312 | 10.6834 | 31.0378 | 13.4231 | 9.7919 | 10.4586 | 31.2522 | 13.1547 | 9.5962 | 9.9685 | 31.4922 | 12.8777 | 9.3941 | 9.4785 | 31.7339 | 12.2943 | 8.9685 | 8.7798 | 32.0616 | 11.6731 | 8.5153 | 7.2979 | 32.3108 | 11.0978 | 8.0957 | 5.7969 | 32.5487 | 10.6388 | 7.7609 | 4.3229 | 33.2288 | 9.7435 | 7.1077 | 0.36884 | 33.8065 | 8.9057 | 6.4966 | -3.4649 | 34.2153 | 8.0451 | 5.8688 | -6.6493 | 34.51 | 7.2882 | 5.3167 | -8.8998 | 34.5797 | 7.1246 | 5.1973 | -8.2214
GILLSROW | PENRITH & SHAP | HARKER / HUTTON | 337117 | 526444 | 7.9074 | 7.9074 | 7.9074 | 3.3153 | 7.9566 | 7.9566 | 7.9566 | 3.161 | 8.028 | 8.028 | 8.028 | 3.0859 | 8.1055 | 8.1055 | 8.1055 | 3.0357 | 8.1786 | 8.1786 | 8.1786 | 2.9145 | 8.2641 | 8.2641 | 8.2641 | 2.7789 | 8.3559 | 8.3559 | 8.3559 | 2.6635 | 8.438 | 8.438 | 8.438 | 2.5698 | 8.4781 | 8.4781 | 8.4781 | 2.4875 | 8.5147 | 8.5147 | 8.5147 | 2.4316 | 8.6338 | 8.6338 | 8.6338 | 1.874 | 8.7623 | 8.7623 | 8.7623 | 0.78107 | 8.8513 | 8.8513 | 8.8513 | -0.13153 | 8.9122 | 8.9122 | 8.9122 | -0.93927 | 8.9496 | 8.9496 | 8.9496 | -1.8139 | 7.9031 | 7.9031 | 7.9031 | 3.3153 | 7.9489 | 7.9489 | 7.9489 | 3.1862 | 7.9981 | 7.9981 | 7.9981 | 3.0551 | 8.0672 | 8.0672 | 8.0672 | 2.9192 | 8.1569 | 8.1569 | 8.1569 | 2.7634 | 8.2366 | 8.2366 | 8.2366 | 2.6388 | 8.332 | 8.332 | 8.332 | 2.4321 | 8.44 | 8.44 | 8.44 | 2.1539 | 8.4764 | 8.4764 | 8.4764 | 2.05 | 8.5138 | 8.5138 | 8.5138 | 1.947 | 8.6282 | 8.6282 | 8.6282 | 1.6498 | 8.7331 | 8.7331 | 8.7331 | 1.3908 | 8.8239 | 8.8239 | 8.8239 | 1.125 | 8.9164 | 8.9164 | 8.9164 | 0.7547 | 8.9873 | 8.9873 | 8.9873 | 0.19274 | 7.9097 | 7.9097 | 7.9097 | 3.3153 | 7.9615 | 7.9615 | 7.9615 | 3.1553 | 8.037 | 8.037 | 8.037 | 3.0861 | 8.1236 | 8.1236 | 8.1236 | 3.0518 | 8.2068 | 8.2068 | 8.2068 | 2.9456 | 8.3048 | 8.3048 | 8.3048 | 2.8276 | 8.3954 | 8.3954 | 8.3954 | 2.7382 | 8.4732 | 8.4732 | 8.4732 | 2.6719 | 8.5174 | 8.5174 | 8.5174 | 2.6323 | 8.5577 | 8.5577 | 8.5577 | 2.6095 | 8.6875 | 8.6875 | 8.6875 | 2.1587 | 8.8238 | 8.8238 | 8.8238 | 1.1688 | 8.9154 | 8.9154 | 8.9154 | 0.35297 | 8.9737 | 8.9737 | 8.9737 | -0.33518 | 9.0024 | 9.0024 | 9.0024 | -1.0684 | 7.9097 | 7.9097 | 7.9097 | 3.3153 | 7.9132 | 7.9132 | 7.9132 | 3.2831 | 7.9458 | 7.9458 | 7.9458 | 3.2322 | 7.9985 | 7.9985 | 7.9985 | 3.13 | 8.0604 | 8.0604 | 8.0604 | 3.0063 | 8.1289 | 8.1289 | 8.1289 | 2.8796 | 8.2154 | 8.2154 | 8.2154 | 2.7166 | 8.2976 | 8.2976 | 8.2976 | 2.3859 | 8.3409 | 8.3409 | 8.3409 | 2.035 | 8.3829 | 8.3829 | 8.3829 | 1.6847 | 8.5103 | 8.5103 | 8.5103 | 0.68461 | 8.6399 | 8.6399 | 8.6399 | -0.26207 | 8.7223 | 8.7223 | 8.7223 | -0.92918 | 8.7652 | 8.7652 | 8.7652 | -1.1644 | 8.7464 | 8.7464 | 8.7464 | -0.73023 | 7.9074 | 7.9074 | 7.9074 | 3.3153 | 7.9491 | 7.9491 | 7.9491 | 3.2065 | 7.9972 | 7.9972 | 7.9972 | 3.131 | 8.0562 | 8.0562 | 8.0562 | 3.0705 | 8.1327 | 8.1327 | 8.1327 | 2.9954 | 8.2074 | 8.2074 | 8.2074 | 2.953 | 8.2954 | 8.2954 | 8.2954 | 2.9184 | 8.384 | 8.384 | 8.384 | 2.8687 | 8.4295 | 8.4295 | 8.4295 | 2.7919 | 8.4639 | 8.4639 | 8.4639 | 2.7179 | 8.5786 | 8.5786 | 8.5786 | 2.3392 | 8.7041 | 8.7041 | 8.7041 | 1.7652 | 8.79 | 8.79 | 8.79 | 1.3808 | 8.8616 | 8.8616 | 8.8616 | 0.93684 | 8.89 | 8.89 | 8.89 | 0.63942 | 7.9074 | 7.9074 | 7.9074 | 3.3153 | 7.9352 | 7.9352 | 7.9352 | 3.2132 | 8.0048 | 8.0048 | 8.0048 | 3.1197 | 8.0915 | 8.0915 | 8.0915 | 2.977 | 8.1666 | 8.1666 | 8.1666 | 2.8129 | 8.2526 | 8.2526 | 8.2526 | 2.6517 | 8.3452 | 8.3452 | 8.3452 | 2.4476 | 8.4355 | 8.4355 | 8.4355 | 2.0668 | 8.4834 | 8.4834 | 8.4834 | 1.6903 | 8.5289 | 8.5289 | 8.5289 | 1.3141 | 8.6589 | 8.6589 | 8.6589 | 0.23733 | 8.7767 | 8.7767 | 8.7767 | -0.76864 | 8.8502 | 8.8502 | 8.8502 | -1.4889 | 8.8825 | 8.8825 | 8.8825 | -1.7856 | 8.8644 | 8.8644 | 8.8644 | -1.421
GLAXO | ULVERSTON | HARKER / HUTTON | 330458 | 477825 | 15.3541 | 2.5279 | 1.8169 | 15.3541 | 14.9662 | 2.4641 | 1.771 | 14.9662 | 14.4048 | 2.3716 | 1.7045 | 14.4048 | 13.7639 | 2.2661 | 1.6287 | 13.7639 | 12.812 | 2.1094 | 1.5161 | 12.812 | 11.6164 | 1.9126 | 1.3746 | 11.6164 | 11.8731 | 1.9548 | 1.405 | 11.8731 | 11.5977 | 1.9095 | 1.3724 | 11.5977 | 11.2241 | 1.848 | 1.3282 | 11.2241 | 10.8237 | 1.782 | 1.2808 | 10.8237 | 7.8779 | 1.297 | 0.9322 | 7.8779 | 4.9087 | 0.80818 | 0.58085 | 4.9087 | 4.6015 | 0.7576 | 0.5445 | 4.6015 | 18.0884 | 2.9781 | 2.1404 | 11.6231 | 27.5922 | 5.9981 | 4.311 | 11.6361 | 15.3541 | 2.5279 | 1.8169 | 15.3541 | 15.0784 | 2.4825 | 1.7842 | 15.0784 | 14.867 | 2.4477 | 1.7592 | 14.867 | 14.6196 | 2.407 | 1.73 | 14.6196 | 14.4355 | 2.3767 | 1.7082 | 14.4355 | 14.2064 | 2.339 | 1.6811 | 14.2064 | 12.9766 | 2.1365 | 1.5355 | 12.9766 | 12.7784 | 2.1039 | 1.5121 | 12.7784 | 12.5666 | 2.069 | 1.487 | 12.5666 | 12.4275 | 2.0461 | 1.4706 | 12.4275 | 11.9693 | 1.9707 | 1.4163 | 11.9693 | 10.7005 | 1.7618 | 1.2662 | 10.7005 | 10.9609 | 1.8046 | 1.297 | 10.9609 | 20.4406 | 3.3654 | 2.4188 | 15.2502 | 27.141 | 5.5799 | 4.0104 | 14.2798 | 15.3541 | 2.5279 | 1.8169 | 15.3541 | 14.91 | 2.4548 | 1.7643 | 14.91 | 14.2826 | 2.3515 | 1.6901 | 14.2826 | 13.5275 | 2.2272 | 1.6007 | 13.5275 | 12.0068 | 1.9768 | 1.4208 | 12.0068 | 12.0442 | 1.983 | 1.4252 | 12.0442 | 11.7717 | 1.9381 | 1.393 | 11.7717 | 11.407 | 1.8781 | 1.3498 | 11.407 | 10.8103 | 1.7798 | 1.2792 | 10.8103 | 10.3668 | 1.7068 | 1.2267 | 10.3668 | 2.0459 | 0.33685 | 0.2421 | 2.0459 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 16.3717 | 2.6955 | 1.9373 | 11.1268 | 28.1542 | 5.6825 | 4.0842 | 11.2371 | 15.3541 | 2.5279 | 1.8169 | 15.3541 | 15.0456 | 2.4771 | 1.7804 | 15.0456 | 14.4578 | 2.3804 | 1.7108 | 14.4578 | 13.4353 | 2.212 | 1.5898 | 13.4353 | 12.8062 | 2.1084 | 1.5154 | 12.8062 | 11.4395 | 1.8834 | 1.3537 | 11.4395 | 8.0689 | 1.3285 | 0.95481 | 8.0689 | 1.9957 | 0.32858 | 0.23615 | 1.9957 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 28.3839 | 4.9149 | 3.5325 | 10.935 | 28.3241 | 4.8219 | 3.4656 | 11.1075 | 15.3541 | 2.5279 | 1.8169 | 15.3541 | 15.1457 | 2.4936 | 1.7922 | 15.1457 | 14.6396 | 2.4103 | 1.7323 | 14.6396 | 14.0212 | 2.3085 | 1.6591 | 14.0212 | 13.0902 | 2.1552 | 1.549 | 13.0902 | 11.8335 | 1.9483 | 1.4003 | 11.8335 | 12.1901 | 2.007 | 1.4425 | 12.1901 | 11.9372 | 1.9654 | 1.4126 | 11.9372 | 11.5687 | 1.9047 | 1.3689 | 11.5687 | 11.1661 | 1.8384 | 1.3213 | 11.1661 | 8.4353 | 1.3888 | 0.99816 | 8.4353 | 5.8558 | 0.96411 | 0.69293 | 5.8558 | 5.8815 | 0.96835 | 0.69597 | 5.8815 | 19.7301 | 3.2484 | 2.3347 | 11.9257 | 27.5616 | 6.3218 | 4.5436 | 12.0038 | 15.3541 | 2.5279 | 1.8169 | 15.3541 | 14.8967 | 2.4526 | 1.7627 | 14.8967 | 14.2584 | 2.3475 | 1.6872 | 14.2584 | 13.2496 | 2.1815 | 1.5679 | 13.2496 | 12.5454 | 2.0655 | 1.4845 | 12.5454 | 11.1555 | 1.8367 | 1.3201 | 11.1555 | 7.7638 | 1.2783 | 0.91871 | 7.7638 | 1.6733 | 0.2755 | 0.198 | 1.6733 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 28.453 | 4.8518 | 3.4871 | 10.8287 | 28.406 | 4.7524 | 3.4156 | 10.9976
GLOSSOP | HYDE | STALYBRIDGE | 402300 | 394074 | 30.2856 | 15.2005 | 10.9249 | 14.0541 | 30.3584 | 14.9922 | 10.7752 | 13.7815 | 30.4489 | 14.8938 | 10.7045 | 13.5858 | 30.561 | 14.6687 | 10.5427 | 13.4317 | 30.7044 | 14.4274 | 10.3693 | 13.1879 | 30.8732 | 14.0101 | 10.0694 | 12.9353 | 31.0468 | 13.8281 | 9.9385 | 12.7064 | 31.2117 | 13.6285 | 9.7951 | 12.4941 | 31.3488 | 13.4332 | 9.6547 | 12.2307 | 31.4866 | 13.2778 | 9.543 | 11.9885 | 31.9514 | 13.0683 | 9.3924 | 10.163 | 32.4405 | 12.4926 | 8.9787 | 6.8512 | 32.794 | 11.9875 | 8.6157 | 4.0795 | 33.108 | 11.187 | 8.0403 | 1.0963 | 33.3382 | 10.7852 | 7.7516 | -1.473 | 30.2676 | 15.2005 | 10.9249 | 14.0541 | 30.3419 | 15.1564 | 10.8932 | 13.843 | 30.4182 | 15.0825 | 10.8401 | 13.651 | 30.5109 | 14.9597 | 10.7519 | 13.4755 | 30.6334 | 14.7801 | 10.6228 | 13.2645 | 30.7846 | 14.7884 | 10.6287 | 13.0476 | 30.9682 | 14.6313 | 10.5158 | 12.7583 | 31.1822 | 14.4947 | 10.4176 | 12.3656 | 31.2879 | 14.3346 | 10.3026 | 12.0471 | 31.4003 | 14.2342 | 10.2304 | 11.7266 | 31.7688 | 13.8445 | 9.9503 | 10.7689 | 32.1393 | 13.4686 | 9.6802 | 9.7681 | 32.4547 | 13.1857 | 9.4768 | 8.8151 | 32.7628 | 12.7527 | 9.1656 | 7.7596 | 32.9849 | 12.131 | 8.7188 | 7.0031 | 30.2933 | 15.2005 | 10.9249 | 14.0541 | 30.3734 | 14.9915 | 10.7747 | 13.7814 | 30.4747 | 14.8079 | 10.6427 | 13.6012 | 30.6026 | 14.5904 | 10.4864 | 13.4812 | 30.765 | 14.285 | 10.2669 | 13.2697 | 30.9475 | 13.8896 | 9.9827 | 13.0541 | 31.0923 | 13.6324 | 9.7978 | 12.8829 | 31.2671 | 13.3508 | 9.5955 | 12.7285 | 31.4037 | 13.4137 | 9.6407 | 12.5529 | 31.5403 | 13.4208 | 9.6458 | 12.38 | 32.0229 | 13.0285 | 9.3639 | 10.7624 | 32.5517 | 12.3767 | 8.8954 | 7.615 | 32.9389 | 11.7594 | 8.4517 | 4.9946 | 33.2684 | 11.1588 | 8.02 | 2.2098 | 33.4907 | 10.6902 | 7.6832 | -0.11515 | 30.2933 | 15.2005 | 10.9249 | 14.0541 | 30.2774 | 15.068 | 10.8297 | 14.1034 | 30.3171 | 14.8866 | 10.6993 | 14.0129 | 30.3766 | 14.6695 | 10.5432 | 13.932 | 30.477 | 14.2686 | 10.2551 | 13.7379 | 30.6341 | 13.7906 | 9.9116 | 13.5236 | 30.8084 | 13.7993 | 9.9178 | 13.1416 | 30.9813 | 13.6445 | 9.8065 | 12.12 | 31.1415 | 13.4018 | 9.6321 | 11.0584 | 31.3058 | 13.1627 | 9.4603 | 9.9981 | 31.8098 | 12.6149 | 9.0666 | 6.9448 | 32.2916 | 11.9473 | 8.5868 | 3.978 | 32.6304 | 11.3631 | 8.1669 | 1.5862 | 32.8793 | 10.8752 | 7.8162 | -0.018801 | 32.9265 | 10.8953 | 7.8307 | 0.88854 | 30.2856 | 15.2005 | 10.9249 | 14.0541 | 30.3493 | 14.9949 | 10.7772 | 13.8512 | 30.4129 | 14.9291 | 10.7298 | 13.6952 | 30.4833 | 14.7046 | 10.5685 | 13.5957 | 30.5802 | 14.513 | 10.4308 | 13.4739 | 30.7275 | 14.1247 | 10.1517 | 13.3364 | 30.924 | 13.9427 | 10.0209 | 13.1775 | 31.0946 | 13.7549 | 9.8859 | 13.003 | 31.2122 | 13.5655 | 9.7498 | 12.7389 | 31.3342 | 13.3496 | 9.5946 | 12.4778 | 31.739 | 13.3411 | 9.5885 | 11.5993 | 32.1536 | 13.1932 | 9.4822 | 10.5963 | 32.4518 | 13.0463 | 9.3767 | 9.853 | 32.7031 | 12.6245 | 9.0735 | 9.1573 | 32.8508 | 12.7143 | 9.138 | 8.7538 | 30.2856 | 15.2005 | 10.9249 | 14.0541 | 30.2986 | 15.029 | 10.8017 | 13.9987 | 30.3797 | 14.843 | 10.668 | 13.828 | 30.4879 | 14.6127 | 10.5024 | 13.6695 | 30.6293 | 14.192 | 10.2001 | 13.4035 | 30.792 | 13.7201 | 9.8609 | 13.1381 | 30.9584 | 13.7002 | 9.8466 | 12.6923 | 31.153 | 13.5304 | 9.7245 | 11.589 | 31.3142 | 13.2763 | 9.5419 | 10.4777 | 31.4779 | 13.032 | 9.3663 | 9.3658 | 31.9833 | 12.4297 | 8.9335 | 6.136 | 32.4682 | 11.7381 | 8.4364 | 3.0022 | 32.8195 | 11.1077 | 7.9833 | 0.4232 | 33.07 | 10.575 | 7.6005 | -1.4403 | 33.1315 | 10.5396 | 7.575 | -0.83838
GOLBORNE T11 & T12 | GOLBORNE | BOLD | 360621 | 397766 | 33.1839 | 6.017 | 4.3245 | 16.817 | 33.3321 | 5.6545 | 4.064 | 16.4813 | 19.5463 | 3.2181 | 2.3129 | 15.9399 | 4.6783 | 0.77025 | 0.55359 | 4.6783 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 0.29449 | 2.6844 | 0.44197 | 0.31765 | -4.1685 | 1.4397 | 0.23703 | 0.17036 | -8.5866 | 5.5345 | 0.91121 | 0.65491 | -12.2012 | 33.1416 | 6.017 | 4.3245 | 16.817 | 33.26 | 5.7028 | 4.0987 | 16.5592 | 20.3859 | 3.3564 | 2.4123 | 16.2374 | 6.0511 | 0.99626 | 0.71603 | 6.0511 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 0.29574 | 2.6844 | 0.44197 | 0.31765 | -1.5095 | 33.1978 | 6.017 | 4.3245 | 16.817 | 33.3547 | 5.6426 | 4.0554 | 16.5233 | 19.2903 | 3.176 | 2.2827 | 16.0344 | 4.3318 | 0.71319 | 0.51259 | 4.3318 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | -0.44255 | 2.6844 | 0.44197 | 0.31765 | -5.3711 | 2.6844 | 0.44197 | 0.31765 | -9.7262 | 0.44937 | 0.073986 | 0.053175 | -12.9838 | 33.1978 | 6.017 | 4.3245 | 16.817 | 33.2525 | 5.9623 | 4.2852 | 16.8128 | 33.385 | 5.8175 | 4.1812 | 16.4986 | 33.5833 | 5.6231 | 4.0414 | 16.1284 | 32.668 | 5.3785 | 3.8657 | 15.5926 | 31.0249 | 5.108 | 3.6712 | 14.9391 | 29.0079 | 4.7759 | 3.4326 | 14.0597 | 27.0301 | 4.4503 | 3.1985 | 12.4229 | 25.1501 | 4.1408 | 2.9761 | 10.6219 | 23.6225 | 3.8893 | 2.7953 | 8.7735 | 26.0075 | 4.2819 | 3.0775 | 3.1743 | 18.3435 | 3.0201 | 2.1706 | -2.1708 | 11.8927 | 1.958 | 1.4073 | -6.1889 | 6.0063 | 0.98889 | 0.71073 | -9.5301 | 3.7254 | 0.61335 | 0.44083 | -10.0295 | 33.1839 | 6.017 | 4.3245 | 16.817 | 33.3084 | 5.6872 | 4.0875 | 16.56 | 19.9069 | 3.2775 | 2.3556 | 16.1505 | 5.2603 | 0.86606 | 0.62246 | 5.2603 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.1194 | 10.9869 | 1.8089 | 1.3001 | -0.49757 | 17.7605 | 2.9241 | 2.1016 | -1.9622 | 33.1839 | 6.017 | 4.3245 | 16.817 | 33.2824 | 5.9205 | 4.2552 | 16.6699 | 33.4869 | 5.7357 | 4.1224 | 16.1458 | 33.4243 | 5.5031 | 3.9552 | 15.5409 | 31.74 | 5.2257 | 3.7558 | 14.8094 | 30.0135 | 4.9415 | 3.5515 | 14.0712 | 27.9292 | 4.5983 | 3.3049 | 13.115 | 25.8004 | 4.2478 | 3.053 | 11.3199 | 23.7493 | 3.9101 | 2.8103 | 9.4009 | 22.0663 | 3.633 | 2.6111 | 7.4498 | 23.9175 | 3.9378 | 2.8302 | 1.4798 | 15.7503 | 2.5932 | 1.8638 | -4.2841 | 8.5137 | 1.4017 | 1.0074 | -8.9038 | 2.7588 | 0.45421 | 0.32645 | -12.104 | 1.21 | 0.19922 | 0.14318 | -11.8901
GOWHOLE | NEW MILLS | STALYBRIDGE | 401104 | 383846 | 30.5182 | 11.0412 | 7.9355 | 10.9218 | 30.6696 | 10.8155 | 7.7733 | 10.3734 | 30.8375 | 10.8325 | 7.7855 | 10.1407 | 31.0499 | 10.7669 | 7.7384 | 10.0292 | 31.3122 | 10.641 | 7.6479 | 9.8051 | 31.6194 | 10.4527 | 7.5125 | 9.5683 | 31.947 | 10.2955 | 7.3996 | 9.3757 | 32.2471 | 10.1184 | 7.2723 | 9.1957 | 32.4854 | 9.9937 | 7.1826 | 8.9106 | 32.7016 | 9.8915 | 7.1092 | 8.6613 | 33.6172 | 9.3415 | 6.7139 | 6.4152 | 34.6045 | 8.5064 | 6.1137 | 2.1922 | 35.1895 | 7.8066 | 5.6107 | -1.3633 | 35.7005 | 7.0598 | 5.074 | -5.0296 | 36.0344 | 6.4164 | 4.6116 | -7.9935 | 30.4313 | 11.0412 | 7.9355 | 10.9218 | 30.549 | 10.9617 | 7.8784 | 10.6487 | 30.67 | 10.8733 | 7.8149 | 10.4166 | 30.8498 | 10.7576 | 7.7317 | 10.2074 | 31.0339 | 10.5481 | 7.5811 | 9.9372 | 31.2632 | 10.5567 | 7.5873 | 9.624 | 31.5393 | 10.2747 | 7.3846 | 9.2219 | 31.8083 | 10.106 | 7.2634 | 8.7402 | 31.9945 | 9.9338 | 7.1396 | 8.3465 | 32.1914 | 9.8156 | 7.0546 | 7.9492 | 32.7446 | 9.5667 | 6.8758 | 6.7617 | 33.2371 | 9.3339 | 6.7084 | 5.5406 | 33.683 | 9.0908 | 6.5337 | 4.3597 | 34.1378 | 8.8674 | 6.3732 | 3.1215 | 34.4632 | 8.6023 | 6.1827 | 2.2829 | 30.5347 | 11.0412 | 7.9355 | 10.9218 | 30.6971 | 10.7518 | 7.7275 | 10.3405 | 30.8853 | 10.8349 | 7.7873 | 10.1336 | 31.1284 | 10.752 | 7.7277 | 10.0913 | 31.4289 | 10.5909 | 7.6119 | 9.9386 | 31.781 | 10.4017 | 7.4759 | 9.7854 | 32.0587 | 10.2141 | 7.3411 | 9.7105 | 32.3559 | 10.0128 | 7.1964 | 9.5158 | 32.5771 | 9.8793 | 7.1004 | 9.2506 | 32.7917 | 9.7552 | 7.0112 | 9.0204 | 33.7246 | 9.1773 | 6.5959 | 7.2681 | 34.7379 | 8.4182 | 6.0503 | 3.7514 | 35.3421 | 7.6956 | 5.531 | 0.56398 | 35.8385 | 6.9711 | 5.0102 | -2.7629 | 36.1249 | 6.3641 | 4.574 | -5.3128 | 30.5347 | 11.0412 | 7.9355 | 10.9218 | 30.5556 | 10.8457 | 7.795 | 10.8978 | 30.6445 | 10.9955 | 7.9027 | 10.8464 | 30.7651 | 10.8862 | 7.8241 | 10.8488 | 30.9525 | 10.668 | 7.6673 | 10.7176 | 31.2511 | 10.3258 | 7.4214 | 10.5507 | 31.6385 | 9.9473 | 7.1493 | 10.1725 | 32.11 | 9.5379 | 6.8551 | 8.9525 | 32.5035 | 9.2946 | 6.6802 | 7.6496 | 32.8264 | 9.0373 | 6.4953 | 6.3465 | 33.6549 | 8.2502 | 5.9296 | 2.5987 | 34.4628 | 7.4628 | 5.3636 | -0.96945 | 35.0124 | 6.7544 | 4.8545 | -3.8864 | 35.3783 | 6.2102 | 4.4634 | -5.6404 | 35.3358 | 6.309 | 4.5344 | -3.8928 | 30.5182 | 11.0412 | 7.9355 | 10.9218 | 30.6495 | 10.8818 | 7.821 | 10.6325 | 30.7621 | 10.9033 | 7.8364 | 10.506 | 30.8896 | 10.8607 | 7.8058 | 10.4901 | 31.059 | 10.7681 | 7.7392 | 10.4543 | 31.3255 | 10.608 | 7.6242 | 10.3747 | 31.6799 | 10.4552 | 7.5143 | 10.2425 | 31.9564 | 10.287 | 7.3934 | 10.0702 | 32.1787 | 10.1604 | 7.3025 | 9.7613 | 32.4053 | 10.0444 | 7.2191 | 9.4573 | 33.1514 | 9.6898 | 6.9642 | 8.3657 | 33.8971 | 9.2864 | 6.6743 | 6.8938 | 34.4379 | 9.0228 | 6.4849 | 5.7822 | 34.9014 | 8.7581 | 6.2946 | 4.7935 | 35.087 | 8.558 | 6.1508 | 4.4554 | 30.5182 | 11.0412 | 7.9355 | 10.9218 | 30.5946 | 10.8046 | 7.7654 | 10.5914 | 30.7506 | 10.9028 | 7.8361 | 10.367 | 30.9591 | 10.7729 | 7.7427 | 10.2225 | 31.2183 | 10.526 | 7.5652 | 9.9567 | 31.5171 | 10.1754 | 7.3132 | 9.6958 | 31.879 | 9.783 | 7.0312 | 9.203 | 32.3582 | 9.3263 | 6.703 | 7.8259 | 32.774 | 9.0668 | 6.5165 | 6.4141 | 33.1248 | 8.7914 | 6.3186 | 5.0017 | 33.9613 | 7.9412 | 5.7075 | 0.90959 | 34.7421 | 7.0871 | 5.0936 | -3.013 | 35.2866 | 6.3099 | 4.5351 | -6.2825 | 34.6009 | 5.6968 | 4.0944 | -8.4487 | 34.7415 | 5.7199 | 4.111 | -7.1602
GRANE RD & PRINNY HILL | ROSSENDALE | PADIHAM | 378312 | 422726 | 24.3676 | 8.1257 | 5.9276 | 15.3903 | 24.4795 | 7.9184 | 5.7764 | 15.1367 | 24.5723 | 7.907 | 5.768 | 14.6661 | 24.6547 | 7.6444 | 5.5765 | 14.5378 | 24.7849 | 7.4163 | 5.4101 | 14.3485 | 24.9502 | 6.897 | 5.0313 | 14.0962 | 25.1375 | 6.3698 | 4.6466 | 13.7707 | 25.354 | 6.101 | 4.4506 | 13.3426 | 25.5795 | 5.9312 | 4.3268 | 12.8058 | 25.8251 | 5.7691 | 4.2085 | 12.2147 | 26.6431 | 5.1885 | 3.7849 | 9.9348 | 27.3976 | 4.6108 | 3.3635 | 7.4359 | 26.0376 | 4.2236 | 3.081 | 5.6444 | 26.21 | 4.2515 | 3.1014 | 4.0849 | 23.9656 | 3.8875 | 2.8358 | 2.9789 | 24.3463 | 8.1257 | 5.9276 | 15.3903 | 24.4145 | 8.0129 | 5.8453 | 15.1396 | 24.4892 | 7.7983 | 5.6887 | 14.8362 | 24.5644 | 7.6953 | 5.6136 | 14.7371 | 24.6213 | 7.5968 | 5.5417 | 14.6145 | 24.6907 | 7.4608 | 5.4425 | 14.4583 | 24.7822 | 7.1248 | 5.1975 | 14.2561 | 24.8999 | 7.0391 | 5.135 | 14.005 | 25.0168 | 6.9445 | 5.0659 | 13.7391 | 25.1514 | 6.8235 | 4.9777 | 13.4373 | 25.6664 | 6.5771 | 4.7979 | 12.3029 | 26.3057 | 6.355 | 4.6359 | 10.8979 | 26.8796 | 6.0633 | 4.4231 | 9.4401 | 27.4639 | 5.9388 | 4.3323 | 7.8666 | 27.8438 | 5.8591 | 4.2741 | 6.8299 | 24.3785 | 8.1257 | 5.9276 | 15.3903 | 24.4993 | 7.9733 | 5.8164 | 15.1369 | 24.581 | 7.9039 | 5.7658 | 14.67 | 24.6662 | 7.5018 | 5.4725 | 14.551 | 24.7973 | 7.2654 | 5.3 | 14.3807 | 24.9592 | 6.6941 | 4.8832 | 14.1608 | 25.1239 | 6.2228 | 4.5394 | 13.8857 | 25.3183 | 5.9461 | 4.3376 | 13.5308 | 25.5126 | 5.783 | 4.2186 | 13.1 | 25.7279 | 5.6232 | 4.102 | 12.6118 | 26.5287 | 4.9872 | 3.6381 | 10.4458 | 26.7814 | 4.3442 | 3.169 | 7.8047 | 24.0388 | 3.8993 | 2.8445 | 5.8544 | 24.2399 | 3.932 | 2.8683 | 4.2636 | 22.1194 | 3.588 | 2.6174 | 3.2812 | 24.3785 | 8.1257 | 5.9276 | 15.3903 | 24.412 | 7.9915 | 5.8297 | 15.2579 | 24.5007 | 8.033 | 5.86 | 14.84 | 24.5692 | 7.6807 | 5.603 | 14.7493 | 24.6918 | 7.4347 | 5.4235 | 14.5877 | 24.8574 | 7.1646 | 5.2265 | 14.3411 | 25.0308 | 6.6647 | 4.8618 | 13.9348 | 25.2647 | 6.0798 | 4.4351 | 13.1936 | 25.5174 | 5.4742 | 3.9933 | 12.3527 | 25.792 | 5.2527 | 3.8318 | 11.4574 | 26.6501 | 4.9283 | 3.5951 | 8.7216 | 27.0449 | 4.3869 | 3.2002 | 6.3596 | 24.005 | 3.8938 | 2.8405 | 4.7283 | 21.3197 | 3.4583 | 2.5228 | 3.7373 | 20.347 | 3.3005 | 2.4077 | 4.019 | 24.3676 | 8.1257 | 5.9276 | 15.3903 | 24.4597 | 7.945 | 5.7957 | 15.1515 | 24.5467 | 7.9151 | 5.774 | 14.7121 | 24.5969 | 7.6751 | 5.5989 | 14.6369 | 24.6739 | 7.4843 | 5.4597 | 14.5305 | 24.7919 | 6.9983 | 5.1052 | 14.3529 | 24.9557 | 6.4815 | 4.7281 | 14.0918 | 25.1487 | 6.2126 | 4.532 | 13.7538 | 25.3571 | 6.0537 | 4.4161 | 13.3208 | 25.5858 | 5.9248 | 4.322 | 12.83 | 26.3018 | 5.4522 | 3.9773 | 11.0712 | 26.9998 | 5.0662 | 3.6957 | 9.3475 | 27.4726 | 4.8129 | 3.5109 | 8.1924 | 27.7954 | 4.9731 | 3.6278 | 7.4168 | 27.9174 | 4.9248 | 3.5926 | 7.1561 | 24.3676 | 8.1257 | 5.9276 | 15.3903 | 24.4421 | 8.0055 | 5.8399 | 15.2299 | 24.528 | 8.0142 | 5.8462 | 14.7721 | 24.6167 | 7.629 | 5.5653 | 14.641 | 24.7512 | 7.3587 | 5.368 | 14.4546 | 24.913 | 7.0865 | 5.1695 | 14.2228 | 25.068 | 6.6105 | 4.8222 | 13.8556 | 25.2976 | 6.0316 | 4.4 | 13.151 | 25.5312 | 5.4621 | 3.9845 | 12.3707 | 25.7844 | 5.2231 | 3.8101 | 11.5334 | 26.6385 | 4.8919 | 3.5686 | 8.792 | 26.5101 | 4.3002 | 3.1369 | 6.1845 | 23.1731 | 3.7589 | 2.7421 | 4.2759 | 20.287 | 3.2907 | 2.4006 | 3.0827 | 18.732 | 3.0385 | 2.2166 | 3.246
GRANGE | ULVERSTON | HARKER / HUTTON | 340240 | 478314 | 21.0128 | 21.0128 | 19.5744 | 11.6206 | 21.0648 | 21.0648 | 19.4603 | 10.9302 | 21.1333 | 21.1333 | 19.4055 | 10.7741 | 21.2188 | 21.2188 | 19.3568 | 10.71 | 21.3265 | 21.3265 | 19.2856 | 10.549 | 21.4464 | 21.4464 | 19.2127 | 10.3807 | 21.5708 | 21.5708 | 19.1454 | 10.2427 | 21.7207 | 21.7207 | 19.0874 | 10.1186 | 21.8194 | 21.8194 | 19.0318 | 10.0024 | 21.9001 | 21.9001 | 18.9811 | 9.9081 | 22.1003 | 22.1003 | 18.7342 | 8.9539 | 22.3273 | 22.3273 | 18.3998 | 7.0832 | 22.4945 | 22.4945 | 18.0972 | 5.4919 | 22.6383 | 22.6383 | 17.8519 | 3.8324 | 22.7351 | 22.7351 | 17.5351 | 2.2926 | 20.9961 | 20.9961 | 19.5744 | 11.6206 | 21.0647 | 21.0647 | 19.5272 | 11.3884 | 21.1411 | 21.1411 | 19.488 | 11.2702 | 21.2343 | 21.2343 | 19.4361 | 11.1427 | 21.3542 | 21.3542 | 19.3713 | 10.9706 | 21.4593 | 21.4593 | 19.3048 | 10.796 | 21.576 | 21.576 | 19.2112 | 10.5687 | 21.7095 | 21.7095 | 19.1317 | 10.2743 | 21.7848 | 21.7848 | 19.0745 | 10.119 | 21.8621 | 21.8621 | 19.0171 | 9.9652 | 22.0976 | 22.0976 | 18.8527 | 9.5064 | 22.3049 | 22.3049 | 18.7043 | 9.0382 | 22.4454 | 22.4454 | 18.5628 | 8.5905 | 22.5817 | 22.5817 | 18.4746 | 8.0342 | 22.6537 | 22.6537 | 18.3795 | 7.5757 | 21.0191 | 21.0191 | 19.5744 | 11.6206 | 21.0764 | 21.0764 | 19.4403 | 10.8442 | 21.1537 | 21.1537 | 19.367 | 10.6842 | 21.2526 | 21.2526 | 19.3023 | 10.6405 | 21.3773 | 21.3773 | 19.2181 | 10.5022 | 21.5066 | 21.5066 | 19.136 | 10.3607 | 21.6527 | 21.6527 | 19.0609 | 10.2632 | 21.8293 | 21.8293 | 18.9932 | 10.1799 | 21.9067 | 21.9067 | 18.9277 | 10.1064 | 21.972 | 21.972 | 18.8688 | 10.0504 | 22.1882 | 22.1882 | 18.5929 | 9.2216 | 22.4262 | 22.4262 | 18.223 | 7.4606 | 22.597 | 22.597 | 17.877 | 5.9678 | 22.7363 | 22.7363 | 17.5913 | 4.4244 | 22.8188 | 22.8188 | 17.2509 | 3.0156 | 21.0191 | 21.0191 | 19.5744 | 11.6206 | 21.0073 | 21.0073 | 19.4941 | 11.2369 | 21.0335 | 21.0335 | 19.4494 | 11.162 | 21.0746 | 21.0746 | 19.3858 | 11.1191 | 21.1424 | 21.1424 | 19.3044 | 10.9936 | 21.249 | 21.249 | 19.2213 | 10.8637 | 21.3694 | 21.3694 | 19.0429 | 10.6491 | 21.5116 | 21.5116 | 18.8228 | 10.0596 | 21.6199 | 21.6199 | 18.6166 | 9.4572 | 21.7251 | 21.7251 | 18.4214 | 8.8668 | 21.9528 | 21.9528 | 18.0705 | 7.165 | 22.1775 | 22.1775 | 17.7034 | 5.4951 | 22.3353 | 22.3353 | 17.3574 | 4.1516 | 22.4429 | 22.4429 | 17.0992 | 3.3093 | 22.4302 | 22.4302 | 16.9871 | 3.8379 | 21.0128 | 21.0128 | 19.5744 | 11.6206 | 21.0583 | 21.0583 | 19.518 | 11.3412 | 21.1079 | 21.1079 | 19.4756 | 11.2654 | 21.164 | 21.164 | 19.4314 | 11.2236 | 21.2385 | 21.2385 | 19.3745 | 11.1494 | 21.3482 | 21.3482 | 19.3169 | 11.0777 | 21.4824 | 21.4824 | 19.2574 | 10.9857 | 21.6225 | 21.6225 | 19.1996 | 10.8531 | 21.7132 | 21.7132 | 19.1392 | 10.6943 | 21.8024 | 21.8024 | 19.0809 | 10.5378 | 22.0184 | 22.0184 | 18.8888 | 9.9575 | 22.2189 | 22.2189 | 18.7182 | 9.2379 | 22.3642 | 22.3642 | 18.5704 | 8.7204 | 22.4915 | 22.4915 | 18.4848 | 8.1742 | 22.5451 | 22.5451 | 18.3506 | 7.9186 | 21.0128 | 21.0128 | 19.5744 | 11.6206 | 21.029 | 21.029 | 19.4479 | 10.907 | 21.0927 | 21.0927 | 19.3881 | 10.73 | 21.1782 | 21.1782 | 19.3154 | 10.6286 | 21.2862 | 21.2862 | 19.2254 | 10.4468 | 21.4036 | 21.4036 | 19.1352 | 10.271 | 21.531 | 21.531 | 18.9489 | 9.9989 | 21.7014 | 21.7014 | 18.7186 | 9.3396 | 21.8184 | 21.8184 | 18.5066 | 8.6978 | 21.9127 | 21.9127 | 18.3063 | 8.0669 | 22.1334 | 22.1334 | 17.9361 | 6.2394 | 22.3397 | 22.3397 | 17.5511 | 4.4666 | 22.4843 | 22.4843 | 17.1934 | 3.0181 | 22.577 | 22.577 | 16.9109 | 2.0341 | 22.5684 | 22.5684 | 16.758 | 2.3973
GREAT HARWOOD | HUNCOAT | PADIHAM | 373765 | 431955 | 17.9257 | 3.1498 | 2.2978 | 17.9257 | 18.0148 | 2.9222 | 2.1317 | 18.0148 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 17.9393 | 3.1498 | 2.2978 | 17.9393 | 18.0614 | 3.1151 | 2.2724 | 18.0614 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 17.9187 | 3.1498 | 2.2978 | 17.9187 | 17.2132 | 2.7922 | 2.0368 | 17.2132 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 17.9187 | 3.1498 | 2.2978 | 17.9187 | 17.9533 | 2.9122 | 2.1244 | 17.9533 | 16.0999 | 2.6116 | 1.9051 | 16.0999 | 14.5501 | 2.3602 | 1.7217 | 14.5501 | 11.7298 | 1.9027 | 1.388 | 11.7298 | 9.0407 | 1.4665 | 1.0698 | 9.0407 | 6.3136 | 1.0241 | 0.74709 | 6.3136 | 3.6889 | 0.59837 | 0.4365 | 3.6889 | 0.93992 | 0.15246 | 0.11122 | 0.93992 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 17.9257 | 3.1498 | 2.2978 | 17.9257 | 18.0913 | 3.0946 | 2.2574 | 18.0913 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 17.9257 | 3.1498 | 2.2978 | 17.9257 | 16.9584 | 2.7508 | 2.0067 | 16.9584 | 15.2162 | 2.4682 | 1.8005 | 15.2162 | 13.0372 | 2.1148 | 1.5427 | 13.0372 | 10.1599 | 1.648 | 1.2022 | 10.1599 | 7.3979 | 1.2 | 0.8754 | 7.3979 | 4.7164 | 0.76504 | 0.55809 | 4.7164 | 1.9766 | 0.32062 | 0.23389 | 1.9766 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914
GREEN LANE (ALTRINCHAM) | ALTRINCHAM | CARRINGTON | 378744 | 387772 | 31.1276 | 15.6235 | 11.2289 | 11.3161 | 31.2074 | 15.4711 | 11.1194 | 10.4923 | 31.3318 | 15.3848 | 11.0573 | 10.2208 | 31.4925 | 15.3101 | 11.0037 | 10.1078 | 31.6881 | 15.2175 | 10.9371 | 9.921 | 31.9109 | 15.1244 | 10.8702 | 9.729 | 32.1677 | 15.0267 | 10.8 | 9.5627 | 32.4847 | 14.9455 | 10.7416 | 9.4224 | 32.7201 | 14.8213 | 10.6524 | 9.2008 | 32.9404 | 14.7435 | 10.5965 | 9.0185 | 33.6337 | 14.3161 | 10.2892 | 7.1967 | 34.3848 | 13.5843 | 9.7633 | 3.653 | 34.9519 | 12.924 | 9.2887 | 0.60555 | 35.4733 | 12.3599 | 8.8833 | -2.7188 | 35.7489 | 11.8701 | 8.5313 | -5.6618 | 31.0861 | 15.6235 | 11.2289 | 11.3161 | 31.1399 | 15.5696 | 11.1902 | 11.0647 | 31.2008 | 15.5119 | 11.1487 | 10.9118 | 31.2865 | 15.4355 | 11.0938 | 10.771 | 31.4103 | 15.3452 | 11.0289 | 10.5664 | 31.5701 | 15.2512 | 10.9613 | 10.3341 | 31.763 | 15.0099 | 10.7879 | 10.0362 | 31.9818 | 14.9009 | 10.7096 | 9.6843 | 32.1043 | 14.8187 | 10.6505 | 9.3555 | 32.2311 | 14.7318 | 10.5881 | 9.0223 | 32.6168 | 14.4688 | 10.399 | 8.0412 | 32.9838 | 14.2478 | 10.2402 | 7.1128 | 33.3074 | 14.0171 | 10.0744 | 6.231 | 33.6349 | 13.9022 | 9.9918 | 5.2935 | 33.8883 | 13.8081 | 9.9241 | 4.6211 | 31.1451 | 15.6235 | 11.2289 | 11.3161 | 31.238 | 15.4424 | 11.0987 | 10.4032 | 31.3831 | 15.3308 | 11.0186 | 10.1467 | 31.5744 | 15.2388 | 10.9524 | 10.0979 | 31.8079 | 15.1133 | 10.8622 | 9.9789 | 32.0755 | 15.0337 | 10.805 | 9.8642 | 32.3865 | 14.8679 | 10.6859 | 9.376 | 32.7701 | 14.6071 | 10.4984 | 8.9234 | 33.0444 | 14.5641 | 10.4675 | 8.4043 | 33.3005 | 14.4286 | 10.3701 | 7.9017 | 34.0968 | 13.8024 | 9.9201 | 5.5593 | 34.8213 | 13.0516 | 9.3804 | 2.322 | 35.2027 | 12.3896 | 8.9047 | -0.45234 | 35.5449 | 11.8109 | 8.4887 | -3.4575 | 35.75 | 11.3383 | 8.1491 | -6.047 | 31.1451 | 15.6235 | 11.2289 | 11.3161 | 31.1091 | 15.5589 | 11.1825 | 11.0074 | 31.1579 | 15.5155 | 11.1513 | 10.9181 | 31.2405 | 15.4173 | 11.0807 | 10.9116 | 31.3771 | 15.3086 | 11.0026 | 10.7894 | 31.6018 | 15.1606 | 10.8962 | 10.6233 | 31.8891 | 15.0123 | 10.7896 | 9.8526 | 32.2286 | 14.6749 | 10.5471 | 8.4119 | 32.4859 | 14.339 | 10.3057 | 6.8906 | 32.7353 | 14.0044 | 10.0653 | 5.3719 | 33.4962 | 13.0747 | 9.397 | 1.3524 | 34.3145 | 12.3559 | 8.8804 | -1.7322 | 34.9175 | 11.734 | 8.4334 | -4.2837 | 35.1774 | 11.5556 | 8.3052 | -5.9321 | 35.1234 | 11.554 | 8.3041 | -4.7283 | 31.1276 | 15.6235 | 11.2289 | 11.3161 | 31.1906 | 15.5582 | 11.182 | 10.9616 | 31.2647 | 15.5091 | 11.1467 | 10.8528 | 31.3513 | 15.4536 | 11.1068 | 10.8528 | 31.4719 | 15.3864 | 11.0585 | 10.8336 | 31.6703 | 15.3258 | 11.0149 | 10.7649 | 31.9333 | 15.2434 | 10.9557 | 10.6733 | 32.2194 | 15.1712 | 10.9039 | 10.587 | 32.4266 | 15.0556 | 10.8207 | 10.387 | 32.6298 | 14.9636 | 10.7547 | 10.1971 | 33.27 | 14.7393 | 10.5934 | 9.4829 | 33.9569 | 14.4463 | 10.3828 | 8.3955 | 34.4757 | 14.1748 | 10.1877 | 7.5481 | 34.8763 | 14.0477 | 10.0963 | 6.7484 | 34.9962 | 14.0056 | 10.0661 | 6.3757 | 31.1276 | 15.6235 | 11.2289 | 11.3161 | 31.138 | 15.4701 | 11.1187 | 10.546 | 31.2529 | 15.3855 | 11.0579 | 10.2539 | 31.4128 | 15.2609 | 10.9683 | 10.1061 | 31.6109 | 15.1318 | 10.8755 | 9.8612 | 31.8337 | 14.9676 | 10.7575 | 9.6205 | 32.1 | 14.8022 | 10.6386 | 8.7571 | 32.4643 | 14.4393 | 10.3778 | 7.1785 | 32.743 | 14.0845 | 10.1228 | 5.5485 | 33.0078 | 13.7302 | 9.8682 | 3.9237 | 33.7628 | 12.749 | 9.163 | -0.40035 | 34.4824 | 11.9784 | 8.6091 | -3.7256 | 35.0155 | 11.3181 | 8.1345 | -6.5044 | 35.3419 | 11.0839 | 7.9662 | -8.4286 | 35.2973 | 11.0328 | 7.9295 | -7.5395
GREEN LANE (HAZEL GROVE) | HAZEL GROVE | BREDBURY | 391570 | 387132 | 31.3717 | 8.9969 | 6.4662 | 11.2774 | 31.4774 | 8.7133 | 6.2624 | 10.395 | 31.6463 | 8.2113 | 5.9016 | 9.9179 | 31.8497 | 7.8635 | 5.6517 | 9.7202 | 31.9889 | 7.7921 | 5.6003 | 9.4307 | 32.1486 | 7.5117 | 5.3988 | 9.1351 | 32.3356 | 7.1782 | 5.1591 | 8.8681 | 32.5649 | 6.9816 | 5.0178 | 8.6253 | 32.7586 | 6.7914 | 4.8811 | 8.2997 | 32.9464 | 6.616 | 4.755 | 7.9865 | 33.5613 | 5.9383 | 4.268 | 5.6863 | 30.3699 | 5.0002 | 3.5937 | 1.5523 | 25.4224 | 4.1856 | 3.0083 | -1.9473 | 28.0444 | 4.6173 | 3.3185 | -5.7616 | 31.6015 | 5.2029 | 3.7395 | -9.1514 | 31.3378 | 8.9969 | 6.4662 | 11.2774 | 31.424 | 8.8808 | 6.3828 | 11.0556 | 31.5282 | 8.5384 | 6.1367 | 10.8464 | 31.653 | 8.2518 | 5.9307 | 10.6485 | 31.8171 | 7.8296 | 5.6273 | 10.3952 | 32.023 | 7.8179 | 5.6189 | 10.1181 | 32.25 | 7.4285 | 5.339 | 9.7573 | 32.4644 | 7.2728 | 5.2271 | 9.2945 | 32.5813 | 7.1341 | 5.1274 | 8.8883 | 32.703 | 6.9964 | 5.0284 | 8.4757 | 33.086 | 6.5798 | 4.729 | 7.1672 | 33.4725 | 6.2606 | 4.4996 | 5.8694 | 33.8274 | 5.9383 | 4.268 | 4.6166 | 34.1926 | 6.6443 | 4.7754 | 3.2362 | 34.4554 | 7.4025 | 5.3203 | 2.2453 | 31.386 | 8.9969 | 6.4662 | 11.2774 | 31.5052 | 8.6606 | 6.2246 | 10.3298 | 31.6962 | 8.1585 | 5.8637 | 9.868 | 31.8874 | 7.818 | 5.619 | 9.7294 | 32.0442 | 7.6492 | 5.4976 | 9.5001 | 32.2241 | 7.3186 | 5.26 | 9.2738 | 32.4353 | 6.9905 | 5.0242 | 9.1029 | 32.693 | 6.7845 | 4.8762 | 8.9655 | 32.8949 | 6.5974 | 4.7417 | 8.7772 | 33.0892 | 6.403 | 4.602 | 8.5938 | 33.6969 | 5.6285 | 4.0453 | 6.6194 | 27.978 | 4.6064 | 3.3107 | 2.781 | 22.4339 | 3.6936 | 2.6546 | -0.47971 | 24.258 | 3.9939 | 2.8705 | -3.9699 | 27.5157 | 4.5303 | 3.256 | -6.9826 | 31.386 | 8.9969 | 6.4662 | 11.2774 | 31.3903 | 8.7511 | 6.2896 | 10.8383 | 31.481 | 8.4186 | 6.0506 | 10.5248 | 31.6019 | 8.277 | 5.9488 | 10.4248 | 31.7354 | 8.12 | 5.836 | 10.1973 | 31.8827 | 7.867 | 5.6542 | 9.9296 | 32.079 | 7.5654 | 5.4374 | 9.4602 | 32.3271 | 7.1627 | 5.1479 | 8.2426 | 32.5446 | 6.7502 | 4.8515 | 6.948 | 32.7608 | 6.3287 | 4.5486 | 5.6493 | 31.8096 | 5.2372 | 3.7641 | 1.8699 | 25.7861 | 4.2455 | 3.0513 | -1.8144 | 21.7012 | 3.5729 | 2.5679 | -4.815 | 30.8687 | 5.0823 | 3.6527 | -6.8138 | 29.281 | 4.8209 | 3.4649 | -5.7051 | 31.3717 | 8.9969 | 6.4662 | 11.2774 | 31.4612 | 8.8192 | 6.3385 | 10.9013 | 31.5789 | 8.3143 | 5.9757 | 10.583 | 31.7062 | 7.998 | 5.7483 | 10.4916 | 31.846 | 7.9852 | 5.7391 | 10.3818 | 31.9846 | 7.7497 | 5.5699 | 10.2335 | 32.1696 | 7.4317 | 5.3413 | 10.0604 | 32.373 | 7.2488 | 5.2099 | 9.8846 | 32.5405 | 7.06 | 5.0742 | 9.5874 | 32.7089 | 6.8892 | 4.9514 | 9.2821 | 33.2514 | 6.4432 | 4.6308 | 8.2028 | 33.8167 | 6.0212 | 4.3276 | 6.8332 | 34.2047 | 5.6677 | 4.0735 | 5.7679 | 34.5395 | 6.6533 | 4.7819 | 4.7796 | 34.7092 | 7.8059 | 5.6103 | 4.2073 | 31.3717 | 8.9969 | 6.4662 | 11.2774 | 31.4216 | 8.6697 | 6.2311 | 10.4676 | 31.5826 | 8.3024 | 5.9671 | 9.9759 | 31.7804 | 8.1361 | 5.8476 | 9.7409 | 31.9207 | 7.9473 | 5.7119 | 9.3922 | 32.0782 | 7.6724 | 5.5143 | 9.0465 | 32.272 | 7.3522 | 5.2841 | 8.4846 | 32.5464 | 6.9224 | 4.9752 | 7.1333 | 32.7764 | 6.4913 | 4.6654 | 5.7417 | 33.0015 | 6.0522 | 4.3498 | 4.3476 | 29.7757 | 4.9023 | 3.5234 | 0.2819 | 23.4177 | 3.8555 | 2.7711 | -3.6477 | 19.0171 | 3.131 | 2.2503 | -6.8919 | 27.8427 | 4.5841 | 3.2947 | -9.1928 | 25.8762 | 4.2603 | 3.062 | -8.4316
GREEN ST T11 | WIGAN | WASHWAY FARM / KIRKBY | 358235 | 404898 | 18.7237 | 18.7237 | 17.8637 | 7.418 | 18.7968 | 18.7968 | 17.7748 | 6.8619 | 18.8682 | 18.8682 | 17.7184 | 6.5994 | 18.9524 | 18.9524 | 17.6714 | 6.4655 | 19.0632 | 19.0632 | 17.6092 | 6.3329 | 19.1799 | 19.1799 | 17.542 | 6.1991 | 19.2955 | 19.2955 | 17.4678 | 6.0751 | 19.4168 | 19.4168 | 17.4161 | 5.9518 | 19.5262 | 19.5262 | 17.369 | 5.7796 | 19.6305 | 19.6305 | 17.35 | 5.6196 | 19.9942 | 19.9942 | 17.2543 | 4.8417 | 20.3704 | 20.3704 | 17.3785 | 3.6665 | 20.6581 | 20.6581 | 18.0013 | 2.7407 | 20.9316 | 20.9316 | 18.7533 | 1.8317 | 21.1525 | 21.1525 | 18.8491 | 0.98296 | 18.7229 | 18.7229 | 17.8637 | 7.418 | 18.7859 | 18.7859 | 17.837 | 7.2715 | 18.8365 | 18.8365 | 17.8004 | 7.1082 | 18.8978 | 18.8978 | 17.7602 | 6.9896 | 18.977 | 18.977 | 17.7193 | 6.8805 | 19.0632 | 19.0632 | 17.6762 | 6.7629 | 19.1661 | 19.1661 | 17.5882 | 6.6197 | 19.2904 | 19.2904 | 17.5355 | 6.4004 | 19.377 | 19.377 | 17.4938 | 6.2569 | 19.4659 | 19.4659 | 17.4468 | 6.0704 | 19.7358 | 19.7358 | 17.3122 | 5.526 | 20.0091 | 20.0091 | 17.2001 | 5.0032 | 20.2176 | 20.2176 | 17.5635 | 4.5501 | 20.3861 | 20.3861 | 18.1894 | 4.0872 | 20.5069 | 20.5069 | 18.2929 | 3.7602 | 18.724 | 18.724 | 17.8637 | 7.418 | 18.8001 | 18.8001 | 17.7564 | 6.78 | 18.8723 | 18.8723 | 17.6806 | 6.5015 | 18.9588 | 18.9588 | 17.6187 | 6.3657 | 19.071 | 19.071 | 17.5467 | 6.233 | 19.1892 | 19.1892 | 17.4728 | 6.0995 | 19.3069 | 19.3069 | 17.385 | 5.9749 | 19.4299 | 19.4299 | 17.3401 | 5.8525 | 19.5402 | 19.5402 | 17.2814 | 5.7132 | 19.643 | 19.643 | 17.2629 | 5.5905 | 20.0108 | 20.0108 | 17.1405 | 4.9295 | 20.3873 | 20.3873 | 17.2507 | 3.879 | 20.6715 | 20.6715 | 17.8509 | 3.086 | 20.9286 | 20.9286 | 18.5784 | 2.3662 | 21.1186 | 21.1186 | 18.6795 | 1.8356 | 18.724 | 18.724 | 17.8637 | 7.418 | 18.7495 | 18.7495 | 17.7909 | 7.0237 | 18.7931 | 18.7931 | 17.7428 | 6.8261 | 18.8492 | 18.8492 | 17.6951 | 6.7333 | 18.9202 | 18.9202 | 17.6295 | 6.6355 | 19.0223 | 19.0223 | 17.5447 | 6.5159 | 19.1381 | 19.1381 | 17.45 | 6.3418 | 19.2622 | 19.2622 | 17.522 | 5.9963 | 19.3991 | 19.3991 | 17.5226 | 5.6145 | 19.5325 | 19.5325 | 17.6077 | 5.2467 | 19.9358 | 19.9358 | 19.3145 | 4.1939 | 20.3381 | 20.3381 | 19.0964 | 3.1893 | 20.6158 | 20.6158 | 18.9115 | 2.4512 | 20.8239 | 20.8239 | 18.7292 | 1.9695 | 20.8784 | 20.8784 | 18.6816 | 2.4417 | 18.7237 | 18.7237 | 17.8637 | 7.418 | 18.7875 | 18.7875 | 17.8233 | 7.2186 | 18.8432 | 18.8432 | 17.7797 | 7.0495 | 18.9011 | 18.9011 | 17.7387 | 6.9552 | 18.9714 | 18.9714 | 17.685 | 6.884 | 19.0568 | 19.0568 | 17.6245 | 6.7983 | 19.1566 | 19.1566 | 17.5528 | 6.7006 | 19.2677 | 19.2677 | 17.5025 | 6.5958 | 19.3755 | 19.3755 | 17.4572 | 6.427 | 19.4858 | 19.4858 | 17.4373 | 6.2594 | 19.8472 | 19.8472 | 17.3747 | 5.731 | 20.0881 | 20.0881 | 17.5873 | 5.1755 | 20.2581 | 20.2581 | 18.2894 | 4.8059 | 20.4034 | 20.4034 | 19.1285 | 4.5014 | 20.4657 | 20.4657 | 19.3335 | 4.4507 | 18.7237 | 18.7237 | 17.8637 | 7.418 | 18.7659 | 18.7659 | 17.7532 | 6.759 | 18.8342 | 18.8342 | 17.6921 | 6.4703 | 18.9245 | 18.9245 | 17.6373 | 6.3272 | 19.0413 | 19.0413 | 17.5656 | 6.185 | 19.162 | 19.162 | 17.48 | 6.0447 | 19.3204 | 19.3204 | 17.3805 | 5.8543 | 19.6094 | 19.6094 | 17.4468 | 5.471 | 19.7412 | 19.7412 | 17.4438 | 5.0658 | 19.8694 | 19.8694 | 17.5258 | 4.677 | 20.2474 | 20.2474 | 19.2221 | 3.5761 | 20.6054 | 20.6054 | 19.005 | 2.547 | 20.8735 | 20.8735 | 18.7929 | 1.6884 | 21.0534 | 21.0534 | 18.6032 | 1.1338 | 21.0306 | 21.0306 | 18.5437 | 1.5099
GREEN ST T12 & T13 | WIGAN | WASHWAY FARM / KIRKBY | 358225 | 404888 | 31.7664 | 9.6674 | 7.0522 | 10.3768 | 31.8822 | 9.3429 | 6.8155 | 9.0683 | 32.0281 | 9.1671 | 6.6873 | 8.686 | 32.2077 | 8.9556 | 6.533 | 8.1787 | 32.4387 | 8.623 | 6.2903 | 7.5331 | 32.7304 | 8.2901 | 6.0475 | 6.8545 | 33.0962 | 7.9683 | 5.8128 | 6.1981 | 33.5584 | 7.691 | 5.6105 | 5.5776 | 33.9162 | 7.4201 | 5.4129 | 4.9295 | 34.2027 | 7.2614 | 5.2971 | 4.2981 | 35.438 | 6.5827 | 4.802 | 2.0683 | 36.4698 | 6.2005 | 4.5232 | -2.0087 | 37.0671 | 6.5999 | 4.8145 | -5.557 | 37.4913 | 7.5825 | 5.5313 | -9.2054 | 37.6988 | 7.1252 | 5.1978 | -12.4772 | 31.7377 | 9.6674 | 7.0522 | 10.3768 | 31.8442 | 9.568 | 6.9797 | 10.0488 | 31.9501 | 9.4462 | 6.8909 | 9.8102 | 32.0695 | 9.3086 | 6.7905 | 9.6019 | 32.2218 | 9.1523 | 6.6764 | 9.3504 | 32.4175 | 8.9886 | 6.5571 | 9.0633 | 32.6588 | 8.5746 | 6.2551 | 8.6901 | 32.9436 | 8.3918 | 6.1217 | 8.2198 | 33.1537 | 8.2584 | 6.0244 | 7.9145 | 33.3885 | 8.1313 | 5.9317 | 7.603 | 34.2516 | 7.7371 | 5.6441 | 6.6216 | 35.121 | 7.4198 | 5.4126 | 5.4769 | 35.8034 | 7.7893 | 5.6822 | 4.3842 | 36.5229 | 8.8093 | 6.4262 | 3.217 | 37.0231 | 9.0605 | 6.6095 | 2.3778 | 31.7743 | 9.6674 | 7.0522 | 10.3768 | 31.8878 | 9.2805 | 6.77 | 8.8842 | 32.0396 | 9.0535 | 6.6044 | 8.4774 | 32.2292 | 8.7939 | 6.415 | 7.9903 | 32.4698 | 8.4108 | 6.1355 | 7.1937 | 32.7688 | 8.0258 | 5.8547 | 6.3734 | 33.1395 | 7.6632 | 5.5902 | 5.5233 | 33.6051 | 7.3319 | 5.3485 | 4.7262 | 33.862 | 7.0179 | 5.1195 | 4.0729 | 34.1159 | 6.8399 | 4.9896 | 3.5271 | 35.3254 | 6.1532 | 4.4887 | 1.5243 | 34.8623 | 5.655 | 4.1252 | -2.3393 | 36.8347 | 5.9749 | 4.3586 | -5.6045 | 37.5513 | 6.9108 | 5.0414 | -8.9595 | 37.6977 | 6.4154 | 4.68 | -11.923 | 31.7744 | 9.6674 | 7.0522 | 10.3768 | 31.7909 | 9.4289 | 6.8783 | 9.593 | 31.8784 | 9.3058 | 6.7884 | 9.3605 | 31.9957 | 9.0696 | 6.6161 | 8.9129 | 32.1742 | 8.7262 | 6.3656 | 8.132 | 32.454 | 8.4008 | 6.1283 | 7.3093 | 32.8338 | 7.7722 | 5.6697 | 6.1936 | 33.3148 | 7.3348 | 5.3506 | 4.3003 | 33.7878 | 6.9379 | 5.0611 | 2.4926 | 34.2834 | 6.6814 | 4.874 | 0.79268 | 35.3501 | 8.8941 | 6.4881 | -3.0691 | 36.2174 | 8.0356 | 5.8619 | -6.7035 | 36.7636 | 7.1426 | 5.2104 | -9.6767 | 37.0632 | 6.3715 | 4.6479 | -11.5063 | 36.9821 | 6.2195 | 4.5371 | -10.3148 | 31.7663 | 9.6674 | 7.0522 | 10.3768 | 31.8609 | 9.5285 | 6.9509 | 10.0061 | 31.9652 | 9.3971 | 6.8551 | 9.8444 | 32.0776 | 9.2052 | 6.7151 | 9.4224 | 32.2272 | 8.913 | 6.5019 | 8.9798 | 32.4601 | 8.6191 | 6.2875 | 8.509 | 32.7793 | 8.3243 | 6.0724 | 7.9941 | 33.1583 | 8.0546 | 5.8757 | 7.4261 | 33.5234 | 7.7799 | 5.6754 | 6.7652 | 33.8384 | 7.6136 | 5.554 | 6.0864 | 34.7676 | 7.1351 | 5.2049 | 4.9388 | 35.7091 | 7.2736 | 5.306 | 3.6737 | 36.3662 | 8.167 | 5.9577 | 2.7753 | 36.8895 | 9.6992 | 7.0754 | 1.8998 | 37.0549 | 9.8293 | 7.1703 | 1.6318 | 31.7663 | 9.6674 | 7.0522 | 10.3768 | 31.8028 | 9.2931 | 6.7792 | 8.9657 | 31.9304 | 9.1252 | 6.6567 | 8.5352 | 32.0957 | 8.8689 | 6.4697 | 7.9936 | 32.3091 | 8.5087 | 6.207 | 7.1242 | 32.5718 | 8.1702 | 5.96 | 6.2369 | 32.9067 | 7.529 | 5.4923 | 5.0575 | 33.3656 | 7.0612 | 5.151 | 3.069 | 33.8022 | 6.662 | 4.8598 | 1.2171 | 34.265 | 6.3954 | 4.6654 | -0.52643 | 35.4455 | 8.5671 | 6.2496 | -4.5529 | 36.3803 | 7.6557 | 5.5847 | -8.4079 | 37.011 | 6.6976 | 4.8858 | -11.7102 | 36.1325 | 5.861 | 4.2755 | -13.9073 | 34.8248 | 5.6489 | 4.1208 | -13.0544
GREENFIELD | HARTSHEAD-HEYROD | STALYBRIDGE | 399322 | 404583 | 29.2275 | 12.0784 | 8.681 | 18.1845 | 29.2897 | 11.94 | 8.5815 | 18.0167 | 29.3739 | 11.7771 | 8.4644 | 17.8529 | 29.4815 | 11.5802 | 8.3229 | 17.6992 | 29.6198 | 11.3201 | 8.136 | 17.4816 | 29.7655 | 10.9867 | 7.8964 | 17.2623 | 29.9048 | 10.9236 | 7.851 | 17.0739 | 30.07 | 10.8171 | 7.7745 | 16.8944 | 30.2143 | 10.7294 | 7.7114 | 16.6623 | 30.3532 | 10.7392 | 7.7184 | 16.4512 | 30.9153 | 10.4449 | 7.5069 | 14.7393 | 31.6465 | 9.9582 | 7.1571 | 12.0618 | 32.1275 | 9.4916 | 6.8218 | 9.8812 | 32.5207 | 8.962 | 6.4412 | 7.4473 | 32.786 | 8.402 | 6.0387 | 5.3725 | 29.1967 | 12.0784 | 8.681 | 18.1845 | 29.258 | 12.0094 | 8.6314 | 18.0279 | 29.3182 | 11.9289 | 8.5735 | 17.8734 | 29.3915 | 11.8416 | 8.5108 | 17.7091 | 29.4878 | 11.7232 | 8.4257 | 17.4972 | 29.5837 | 11.5855 | 8.3267 | 17.261 | 29.6972 | 11.4179 | 8.2063 | 16.968 | 29.8182 | 11.2909 | 8.115 | 16.6041 | 29.9092 | 11.1822 | 8.0368 | 16.3055 | 30.0034 | 11.0649 | 7.9526 | 16.0025 | 30.296 | 10.7225 | 7.7065 | 15.0904 | 30.5902 | 10.4097 | 7.4816 | 14.1099 | 30.8522 | 10.0537 | 7.2258 | 13.171 | 31.123 | 9.6912 | 6.9653 | 12.2236 | 31.3282 | 9.5533 | 6.8661 | 11.6088 | 29.2336 | 12.0784 | 8.681 | 18.1845 | 29.301 | 11.9167 | 8.5648 | 18.0319 | 29.3939 | 11.7023 | 8.4107 | 17.8939 | 29.5143 | 11.4429 | 8.2243 | 17.7835 | 29.6685 | 11.1255 | 7.9961 | 17.5527 | 29.8124 | 10.8993 | 7.8335 | 17.3287 | 29.9673 | 10.7636 | 7.736 | 17.1548 | 30.1507 | 10.7594 | 7.733 | 17 | 30.3045 | 10.7326 | 7.7138 | 16.7986 | 30.4514 | 10.6977 | 7.6887 | 16.6197 | 31.042 | 10.3088 | 7.4091 | 15.0684 | 31.8178 | 9.6883 | 6.9632 | 12.5445 | 32.3256 | 9.181 | 6.5986 | 10.4874 | 32.6738 | 8.5689 | 6.1586 | 8.4121 | 32.9205 | 8.0016 | 5.7509 | 6.7756 | 29.2336 | 12.0784 | 8.681 | 18.1845 | 29.2305 | 11.9641 | 8.5988 | 18.2537 | 29.2717 | 11.7836 | 8.4691 | 18.1976 | 29.3355 | 11.4716 | 8.2449 | 18.1311 | 29.4388 | 11.0923 | 7.9722 | 17.9203 | 29.5901 | 10.9609 | 7.8778 | 17.6864 | 29.7915 | 11.0639 | 7.9518 | 17.3307 | 30.067 | 10.9207 | 7.8489 | 16.4812 | 30.2903 | 10.7337 | 7.7145 | 15.5779 | 30.5048 | 10.5331 | 7.5703 | 14.7402 | 31.1522 | 10.0038 | 7.1899 | 12.313 | 31.7583 | 9.3441 | 6.7158 | 9.9237 | 32.1243 | 8.7527 | 6.2907 | 7.9915 | 32.4041 | 8.2056 | 5.8975 | 6.7025 | 32.4525 | 8.0508 | 5.7863 | 7.4418 | 29.2275 | 12.0784 | 8.681 | 18.1845 | 29.2801 | 11.9632 | 8.5982 | 18.0537 | 29.3382 | 11.8114 | 8.4891 | 17.9371 | 29.405 | 11.6306 | 8.3592 | 17.8523 | 29.4939 | 11.399 | 8.1927 | 17.7502 | 29.6238 | 11.0912 | 7.9714 | 17.6194 | 29.761 | 11.002 | 7.9073 | 17.472 | 29.9098 | 10.9188 | 7.8476 | 17.3174 | 30.0422 | 10.7889 | 7.7542 | 17.089 | 30.1759 | 10.8117 | 7.7706 | 16.8639 | 30.6103 | 10.6636 | 7.6641 | 15.9393 | 31.0725 | 10.4558 | 7.5148 | 14.749 | 31.4116 | 10.2423 | 7.3613 | 13.9146 | 31.7299 | 10.0463 | 7.2205 | 13.1651 | 31.9136 | 9.7869 | 7.034 | 12.7602 | 29.2275 | 12.0784 | 8.681 | 18.1845 | 29.2501 | 11.9419 | 8.5829 | 18.1762 | 29.3293 | 11.7397 | 8.4375 | 18.0296 | 29.4383 | 11.4113 | 8.2015 | 17.8641 | 29.5794 | 11.0262 | 7.9247 | 17.5631 | 29.7294 | 10.8808 | 7.8202 | 17.2673 | 29.8989 | 10.9649 | 7.8807 | 16.8379 | 30.1869 | 10.802 | 7.7636 | 15.8832 | 30.433 | 10.6007 | 7.6189 | 14.9023 | 30.6571 | 10.3735 | 7.4556 | 13.9882 | 31.3126 | 9.7981 | 7.0421 | 11.2958 | 31.9349 | 9.0984 | 6.5392 | 8.6885 | 32.2905 | 8.4644 | 6.0835 | 6.5548 | 32.5493 | 7.8829 | 5.6656 | 5.0191 | 32.6022 | 7.6789 | 5.519 | 5.4821
GREENHILL | GREENHILL | WHITEGATE | 393262 | 404755 | 27.4627 | 4.4547 | 3.2497 | 27.4627 | 25.2298 | 4.0925 | 2.9854 | 25.2298 | 18.9307 | 3.0707 | 2.2401 | 18.9307 | 12.0605 | 1.9563 | 1.4271 | 12.0605 | 4.883 | 0.79207 | 0.57781 | 4.883 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 27.4627 | 4.4547 | 3.2497 | 27.4627 | 26.5928 | 4.3136 | 3.1467 | 26.5928 | 22.2074 | 3.6023 | 2.6278 | 22.2074 | 17.4438 | 2.8296 | 2.0641 | 17.4438 | 12.5221 | 2.0312 | 1.4817 | 12.5221 | 7.3179 | 1.187 | 0.86592 | 7.3179 | 0.36468 | 0.059155 | 0.043153 | 0.36468 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 27.4627 | 4.4547 | 3.2497 | 27.4627 | 24.6253 | 3.9945 | 2.9139 | 24.6253 | 17.5033 | 2.8392 | 2.0712 | 17.5033 | 9.6893 | 1.5717 | 1.1465 | 9.6893 | 2.0131 | 0.32654 | 0.23821 | 2.0131 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 1.5802 | 27.4627 | 4.4547 | 3.2497 | 27.4627 | 25.5361 | 4.1422 | 3.0217 | 25.5361 | 22.3246 | 3.6213 | 2.6417 | 22.3246 | 17.8197 | 2.8905 | 2.1086 | 17.8197 | 13.2753 | 2.1534 | 1.5709 | 13.2753 | 7.8763 | 1.2776 | 0.932 | 7.8763 | 4.2834 | 0.69481 | 0.50685 | 4.2834 | 0.90262 | 0.14641 | 0.10681 | 0.90262 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 27.4627 | 4.4547 | 3.2497 | 27.4627 | 26.1805 | 4.2467 | 3.0979 | 26.1805 | 20.106 | 3.2614 | 2.3791 | 20.106 | 13.4059 | 2.1746 | 1.5863 | 13.4059 | 6.4737 | 1.0501 | 0.76603 | 6.4737 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 27.4627 | 4.4547 | 3.2497 | 27.4627 | 24.7142 | 4.0089 | 2.9244 | 24.7142 | 21.1557 | 3.4317 | 2.5034 | 21.1557 | 16.4555 | 2.6692 | 1.9472 | 16.4555 | 11.7915 | 1.9127 | 1.3953 | 11.7915 | 6.2897 | 1.0203 | 0.74426 | 6.2897 | 2.6129 | 0.42384 | 0.30918 | 2.6129 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 1.6563 | 2.6914 | 0.43658 | 0.31848 | 1.1138
GRIFFIN | LOWER DARWEN | ROCHDALE | 367171 | 427130 | 28.8154 | 16.6839 | 12.1707 | 12.3013 | 28.9213 | 16.5242 | 12.0542 | 11.6989 | 29.0447 | 16.3385 | 11.9187 | 11.4508 | 29.1788 | 16.2708 | 11.8693 | 11.2187 | 29.3609 | 16.1177 | 11.7576 | 10.8687 | 29.5725 | 15.9111 | 11.6069 | 10.4986 | 29.8157 | 15.6556 | 11.4206 | 10.1505 | 30.1042 | 15.3753 | 11.216 | 9.8052 | 30.354 | 15.2219 | 11.1041 | 9.3728 | 30.6059 | 15.0666 | 10.9909 | 8.9553 | 31.3891 | 14.2998 | 10.4315 | 6.5017 | 32.1045 | 13.5147 | 9.8588 | 2.7589 | 32.6037 | 12.959 | 9.4534 | -0.050449 | 33.0172 | 12.4025 | 9.0475 | -2.573 | 33.2525 | 11.9372 | 8.708 | -4.0375 | 28.796 | 16.6839 | 12.1707 | 12.3013 | 28.8889 | 16.611 | 12.1175 | 12.0083 | 28.9691 | 16.5593 | 12.0798 | 11.8555 | 29.0604 | 16.4863 | 12.0265 | 11.6541 | 29.1876 | 16.329 | 11.9118 | 11.384 | 29.343 | 16.1242 | 11.7624 | 11.0843 | 29.5375 | 15.8826 | 11.5862 | 10.6937 | 29.7691 | 15.7046 | 11.4563 | 10.2131 | 29.8903 | 15.5864 | 11.3701 | 9.8945 | 30.0236 | 15.4445 | 11.2666 | 9.556 | 30.4734 | 14.9774 | 10.9258 | 8.4828 | 30.9667 | 14.6572 | 10.6922 | 7.3162 | 31.4345 | 14.5962 | 10.6477 | 6.2571 | 31.9146 | 14.313 | 10.4411 | 5.1819 | 32.2412 | 13.9487 | 10.1753 | 4.4594 | 28.8236 | 16.6839 | 12.1707 | 12.3013 | 28.9495 | 16.4684 | 12.0134 | 11.5473 | 29.1094 | 16.1884 | 11.8092 | 11.1786 | 29.3012 | 16.0916 | 11.7386 | 10.8391 | 29.5343 | 15.7802 | 11.5114 | 10.3725 | 29.7999 | 15.576 | 11.3625 | 9.8816 | 30.1025 | 15.2237 | 11.1055 | 9.426 | 30.4554 | 15.0184 | 10.9557 | 8.9641 | 30.7248 | 14.7841 | 10.7848 | 8.4686 | 30.9483 | 14.5235 | 10.5947 | 7.9222 | 31.73 | 13.5655 | 9.8959 | 5.0288 | 32.5262 | 12.614 | 9.2017 | 1.317 | 33.0644 | 12.0015 | 8.7549 | -1.1448 | 33.4716 | 11.4379 | 8.3438 | -2.956 | 33.6346 | 11.079 | 8.0819 | -3.3584 | 28.8236 | 16.6839 | 12.1707 | 12.3013 | 28.8243 | 16.5607 | 12.0808 | 12.0462 | 28.9017 | 16.3257 | 11.9094 | 11.8187 | 29.0035 | 16.3072 | 11.8959 | 11.542 | 29.1573 | 16.0164 | 11.6837 | 11.1123 | 29.3861 | 15.7702 | 11.5041 | 10.6294 | 29.6818 | 15.5387 | 11.3353 | 9.9422 | 30.0414 | 15.1631 | 11.0613 | 8.549 | 30.3447 | 14.7481 | 10.7586 | 7.1588 | 30.6249 | 14.2871 | 10.4223 | 5.8044 | 31.4724 | 13.7099 | 10.0012 | 2.0896 | 32.1776 | 12.7953 | 9.334 | -0.85938 | 32.626 | 12.0494 | 8.7898 | -2.5386 | 32.9092 | 11.6633 | 8.5082 | -2.928 | 32.9077 | 11.4771 | 8.3724 | -1.7523 | 28.8154 | 16.6839 | 12.1707 | 12.3013 | 28.9058 | 16.5774 | 12.093 | 11.9367 | 29 | 16.4333 | 11.9878 | 11.7765 | 29.0852 | 16.3549 | 11.9307 | 11.6311 | 29.2028 | 16.2528 | 11.8562 | 11.4486 | 29.3705 | 16.0631 | 11.7178 | 11.2291 | 29.5894 | 15.8387 | 11.5541 | 10.9576 | 29.8414 | 15.5866 | 11.3702 | 10.6378 | 30.0628 | 15.4194 | 11.2483 | 10.2268 | 30.2968 | 15.2607 | 11.1325 | 9.7654 | 31.0765 | 14.6794 | 10.7084 | 8.2229 | 31.6916 | 14.2826 | 10.419 | 6.5283 | 32.1178 | 13.9996 | 10.2125 | 5.2691 | 32.4739 | 13.6394 | 9.9498 | 4.1809 | 32.634 | 13.5126 | 9.8572 | 3.7402 | 28.8154 | 16.6839 | 12.1707 | 12.3013 | 28.856 | 16.5065 | 12.0413 | 11.8152 | 28.9923 | 16.2636 | 11.8641 | 11.4472 | 29.1623 | 16.2027 | 11.8196 | 11.042 | 29.3737 | 15.905 | 11.6025 | 10.4945 | 29.615 | 15.5987 | 11.379 | 9.9308 | 29.9067 | 15.3597 | 11.2047 | 9.1377 | 30.293 | 14.9586 | 10.9121 | 7.6052 | 30.5983 | 14.5278 | 10.5978 | 6.1243 | 30.8794 | 14.0482 | 10.2479 | 4.6776 | 31.7423 | 13.4247 | 9.7931 | 0.65782 | 32.4685 | 12.4582 | 9.0881 | -2.5751 | 32.9441 | 11.7031 | 8.5372 | -4.5356 | 33.2325 | 11.1919 | 8.1644 | -5.2144 | 33.255 | 10.961 | 7.9959 | -4.2828
HADFIELD | HYDE | STALYBRIDGE | 401790 | 395876 | 8.1738 | 1.3457 | 0.96722 | 8.1738 | 7.8853 | 1.2983 | 0.93308 | 7.8853 | 7.0887 | 1.1671 | 0.83882 | 7.0887 | 6.2298 | 1.0257 | 0.73718 | 6.2298 | 5.2361 | 0.86208 | 0.6196 | 5.2361 | 4.0128 | 0.66068 | 0.47484 | 4.0128 | 2.9841 | 0.4913 | 0.35311 | 2.9841 | 2.222 | 0.36584 | 0.26293 | 2.222 | 1.5751 | 0.25932 | 0.18638 | 1.5751 | 1.7523 | 0.2885 | 0.20735 | 1.7523 | 1.9279 | 0.31741 | 0.22813 | 1.9279 | 9.6688 | 1.5919 | 1.1441 | 9.6688 | 19.6186 | 5.3707 | 3.86 | 8.3342 | 20.0706 | 10.1303 | 7.2808 | 5.7143 | 20.4099 | 11.2251 | 8.0677 | 3.3236 | 8.1738 | 1.3457 | 0.96722 | 8.1738 | 8.1933 | 1.349 | 0.96952 | 8.1933 | 7.7588 | 1.2774 | 0.91811 | 7.7588 | 7.4793 | 1.2314 | 0.88504 | 7.4793 | 7.0923 | 1.1677 | 0.83924 | 7.0923 | 6.7451 | 1.1105 | 0.79816 | 6.7451 | 5.955 | 0.98045 | 0.70467 | 5.955 | 5.4447 | 0.89643 | 0.64428 | 5.4447 | 4.904 | 0.80741 | 0.5803 | 4.904 | 4.3177 | 0.71088 | 0.51092 | 4.3177 | 2.7544 | 0.45348 | 0.32593 | 2.7544 | 1.5924 | 0.26218 | 0.18843 | 1.5924 | 15.7608 | 2.5949 | 1.865 | 13.4468 | 18.8955 | 6.2862 | 4.518 | 12.3982 | 19.3254 | 7.2089 | 5.1812 | 11.7827 | 8.1738 | 1.3457 | 0.96722 | 8.1738 | 7.8413 | 1.291 | 0.92787 | 7.8413 | 6.911 | 1.1378 | 0.81779 | 6.911 | 5.9345 | 0.97707 | 0.70224 | 5.9345 | 4.6715 | 0.76912 | 0.55278 | 4.6715 | 3.1969 | 0.52634 | 0.37829 | 3.1969 | 2.1271 | 0.35022 | 0.25171 | 2.1271 | 1.2952 | 0.21324 | 0.15326 | 1.2952 | 0.38898 | 0.064043 | 0.046029 | 0.38898 | 0.45921 | 0.075605 | 0.054339 | 0.45921 | 0.28771 | 0.04737 | 0.034046 | 0.28771 | 8.1322 | 1.3389 | 0.9623 | 8.1322 | 19.588 | 5.2181 | 3.7504 | 8.099 | 20.0382 | 9.9702 | 7.1658 | 6.4287 | 20.3686 | 11.1485 | 8.0126 | 4.5757 | 8.1738 | 1.3457 | 0.96722 | 8.1738 | 7.9942 | 1.3162 | 0.94597 | 7.9942 | 7.2967 | 1.2013 | 0.86343 | 7.2967 | 6.4371 | 1.0598 | 0.76171 | 6.4371 | 5.103 | 0.84017 | 0.60385 | 5.103 | 3.7362 | 0.61513 | 0.44211 | 3.7362 | 2.3717 | 0.39048 | 0.28065 | 2.3717 | 6.7515 | 1.1116 | 0.79891 | 6.7515 | 9.2903 | 1.5296 | 1.0993 | 9.2903 | 15.06 | 2.4795 | 1.7821 | 13.2072 | 18.2183 | 12.8044 | 9.2028 | 10.4934 | 18.8852 | 12.1325 | 8.7198 | 7.5968 | 19.3776 | 11.5527 | 8.3032 | 5.2486 | 19.7468 | 11.1365 | 8.004 | 3.8756 | 19.8128 | 11.2343 | 8.0743 | 5.0545 | 8.1738 | 1.3457 | 0.96722 | 8.1738 | 7.9851 | 1.3147 | 0.94489 | 7.9851 | 7.3019 | 1.2022 | 0.86405 | 7.3019 | 6.533 | 1.0756 | 0.77306 | 6.533 | 5.7557 | 0.94762 | 0.68108 | 5.7557 | 4.6545 | 0.76633 | 0.55077 | 4.6545 | 3.7122 | 0.61118 | 0.43927 | 3.7122 | 3.026 | 0.49821 | 0.35808 | 3.026 | 2.435 | 0.4009 | 0.28813 | 2.435 | 2.6361 | 0.43402 | 0.31194 | 2.6361 | 3.4248 | 0.56387 | 0.40526 | 3.4248 | 12.2867 | 2.0229 | 1.4539 | 12.2867 | 19.0651 | 6.1495 | 4.4197 | 11.9707 | 19.4016 | 11.2253 | 8.0678 | 11.2943 | 19.5588 | 12.7294 | 9.1489 | 11.1127 | 8.1738 | 1.3457 | 0.96722 | 8.1738 | 7.8546 | 1.2932 | 0.92945 | 7.8546 | 7.0862 | 1.1667 | 0.83853 | 7.0862 | 6.0981 | 1.004 | 0.7216 | 6.0981 | 4.7149 | 0.77626 | 0.55792 | 4.7149 | 3.3473 | 0.55111 | 0.39609 | 3.3473 | 2.0619 | 0.33948 | 0.24399 | 2.0619 | 6.3571 | 1.0466 | 0.75225 | 6.3571 | 9.0044 | 1.4825 | 1.0655 | 9.0044 | 14.5205 | 2.3907 | 1.7182 | 12.9492 | 18.7661 | 12.6438 | 9.0874 | 9.8108 | 19.4557 | 11.9503 | 8.5889 | 6.8112 | 19.9664 | 11.3437 | 8.153 | 4.3238 | 20.3353 | 10.8985 | 7.833 | 2.7716 | 20.4219 | 10.9517 | 7.8712 | 3.7457
HALL CROSS | PEEL | PENWORTHAM WEST / STANAH | 342288 | 430650 | 24.5299 | 10.6893 | 7.7977 | 8.7046 | 24.6549 | 10.4604 | 7.6307 | 7.1526 | 24.8662 | 10.1873 | 7.4315 | 6.5462 | 25.0933 | 9.8488 | 7.1845 | 6.0563 | 25.345 | 9.3851 | 6.8463 | 5.4273 | 25.628 | 8.9973 | 6.5634 | 4.8005 | 25.9524 | 8.6607 | 6.3178 | 4.2081 | 26.2062 | 8.385 | 6.1168 | 3.7797 | 26.4119 | 8.262 | 6.027 | 3.3175 | 26.6108 | 8.1672 | 5.9578 | 2.8914 | 27.265 | 7.594 | 5.5397 | 0.67159 | 27.968 | 6.8202 | 4.9753 | -2.8747 | 28.4799 | 6.1763 | 4.5055 | -5.7133 | 28.9417 | 5.6175 | 4.0979 | -8.7023 | 29.2761 | 5.1346 | 3.7456 | -11.4093 | 24.4953 | 10.6893 | 7.7977 | 8.7046 | 24.5972 | 10.5956 | 7.7294 | 8.0076 | 24.7428 | 10.507 | 7.6647 | 7.5886 | 24.887 | 10.4225 | 7.6031 | 7.2688 | 25.0533 | 10.2877 | 7.5047 | 6.9153 | 25.2546 | 10.1219 | 7.3838 | 6.5508 | 25.4908 | 9.9135 | 7.2317 | 6.093 | 25.7595 | 9.7176 | 7.0888 | 5.4807 | 25.964 | 9.5572 | 6.9719 | 4.9193 | 26.1747 | 9.3849 | 6.8462 | 4.3526 | 26.8238 | 8.822 | 6.4355 | 2.686 | 27.4644 | 8.3306 | 6.0771 | 0.92916 | 28.0264 | 7.8792 | 5.7478 | -0.64968 | 28.4711 | 7.4579 | 5.4405 | -2.3385 | 28.8061 | 7.1906 | 5.2455 | -3.4775 | 24.5446 | 10.6893 | 7.7977 | 8.7046 | 24.6832 | 10.4055 | 7.5907 | 6.9764 | 24.9157 | 10.0762 | 7.3504 | 6.3684 | 25.1747 | 9.6392 | 7.0317 | 5.942 | 25.4651 | 9.2077 | 6.7169 | 5.3743 | 25.7934 | 8.8171 | 6.4319 | 4.8177 | 26.0663 | 8.4712 | 6.1796 | 4.3241 | 26.2899 | 8.2744 | 6.036 | 4.0034 | 26.4851 | 8.171 | 5.9606 | 3.7014 | 26.6697 | 8.0314 | 5.8588 | 3.3992 | 27.2934 | 7.3958 | 5.3952 | 1.5561 | 27.9753 | 6.6068 | 4.8195 | -1.6517 | 28.4533 | 5.9192 | 4.318 | -4.1787 | 28.8369 | 5.3195 | 3.8805 | -6.7747 | 29.042 | 4.8391 | 3.53 | -9.0109 | 24.5446 | 10.6893 | 7.7977 | 8.7046 | 24.5642 | 10.5386 | 7.6878 | 7.7172 | 24.7001 | 10.2772 | 7.4971 | 7.296 | 24.8459 | 9.7907 | 7.1421 | 6.9213 | 25.0317 | 9.3425 | 6.8152 | 6.3812 | 25.3103 | 8.866 | 6.4676 | 5.8147 | 25.6395 | 8.6079 | 6.2794 | 5.1191 | 25.9524 | 8.2954 | 6.0514 | 4.0352 | 26.1901 | 8.0209 | 5.8512 | 2.9549 | 26.4171 | 7.7388 | 5.6453 | 1.8674 | 27.0867 | 6.9405 | 5.063 | -1.2503 | 27.7261 | 6.1682 | 4.4996 | -4.3168 | 28.1599 | 5.535 | 4.0377 | -6.6378 | 28.4365 | 5.3137 | 3.8763 | -8.1443 | 28.3714 | 5.149 | 3.7562 | -7.4274 | 24.5299 | 10.6893 | 7.7977 | 8.7046 | 24.6383 | 10.5504 | 7.6964 | 7.6414 | 24.8004 | 10.3212 | 7.5292 | 7.1679 | 24.952 | 10.0025 | 7.2967 | 6.7639 | 25.1235 | 9.5796 | 6.9882 | 6.2815 | 25.3757 | 9.1983 | 6.71 | 5.7734 | 25.7007 | 8.8611 | 6.4641 | 5.2456 | 26.0447 | 8.5254 | 6.2192 | 4.8365 | 26.2334 | 8.4917 | 6.1945 | 4.3408 | 26.422 | 8.3738 | 6.1086 | 3.8526 | 27.0138 | 7.9143 | 5.7734 | 2.2756 | 27.6069 | 7.454 | 5.4376 | 0.44195 | 28.0253 | 7.0978 | 5.1777 | -0.81708 | 28.3795 | 6.8784 | 5.0177 | -1.9595 | 28.5332 | 6.7826 | 4.9478 | -2.5132 | 24.5299 | 10.6893 | 7.7977 | 8.7046 | 24.593 | 10.4148 | 7.5974 | 6.9999 | 24.7947 | 10.0982 | 7.3665 | 6.3511 | 25.0198 | 9.5619 | 6.9753 | 5.844 | 25.2704 | 9.1141 | 6.6486 | 5.1842 | 25.5481 | 8.5804 | 6.2593 | 4.5384 | 25.8721 | 8.3405 | 6.0843 | 3.7485 | 26.1899 | 8.0075 | 5.8413 | 2.5312 | 26.4322 | 7.716 | 5.6287 | 1.3587 | 26.6668 | 7.4166 | 5.4103 | 0.18067 | 27.3483 | 6.5647 | 4.7888 | -3.2083 | 27.9766 | 5.7421 | 4.1888 | -6.4991 | 28.4081 | 5.0649 | 3.6948 | -9.0286 | 28.6676 | 4.7949 | 3.4978 | -10.7719 | 28.2462 | 4.5818 | 3.3424 | -10.3202
HANDFORTH | MOSS NOOK | SOUTH MANCHESTER | 385958 | 383397 | 30.2969 | 9.6958 | 6.9686 | 15.4068 | 30.3818 | 9.3363 | 6.7102 | 13.5353 | 30.5088 | 9.2304 | 6.6341 | 12.7528 | 30.6673 | 8.9901 | 6.4614 | 11.8643 | 30.8588 | 8.7813 | 6.3113 | 11.0155 | 31.0797 | 8.6868 | 6.2434 | 10.1512 | 31.338 | 8.4155 | 6.0484 | 9.2951 | 31.6574 | 8.1574 | 5.8629 | 8.4551 | 31.9286 | 7.9122 | 5.6866 | 7.5749 | 32.1968 | 7.6556 | 5.5022 | 6.7244 | 32.9887 | 6.9487 | 4.9942 | 3.6097 | 33.6694 | 6.237 | 4.4826 | 0.24662 | 34.1151 | 5.8153 | 4.1796 | -1.7167 | 34.4857 | 5.7193 | 4.1105 | -3.7427 | 32.7464 | 5.3914 | 3.8749 | -5.6753 | 30.2613 | 9.6958 | 6.9686 | 15.4068 | 30.3218 | 9.6251 | 6.9178 | 14.8258 | 30.3893 | 9.577 | 6.8832 | 14.5616 | 30.4721 | 9.469 | 6.8056 | 14.3776 | 30.5855 | 9.3659 | 6.7314 | 14.1449 | 30.7269 | 9.2718 | 6.6638 | 13.9005 | 30.8949 | 9.003 | 6.4706 | 13.591 | 31.0864 | 8.9038 | 6.3994 | 13.186 | 31.2249 | 8.8131 | 6.3341 | 12.8325 | 31.3715 | 8.7354 | 6.2783 | 12.4773 | 31.8488 | 8.4619 | 6.0817 | 11.4099 | 32.3541 | 8.2359 | 5.9193 | 10.1981 | 32.8325 | 7.9835 | 5.7379 | 9.052 | 33.3387 | 8.0768 | 5.8049 | 7.8195 | 33.715 | 8.1115 | 5.8299 | 6.9774 | 30.3103 | 9.6958 | 6.9686 | 15.4068 | 30.4055 | 9.2293 | 6.6333 | 13.2728 | 30.5485 | 9.178 | 6.5964 | 12.4573 | 30.7301 | 8.9605 | 6.4401 | 11.6093 | 30.949 | 8.7453 | 6.2854 | 10.8031 | 31.2009 | 8.5391 | 6.1372 | 9.988 | 31.4948 | 8.2344 | 5.9182 | 9.2033 | 31.8564 | 7.9959 | 5.7468 | 8.4391 | 32.1459 | 7.7338 | 5.5584 | 7.6498 | 32.3864 | 7.4661 | 5.366 | 6.8752 | 33.08 | 6.7376 | 4.8424 | 3.9834 | 33.892 | 6.0084 | 4.3184 | 0.79345 | 33.6914 | 5.547 | 3.9868 | -1.0175 | 33.7741 | 5.5607 | 3.9965 | -2.8505 | 31.1386 | 5.1267 | 3.6847 | -4.554 | 30.3103 | 9.6958 | 6.9686 | 15.4068 | 30.3102 | 9.3983 | 6.7547 | 14.1092 | 30.3786 | 9.4314 | 6.7785 | 13.4985 | 30.4753 | 9.2454 | 6.6449 | 12.6927 | 30.6201 | 9.0302 | 6.4902 | 11.8983 | 30.8437 | 8.8603 | 6.3681 | 11.0632 | 31.1249 | 8.6043 | 6.1841 | 10.1414 | 31.4499 | 8.3233 | 5.9821 | 8.875 | 31.7238 | 8.031 | 5.7721 | 7.557 | 32 | 7.7213 | 5.5495 | 6.2399 | 32.8173 | 7.1533 | 5.1412 | 2.4679 | 33.4703 | 6.3933 | 4.595 | -0.60575 | 33.9171 | 5.9271 | 4.2599 | -2.2572 | 34.1163 | 5.617 | 4.037 | -3.316 | 33.5195 | 5.5187 | 3.9664 | -2.9436 | 30.2969 | 9.6958 | 6.9686 | 15.4068 | 30.368 | 9.4966 | 6.8254 | 14.4415 | 30.4541 | 9.4241 | 6.7733 | 13.8844 | 30.5509 | 9.1902 | 6.6052 | 13.0751 | 30.6787 | 8.9958 | 6.4654 | 12.3546 | 30.8742 | 8.957 | 6.4376 | 11.5996 | 31.1291 | 8.7081 | 6.2587 | 10.83 | 31.4116 | 8.457 | 6.0782 | 10.0519 | 31.6452 | 8.2209 | 5.9085 | 9.19 | 31.884 | 7.9609 | 5.7217 | 8.3352 | 32.6191 | 7.3623 | 5.2915 | 5.776 | 33.2114 | 6.893 | 4.9542 | 3.7641 | 33.6338 | 6.6878 | 4.8066 | 3.0063 | 34.0024 | 6.9269 | 4.9785 | 2.2051 | 34.2291 | 6.8376 | 4.9143 | 1.7057 | 30.2969 | 9.6958 | 6.9686 | 15.4068 | 30.3313 | 9.2446 | 6.6443 | 13.1949 | 30.4504 | 9.2215 | 6.6276 | 12.3236 | 30.6062 | 9.015 | 6.4792 | 11.4204 | 30.7959 | 8.7809 | 6.311 | 10.5404 | 31.011 | 8.5981 | 6.1796 | 9.6533 | 31.2649 | 8.3287 | 5.986 | 8.6678 | 31.5962 | 8.0306 | 5.7718 | 7.311 | 31.8746 | 7.7269 | 5.5535 | 5.9295 | 32.1511 | 7.4042 | 5.3216 | 4.5496 | 32.9819 | 6.84 | 4.9161 | 0.58186 | 33.6166 | 6.0428 | 4.3431 | -2.653 | 33.5032 | 5.516 | 3.9645 | -4.4564 | 31.3125 | 5.1554 | 3.7053 | -5.6813 | 30.511 | 5.0234 | 3.6104 | -5.4965
HANGING BRIDGE | WRIGHTINGTON | PENWORTHAM WEST / STANAH | 346186 | 417486 | 11.2055 | 11.2055 | 11.2055 | 6.2211 | 11.3249 | 11.3249 | 11.3249 | 5.5036 | 11.4441 | 11.4441 | 11.4441 | 5.3111 | 11.5608 | 11.5608 | 11.5608 | 5.2224 | 11.6803 | 11.6803 | 11.6803 | 5.0889 | 11.8332 | 11.8332 | 11.8332 | 4.945 | 11.9801 | 11.9801 | 11.9801 | 4.7632 | 12.0937 | 12.0937 | 12.0937 | 4.5636 | 12.2168 | 12.2168 | 12.2168 | 4.3239 | 12.3473 | 12.3473 | 12.3473 | 4.0838 | 12.8051 | 12.8051 | 12.8051 | 2.3594 | 13.274 | 13.274 | 13.274 | 0.24846 | 13.6013 | 13.6013 | 13.6013 | -1.2185 | 13.8799 | 13.8799 | 13.8799 | -2.384 | 14.0934 | 14.0934 | 14.0934 | -3.1658 | 11.1908 | 11.1908 | 11.1908 | 6.2211 | 11.2589 | 11.2589 | 11.2589 | 6.087 | 11.3139 | 11.3139 | 11.3139 | 6.0199 | 11.3887 | 11.3887 | 11.3887 | 5.9596 | 11.4903 | 11.4903 | 11.4903 | 5.8367 | 11.6125 | 11.6125 | 11.6125 | 5.7013 | 11.7665 | 11.7665 | 11.7665 | 5.5174 | 11.9174 | 11.9174 | 11.9174 | 5.2532 | 12.0337 | 12.0337 | 12.0337 | 5.0475 | 12.1678 | 12.1678 | 12.1678 | 4.8342 | 12.5057 | 12.5057 | 12.5057 | 4.1355 | 12.8212 | 12.8212 | 12.8212 | 3.177 | 13.1295 | 13.1295 | 13.1295 | 1.9819 | 13.453 | 13.453 | 13.453 | 0.63463 | 13.6652 | 13.6652 | 13.6652 | -0.16834 | 11.2114 | 11.2114 | 11.2114 | 6.2211 | 11.3161 | 11.3161 | 11.3161 | 5.3963 | 11.4296 | 11.4296 | 11.4296 | 5.1856 | 11.5498 | 11.5498 | 11.5498 | 5.0979 | 11.6612 | 11.6612 | 11.6612 | 4.9675 | 11.8005 | 11.8005 | 11.8005 | 4.8293 | 11.9608 | 11.9608 | 11.9608 | 4.7019 | 12.0618 | 12.0618 | 12.0618 | 4.5664 | 12.168 | 12.168 | 12.168 | 4.415 | 12.2825 | 12.2825 | 12.2825 | 4.2662 | 12.7269 | 12.7269 | 12.7269 | 2.4631 | 13.2259 | 13.2259 | 13.2259 | 0.096385 | 13.5859 | 13.5859 | 13.5859 | -1.6214 | 13.8758 | 13.8758 | 13.8758 | -2.9852 | 14.0746 | 14.0746 | 14.0746 | -3.8544 | 11.2116 | 11.2116 | 11.2116 | 6.2211 | 11.2868 | 11.2868 | 11.2868 | 5.6985 | 11.38 | 11.38 | 11.38 | 5.5516 | 11.4838 | 11.4838 | 11.4838 | 5.4691 | 11.5868 | 11.5868 | 11.5868 | 5.3484 | 11.7338 | 11.7338 | 11.7338 | 5.2117 | 11.8426 | 11.8426 | 11.8426 | 5.0145 | 11.9831 | 11.9831 | 11.9831 | 4.6085 | 12.1345 | 12.1345 | 12.1345 | 4.1546 | 12.296 | 12.296 | 12.296 | 3.6265 | 12.7944 | 12.7944 | 12.7944 | 1.8616 | 13.2304 | 13.2304 | 13.2304 | -0.26117 | 13.5129 | 13.5129 | 13.5129 | -1.7078 | 13.7044 | 13.7044 | 13.7044 | -2.6812 | 13.7371 | 13.7371 | 13.7371 | -2.7907 | 11.2054 | 11.2054 | 11.2054 | 6.2211 | 11.2961 | 11.2961 | 11.2961 | 6.015 | 11.3826 | 11.3826 | 11.3826 | 5.9178 | 11.4925 | 11.4925 | 11.4925 | 5.8478 | 11.5884 | 11.5884 | 11.5884 | 5.7714 | 11.7019 | 11.7019 | 11.7019 | 5.6892 | 11.8529 | 11.8529 | 11.8529 | 5.5898 | 12.0035 | 12.0035 | 12.0035 | 5.4175 | 12.1088 | 12.1088 | 12.1088 | 5.1744 | 12.2238 | 12.2238 | 12.2238 | 4.9179 | 12.6248 | 12.6248 | 12.6248 | 3.6677 | 13.0278 | 13.0278 | 13.0278 | 1.783 | 13.3073 | 13.3073 | 13.3073 | 0.45834 | 13.5214 | 13.5214 | 13.5214 | -0.57109 | 13.6163 | 13.6163 | 13.6163 | -1.0329 | 11.2054 | 11.2054 | 11.2054 | 6.2211 | 11.276 | 11.276 | 11.276 | 5.3622 | 11.3783 | 11.3783 | 11.3783 | 5.138 | 11.5066 | 11.5066 | 11.5066 | 5.0315 | 11.6127 | 11.6127 | 11.6127 | 4.8912 | 11.7435 | 11.7435 | 11.7435 | 4.7492 | 11.9152 | 11.9152 | 11.9152 | 4.5524 | 12.0567 | 12.0567 | 12.0567 | 4.0854 | 12.2032 | 12.2032 | 12.2032 | 3.5622 | 12.3594 | 12.3594 | 12.3594 | 3.025 | 12.8673 | 12.8673 | 12.8673 | 1.3858 | 13.3552 | 13.3552 | 13.3552 | -0.41797 | 13.7022 | 13.7022 | 13.7022 | -1.9886 | 13.9292 | 13.9292 | 13.9292 | -3.0996 | 13.9758 | 13.9758 | 13.9758 | -3.306
HAREHOLME | ROSSENDALE | PADIHAM | 382535 | 422283 | 29.5983 | 14.8591 | 10.8395 | 13.4602 | 29.7178 | 14.789 | 10.7884 | 13.2554 | 29.8918 | 14.5352 | 10.6033 | 13.0523 | 30.1107 | 13.9668 | 10.1886 | 12.7566 | 30.3758 | 13.4638 | 9.8216 | 12.4346 | 30.6299 | 13.0645 | 9.5303 | 12.103 | 30.9062 | 12.5985 | 9.1904 | 11.818 | 31.2424 | 12.5125 | 9.1277 | 11.4807 | 31.5223 | 12.3753 | 9.0276 | 11.0415 | 31.7924 | 12.2414 | 8.93 | 10.6393 | 32.4887 | 11.6031 | 8.4643 | 8.1452 | 33.2078 | 10.7439 | 7.8375 | 3.9518 | 33.724 | 10.0154 | 7.3061 | 0.44211 | 34.1609 | 9.1753 | 6.6933 | -3.4458 | 34.4426 | 8.3728 | 6.1078 | -6.7171 | 29.5652 | 14.8591 | 10.8395 | 13.4602 | 29.6884 | 14.7973 | 10.7944 | 13.2232 | 29.8286 | 14.6308 | 10.673 | 12.9917 | 29.9908 | 14.4383 | 10.5326 | 12.7399 | 30.1183 | 14.2134 | 10.3685 | 12.4125 | 30.2787 | 13.9509 | 10.177 | 12.037 | 30.4717 | 13.53 | 9.87 | 11.5718 | 30.6946 | 13.3472 | 9.7366 | 11.0056 | 30.8479 | 13.198 | 9.6277 | 10.6072 | 31.0079 | 13.0477 | 9.5181 | 10.1702 | 31.5084 | 12.5581 | 9.1609 | 8.672 | 32.0041 | 12.1625 | 8.8723 | 7.2692 | 32.4553 | 11.7572 | 8.5767 | 6.0368 | 32.9147 | 11.2714 | 8.2223 | 4.8165 | 33.2429 | 10.8715 | 7.9306 | 4.0445 | 29.6124 | 14.8591 | 10.8395 | 13.4602 | 29.7449 | 14.7875 | 10.7872 | 13.2827 | 29.9402 | 14.4164 | 10.5166 | 13.1149 | 30.1906 | 13.7992 | 10.0663 | 12.8773 | 30.4776 | 13.3244 | 9.7199 | 12.619 | 30.7569 | 12.9072 | 9.4156 | 12.3625 | 31.076 | 12.5504 | 9.1553 | 12.1802 | 31.4639 | 12.3983 | 9.0444 | 11.9702 | 31.7478 | 12.2497 | 8.936 | 11.6618 | 31.9633 | 12.1003 | 8.827 | 11.3688 | 32.6531 | 11.3908 | 8.3095 | 9.0644 | 33.452 | 10.489 | 7.6516 | 5.1499 | 34.0447 | 9.71 | 7.0833 | 1.9498 | 34.5072 | 8.8423 | 6.4503 | -1.386 | 34.7741 | 8.0091 | 5.8425 | -4.3568 | 29.6124 | 14.8591 | 10.8395 | 13.4602 | 29.6179 | 14.8514 | 10.8339 | 13.6128 | 29.7022 | 14.7033 | 10.7259 | 13.5683 | 29.8219 | 13.7913 | 10.0606 | 13.3952 | 30.0028 | 13.5722 | 9.9007 | 13.1659 | 30.2859 | 13.3791 | 9.7599 | 12.8962 | 30.5826 | 12.8632 | 9.3835 | 12.409 | 30.9395 | 12.5045 | 9.1219 | 11.0756 | 31.2332 | 12.0372 | 8.781 | 9.6776 | 31.4999 | 11.4646 | 8.3633 | 8.2921 | 32.2333 | 10.5087 | 7.6659 | 4.3095 | 32.9682 | 9.6507 | 7.0401 | 0.48645 | 33.4852 | 8.7787 | 6.404 | -2.6453 | 33.8658 | 8.0683 | 5.8857 | -4.6614 | 33.9182 | 8.0082 | 5.8419 | -3.2897 | 29.5983 | 14.8591 | 10.8395 | 13.4602 | 29.7016 | 14.8094 | 10.8032 | 13.2931 | 29.8247 | 14.582 | 10.6373 | 13.1556 | 29.9642 | 14.0483 | 10.2481 | 12.9692 | 30.144 | 13.5761 | 9.9036 | 12.8449 | 30.3842 | 13.197 | 9.627 | 12.6734 | 30.6511 | 12.742 | 9.2951 | 12.466 | 30.9473 | 12.6763 | 9.2472 | 12.235 | 31.1928 | 12.5479 | 9.1535 | 11.8323 | 31.4395 | 12.4123 | 9.0546 | 11.4206 | 32.1592 | 11.9833 | 8.7416 | 10.0478 | 32.7861 | 11.6127 | 8.4713 | 8.4867 | 33.2101 | 11.3206 | 8.2582 | 7.3506 | 33.5756 | 11.0241 | 8.042 | 6.3564 | 33.7444 | 10.7218 | 7.8214 | 5.9497 | 29.5983 | 14.8591 | 10.8395 | 13.4602 | 29.66 | 14.8328 | 10.8203 | 13.5147 | 29.8255 | 14.631 | 10.6731 | 13.3382 | 30.0423 | 13.7008 | 9.9946 | 13.016 | 30.3073 | 13.4599 | 9.8188 | 12.6495 | 30.5715 | 13.2471 | 9.6636 | 12.2835 | 30.8663 | 12.7074 | 9.2699 | 11.6834 | 31.264 | 12.3287 | 8.9936 | 10.1908 | 31.5751 | 11.8398 | 8.6369 | 8.684 | 31.8432 | 11.2327 | 8.1941 | 7.1911 | 32.5873 | 10.2432 | 7.4723 | 2.8838 | 33.2833 | 9.2982 | 6.7829 | -1.28 | 33.7768 | 8.3479 | 6.0897 | -4.7239 | 34.1187 | 7.5866 | 5.5343 | -7.1163 | 34.1757 | 7.4417 | 5.4286 | -6.1921
HARPURHEY | RED BANK | WHITEGATE | 385907 | 402469 | 30.108 | 13.3785 | 9.7594 | 15.9038 | 30.1691 | 13.0858 | 9.5459 | 14.9695 | 30.2543 | 12.7562 | 9.3054 | 13.9626 | 30.3654 | 12.4523 | 9.0838 | 13.1648 | 30.5083 | 12.0864 | 8.8168 | 11.9284 | 30.6635 | 11.7077 | 8.5406 | 10.8825 | 30.7548 | 11.6615 | 8.5069 | 10.5186 | 30.8664 | 11.604 | 8.4649 | 10.1975 | 30.9611 | 11.5261 | 8.4081 | 9.8568 | 31.0504 | 11.4697 | 8.367 | 9.6971 | 31.3858 | 11.1039 | 8.1001 | 8.2704 | 31.8063 | 10.5548 | 7.6996 | 5.5557 | 32.1285 | 10.0624 | 7.3404 | 3.2873 | 32.4286 | 9.576 | 6.9856 | 1.0164 | 32.617 | 9.42 | 6.8718 | -1.1136 | 30.0882 | 13.3785 | 9.7594 | 15.9038 | 30.1347 | 13.2736 | 9.6829 | 15.5409 | 30.1799 | 13.1374 | 9.5836 | 15.1656 | 30.2391 | 12.9864 | 9.4734 | 14.8565 | 30.3252 | 12.8473 | 9.3719 | 14.4979 | 30.4371 | 12.7099 | 9.2717 | 14.1397 | 30.5744 | 12.532 | 9.1419 | 13.9302 | 30.7333 | 12.4333 | 9.0699 | 13.6415 | 30.8273 | 12.3416 | 9.003 | 13.3863 | 30.9251 | 12.2439 | 8.9318 | 13.1295 | 31.1556 | 11.9603 | 8.7249 | 12.3733 | 31.3574 | 11.7354 | 8.5608 | 11.6296 | 31.5307 | 11.4181 | 8.3294 | 10.9304 | 31.6997 | 11.4229 | 8.3328 | 10.1691 | 31.815 | 11.4133 | 8.3259 | 9.6983 | 30.1164 | 13.3785 | 9.7594 | 15.9038 | 30.1864 | 13.0414 | 9.5135 | 14.9433 | 30.2857 | 12.6394 | 9.2203 | 13.949 | 30.4175 | 12.2735 | 8.9533 | 13.1897 | 30.5861 | 11.8441 | 8.6401 | 11.9974 | 30.6971 | 11.7402 | 8.5643 | 10.9977 | 30.8003 | 11.6775 | 8.5186 | 10.7011 | 30.925 | 11.5958 | 8.459 | 10.4496 | 31.0244 | 11.4996 | 8.3888 | 10.1837 | 31.1179 | 11.4153 | 8.3273 | 10.0885 | 31.469 | 10.9994 | 8.0239 | 8.8624 | 31.9036 | 10.4043 | 7.5898 | 6.3136 | 32.2328 | 9.8439 | 7.181 | 4.1896 | 32.5333 | 9.5668 | 6.9789 | 2.0865 | 32.7539 | 9.2796 | 6.7694 | 0.094781 | 30.1164 | 13.3785 | 9.7594 | 15.9038 | 30.0918 | 13.1382 | 9.5841 | 15.3448 | 30.1269 | 12.7352 | 9.2902 | 14.4474 | 30.1857 | 12.2671 | 8.9487 | 13.704 | 30.288 | 12.1698 | 8.8777 | 12.5019 | 30.4536 | 12.0027 | 8.7558 | 11.4691 | 30.5847 | 11.8365 | 8.6346 | 10.9744 | 30.7331 | 11.5444 | 8.4215 | 9.991 | 30.8674 | 11.2729 | 8.2235 | 8.9712 | 31.0012 | 10.902 | 7.9528 | 8.1147 | 31.4008 | 10.5117 | 7.6681 | 5.6528 | 31.7969 | 9.917 | 7.2343 | 3.2482 | 32.082 | 9.3946 | 6.8533 | 1.3227 | 32.2879 | 9.3933 | 6.8522 | 0.25413 | 32.3046 | 9.3686 | 6.8343 | 1.1268 | 30.108 | 13.3785 | 9.7594 | 15.9038 | 30.1592 | 13.1591 | 9.5994 | 15.0952 | 30.2128 | 12.8532 | 9.3762 | 14.1452 | 30.2733 | 12.5744 | 9.1729 | 13.436 | 30.3597 | 12.2338 | 8.9244 | 12.3917 | 30.5014 | 11.8917 | 8.6748 | 11.5145 | 30.6488 | 11.8356 | 8.6339 | 11.267 | 30.7505 | 11.792 | 8.6021 | 10.9976 | 30.838 | 11.7187 | 8.5486 | 10.6529 | 30.9258 | 11.659 | 8.5051 | 10.4613 | 31.2144 | 11.4248 | 8.3343 | 9.7572 | 31.5226 | 11.2033 | 8.1726 | 8.9051 | 31.7458 | 10.9613 | 7.9961 | 8.2116 | 31.9488 | 10.8693 | 7.929 | 7.5848 | 32.0407 | 10.9998 | 8.0242 | 7.3475 | 30.108 | 13.3785 | 9.7594 | 15.9038 | 30.1094 | 13.0626 | 9.529 | 15.1698 | 30.1864 | 12.6358 | 9.2176 | 14.1739 | 30.2966 | 12.1509 | 8.8639 | 13.328 | 30.4412 | 12.0449 | 8.7866 | 12.0451 | 30.5881 | 11.8675 | 8.6572 | 10.9621 | 30.6895 | 11.6897 | 8.5275 | 10.404 | 30.8536 | 11.3894 | 8.3084 | 9.3315 | 30.9986 | 11.1071 | 8.1024 | 8.2414 | 31.1406 | 10.7374 | 7.8328 | 7.3148 | 31.556 | 10.2776 | 7.4973 | 4.6442 | 31.9298 | 9.6532 | 7.0419 | 2.076 | 32.2007 | 9.1307 | 6.6607 | -0.012628 | 32.3862 | 9.0693 | 6.6159 | -1.2777 | 32.4085 | 9.0022 | 6.567 | -0.64219
HARWOOD | BOLTON | KEARSLEY | 374043 | 410941 | 24.4044 | 11.9707 | 8.6036 | 7.4867 | 24.4983 | 11.8915 | 8.5467 | 7.2995 | 24.6362 | 11.8105 | 8.4885 | 7.1974 | 24.8178 | 11.7144 | 8.4194 | 7.0753 | 25.0029 | 11.5228 | 8.2816 | 6.5352 | 25.1921 | 11.2906 | 8.1148 | 5.977 | 25.4007 | 11.1138 | 7.9877 | 5.4581 | 25.6381 | 10.9955 | 7.9027 | 5.0003 | 25.8206 | 10.8528 | 7.8001 | 4.5017 | 25.99 | 10.7013 | 7.6912 | 4.0414 | 26.6582 | 10.0687 | 7.2365 | 1.2772 | 27.2682 | 9.151 | 6.577 | -3.1362 | 27.7294 | 8.4136 | 6.047 | -6.3075 | 28.1407 | 7.5876 | 5.4533 | -9.5806 | 28.4463 | 6.7963 | 4.8846 | -12.7753 | 24.3545 | 11.9707 | 8.6036 | 7.4867 | 24.4312 | 11.9262 | 8.5716 | 7.353 | 24.5026 | 11.8931 | 8.5478 | 7.2737 | 24.5964 | 11.8281 | 8.5011 | 7.1723 | 24.7333 | 11.7325 | 8.4324 | 6.9886 | 24.8717 | 11.6094 | 8.3439 | 6.7606 | 25.003 | 11.3873 | 8.1843 | 6.4575 | 25.1578 | 11.2661 | 8.0972 | 6.07 | 25.2661 | 11.1543 | 8.0168 | 5.7086 | 25.3781 | 11.0333 | 7.9298 | 5.339 | 25.7195 | 10.7003 | 7.6905 | 4.1949 | 26.0524 | 10.43 | 7.4962 | 3.0335 | 26.3627 | 10.1294 | 7.2802 | 1.9571 | 26.6885 | 9.8625 | 7.0884 | 0.86182 | 26.9359 | 9.5945 | 6.8958 | 0.14372 | 24.42 | 11.9707 | 8.6036 | 7.4867 | 24.5278 | 11.8721 | 8.5327 | 7.314 | 24.6884 | 11.7461 | 8.4421 | 7.2473 | 24.8839 | 11.6273 | 8.3568 | 7.184 | 25.0717 | 11.3999 | 8.1933 | 6.711 | 25.288 | 11.22 | 8.064 | 6.2315 | 25.5305 | 11.0575 | 7.9473 | 5.8218 | 25.8086 | 10.9316 | 7.8567 | 5.4926 | 26.0148 | 10.7935 | 7.7575 | 5.1274 | 26.2065 | 10.6397 | 7.647 | 4.7058 | 26.9283 | 9.9085 | 7.1215 | 2.0919 | 27.5852 | 8.9351 | 6.4218 | -2.1199 | 28.0466 | 8.1527 | 5.8595 | -5.1304 | 28.4462 | 7.3318 | 5.2695 | -8.0845 | 28.7317 | 6.6637 | 4.7893 | -10.8303 | 24.42 | 11.9707 | 8.6036 | 7.4867 | 24.396 | 11.958 | 8.5945 | 7.7222 | 24.4556 | 11.8781 | 8.537 | 7.7753 | 24.5533 | 11.7604 | 8.4524 | 7.7452 | 24.716 | 11.5372 | 8.292 | 7.2618 | 24.9478 | 11.3739 | 8.1747 | 6.7268 | 25.2128 | 11.2 | 8.0497 | 6.034 | 25.5537 | 10.8325 | 7.7855 | 4.6866 | 25.7549 | 10.4646 | 7.5211 | 3.2739 | 25.9502 | 10.1104 | 7.2665 | 1.8726 | 26.5439 | 8.9633 | 6.4421 | -2.2222 | 27.1742 | 8.1472 | 5.8556 | -6.2634 | 27.6396 | 7.4561 | 5.3588 | -9.0378 | 27.9949 | 6.9043 | 4.9623 | -10.675 | 28.0649 | 6.8789 | 4.944 | -9.6287 | 24.4044 | 11.9707 | 8.6036 | 7.4867 | 24.4817 | 11.9198 | 8.567 | 7.3671 | 24.5675 | 11.8576 | 8.5223 | 7.3414 | 24.6681 | 11.7876 | 8.472 | 7.359 | 24.805 | 11.644 | 8.3688 | 7.0871 | 24.9392 | 11.4774 | 8.249 | 6.7625 | 25.1212 | 11.3014 | 8.1226 | 6.3984 | 25.3231 | 11.2054 | 8.0535 | 6.021 | 25.4858 | 11.0741 | 7.9591 | 5.538 | 25.6471 | 10.9277 | 7.854 | 5.0594 | 26.1741 | 10.4964 | 7.544 | 3.3765 | 26.7604 | 10.0362 | 7.2132 | 1.3834 | 27.2014 | 9.696 | 6.9687 | 0.34493 | 27.6251 | 9.255 | 6.6518 | -0.63471 | 27.7882 | 8.9695 | 6.4465 | -1.143 | 24.4044 | 11.9707 | 8.6036 | 7.4867 | 24.425 | 11.9191 | 8.5665 | 7.5942 | 24.553 | 11.8209 | 8.4959 | 7.5164 | 24.7338 | 11.6656 | 8.3843 | 7.3483 | 24.9225 | 11.4287 | 8.214 | 6.7423 | 25.1195 | 11.2456 | 8.0824 | 6.1217 | 25.3712 | 11.0345 | 7.9307 | 5.3293 | 25.7482 | 10.6466 | 7.6519 | 3.8524 | 25.9703 | 10.26 | 7.3741 | 2.325 | 26.1818 | 9.8839 | 7.1037 | 0.81071 | 26.7854 | 8.6761 | 6.2357 | -3.6107 | 27.3589 | 7.792 | 5.6003 | -7.9124 | 27.7812 | 7.0606 | 5.0746 | -10.9328 | 28.0834 | 6.4578 | 4.6414 | -12.8644 | 28.1507 | 6.367 | 4.5761 | -12.1571
HATTERSLEY | HYDE | STALYBRIDGE | 398419 | 395120 | 15.167 | 4.6622 | 3.3508 | 10.6136 | 15.2306 | 4.1601 | 2.9899 | 8.2058 | 15.2934 | 3.9061 | 2.8074 | 7.5855 | 15.3728 | 3.7158 | 2.6706 | 7.4611 | 15.4895 | 3.3345 | 2.3966 | 6.8459 | 15.6209 | 3.2027 | 2.3018 | 6.1593 | 15.7642 | 3.0486 | 2.1911 | 5.4938 | 15.9243 | 2.8977 | 2.0826 | 4.8633 | 16.0675 | 2.7355 | 1.966 | 4.1428 | 16.1327 | 2.6561 | 1.909 | 3.4453 | 13.9599 | 2.2984 | 1.6519 | 0.51665 | 15.415 | 2.538 | 1.8241 | -3.5842 | 17.4967 | 4.286 | 3.0805 | -7.2509 | 17.8326 | 7.0307 | 5.0531 | -10.2714 | 18.1093 | 7.4015 | 5.3196 | -12.7975 | 15.1599 | 4.6622 | 3.3508 | 10.6136 | 15.2096 | 4.5035 | 3.2367 | 9.8047 | 15.2441 | 4.4242 | 3.1798 | 9.48 | 15.2865 | 4.3619 | 3.135 | 9.2964 | 15.3481 | 4.2245 | 3.0363 | 8.6956 | 15.4221 | 4.0658 | 2.9221 | 8.0361 | 15.5174 | 3.816 | 2.7427 | 7.3128 | 15.637 | 3.6404 | 2.6164 | 6.5269 | 15.7396 | 3.5022 | 2.5171 | 5.9515 | 15.8438 | 3.3588 | 2.4141 | 5.3766 | 16.1693 | 2.8422 | 2.0428 | 3.1511 | 14.5637 | 2.3978 | 1.7233 | 0.78015 | 16.8354 | 3.3712 | 2.4229 | -1.5136 | 17.1425 | 5.3503 | 3.8454 | -3.1837 | 17.3399 | 5.9982 | 4.311 | -4.0859 | 15.17 | 4.6622 | 3.3508 | 10.6136 | 15.2373 | 4.084 | 2.9353 | 7.8176 | 15.3055 | 3.7731 | 2.7118 | 6.9638 | 15.393 | 3.5459 | 2.5485 | 6.6846 | 15.5192 | 3.1453 | 2.2606 | 6.0224 | 15.6617 | 2.9999 | 2.1561 | 5.3023 | 15.8192 | 2.8195 | 2.0265 | 4.5605 | 15.9954 | 2.6506 | 1.905 | 3.8601 | 14.9694 | 2.4646 | 1.7714 | 3.1049 | 14.3205 | 2.3578 | 1.6946 | 2.3321 | 12.0873 | 1.9901 | 1.4303 | -0.37873 | 13.4837 | 2.22 | 1.5955 | -4.2934 | 17.6186 | 3.9544 | 2.8421 | -7.8071 | 17.9479 | 6.7288 | 4.8361 | -10.6345 | 18.2013 | 7.1186 | 5.1163 | -12.9508 | 15.17 | 4.6622 | 3.3508 | 10.6136 | 15.1492 | 4.248 | 3.0532 | 8.7562 | 15.1773 | 3.9932 | 2.87 | 8.1554 | 15.2293 | 3.7499 | 2.6952 | 7.9738 | 15.3266 | 3.4188 | 2.4572 | 7.3708 | 15.4597 | 3.2785 | 2.3563 | 6.5577 | 15.6447 | 3.0718 | 2.2077 | 5.6222 | 15.8815 | 3.3309 | 2.394 | 4.211 | 16.0316 | 3.4104 | 2.4511 | 2.741 | 16.1779 | 3.7583 | 2.7012 | 1.2816 | 16.6215 | 9.6203 | 6.9143 | -2.5752 | 17.0759 | 8.766 | 6.3003 | -6.4466 | 17.4101 | 7.9942 | 5.7456 | -9.7684 | 17.6665 | 7.4622 | 5.3632 | -11.5943 | 17.7284 | 7.4121 | 5.3272 | -11.1711 | 15.167 | 4.6622 | 3.3508 | 10.6136 | 15.2209 | 4.3285 | 3.1109 | 9.1719 | 15.2641 | 4.1132 | 2.9562 | 8.7807 | 15.3089 | 3.9344 | 2.8278 | 8.7076 | 15.3735 | 3.5982 | 2.5861 | 8.2514 | 15.4675 | 3.491 | 2.5091 | 7.7472 | 15.588 | 3.3621 | 2.4164 | 7.197 | 15.7234 | 3.2241 | 2.3172 | 6.6266 | 15.8565 | 3.0665 | 2.204 | 5.9308 | 15.9892 | 2.9893 | 2.1484 | 5.2307 | 16.4277 | 2.7703 | 1.9911 | 3.0129 | 16.8572 | 3.3321 | 2.3948 | 0.60475 | 17.1375 | 5.4058 | 3.8853 | -1.4121 | 17.4006 | 8.5359 | 6.1349 | -2.6742 | 17.5695 | 9.2995 | 6.6837 | -3.3207 | 15.167 | 4.6622 | 3.3508 | 10.6136 | 15.1628 | 4.0384 | 2.9025 | 7.5342 | 15.2175 | 3.7285 | 2.6798 | 6.6172 | 15.3016 | 3.4722 | 2.4955 | 6.3434 | 15.4251 | 3.1244 | 2.2456 | 5.6658 | 15.5601 | 2.9704 | 2.1349 | 4.7995 | 15.739 | 2.7512 | 1.9773 | 3.7983 | 16.0106 | 2.9896 | 2.1487 | 2.2922 | 16.1724 | 3.0548 | 2.1955 | 0.74419 | 16.3278 | 3.387 | 2.4343 | -0.79248 | 16.7823 | 9.188 | 6.6036 | -4.8784 | 17.2198 | 8.2937 | 5.9609 | -8.9389 | 17.5435 | 7.4835 | 5.3786 | -12.4449 | 17.7822 | 6.9064 | 4.9638 | -14.4955 | 17.8504 | 6.805 | 4.8909 | -14.3335
HAVERTHWAITE | ULVERSTON | HARKER / HUTTON | 334234 | 483827 | 13.0402 | 13.0402 | 13.0402 | 7.2543 | 13.0861 | 13.0861 | 13.0861 | 6.945 | 13.1498 | 13.1498 | 13.1498 | 6.829 | 13.2372 | 13.2372 | 13.2372 | 6.7762 | 13.3447 | 13.3447 | 13.3447 | 6.6849 | 13.4159 | 13.4159 | 13.4159 | 6.5848 | 13.5008 | 13.5008 | 13.5008 | 6.4947 | 13.5911 | 13.5911 | 13.5911 | 6.4136 | 13.6568 | 13.6568 | 13.6568 | 6.3194 | 13.7214 | 13.7214 | 13.7214 | 6.2401 | 13.9452 | 13.9452 | 13.9452 | 5.6929 | 14.1862 | 14.1862 | 14.1862 | 4.7265 | 14.3558 | 14.3558 | 14.3558 | 3.8376 | 14.4623 | 14.4623 | 14.4623 | 2.9926 | 14.5243 | 14.5243 | 14.5243 | 2.1726 | 13.0354 | 13.0354 | 13.0354 | 7.2543 | 13.0849 | 13.0849 | 13.0849 | 7.142 | 13.1385 | 13.1385 | 13.1385 | 7.0417 | 13.2166 | 13.2166 | 13.2166 | 6.9639 | 13.3249 | 13.3249 | 13.3249 | 6.8877 | 13.4231 | 13.4231 | 13.4231 | 6.8337 | 13.4849 | 13.4849 | 13.4849 | 6.7657 | 13.5468 | 13.5468 | 13.5468 | 6.6814 | 13.5812 | 13.5812 | 13.5812 | 6.592 | 13.6175 | 13.6175 | 13.6175 | 6.5041 | 13.7381 | 13.7381 | 13.7381 | 6.2459 | 13.866 | 13.866 | 13.866 | 5.9921 | 13.9941 | 13.9941 | 13.9941 | 5.7136 | 14.1411 | 14.1411 | 14.1411 | 5.3046 | 14.2563 | 14.2563 | 14.2563 | 4.875 | 13.0427 | 13.0427 | 13.0427 | 7.2543 | 13.0907 | 13.0907 | 13.0907 | 6.9019 | 13.1577 | 13.1577 | 13.1577 | 6.7785 | 13.2499 | 13.2499 | 13.2499 | 6.7251 | 13.3643 | 13.3643 | 13.3643 | 6.6338 | 13.4482 | 13.4482 | 13.4482 | 6.5341 | 13.5416 | 13.5416 | 13.5416 | 6.4439 | 13.6248 | 13.6248 | 13.6248 | 6.3638 | 13.6915 | 13.6915 | 13.6915 | 6.2887 | 13.7565 | 13.7565 | 13.7565 | 6.2299 | 13.9903 | 13.9903 | 13.9903 | 5.7437 | 14.2504 | 14.2504 | 14.2504 | 4.845 | 14.4341 | 14.4341 | 14.4341 | 4.0253 | 14.5622 | 14.5622 | 14.5622 | 3.2916 | 14.6405 | 14.6405 | 14.6405 | 2.6227 | 13.0427 | 13.0427 | 13.0427 | 7.2543 | 13.0382 | 13.0382 | 13.0382 | 7.055 | 13.0617 | 13.0617 | 13.0617 | 6.9575 | 13.1061 | 13.1061 | 13.1061 | 6.8698 | 13.1757 | 13.1757 | 13.1757 | 6.7713 | 13.2834 | 13.2834 | 13.2834 | 6.6664 | 13.4085 | 13.4085 | 13.4085 | 6.5127 | 13.5059 | 13.5059 | 13.5059 | 6.2035 | 13.584 | 13.584 | 13.584 | 5.8684 | 13.6632 | 13.6632 | 13.6632 | 5.5034 | 13.9078 | 13.9078 | 13.9078 | 4.4602 | 14.1417 | 14.1417 | 14.1417 | 3.4928 | 14.2931 | 14.2931 | 14.2931 | 2.7854 | 14.3872 | 14.3872 | 14.3872 | 2.4637 | 14.3921 | 14.3921 | 14.3921 | 2.8855 | 13.0402 | 13.0402 | 13.0402 | 7.2543 | 13.0783 | 13.0783 | 13.0783 | 7.1063 | 13.1202 | 13.1202 | 13.1202 | 7.0163 | 13.1753 | 13.1753 | 13.1753 | 6.9634 | 13.2499 | 13.2499 | 13.2499 | 6.9095 | 13.3604 | 13.3604 | 13.3604 | 6.871 | 13.4418 | 13.4418 | 13.4418 | 6.8298 | 13.5251 | 13.5251 | 13.5251 | 6.7768 | 13.5804 | 13.5804 | 13.5804 | 6.6875 | 13.6376 | 13.6376 | 13.6376 | 6.5989 | 13.8364 | 13.8364 | 13.8364 | 6.2455 | 14.0493 | 14.0493 | 14.0493 | 5.7853 | 14.1951 | 14.1951 | 14.1951 | 5.474 | 14.3134 | 14.3134 | 14.3134 | 5.143 | 14.373 | 14.373 | 14.373 | 4.9519 | 13.0402 | 13.0402 | 13.0402 | 7.2543 | 13.0633 | 13.0633 | 13.0633 | 6.9154 | 13.1243 | 13.1243 | 13.1243 | 6.7781 | 13.2128 | 13.2128 | 13.2128 | 6.6698 | 13.3211 | 13.3211 | 13.3211 | 6.5528 | 13.3985 | 13.3985 | 13.3985 | 6.438 | 13.4831 | 13.4831 | 13.4831 | 6.2767 | 13.5881 | 13.5881 | 13.5881 | 5.9509 | 13.6669 | 13.6669 | 13.6669 | 5.6141 | 13.7458 | 13.7458 | 13.7458 | 5.2852 | 13.9884 | 13.9884 | 13.9884 | 4.2292 | 14.2133 | 14.2133 | 14.2133 | 3.2404 | 14.3617 | 14.3617 | 14.3617 | 2.5019 | 14.4464 | 14.4464 | 14.4464 | 2.133 | 14.4523 | 14.4523 | 14.4523 | 2.4923
HAWK GREEN | HAZEL GROVE | BREDBURY | 395915 | 387138 | 30.0071 | 17.3629 | 12.479 | 17.3649 | 30.0673 | 17.4272 | 12.5253 | 17.2572 | 30.1203 | 17.2519 | 12.3993 | 17.1305 | 30.1832 | 17.0911 | 12.2837 | 17.0104 | 30.268 | 16.9147 | 12.157 | 16.8332 | 30.3628 | 16.6443 | 11.9626 | 16.6535 | 30.4676 | 16.358 | 11.7568 | 16.4901 | 30.5895 | 16.1789 | 11.6281 | 16.3361 | 30.688 | 16.1313 | 11.5939 | 16.1311 | 30.7794 | 16.0381 | 11.5269 | 15.9498 | 31.2108 | 15.592 | 11.2063 | 14.4807 | 31.7375 | 14.9712 | 10.7601 | 11.7467 | 32.0305 | 14.42 | 10.364 | 9.4299 | 32.3079 | 13.8689 | 9.9679 | 6.879 | 32.5092 | 13.4106 | 9.6385 | 4.6957 | 29.976 | 17.3629 | 12.479 | 17.3649 | 30.0406 | 17.4389 | 12.5337 | 17.2575 | 30.0969 | 17.3426 | 12.4645 | 17.1468 | 30.1459 | 17.1816 | 12.3488 | 17.024 | 30.2132 | 17.0168 | 12.2303 | 16.8527 | 30.2946 | 16.8414 | 12.1042 | 16.6587 | 30.3969 | 16.574 | 11.9121 | 16.4039 | 30.5219 | 16.4613 | 11.831 | 16.0703 | 30.5928 | 16.3665 | 11.7629 | 15.789 | 30.6647 | 16.2746 | 11.6969 | 15.506 | 30.8827 | 15.9928 | 11.4943 | 14.6643 | 31.0997 | 15.7713 | 11.3351 | 13.8279 | 31.3075 | 15.5302 | 11.1618 | 12.9979 | 31.5365 | 15.3056 | 11.0004 | 12.0626 | 31.7121 | 15.0699 | 10.831 | 11.3853 | 30.0188 | 17.3629 | 12.479 | 17.3649 | 30.0742 | 17.4114 | 12.5139 | 17.2767 | 30.1322 | 17.2151 | 12.3729 | 17.1751 | 30.2025 | 17.0021 | 12.2198 | 17.0957 | 30.2964 | 16.8186 | 12.0878 | 16.9625 | 30.402 | 16.516 | 11.8704 | 16.8338 | 30.5204 | 16.2514 | 11.6802 | 16.7403 | 30.6583 | 16.0526 | 11.5373 | 16.6629 | 30.7645 | 16.0287 | 11.5201 | 16.541 | 30.8623 | 15.8918 | 11.4217 | 16.4296 | 31.3117 | 15.3869 | 11.0588 | 15.1139 | 31.9121 | 14.7308 | 10.5873 | 12.5501 | 32.2102 | 14.1154 | 10.145 | 10.4196 | 32.4903 | 13.5136 | 9.7125 | 8.136 | 32.685 | 13.0002 | 9.3435 | 6.1712 | 30.0188 | 17.3629 | 12.479 | 17.3649 | 29.9978 | 17.4771 | 12.5611 | 17.5224 | 30.0172 | 17.3946 | 12.5018 | 17.4978 | 30.0538 | 17.2632 | 12.4074 | 17.4371 | 30.1198 | 17.0801 | 12.2758 | 17.2942 | 30.2146 | 16.8025 | 12.0763 | 17.1267 | 30.3541 | 16.5644 | 11.9052 | 16.8243 | 30.5889 | 16.191 | 11.6368 | 16.0241 | 30.7728 | 16.0794 | 11.5566 | 15.1747 | 30.8953 | 15.8248 | 11.3736 | 14.3311 | 31.2659 | 15.1142 | 10.8629 | 11.8818 | 31.6556 | 14.443 | 10.3804 | 9.4719 | 31.9422 | 13.8496 | 9.954 | 7.5161 | 32.1664 | 13.3377 | 9.5861 | 6.1939 | 32.1997 | 13.1955 | 9.4838 | 6.9404 | 30.0071 | 17.3629 | 12.479 | 17.3649 | 30.0595 | 17.4436 | 12.5371 | 17.2855 | 30.0946 | 17.2868 | 12.4244 | 17.204 | 30.1296 | 17.1429 | 12.321 | 17.1514 | 30.1793 | 16.9881 | 12.2097 | 17.0773 | 30.2544 | 16.7353 | 12.028 | 16.9723 | 30.3515 | 16.4522 | 11.8245 | 16.8502 | 30.4577 | 16.2751 | 11.6973 | 16.7314 | 30.5474 | 16.2347 | 11.6682 | 16.5394 | 30.6355 | 16.1478 | 11.6057 | 16.3559 | 30.926 | 15.855 | 11.3953 | 15.6981 | 31.2549 | 15.5744 | 11.1936 | 14.832 | 31.4989 | 15.3156 | 11.0076 | 14.1155 | 31.7408 | 15.1246 | 10.8703 | 13.415 | 31.9003 | 15.0125 | 10.7898 | 12.9541 | 30.0071 | 17.3629 | 12.479 | 17.3649 | 30.0144 | 17.4519 | 12.543 | 17.4577 | 30.062 | 17.3533 | 12.4722 | 17.3481 | 30.1315 | 17.1991 | 12.3613 | 17.193 | 30.2253 | 16.9973 | 12.2163 | 16.9658 | 30.3271 | 16.7196 | 12.0167 | 16.7429 | 30.4677 | 16.4696 | 11.8371 | 16.3724 | 30.7208 | 16.0754 | 11.5537 | 15.4748 | 30.9353 | 15.938 | 11.455 | 14.5519 | 31.067 | 15.6697 | 11.2621 | 13.6358 | 31.4428 | 14.9197 | 10.7231 | 10.9737 | 31.8004 | 14.209 | 10.2123 | 8.387 | 32.0634 | 13.5814 | 9.7612 | 6.2568 | 32.26 | 13.0292 | 9.3644 | 4.7099 | 32.2953 | 12.8425 | 9.2302 | 5.1977
HAYDOCK | GOLBORNE | BOLD | 357489 | 397336 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 1.6738 | 2.6844 | 0.44197 | 0.31765 | -2.0796 | 1.5785 | 0.25989 | 0.18679 | -5.293 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.5603 | 2.6844 | 0.44197 | 0.31765 | -0.96212 | 2.6844 | 0.44197 | 0.31765 | -3.8335 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 17.5896 | 2.896 | 2.0814 | 6.9322 | 11.1458 | 1.8351 | 1.3189 | 2.7316 | 5.7756 | 0.95091 | 0.68344 | -0.5514 | 1.8115 | 0.29825 | 0.21436 | -2.5962 | 0.82683 | 0.13613 | 0.09784 | -1.4754 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 9.3238 | 1.5351 | 1.1033 | 8.2104 | 16.0335 | 2.6398 | 1.8973 | 7.7425 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 14.8517 | 2.4452 | 1.7574 | 4.4923 | 7.9454 | 1.3081 | 0.94019 | -0.11209 | 2.0375 | 0.33545 | 0.2411 | -3.8125 | 2.6844 | 0.44197 | 0.31765 | -6.2481 | 2.6844 | 0.44197 | 0.31765 | -5.4515
HDA NO1 & HDA NO2 | STAINBURN & SIDDICK | HARKER / HUTTON | 301743 | 524532 | 8.7163 | 1.6027 | 1.1519 | 8.7163 | 8.8229 | 1.534 | 1.1025 | 8.8229 | 8.3167 | 1.3693 | 0.98413 | 8.3167 | 7.3571 | 1.2113 | 0.87058 | 7.3571 | 6.2125 | 1.0228 | 0.73513 | 6.2125 | 5.0178 | 0.82614 | 0.59376 | 5.0178 | 3.3009 | 0.54347 | 0.3906 | 3.3009 | 1.5203 | 0.25031 | 0.1799 | 1.5203 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 8.6981 | 1.6027 | 1.1519 | 8.6981 | 8.7844 | 1.5539 | 1.1168 | 8.7844 | 8.8509 | 1.4669 | 1.0543 | 8.8509 | 8.3759 | 1.379 | 0.99114 | 8.3759 | 7.73 | 1.2727 | 0.9147 | 7.73 | 7.0438 | 1.1597 | 0.8335 | 7.0438 | 6.3013 | 1.0375 | 0.74564 | 6.3013 | 5.603 | 0.92249 | 0.66301 | 5.603 | 4.9286 | 0.81146 | 0.58321 | 4.9286 | 3.9637 | 0.6526 | 0.46903 | 3.9637 | 0.29871 | 0.049181 | 0.035347 | 0.29871 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 8.7187 | 1.6027 | 1.1519 | 8.7187 | 8.8232 | 1.5126 | 1.0871 | 8.8232 | 7.9022 | 1.301 | 0.93509 | 7.9022 | 6.6626 | 1.097 | 0.7884 | 6.6626 | 5.2778 | 0.86894 | 0.62453 | 5.2778 | 3.8173 | 0.6285 | 0.45171 | 3.8173 | 1.8786 | 0.3093 | 0.2223 | 1.8786 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 8.7188 | 1.6027 | 1.1519 | 8.7188 | 8.8024 | 1.5284 | 1.0985 | 8.8024 | 8.2386 | 1.3564 | 0.97488 | 8.2386 | 7.0442 | 1.1598 | 0.83355 | 7.0442 | 5.7056 | 0.93939 | 0.67516 | 5.7056 | 4.174 | 0.68722 | 0.49392 | 4.174 | 1.7387 | 0.28626 | 0.20574 | 1.7387 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 8.7162 | 1.6027 | 1.1519 | 8.7162 | 8.8092 | 1.5428 | 1.1089 | 8.8092 | 8.4275 | 1.3875 | 0.99724 | 8.4275 | 7.5542 | 1.2437 | 0.89391 | 7.5542 | 6.5513 | 1.0786 | 0.77522 | 6.5513 | 5.5201 | 0.90885 | 0.65321 | 5.5201 | 4.3376 | 0.71415 | 0.51327 | 4.3376 | 2.7902 | 0.45938 | 0.33016 | 2.7902 | 1.1898 | 0.19589 | 0.14079 | 1.1898 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 8.7162 | 1.6027 | 1.1519 | 8.7162 | 8.8117 | 1.5162 | 1.0897 | 8.8117 | 8.0767 | 1.3298 | 0.95572 | 8.0767 | 6.7882 | 1.1176 | 0.80326 | 6.7882 | 5.3693 | 0.88402 | 0.63536 | 5.3693 | 3.8184 | 0.62866 | 0.45183 | 3.8184 | 1.7568 | 0.28924 | 0.20788 | 1.7568 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844
HDA NO1 & HDA NO2 | STAINBURN & SIDDICK | HARKER / HUTTON | 301429 | 525527 | -2.5607 | -0.42159 | -0.30301 | -2.5607 | -2.9777 | -0.49026 | -0.35236 | -2.9777 | -3.9784 | -0.65501 | -0.47077 | -3.9784 | -4.9379 | -0.81299 | -0.58431 | -4.9379 | -6.0826 | -1.0015 | -0.71977 | -6.0826 | -7.2773 | -1.1982 | -0.86114 | -7.2773 | -8.9942 | -1.4808 | -1.0643 | -8.9942 | -10.7748 | -1.774 | -1.275 | -10.7748 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | -2.5607 | -0.42159 | -0.30301 | -2.5607 | -2.8571 | -0.47041 | -0.33809 | -2.8571 | -3.3856 | -0.55742 | -0.40063 | -3.3856 | -3.9191 | -0.64526 | -0.46376 | -3.9191 | -4.5651 | -0.75161 | -0.5402 | -4.5651 | -5.2513 | -0.86459 | -0.6214 | -5.2513 | -5.9938 | -0.98684 | -0.70926 | -5.9938 | -6.6921 | -1.1018 | -0.79189 | -6.6921 | -7.3665 | -1.2128 | -0.87169 | -7.3665 | -8.3314 | -1.3717 | -0.98586 | -8.3314 | -11.9964 | -1.9751 | -1.4196 | -11.9964 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | -2.5607 | -0.42159 | -0.30301 | -2.5607 | -3.1082 | -0.51174 | -0.3678 | -3.1082 | -4.3928 | -0.72325 | -0.51981 | -4.3928 | -5.6324 | -0.92734 | -0.6665 | -5.6324 | -7.0173 | -1.1553 | -0.83037 | -7.0173 | -8.4777 | -1.3958 | -1.0032 | -8.4777 | -10.4165 | -1.715 | -1.2326 | -10.4165 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | -2.5607 | -0.42159 | -0.30301 | -2.5607 | -3.012 | -0.4959 | -0.35641 | -3.012 | -4.0565 | -0.66788 | -0.48002 | -4.0565 | -5.2509 | -0.86452 | -0.62135 | -5.2509 | -6.5894 | -1.0849 | -0.77974 | -6.5894 | -8.1211 | -1.3371 | -0.96098 | -8.1211 | -10.5564 | -1.738 | -1.2492 | -10.5564 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | -2.5607 | -0.42159 | -0.30301 | -2.5607 | -2.9244 | -0.48148 | -0.34605 | -2.9244 | -3.8676 | -0.63677 | -0.45766 | -3.8676 | -4.7408 | -0.78054 | -0.56099 | -4.7408 | -5.7438 | -0.94568 | -0.67968 | -5.7438 | -6.775 | -1.1154 | -0.80169 | -6.775 | -7.9575 | -1.3101 | -0.94163 | -7.9575 | -9.5049 | -1.5649 | -1.1247 | -9.5049 | -11.1053 | -1.8284 | -1.3141 | -11.1053 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | -2.5607 | -0.42159 | -0.30301 | -2.5607 | -3.0861 | -0.5081 | -0.36518 | -3.0861 | -4.2184 | -0.69453 | -0.49917 | -4.2184 | -5.5069 | -0.90667 | -0.65164 | -5.5069 | -6.9258 | -1.1403 | -0.81954 | -6.9258 | -8.4767 | -1.3956 | -1.0031 | -8.4767 | -10.5383 | -1.7351 | -1.247 | -10.5383 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844
HEADY HILL | CASTLETON | ROCHDALE | 384370 | 410583 | 22.8913 | 11.0127 | 8.0336 | 12.6036 | 22.9606 | 10.9166 | 7.9635 | 10.3412 | 23.0357 | 9.6546 | 7.0429 | 9.7561 | 23.1486 | 8.5405 | 6.2302 | 9.5928 | 23.3294 | 7.2074 | 5.2577 | 9.3424 | 23.5809 | 5.6408 | 4.1149 | 9.0156 | 24.4364 | 4.2809 | 3.1228 | 8.096 | 24.8481 | 4.0808 | 2.9769 | 7.6938 | 23.9932 | 3.8919 | 2.8391 | 7.2109 | 23.451 | 3.804 | 2.7749 | 6.7047 | 20.5977 | 3.3411 | 2.4373 | 4.2421 | 19.7492 | 3.2035 | 2.3369 | 0.72227 | 27.1011 | 4.3961 | 3.2069 | -2.415 | 29.9852 | 5.8648 | 4.2783 | -4.8806 | 30.3453 | 5.7943 | 4.2269 | -7.1862 | 22.8844 | 11.0127 | 8.0336 | 12.6036 | 22.9442 | 10.9489 | 7.9871 | 12.1255 | 22.9983 | 9.7564 | 7.1172 | 11.9364 | 23.0686 | 8.5677 | 6.25 | 11.8246 | 23.1666 | 7.4318 | 5.4214 | 11.6489 | 23.2903 | 6.3051 | 4.5995 | 11.4558 | 23.4538 | 4.7347 | 3.4539 | 11.1902 | 23.6692 | 4.7249 | 3.4467 | 10.8053 | 23.8722 | 4.6937 | 3.424 | 10.4549 | 24.1141 | 4.6859 | 3.4183 | 10.078 | 25.1 | 4.5526 | 3.3211 | 8.7691 | 26.2276 | 4.3603 | 3.1808 | 7.118 | 27.7732 | 5.0128 | 3.6568 | 4.7945 | 28.6708 | 6.1618 | 4.4949 | 2.5933 | 29.2461 | 6.1526 | 4.4883 | 1.0165 | 22.8939 | 11.0127 | 8.0336 | 12.6036 | 22.9593 | 10.8505 | 7.9153 | 9.9844 | 23.0316 | 9.5512 | 6.9675 | 9.3286 | 23.1365 | 8.4017 | 6.1289 | 9.1691 | 23.3012 | 7.0178 | 5.1194 | 8.927 | 23.5237 | 5.4606 | 3.9834 | 8.6482 | 24.3061 | 4.0769 | 2.974 | 7.8565 | 23.8223 | 3.8642 | 2.8189 | 7.5714 | 22.9183 | 3.7176 | 2.7119 | 7.2363 | 22.0961 | 3.5842 | 2.6146 | 6.8251 | 18.1777 | 2.9486 | 2.151 | 4.1235 | 18.6686 | 3.0282 | 2.2091 | 0.60652 | 25.639 | 4.1589 | 3.0339 | -2.1492 | 29.9342 | 5.369 | 3.9166 | -4.6352 | 30.2781 | 5.5816 | 4.0717 | -6.8396 | 22.894 | 11.0127 | 8.0336 | 12.6036 | 22.8938 | 11.0107 | 8.0321 | 10.8631 | 22.9434 | 10.8187 | 7.8921 | 10.399 | 23.6203 | 10.7048 | 7.809 | 9.6684 | 24.3385 | 10.2933 | 7.5088 | 8.8715 | 25.0283 | 9.8157 | 7.1604 | 8.1284 | 25.2925 | 9.4606 | 6.9013 | 7.7878 | 25.7164 | 9.0258 | 6.5842 | 6.9323 | 26.1773 | 8.9281 | 6.5129 | 5.9089 | 26.6346 | 8.6749 | 6.3282 | 4.8488 | 28.0995 | 7.6829 | 5.6045 | 1.552 | 29.0213 | 6.9965 | 5.1038 | -1.7394 | 29.6157 | 6.3968 | 4.6663 | -4.1484 | 29.9145 | 6.0505 | 4.4137 | -5.6223 | 29.9891 | 5.9239 | 4.3214 | -5.5036 | 22.8912 | 11.0127 | 8.0336 | 12.6036 | 22.9487 | 11.1625 | 8.1429 | 11.7542 | 23.006 | 9.9522 | 7.26 | 11.4756 | 23.0839 | 8.8488 | 6.455 | 11.3658 | 23.2077 | 7.5492 | 5.507 | 11.2283 | 23.3936 | 5.9971 | 4.3748 | 11.0504 | 24.1682 | 4.6737 | 3.4094 | 10.2859 | 24.4748 | 4.4891 | 3.2747 | 9.9829 | 24.8607 | 4.3269 | 3.1564 | 9.5588 | 25.3091 | 4.2273 | 3.0838 | 9.0959 | 23.9534 | 3.8855 | 2.8344 | 7.3304 | 24.2407 | 3.9321 | 2.8684 | 5.1337 | 28.8554 | 5.4421 | 3.9699 | 3.085 | 29.2555 | 7.0808 | 5.1654 | 1.8433 | 29.4678 | 7.4299 | 5.42 | 1.1254 | 22.8912 | 11.0127 | 8.0336 | 12.6036 | 22.8974 | 10.8088 | 7.8849 | 9.7768 | 22.9584 | 10.5752 | 7.7144 | 9.0646 | 23.6432 | 10.4443 | 7.619 | 8.2998 | 24.357 | 10.039 | 7.3233 | 7.4783 | 25.0143 | 9.559 | 6.9731 | 6.7375 | 25.2209 | 9.2123 | 6.7203 | 6.377 | 25.5769 | 8.7272 | 6.3664 | 5.4851 | 26.036 | 8.655 | 6.3137 | 4.4825 | 26.4335 | 8.4065 | 6.1324 | 3.4375 | 27.9351 | 7.4639 | 5.4448 | 0.083882 | 29.2361 | 6.6465 | 4.8485 | -3.3875 | 29.945 | 6.0174 | 4.3896 | -6.1145 | 30.3113 | 5.6083 | 4.0912 | -7.8672 | 30.4165 | 5.4463 | 3.973 | -7.9589
HEAP BRIDGE | BURY | KEARSLEY | 382793 | 410428 | 6.7708 | 6.7708 | 6.7708 | 6.7708 | 6.8623 | 6.8623 | 6.8623 | 5.8287 | 7.0032 | 7.0032 | 7.0032 | 5.2899 | 7.1674 | 7.1674 | 7.057 | 5.126 | 7.3612 | 7.3612 | 6.9865 | 4.8805 | 7.5863 | 7.5863 | 6.9128 | 4.5791 | 7.8023 | 7.8023 | 6.8409 | 4.2272 | 7.9657 | 7.9657 | 6.766 | 3.8114 | 8.1543 | 8.1543 | 6.6822 | 3.3289 | 8.3509 | 8.3509 | 6.6369 | 2.8255 | 9.0293 | 8.9067 | 6.4973 | 1.1171 | 9.7373 | 9.32 | 6.7988 | -0.63058 | 10.2517 | 10.2517 | 7.8737 | -1.8524 | 10.714 | 10.714 | 9.219 | -2.8534 | 11.0611 | 11.0611 | 9.5239 | -3.6974 | 6.7711 | 6.7711 | 6.7711 | 6.7711 | 6.8403 | 6.8403 | 6.8403 | 6.8403 | 6.9243 | 6.9243 | 6.9243 | 6.9243 | 7.0211 | 7.0211 | 7.0211 | 6.8234 | 7.1427 | 7.1427 | 7.1427 | 6.7312 | 7.2912 | 7.2912 | 7.2343 | 6.6262 | 7.4664 | 7.4664 | 7.1805 | 6.4955 | 7.6695 | 7.6695 | 7.14 | 6.3267 | 7.8878 | 7.8878 | 7.0926 | 6.085 | 8.1236 | 8.1236 | 7.0374 | 5.7776 | 8.7857 | 8.7857 | 6.8443 | 4.6462 | 9.5309 | 9.1057 | 6.6425 | 3.3645 | 10.0817 | 9.8731 | 7.2023 | 2.0942 | 10.66 | 10.66 | 8.1502 | 0.70229 | 11.0581 | 11.0581 | 8.2698 | -0.3048 | 6.771 | 6.771 | 6.771 | 6.771 | 6.863 | 6.863 | 6.863 | 5.5366 | 7.0027 | 7.0027 | 7.0027 | 4.9345 | 7.1635 | 7.1635 | 6.9761 | 4.7529 | 7.3494 | 7.3494 | 6.8978 | 4.4814 | 7.5602 | 7.5602 | 6.8186 | 4.1654 | 7.7139 | 7.7139 | 6.7302 | 3.802 | 7.8406 | 7.8406 | 6.627 | 3.3773 | 7.9905 | 7.9905 | 6.5538 | 2.941 | 8.1485 | 8.1485 | 6.5386 | 2.4853 | 8.7529 | 8.7529 | 6.3914 | 0.81788 | 9.439 | 9.1121 | 6.6472 | -1.022 | 9.9387 | 9.9387 | 7.6889 | -2.3208 | 10.3222 | 10.3222 | 9.0137 | -3.2813 | 10.5985 | 10.5985 | 9.329 | -3.8964 | 6.771 | 6.771 | 6.771 | 6.771 | 6.8085 | 6.8085 | 6.8085 | 6.1671 | 6.9017 | 6.9017 | 6.9017 | 5.7158 | 7.0156 | 7.0156 | 7.0156 | 5.5779 | 7.1694 | 7.1694 | 7.019 | 5.3727 | 7.3865 | 7.3865 | 6.929 | 5.0589 | 7.587 | 7.587 | 6.8367 | 4.6526 | 7.7684 | 7.7684 | 7.049 | 4.1054 | 7.9861 | 7.9861 | 7.1516 | 3.5223 | 8.2136 | 8.2136 | 7.385 | 2.9172 | 8.8712 | 8.8712 | 8.8712 | 1.0702 | 9.461 | 9.461 | 9.461 | -0.6086 | 9.8624 | 9.8624 | 9.777 | -1.7311 | 10.146 | 10.146 | 9.5818 | -2.5108 | 10.2518 | 10.2518 | 9.5103 | -2.473 | 6.7708 | 6.7708 | 6.7708 | 6.7708 | 6.8491 | 6.8491 | 6.8491 | 6.7794 | 6.9563 | 6.9563 | 6.9563 | 6.4503 | 7.0683 | 7.0683 | 7.0683 | 6.3221 | 7.2019 | 7.2019 | 7.1609 | 6.1785 | 7.3907 | 7.3907 | 7.0939 | 5.9489 | 7.6291 | 7.6291 | 7.0302 | 5.6583 | 7.8338 | 7.8338 | 6.9645 | 5.3216 | 7.9986 | 7.9986 | 6.89 | 4.9089 | 8.1742 | 8.1742 | 6.8527 | 4.4682 | 8.7657 | 8.7657 | 6.7426 | 2.9911 | 9.3574 | 9.3574 | 7.0951 | 1.5165 | 9.7803 | 9.7803 | 8.2081 | 0.46515 | 10.1372 | 10.1372 | 9.5922 | -0.35968 | 10.3765 | 10.3765 | 9.9673 | -0.82076 | 6.7708 | 6.7708 | 6.7708 | 6.7708 | 6.8364 | 6.8364 | 6.8364 | 5.2905 | 6.9719 | 6.9719 | 6.9719 | 4.6418 | 7.1325 | 7.1325 | 6.9439 | 4.48 | 7.3193 | 7.3193 | 6.8713 | 4.2581 | 7.53 | 7.53 | 6.7856 | 3.9696 | 7.7481 | 7.7481 | 6.6988 | 3.6126 | 7.9532 | 7.9532 | 6.9149 | 3.0998 | 8.1764 | 8.1764 | 7.0194 | 2.5535 | 8.4088 | 8.4088 | 7.257 | 1.9857 | 9.1318 | 9.1318 | 9.1318 | 0.17506 | 9.819 | 9.819 | 9.819 | -1.5564 | 10.3132 | 10.3132 | 9.6235 | -2.766 | 10.6649 | 10.6649 | 9.4169 | -3.6254 | 10.816 | 10.816 | 9.3412 | -3.6103
HEASANDFORD | BURNLEY | ROCHDALE | 385349 | 433821 | 28.7089 | 9.1899 | 6.7039 | 19.5645 | 28.7634 | 8.9524 | 6.5306 | 18.3047 | 28.8198 | 8.8793 | 6.4773 | 17.9895 | 28.8839 | 8.849 | 6.4552 | 17.9322 | 28.9604 | 8.7934 | 6.4146 | 17.8918 | 29.0488 | 8.7484 | 6.3818 | 17.8563 | 29.1291 | 8.7129 | 6.3559 | 17.8359 | 29.1777 | 8.6318 | 6.2968 | 17.8178 | 29.2288 | 8.5964 | 6.2709 | 17.7328 | 29.2782 | 8.5848 | 6.2625 | 17.656 | 29.5667 | 8.4402 | 6.157 | 17.1651 | 30.0256 | 8.2432 | 6.0133 | 16.3264 | 30.195 | 8.1816 | 5.9684 | 15.6321 | 30.2621 | 9.013 | 6.5748 | 14.9218 | 30.2735 | 8.869 | 6.4698 | 14.4062 | 28.7009 | 9.1899 | 6.7039 | 19.5645 | 28.7355 | 9.1081 | 6.6442 | 19.1219 | 28.766 | 9.0557 | 6.606 | 18.9566 | 28.798 | 9.0267 | 6.5848 | 18.91 | 28.8367 | 8.9902 | 6.5582 | 18.8928 | 28.8838 | 8.9626 | 6.5381 | 18.8769 | 28.9401 | 8.781 | 6.4056 | 18.8584 | 29.0049 | 8.7524 | 6.3848 | 18.8372 | 29.067 | 8.7163 | 6.3584 | 18.7287 | 29.1214 | 8.6842 | 6.335 | 18.6223 | 29.2468 | 8.586 | 6.2633 | 18.3212 | 29.3804 | 8.5257 | 6.2194 | 18.0446 | 29.4965 | 8.5463 | 6.2344 | 17.8226 | 29.6059 | 9.1089 | 6.6448 | 17.6094 | 29.671 | 9.7469 | 7.1102 | 17.4599 | 28.7104 | 9.1899 | 6.7039 | 19.5645 | 28.7614 | 8.9122 | 6.5013 | 18.0987 | 28.8167 | 8.8206 | 6.4345 | 17.7481 | 28.8812 | 8.7612 | 6.3911 | 17.6888 | 28.9576 | 8.7157 | 6.358 | 17.6477 | 29.045 | 8.6659 | 6.3216 | 17.6116 | 29.1307 | 8.5584 | 6.2433 | 17.59 | 29.1798 | 8.5772 | 6.257 | 17.5709 | 29.2262 | 8.5386 | 6.2288 | 17.5148 | 29.2714 | 8.507 | 6.2057 | 17.471 | 29.559 | 8.3063 | 6.0594 | 17.0848 | 30.0243 | 8.0971 | 5.9067 | 16.365 | 30.1561 | 8.0222 | 5.8521 | 15.7988 | 30.2056 | 8.807 | 6.4246 | 15.2697 | 30.1829 | 8.6686 | 6.3236 | 14.9909 | 28.7105 | 9.1899 | 6.7039 | 19.5645 | 28.7462 | 9.0006 | 6.5658 | 18.5452 | 28.7881 | 8.9427 | 6.5236 | 18.2837 | 28.8366 | 8.8884 | 6.4839 | 18.2382 | 28.9007 | 8.7993 | 6.419 | 18.2077 | 28.9895 | 8.7956 | 6.4163 | 18.1736 | 29.1068 | 8.6199 | 6.2881 | 18.0931 | 29.2699 | 8.3828 | 6.1151 | 17.8457 | 29.4245 | 8.039 | 5.8643 | 17.5602 | 29.5782 | 8.0548 | 5.8758 | 17.2884 | 29.8705 | 8.8432 | 6.451 | 16.5352 | 30.026 | 8.5642 | 6.2474 | 15.8491 | 30.0978 | 8.35 | 6.0912 | 15.3238 | 30.1228 | 8.3659 | 6.1028 | 15.0816 | 30.0548 | 8.3811 | 6.1139 | 15.6016 | 28.7088 | 9.1899 | 6.7039 | 19.5645 | 28.7515 | 9.0302 | 6.5874 | 18.7125 | 28.7919 | 8.9683 | 6.5422 | 18.4779 | 28.8325 | 8.9442 | 6.5246 | 18.4393 | 28.8799 | 8.8992 | 6.4919 | 18.434 | 28.9458 | 8.8653 | 6.4671 | 18.4264 | 29.0303 | 8.8308 | 6.4419 | 18.4134 | 29.0946 | 8.7378 | 6.3741 | 18.3945 | 29.1406 | 8.7203 | 6.3613 | 18.3037 | 29.1891 | 8.7052 | 6.3503 | 18.2148 | 29.3515 | 8.6207 | 6.2887 | 17.9443 | 29.5125 | 8.5568 | 6.2421 | 17.6813 | 29.6263 | 8.6237 | 6.2908 | 17.5171 | 29.716 | 9.627 | 7.0228 | 17.4017 | 29.7288 | 9.5851 | 6.9922 | 17.4941 | 28.7088 | 9.1899 | 6.7039 | 19.5645 | 28.7427 | 8.8922 | 6.4868 | 17.9264 | 28.7917 | 8.8079 | 6.4253 | 17.543 | 28.8491 | 8.7399 | 6.3756 | 17.4785 | 28.9173 | 8.664 | 6.3203 | 17.4318 | 28.9945 | 8.6434 | 6.3052 | 17.3922 | 29.0927 | 8.4662 | 6.176 | 17.3083 | 29.2446 | 8.2294 | 6.0032 | 17.0477 | 29.3896 | 7.9238 | 5.7803 | 16.7506 | 29.5371 | 7.8922 | 5.7573 | 16.4682 | 29.8802 | 8.6654 | 6.3213 | 15.6893 | 30.0405 | 8.3777 | 6.1114 | 14.9869 | 30.1288 | 8.1556 | 5.9494 | 14.4383 | 30.1617 | 8.1596 | 5.9523 | 14.1587 | 30.1045 | 8.158 | 5.9512 | 14.6239
HEATON MOOR | VERNON PARK | BREDBURY | 387623 | 391345 | 29.6186 | 10.0245 | 7.3127 | 15.8512 | 29.8379 | 9.6737 | 7.0568 | 14.4404 | 30.0559 | 9.3982 | 6.8559 | 13.6562 | 30.335 | 9.1608 | 6.6826 | 12.9256 | 30.6768 | 8.8481 | 6.4546 | 12.1348 | 31.0795 | 8.3474 | 6.0893 | 11.3271 | 31.4622 | 8.0691 | 5.8863 | 10.5142 | 31.7741 | 7.9145 | 5.7735 | 9.6816 | 32.0714 | 7.6523 | 5.5823 | 8.7824 | 32.3769 | 7.3615 | 5.3701 | 7.8853 | 33.43 | 6.7001 | 4.8877 | 5.5635 | 34.5114 | 6.0053 | 4.3808 | 2.5853 | 33.5951 | 5.4495 | 3.9753 | 0.42789 | 30.1443 | 4.8897 | 3.567 | -1.5115 | 27.3608 | 4.4382 | 3.2376 | -2.7402 | 29.5701 | 10.0245 | 7.3127 | 15.8512 | 29.7225 | 9.7783 | 7.1332 | 14.777 | 29.8323 | 9.5664 | 6.9786 | 14.1597 | 29.9786 | 9.3577 | 6.8263 | 13.5338 | 30.1749 | 9.1251 | 6.6566 | 12.8424 | 30.416 | 8.8172 | 6.432 | 12.1383 | 30.7037 | 8.4663 | 6.176 | 11.3679 | 31.035 | 8.2533 | 6.0207 | 10.5313 | 31.2794 | 8.0535 | 5.8749 | 9.744 | 31.535 | 7.8501 | 5.7265 | 8.9328 | 32.1189 | 7.4397 | 5.4272 | 7.6334 | 32.7973 | 6.9918 | 5.1004 | 6.2939 | 33.438 | 6.6997 | 4.8874 | 5.059 | 34.0589 | 6.2398 | 4.5519 | 3.756 | 34.4498 | 6.0523 | 4.4151 | 2.91 | 29.6336 | 10.0245 | 7.3127 | 15.8512 | 29.8466 | 9.6291 | 7.0243 | 14.3353 | 30.0785 | 9.3129 | 6.7936 | 13.4822 | 30.3771 | 8.9931 | 6.5603 | 12.7028 | 30.7383 | 8.6385 | 6.3016 | 11.8613 | 31.1571 | 8.067 | 5.8848 | 11.0057 | 31.5909 | 7.8851 | 5.7521 | 10.1611 | 31.9251 | 7.6357 | 5.5701 | 9.2957 | 32.2326 | 7.3173 | 5.3378 | 8.3543 | 32.5566 | 6.9848 | 5.0953 | 7.3535 | 33.7448 | 6.2037 | 4.5255 | 4.7759 | 33.3247 | 5.4056 | 3.9433 | 1.7348 | 29.4703 | 4.7804 | 3.4872 | -0.31027 | 25.6288 | 4.1572 | 3.0327 | -1.9093 | 22.9341 | 3.7201 | 2.7138 | -2.4904 | 29.6338 | 10.0245 | 7.3127 | 15.8512 | 29.7805 | 9.709 | 7.0826 | 14.6808 | 29.9477 | 9.4609 | 6.9016 | 13.9498 | 30.1713 | 9.1258 | 6.6572 | 13.2327 | 30.4741 | 8.7394 | 6.3753 | 12.4164 | 30.8954 | 8.3601 | 6.0986 | 11.5311 | 31.419 | 7.9979 | 5.8344 | 10.5124 | 31.8631 | 7.5895 | 5.5364 | 9.0922 | 32.2697 | 7.3339 | 5.35 | 7.6399 | 32.6843 | 7.0294 | 5.1278 | 6.1956 | 33.9267 | 6.1923 | 4.5172 | 3.18 | 33.5072 | 5.4352 | 3.9649 | 0.58692 | 29.9931 | 4.8652 | 3.5491 | -0.99771 | 27.01 | 4.3813 | 3.1961 | -1.7825 | 25.6071 | 4.1537 | 3.0301 | -1.2326 | 29.6183 | 10.0245 | 7.3127 | 15.8512 | 29.7932 | 9.7381 | 7.1038 | 14.6491 | 29.9449 | 9.4762 | 6.9128 | 13.9712 | 30.1278 | 9.2768 | 6.7673 | 13.3463 | 30.3619 | 8.9895 | 6.5578 | 12.6901 | 30.6876 | 8.4989 | 6.1999 | 11.9881 | 31.1019 | 8.2363 | 6.0083 | 11.2552 | 31.4584 | 8.112 | 5.9176 | 10.5096 | 31.6982 | 7.865 | 5.7374 | 9.6772 | 31.957 | 7.5797 | 5.5293 | 8.8284 | 32.8414 | 7.0579 | 5.1487 | 7.2401 | 33.7001 | 6.6221 | 4.8307 | 5.5701 | 34.2523 | 6.2621 | 4.5681 | 4.3913 | 34.7207 | 5.8885 | 4.2956 | 3.3419 | 34.365 | 5.5743 | 4.0664 | 2.7051 | 29.6183 | 10.0245 | 7.3127 | 15.8512 | 29.7755 | 9.644 | 7.0351 | 14.4447 | 29.9815 | 9.3669 | 6.833 | 13.5756 | 30.2504 | 9.0102 | 6.5728 | 12.7429 | 30.5768 | 8.6098 | 6.2807 | 11.8326 | 30.9522 | 8.2186 | 5.9954 | 10.9092 | 31.3974 | 7.8598 | 5.7336 | 9.8511 | 31.8868 | 7.407 | 5.4033 | 8.3528 | 32.2721 | 7.1464 | 5.2132 | 6.8464 | 32.67 | 6.8343 | 4.9855 | 5.3435 | 33.9217 | 5.9637 | 4.3505 | 2.1477 | 31.8207 | 5.1616 | 3.7653 | -0.67276 | 28.0339 | 4.5474 | 3.3172 | -2.4832 | 24.7864 | 4.0206 | 2.933 | -3.4961 | 23.1034 | 3.7476 | 2.7338 | -3.1912
HEATON NORRIS | VERNON PARK | BREDBURY | 388860 | 391967 | 24.1563 | 6.6236 | 4.8318 | 12.8187 | 24.2429 | 6.2488 | 4.5584 | 11.0053 | 24.3647 | 5.9665 | 4.3525 | 10.2446 | 24.5118 | 5.728 | 4.1785 | 9.7633 | 24.6856 | 5.4148 | 3.9501 | 9.261 | 27.5255 | 4.4649 | 3.2571 | 5.9977 | 24.8474 | 4.0305 | 2.9402 | 5.5909 | 24.9345 | 4.0446 | 2.9505 | 5.194 | 23.7488 | 3.8523 | 2.8102 | 4.7417 | 22.3462 | 3.6248 | 2.6442 | 4.2959 | 14.0491 | 2.2789 | 1.6624 | -1.5386 | 9.1507 | 1.4843 | 1.0828 | -4.6195 | 5.9454 | 0.9644 | 0.70351 | -6.4665 | 10.8683 | 1.7629 | 1.286 | -8.201 | 17.2027 | 2.7905 | 2.0356 | -8.8706 | 24.1399 | 6.6236 | 4.8318 | 12.8187 | 24.2183 | 6.4609 | 4.7131 | 11.9277 | 24.3103 | 6.2513 | 4.5602 | 11.4308 | 24.4216 | 5.9793 | 4.3618 | 11.0449 | 24.552 | 5.8192 | 4.245 | 10.6629 | 24.7078 | 5.5439 | 4.0442 | 10.2858 | 24.8927 | 5.1963 | 3.7906 | 9.8694 | 25.1048 | 5.0345 | 3.6726 | 9.4094 | 25.2226 | 4.8744 | 3.5558 | 8.9218 | 25.3504 | 4.7033 | 3.431 | 8.4241 | 25.7683 | 4.3484 | 3.1721 | 7.5618 | 24.2525 | 3.934 | 2.8698 | 5.9322 | 21.9197 | 3.5556 | 2.5937 | 4.8718 | 26.3702 | 4.2775 | 3.1204 | 3.7787 | 27.5543 | 5.0304 | 3.6696 | 3.0751 | 24.1633 | 6.6236 | 4.8318 | 12.8187 | 24.2709 | 6.1639 | 4.4965 | 10.7312 | 24.4171 | 5.8164 | 4.243 | 9.8611 | 24.5956 | 5.4997 | 4.0119 | 9.3025 | 24.8052 | 5.1451 | 3.7533 | 8.7192 | 25.5532 | 4.145 | 3.0237 | 5.4231 | 23.6838 | 3.8417 | 2.8025 | 4.9259 | 22.695 | 3.6813 | 2.6855 | 4.3963 | 21.069 | 3.4176 | 2.4931 | 3.8934 | 19.4198 | 3.1501 | 2.2979 | 3.3733 | 9.7718 | 1.5851 | 1.1563 | -3.0722 | 4.8276 | 0.78308 | 0.57125 | -5.5919 | 1.3862 | 0.22486 | 0.16403 | -7.1973 | 6.0821 | 0.98657 | 0.71969 | -8.4508 | 12.7615 | 2.07 | 1.5101 | -8.3204 | 24.1633 | 6.6236 | 4.8318 | 12.8187 | 24.2036 | 6.2644 | 4.5698 | 11.2796 | 24.2883 | 6.0025 | 4.3787 | 10.5674 | 24.3955 | 5.6793 | 4.143 | 10.0658 | 24.5386 | 5.3513 | 3.9037 | 9.5261 | 27.3336 | 4.4621 | 3.255 | 6.2558 | 25.8974 | 4.2008 | 3.0644 | 5.6503 | 20.3699 | 3.3042 | 2.4104 | 1.724 | 15.7548 | 2.5556 | 1.8643 | -1.3923 | 14.8539 | 2.4095 | 1.7577 | -2.1708 | 10.1653 | 1.6489 | 1.2029 | -4.3087 | 5.7713 | 0.93616 | 0.68291 | -6.4863 | 4.0531 | 0.65746 | 0.47961 | -7.6998 | 16.5074 | 2.6777 | 1.9533 | -8.2034 | 15.7192 | 2.5498 | 1.86 | -6.9825 | 24.1563 | 6.6236 | 4.8318 | 12.8187 | 24.2338 | 6.3619 | 4.6409 | 11.5234 | 24.327 | 6.1096 | 4.4569 | 10.9046 | 24.4294 | 5.8941 | 4.2997 | 10.4939 | 24.5549 | 5.6154 | 4.0964 | 10.1027 | 27.3912 | 4.6845 | 3.4173 | 6.9382 | 26.282 | 4.2632 | 3.1099 | 6.5987 | 26.4367 | 4.2883 | 3.1283 | 6.2487 | 25.3291 | 4.1086 | 2.9972 | 5.8105 | 23.935 | 3.8825 | 2.8322 | 5.3569 | 16.5218 | 2.68 | 1.955 | 0.17819 | 13.5149 | 2.1922 | 1.5992 | -1.491 | 11.7532 | 1.9065 | 1.3908 | -2.3203 | 17.9879 | 2.9178 | 2.1285 | -3.1718 | 25.4184 | 4.1231 | 3.0078 | -3.1621 | 24.1563 | 6.6236 | 4.8318 | 12.8187 | 24.2286 | 6.1177 | 4.4628 | 10.6268 | 24.3597 | 5.8212 | 4.2465 | 9.7225 | 24.5215 | 5.4841 | 4.0006 | 9.1412 | 24.7112 | 5.1353 | 3.7461 | 8.5327 | 26.1966 | 4.2493 | 3.0998 | 5.2349 | 24.5024 | 3.9745 | 2.8994 | 4.6101 | 18.9524 | 3.0743 | 2.2426 | 0.62802 | 14.0915 | 2.2858 | 1.6674 | -2.4988 | 13.1771 | 2.1375 | 1.5592 | -3.3523 | 7.9286 | 1.2861 | 0.93819 | -5.9651 | 3.2961 | 0.53467 | 0.39003 | -8.3105 | 1.3357 | 0.21666 | 0.15805 | -9.6865 | 13.5616 | 2.1998 | 1.6047 | -10.3591 | 12.4761 | 2.0238 | 1.4763 | -9.3581
HELWITH BRIDGE | PADIHAM | PADIHAM | 381025 | 469428 | 12.5074 | 12.5074 | 12.5074 | 8.3603 | 12.5239 | 12.5239 | 12.5239 | 8.1308 | 12.5521 | 12.5521 | 12.5521 | 8.0397 | 12.5886 | 12.5886 | 12.5886 | 7.997 | 12.6334 | 12.6334 | 12.6334 | 7.9495 | 12.6855 | 12.6855 | 12.6855 | 7.9002 | 12.7451 | 12.7451 | 12.7451 | 7.8512 | 12.8182 | 12.8182 | 12.8182 | 7.7918 | 12.8802 | 12.8802 | 12.8802 | 7.7153 | 12.9406 | 12.9406 | 12.9406 | 7.6459 | 13.1253 | 13.1253 | 13.1253 | 7.3311 | 13.304 | 13.304 | 13.304 | 6.8732 | 13.4261 | 13.4261 | 13.4261 | 6.5137 | 13.5156 | 13.5156 | 13.5156 | 6.1909 | 13.5665 | 13.5665 | 13.5665 | 5.923 | 12.4916 | 12.4916 | 12.4916 | 8.3603 | 12.5094 | 12.5094 | 12.5094 | 8.2597 | 12.5284 | 12.5284 | 12.5284 | 8.1964 | 12.5477 | 12.5477 | 12.5477 | 8.1603 | 12.5733 | 12.5733 | 12.5733 | 8.1171 | 12.6049 | 12.6049 | 12.6049 | 8.0577 | 12.6422 | 12.6422 | 12.6422 | 7.9885 | 12.6844 | 12.6844 | 12.6844 | 7.908 | 12.7163 | 12.7163 | 12.7163 | 7.8294 | 12.7499 | 12.7499 | 12.7499 | 7.7509 | 12.8554 | 12.8554 | 12.8554 | 7.5246 | 12.9581 | 12.9581 | 12.9581 | 7.3204 | 13.0505 | 13.0505 | 13.0505 | 7.139 | 13.1438 | 13.1438 | 13.1438 | 6.9363 | 13.2099 | 13.2099 | 13.2099 | 6.773 | 12.5097 | 12.5097 | 12.5097 | 8.3603 | 12.5279 | 12.5279 | 12.5279 | 8.0963 | 12.5593 | 12.5593 | 12.5593 | 7.999 | 12.6006 | 12.6006 | 12.6006 | 7.9557 | 12.6515 | 12.6515 | 12.6515 | 7.9078 | 12.711 | 12.711 | 12.711 | 7.8582 | 12.7793 | 12.7793 | 12.7793 | 7.8159 | 12.8413 | 12.8413 | 12.8413 | 7.7709 | 12.8664 | 12.8664 | 12.8664 | 7.7107 | 12.8892 | 12.8892 | 12.8892 | 7.6584 | 12.9878 | 12.9878 | 12.9878 | 7.3952 | 13.1225 | 13.1225 | 13.1225 | 6.9917 | 13.1941 | 13.1941 | 13.1941 | 6.6874 | 13.2432 | 13.2432 | 13.2432 | 6.4406 | 13.2683 | 13.2683 | 13.2683 | 6.2703 | 12.5097 | 12.5097 | 12.5097 | 8.3603 | 12.5135 | 12.5135 | 12.5135 | 8.1867 | 12.5304 | 12.5304 | 12.5304 | 8.1105 | 12.5549 | 12.5549 | 12.5549 | 8.064 | 12.589 | 12.589 | 12.589 | 8.0198 | 12.641 | 12.641 | 12.641 | 7.969 | 12.7057 | 12.7057 | 12.7057 | 7.9008 | 12.7812 | 12.7812 | 12.7812 | 7.7684 | 12.8446 | 12.8446 | 12.8446 | 7.6218 | 12.9077 | 12.9077 | 12.9077 | 7.4795 | 13.0189 | 13.0189 | 13.0189 | 7.0676 | 13.1181 | 13.1181 | 13.1181 | 6.6867 | 13.1815 | 13.1815 | 13.1815 | 6.4181 | 13.206 | 13.206 | 13.206 | 6.308 | 13.1618 | 13.1618 | 13.1618 | 6.5126 | 12.5074 | 12.5074 | 12.5074 | 8.3603 | 12.5211 | 12.5211 | 12.5211 | 8.1813 | 12.5411 | 12.5411 | 12.5411 | 8.1031 | 12.5649 | 12.5649 | 12.5649 | 8.0685 | 12.5949 | 12.5949 | 12.5949 | 8.0433 | 12.6398 | 12.6398 | 12.6398 | 8.0182 | 12.6974 | 12.6974 | 12.6974 | 7.9909 | 12.7617 | 12.7617 | 12.7617 | 7.9438 | 12.8156 | 12.8156 | 12.8156 | 7.8704 | 12.8701 | 12.8701 | 12.8701 | 7.7981 | 13.0452 | 13.0452 | 13.0452 | 7.5586 | 13.2111 | 13.2111 | 13.2111 | 7.2958 | 13.2966 | 13.2966 | 13.2966 | 7.1221 | 13.3659 | 13.3659 | 13.3659 | 6.9716 | 13.3839 | 13.3839 | 13.3839 | 6.9305 | 12.5074 | 12.5074 | 12.5074 | 8.3603 | 12.5183 | 12.5183 | 12.5183 | 8.0766 | 12.5461 | 12.5461 | 12.5461 | 7.9712 | 12.584 | 12.584 | 12.584 | 7.9112 | 12.6292 | 12.6292 | 12.6292 | 7.8556 | 12.6809 | 12.6809 | 12.6809 | 7.8015 | 12.7412 | 12.7412 | 12.7412 | 7.7318 | 12.82 | 12.82 | 12.82 | 7.5785 | 12.8867 | 12.8867 | 12.8867 | 7.4139 | 12.9521 | 12.9521 | 12.9521 | 7.2551 | 13.1452 | 13.1452 | 13.1452 | 6.8094 | 13.3228 | 13.3228 | 13.3228 | 6.405 | 13.4384 | 13.4384 | 13.4384 | 6.1174 | 13.5076 | 13.5076 | 13.5076 | 5.9847 | 13.5281 | 13.5281 | 13.5281 | 6.1521
HENSINGHAM | EGREMONT | HARKER / HUTTON | 298465 | 517239 | 25.0982 | 13.1008 | 9.4158 | 18.6536 | 25.1442 | 13.0023 | 9.345 | 18.4299 | 25.2166 | 12.9162 | 9.2831 | 18.5134 | 25.2781 | 12.7657 | 9.1749 | 18.4674 | 25.3498 | 12.5143 | 8.9943 | 18.3459 | 25.4313 | 12.3837 | 8.9004 | 18.2172 | 25.5189 | 12.432 | 8.9351 | 18.1167 | 25.6189 | 12.425 | 8.9301 | 18.0468 | 25.7017 | 12.3664 | 8.888 | 17.9556 | 25.7798 | 12.3416 | 8.8702 | 17.8861 | 26.1427 | 12.106 | 8.7008 | 16.8857 | 26.6675 | 11.9488 | 8.5878 | 14.851 | 27.0906 | 11.9059 | 8.557 | 13.0899 | 27.4957 | 14.6596 | 10.5362 | 11.2936 | 27.7844 | 13.98 | 10.0477 | 9.7037 | 25.0779 | 13.1008 | 9.4158 | 18.6536 | 25.1255 | 13.0474 | 9.3774 | 18.4581 | 25.1648 | 13.0304 | 9.3652 | 18.5302 | 25.2125 | 12.9748 | 9.3253 | 18.4664 | 25.2554 | 12.9086 | 9.2777 | 18.3695 | 25.3107 | 12.823 | 9.2161 | 18.243 | 25.3788 | 12.5605 | 9.0275 | 18.0783 | 25.4584 | 12.4634 | 8.9577 | 17.8786 | 25.5218 | 12.4024 | 8.9138 | 17.742 | 25.5875 | 12.3397 | 8.8688 | 17.606 | 25.7922 | 12.1343 | 8.7211 | 17.208 | 25.9526 | 11.9524 | 8.5904 | 16.7618 | 26.1058 | 11.7248 | 8.4269 | 16.3195 | 26.261 | 13.7446 | 9.8785 | 15.8544 | 26.3639 | 15.7559 | 11.3241 | 15.5864 | 25.1041 | 13.1008 | 9.4158 | 18.6536 | 25.1564 | 12.9927 | 9.3381 | 18.4359 | 25.2368 | 12.8729 | 9.252 | 18.5363 | 25.2921 | 12.6861 | 9.1177 | 18.5205 | 25.3702 | 12.3598 | 8.8832 | 18.4309 | 25.4592 | 12.4075 | 8.9175 | 18.3391 | 25.5558 | 12.4146 | 8.9226 | 18.2899 | 25.6663 | 12.3584 | 8.8822 | 18.2758 | 25.752 | 12.2933 | 8.8354 | 18.2495 | 25.8321 | 12.2345 | 8.7932 | 18.2338 | 26.2064 | 12.1257 | 8.715 | 17.3988 | 26.7469 | 11.7461 | 8.4422 | 15.5025 | 27.1803 | 11.599 | 8.3364 | 13.866 | 27.5864 | 13.9625 | 10.0351 | 12.2163 | 27.9079 | 13.0834 | 9.4033 | 10.7882 | 25.1041 | 13.1008 | 9.4158 | 18.6536 | 25.0969 | 13.0327 | 9.3668 | 18.6406 | 25.1305 | 12.9464 | 9.3048 | 18.8018 | 25.1799 | 12.7238 | 9.1448 | 18.7911 | 25.2373 | 12.4958 | 8.981 | 18.6868 | 25.3197 | 12.6284 | 9.0763 | 18.5583 | 25.4358 | 12.4983 | 8.9828 | 18.3347 | 25.6273 | 11.697 | 8.4068 | 17.7132 | 25.8066 | 11.2552 | 8.0893 | 17.0568 | 25.983 | 10.9609 | 7.8778 | 16.4081 | 26.5037 | 12.9145 | 9.2819 | 14.5406 | 26.9825 | 12.3407 | 8.8695 | 12.7492 | 27.3261 | 11.8026 | 8.4828 | 11.2742 | 27.5883 | 11.4032 | 8.1957 | 10.4938 | 27.5855 | 11.3054 | 8.1254 | 11.3791 | 25.0982 | 13.1008 | 9.4158 | 18.6536 | 25.137 | 13.022 | 9.3592 | 18.4893 | 25.1851 | 12.9482 | 9.3061 | 18.6144 | 25.2294 | 12.8129 | 9.2089 | 18.6381 | 25.2617 | 12.5931 | 9.0509 | 18.6525 | 25.3172 | 12.4748 | 8.9659 | 18.6396 | 25.3929 | 12.5403 | 9.013 | 18.6086 | 25.4782 | 12.5411 | 9.0136 | 18.5736 | 25.5509 | 12.4936 | 8.9794 | 18.4926 | 25.6237 | 12.46 | 8.9552 | 18.4181 | 25.8707 | 12.397 | 8.9099 | 18.0838 | 26.1423 | 12.4643 | 8.9583 | 17.4945 | 26.3384 | 12.6898 | 9.1204 | 17.0879 | 26.5089 | 15.6977 | 11.2822 | 16.746 | 26.5798 | 15.0644 | 10.8271 | 16.6431 | 25.0982 | 13.1008 | 9.4158 | 18.6536 | 25.1132 | 13.0147 | 9.3539 | 18.5678 | 25.1807 | 12.9098 | 9.2785 | 18.6571 | 25.2477 | 12.6691 | 9.1055 | 18.5705 | 25.328 | 12.4301 | 8.9337 | 18.3973 | 25.4162 | 12.5515 | 9.021 | 18.2226 | 25.5327 | 12.4208 | 8.927 | 17.9444 | 25.7384 | 11.7471 | 8.4429 | 17.2464 | 25.9262 | 11.2432 | 8.0807 | 16.5366 | 26.1094 | 10.8757 | 7.8166 | 15.8354 | 26.6428 | 12.7599 | 9.1708 | 13.8136 | 27.0792 | 12.1579 | 8.7381 | 11.895 | 27.3927 | 11.5909 | 8.3306 | 10.2962 | 27.6135 | 11.1729 | 8.0302 | 9.366 | 27.6694 | 11.0702 | 7.9564 | 10.0771
HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 397310 | 399981 | 30.6355 | 9.0319 | 6.5887 | 13.6544 | 30.693 | 8.7603 | 6.3905 | 13.4787 | 30.7626 | 8.6786 | 6.3309 | 13.3189 | 30.846 | 8.5987 | 6.2726 | 13.156 | 30.9539 | 8.6111 | 6.2817 | 12.8883 | 31.0854 | 8.4924 | 6.1951 | 12.5944 | 31.2463 | 8.3732 | 6.1081 | 12.3078 | 31.4439 | 8.2754 | 6.0368 | 12.0531 | 31.6129 | 8.1614 | 5.9536 | 11.7692 | 31.7849 | 8.0461 | 5.8695 | 11.494 | 32.3441 | 7.552 | 5.5091 | 9.8065 | 32.8874 | 6.9743 | 5.0876 | 7.2376 | 33.2611 | 6.4966 | 4.7392 | 5.3009 | 33.5664 | 6.0509 | 4.414 | 3.5396 | 33.7728 | 5.6579 | 4.1274 | 2.1764 | 30.6204 | 9.0319 | 6.5887 | 13.6544 | 30.692 | 8.9353 | 6.5182 | 13.5129 | 30.763 | 8.8356 | 6.4455 | 13.3804 | 30.8469 | 8.7063 | 6.3511 | 13.2517 | 30.956 | 8.6048 | 6.2771 | 13.0861 | 31.0927 | 8.5016 | 6.2018 | 12.91 | 31.2617 | 8.3158 | 6.0663 | 12.6675 | 31.4621 | 8.1604 | 5.9529 | 12.3258 | 31.5454 | 8.0265 | 5.8552 | 12.0786 | 31.6355 | 7.9092 | 5.7696 | 11.8238 | 31.9454 | 7.6448 | 5.5768 | 11.0265 | 32.2952 | 7.5054 | 5.4751 | 10.1362 | 32.6338 | 7.3186 | 5.3388 | 9.2181 | 32.9926 | 7.0933 | 5.1745 | 8.1992 | 33.2529 | 6.839 | 4.9889 | 7.4261 | 30.6394 | 9.0319 | 6.5887 | 13.6544 | 30.7115 | 8.7674 | 6.3957 | 13.415 | 30.799 | 8.5389 | 6.229 | 13.1844 | 30.9044 | 8.5805 | 6.2593 | 12.955 | 31.0365 | 8.4918 | 6.1947 | 12.6148 | 31.194 | 8.3434 | 6.0864 | 12.2463 | 31.3839 | 8.2018 | 5.9831 | 11.8967 | 31.6124 | 8.0657 | 5.8838 | 11.5644 | 31.7994 | 7.9199 | 5.7775 | 11.2258 | 31.9896 | 7.763 | 5.663 | 10.8768 | 32.6364 | 7.1625 | 5.2249 | 8.9879 | 33.2813 | 6.5254 | 4.7602 | 6.482 | 33.7171 | 6.0525 | 4.4152 | 4.8057 | 33.9877 | 5.6367 | 4.1119 | 3.5195 | 32.8404 | 5.327 | 3.886 | 2.9468 | 30.6394 | 9.0319 | 6.5887 | 13.6544 | 30.6236 | 8.8073 | 6.4248 | 13.7078 | 30.6614 | 8.6019 | 6.275 | 13.5543 | 30.7143 | 8.7906 | 6.4126 | 13.3561 | 30.7993 | 8.677 | 6.3297 | 13.0261 | 30.9284 | 8.5245 | 6.2185 | 12.6568 | 31.0996 | 8.3536 | 6.0939 | 12.175 | 31.3105 | 8.0919 | 5.9029 | 11.2932 | 31.5055 | 7.8392 | 5.7186 | 10.4071 | 31.7063 | 7.5737 | 5.5249 | 9.5413 | 32.3333 | 6.9604 | 5.0775 | 7.0588 | 32.9141 | 6.3975 | 4.6669 | 4.9678 | 33.3 | 5.9503 | 4.3407 | 3.7165 | 33.5925 | 5.6046 | 4.0885 | 3.266 | 33.6362 | 5.4941 | 4.0079 | 3.9024 | 30.6355 | 9.0319 | 6.5887 | 13.6544 | 30.6874 | 8.8072 | 6.4247 | 13.4979 | 30.7389 | 8.7093 | 6.3533 | 13.3657 | 30.7926 | 8.6207 | 6.2887 | 13.2671 | 30.8663 | 8.6753 | 6.3285 | 13.1414 | 30.9785 | 8.5946 | 6.2696 | 12.9918 | 31.1301 | 8.4945 | 6.1966 | 12.8119 | 31.3042 | 8.41 | 6.135 | 12.6045 | 31.4491 | 8.3005 | 6.0551 | 12.3187 | 31.6011 | 8.1817 | 5.9685 | 12.028 | 32.111 | 7.8109 | 5.6979 | 10.9553 | 32.6265 | 7.5006 | 5.4716 | 9.7973 | 32.9967 | 7.2347 | 5.2776 | 8.9873 | 33.3099 | 6.9872 | 5.0971 | 8.1955 | 33.5025 | 6.7628 | 4.9333 | 7.6433 | 30.6355 | 9.0319 | 6.5887 | 13.6544 | 30.644 | 8.806 | 6.4238 | 13.6597 | 30.7158 | 8.5863 | 6.2636 | 13.4421 | 30.8083 | 8.7396 | 6.3754 | 13.1722 | 30.928 | 8.6084 | 6.2797 | 12.7753 | 31.0681 | 8.4436 | 6.1595 | 12.3567 | 31.2407 | 8.2594 | 6.0251 | 11.8121 | 31.469 | 7.9819 | 5.8227 | 10.8546 | 31.6618 | 7.7213 | 5.6326 | 9.9247 | 31.8588 | 7.4446 | 5.4308 | 9.0021 | 32.482 | 6.7964 | 4.9579 | 6.3414 | 33.0641 | 6.2003 | 4.5231 | 4.0937 | 33.4631 | 5.7226 | 4.1745 | 2.6898 | 32.9508 | 5.3449 | 3.8991 | 2.0698 | 32.0421 | 5.1975 | 3.7915 | 2.5105
HEYSIDE | ROYTON | WHITEGATE | 393433 | 407129 | 28.8574 | 12.9623 | 9.4558 | 17.5478 | 29.005 | 12.679 | 9.2491 | 15.9134 | 29.1844 | 12.3378 | 9.0002 | 15.4152 | 29.42 | 12.0892 | 8.8189 | 15.2391 | 29.613 | 11.7854 | 8.5973 | 15.0321 | 29.8464 | 11.521 | 8.4044 | 14.7978 | 30.1503 | 11.1991 | 8.1696 | 14.5387 | 30.5439 | 11.1064 | 8.1019 | 14.1619 | 30.9685 | 10.9895 | 8.0167 | 13.7087 | 31.312 | 10.8812 | 7.9377 | 13.2421 | 32.3605 | 10.4195 | 7.6009 | 11.0289 | 33.1626 | 9.9851 | 7.284 | 8.4215 | 33.6931 | 9.7996 | 7.1487 | 6.5602 | 34.1056 | 9.7239 | 7.0934 | 4.8904 | 34.3821 | 9.428 | 6.8776 | 3.5246 | 28.8323 | 12.9623 | 9.4558 | 17.5478 | 28.9197 | 12.896 | 9.4074 | 17.1492 | 28.9992 | 12.8275 | 9.3575 | 16.9246 | 29.0999 | 12.7516 | 9.3021 | 16.7767 | 29.2381 | 12.6715 | 9.2437 | 16.6185 | 29.4077 | 12.6102 | 9.199 | 16.436 | 29.587 | 12.4441 | 9.0778 | 16.2118 | 29.7833 | 12.3559 | 9.0135 | 15.9314 | 29.9806 | 12.2841 | 8.9611 | 15.679 | 30.2073 | 12.2234 | 8.9168 | 15.4138 | 31.0549 | 11.959 | 8.7239 | 14.1964 | 31.9654 | 11.6801 | 8.5205 | 12.6487 | 32.7205 | 11.5477 | 8.4239 | 11.1073 | 33.4941 | 11.4159 | 8.3277 | 9.4093 | 33.9761 | 11.1936 | 8.1656 | 8.2016 | 28.8683 | 12.9623 | 9.4558 | 17.5478 | 29.0421 | 12.6181 | 9.2048 | 15.6324 | 29.2566 | 12.2558 | 8.9404 | 15.0517 | 29.4748 | 11.9573 | 8.7227 | 14.727 | 29.6653 | 11.5971 | 8.4599 | 14.1914 | 29.904 | 11.222 | 8.1863 | 13.6289 | 30.2046 | 10.8694 | 7.9291 | 13.0409 | 30.5859 | 10.6998 | 7.8053 | 12.4215 | 30.9762 | 10.5267 | 7.6791 | 11.6871 | 31.3033 | 10.3685 | 7.5637 | 11.0215 | 32.3734 | 9.771 | 7.1278 | 8.3778 | 33.27 | 9.2585 | 6.7539 | 5.7085 | 33.8834 | 9.0445 | 6.5978 | 3.734 | 34.3304 | 8.8721 | 6.472 | 2.1457 | 34.5781 | 8.5906 | 6.2667 | 1.1326 | 28.8683 | 12.9623 | 9.4558 | 17.5478 | 28.9606 | 12.7331 | 9.2886 | 16.2838 | 29.1171 | 12.4344 | 9.0707 | 15.8645 | 29.3322 | 12.1171 | 8.8393 | 15.5857 | 29.5107 | 11.7916 | 8.6018 | 15.0826 | 29.7526 | 11.4195 | 8.3304 | 14.5316 | 30.0778 | 11.0032 | 8.0267 | 13.8165 | 30.4911 | 10.8488 | 7.914 | 12.721 | 30.9351 | 10.6498 | 7.7689 | 11.5887 | 31.3733 | 10.4608 | 7.631 | 10.5482 | 32.3579 | 10.4358 | 7.6128 | 7.4893 | 33.1382 | 9.8222 | 7.1652 | 5.1523 | 33.6289 | 9.3617 | 6.8293 | 3.6747 | 33.9595 | 8.9674 | 6.5416 | 2.8212 | 34.1047 | 8.6529 | 6.3122 | 2.5474 | 28.8574 | 12.9623 | 9.4558 | 17.5478 | 28.9851 | 12.841 | 9.3673 | 16.8748 | 29.1231 | 12.5269 | 9.1382 | 16.5944 | 29.289 | 12.2949 | 8.969 | 16.462 | 29.49 | 12.0129 | 8.7632 | 16.3228 | 29.683 | 11.7546 | 8.5748 | 16.1429 | 29.9447 | 11.4502 | 8.3527 | 15.9211 | 30.2648 | 11.3768 | 8.2992 | 15.6685 | 30.6043 | 11.2627 | 8.216 | 15.2652 | 30.9861 | 11.1592 | 8.1405 | 14.8235 | 31.983 | 10.8014 | 7.8795 | 13.12 | 32.8296 | 10.5411 | 7.6896 | 11.3213 | 33.3722 | 10.5003 | 7.6598 | 9.9827 | 33.7857 | 10.543 | 7.691 | 8.8279 | 34.0221 | 10.3546 | 7.5536 | 7.9795 | 28.8574 | 12.9623 | 9.4558 | 17.5478 | 28.9663 | 12.6023 | 9.1932 | 15.5082 | 29.1561 | 12.2728 | 8.9528 | 14.8933 | 29.4022 | 11.9366 | 8.7076 | 14.5653 | 29.578 | 11.6071 | 8.4672 | 14.0209 | 29.7976 | 11.2295 | 8.1918 | 13.4551 | 30.0784 | 10.8212 | 7.8939 | 12.7367 | 30.4503 | 10.6406 | 7.7622 | 11.6094 | 30.8389 | 10.444 | 7.6187 | 10.4687 | 31.2731 | 10.2504 | 7.4775 | 9.4168 | 32.3803 | 10.1966 | 7.4383 | 6.2408 | 33.2404 | 9.5496 | 6.9663 | 3.7291 | 33.8198 | 9.0473 | 6.5999 | 2.0223 | 34.2038 | 8.6207 | 6.2886 | 0.96807 | 34.3787 | 8.3383 | 6.0827 | 0.66639
HEYWOOD | CASTLETON | ROCHDALE | 385429 | 410369 | 18.4743 | 9.0282 | 6.5859 | 8.0862 | 18.5422 | 8.397 | 6.1255 | 5.2139 | 18.6383 | 7.2662 | 5.3006 | 4.4602 | 18.7674 | 6.2037 | 4.5255 | 4.2235 | 18.9382 | 5.0762 | 3.703 | 3.9607 | 19.1561 | 3.9021 | 2.8465 | 3.6817 | 17.2366 | 2.796 | 2.0396 | 3.4069 | 16.2211 | 2.6312 | 1.9194 | 3.1161 | 15.7738 | 2.5587 | 1.8665 | 2.7336 | 15.4106 | 2.4998 | 1.8235 | 2.3507 | 13.375 | 2.1696 | 1.5827 | 0.51941 | 13.3657 | 2.168 | 1.5816 | -2.1687 | 18.9751 | 3.0779 | 2.2453 | -4.293 | 24.1203 | 4.5271 | 3.3025 | -6.4631 | 24.4019 | 4.8446 | 3.5341 | -8.4211 | 18.4611 | 9.0282 | 6.5859 | 8.0862 | 18.5391 | 8.8408 | 6.4492 | 7.1393 | 18.6279 | 7.8249 | 5.7081 | 6.8111 | 18.7378 | 6.8259 | 4.9794 | 6.6203 | 18.8787 | 5.8345 | 4.2562 | 6.4459 | 19.0524 | 4.8183 | 3.5149 | 6.2652 | 19.2642 | 3.6829 | 2.6866 | 6.0373 | 19.5205 | 3.537 | 2.5802 | 5.72 | 19.6665 | 3.3654 | 2.455 | 5.3786 | 19.8366 | 3.2283 | 2.355 | 5.0289 | 18.5917 | 3.0158 | 2.1999 | 3.9345 | 16.9813 | 2.7545 | 2.0094 | 2.7442 | 20.2974 | 3.2924 | 2.4018 | 1.597 | 23.1422 | 4.4989 | 3.2819 | 0.30174 | 23.7754 | 4.8181 | 3.5147 | -0.64535 | 18.4794 | 9.0282 | 6.5859 | 8.0862 | 18.5508 | 8.2933 | 6.0499 | 4.7697 | 18.6523 | 7.1131 | 5.1889 | 3.9271 | 18.7871 | 6.0007 | 4.3774 | 3.5713 | 18.9609 | 4.807 | 3.5066 | 3.1928 | 19.1767 | 3.5849 | 2.6151 | 2.8016 | 14.6911 | 2.383 | 1.7384 | 2.3581 | 14.5557 | 2.3611 | 1.7224 | 2.0866 | 13.7023 | 2.2227 | 1.6214 | 1.7723 | 13.191 | 2.1397 | 1.5609 | 1.4601 | 10.9158 | 1.7707 | 1.2917 | -0.20083 | 10.5392 | 1.7096 | 1.2471 | -2.7639 | 15.6817 | 2.5437 | 1.8556 | -4.7549 | 24.2611 | 3.9354 | 2.8708 | -6.6872 | 24.6208 | 4.2535 | 3.1029 | -8.3022 | 18.4794 | 9.0282 | 6.5859 | 8.0862 | 18.4984 | 8.4636 | 6.1741 | 5.7632 | 18.5562 | 8.2463 | 6.0156 | 5.1519 | 18.6438 | 8.0731 | 5.8892 | 4.8265 | 18.7781 | 7.7867 | 5.6803 | 4.4685 | 18.9822 | 7.4169 | 5.4105 | 4.0761 | 19.2615 | 7.2254 | 5.2708 | 3.4901 | 19.6271 | 7.0044 | 5.1096 | 2.6725 | 20.0104 | 6.8001 | 4.9606 | 1.7845 | 20.4302 | 6.5545 | 4.7814 | 0.90084 | 21.7533 | 5.8611 | 4.2756 | -1.6677 | 22.892 | 5.2053 | 3.7972 | -4.0903 | 23.5561 | 4.6926 | 3.4232 | -6.0449 | 23.9925 | 4.8004 | 3.5019 | -7.5132 | 24.1005 | 4.6524 | 3.3938 | -6.9664 | 18.4743 | 9.0282 | 6.5859 | 8.0862 | 18.5346 | 8.6108 | 6.2814 | 6.4126 | 18.6096 | 7.5351 | 5.4968 | 5.9231 | 18.7031 | 6.4852 | 4.7309 | 5.7334 | 18.8299 | 5.3802 | 3.9248 | 5.5645 | 19.0148 | 4.2216 | 3.0796 | 5.3736 | 19.262 | 3.1251 | 2.2797 | 5.1616 | 18.1946 | 2.9513 | 2.153 | 4.9167 | 17.8277 | 2.8918 | 2.1096 | 4.5497 | 17.4919 | 2.8374 | 2.0698 | 4.1683 | 16.147 | 2.6192 | 1.9107 | 2.921 | 17.8393 | 2.8937 | 2.1109 | 1.6103 | 23.211 | 4.0418 | 2.9484 | 0.72771 | 23.7176 | 5.7839 | 4.2193 | -0.031719 | 23.9457 | 6.403 | 4.6709 | -0.41019 | 18.4743 | 9.0282 | 6.5859 | 8.0862 | 18.5172 | 8.2343 | 6.0068 | 4.402 | 18.6073 | 7.9546 | 5.8028 | 3.4743 | 18.7299 | 7.7578 | 5.6592 | 3.0969 | 18.8896 | 7.4579 | 5.4404 | 2.6945 | 19.0874 | 7.0981 | 5.178 | 2.2836 | 19.3416 | 6.8977 | 5.0318 | 1.6874 | 19.6878 | 6.6515 | 4.8522 | 0.84219 | 20.0268 | 6.4541 | 4.7082 | -0.049456 | 20.4031 | 6.198 | 4.5214 | -0.93621 | 21.6965 | 5.5001 | 4.0123 | -3.551 | 22.9356 | 4.8182 | 3.5148 | -6.0704 | 23.7478 | 4.2997 | 3.1366 | -8.0064 | 24.2486 | 4.4074 | 3.2152 | -9.4407 | 24.3923 | 4.2242 | 3.0815 | -9.0752
HIGHER MILL | MOSS NOOK | SOUTH MANCHESTER | 385731 | 388090 | 30.0419 | 13.2606 | 9.6734 | 13.9317 | 30.1746 | 13.0217 | 9.4991 | 12.5336 | 30.3092 | 12.8733 | 9.3909 | 12.0605 | 30.4765 | 12.7758 | 9.3198 | 11.8411 | 30.6823 | 12.653 | 9.2302 | 11.5465 | 30.9246 | 12.3089 | 8.9792 | 11.1597 | 31.2137 | 12.2062 | 8.9042 | 10.766 | 31.4298 | 12.1135 | 8.8366 | 10.3455 | 31.6202 | 11.9938 | 8.7493 | 9.8429 | 31.811 | 11.8049 | 8.6115 | 9.3616 | 32.4514 | 11.2036 | 8.1729 | 7.0967 | 33.1267 | 10.4518 | 7.6245 | 3.7972 | 33.6213 | 9.8415 | 7.1793 | 1.1682 | 34.0674 | 9.212 | 6.7201 | -1.5162 | 34.3857 | 8.6436 | 6.3054 | -3.7926 | 30.0242 | 13.2606 | 9.6734 | 13.9317 | 30.1225 | 13.209 | 9.6357 | 13.4885 | 30.2099 | 13.1568 | 9.5977 | 13.2441 | 30.3195 | 13.0815 | 9.5427 | 13.0525 | 30.4639 | 12.9885 | 9.4749 | 12.813 | 30.6412 | 12.8565 | 9.3787 | 12.559 | 30.8547 | 12.6207 | 9.2067 | 12.2313 | 31.1033 | 12.4918 | 9.1126 | 11.7456 | 31.2671 | 12.3706 | 9.0242 | 11.2843 | 31.4484 | 12.2409 | 8.9295 | 10.8052 | 31.9655 | 11.8364 | 8.6345 | 9.2836 | 32.4371 | 11.4782 | 8.3732 | 7.7126 | 32.8621 | 11.111 | 8.1053 | 6.2593 | 33.2831 | 10.7074 | 7.8109 | 4.7558 | 33.566 | 10.3703 | 7.565 | 3.7777 | 30.0491 | 13.2606 | 9.6734 | 13.9317 | 30.1715 | 12.9743 | 9.4646 | 12.3699 | 30.3055 | 12.7699 | 9.3155 | 11.8926 | 30.4745 | 12.6354 | 9.2173 | 11.7326 | 30.6807 | 12.4803 | 9.1042 | 11.4835 | 30.9205 | 12.0495 | 8.7899 | 11.1619 | 31.2046 | 12.0942 | 8.8226 | 10.8587 | 31.4166 | 11.953 | 8.7195 | 10.5367 | 31.5934 | 11.7611 | 8.5796 | 9.8687 | 31.7728 | 11.5456 | 8.4224 | 9.3474 | 32.4216 | 10.8635 | 7.9248 | 7.2911 | 33.143 | 10.0597 | 7.3384 | 4.0935 | 33.68 | 9.3488 | 6.8198 | 1.5432 | 34.152 | 8.634 | 6.2984 | -1.0207 | 34.4627 | 8.0245 | 5.8538 | -3.104 | 30.0493 | 13.2606 | 9.6734 | 13.9317 | 30.1056 | 13.0802 | 9.5419 | 13.0112 | 30.1895 | 12.9062 | 9.4149 | 12.6986 | 30.304 | 12.7201 | 9.2792 | 12.5665 | 30.4672 | 12.6933 | 9.2596 | 12.3366 | 30.7019 | 12.5054 | 9.1225 | 12.0297 | 31.0022 | 12.239 | 8.9281 | 11.5178 | 31.2691 | 11.8298 | 8.6297 | 10.5407 | 31.4965 | 11.6698 | 8.513 | 9.202 | 31.7275 | 11.4376 | 8.3436 | 8.0077 | 32.4257 | 10.6253 | 7.751 | 4.9 | 33.0831 | 9.8258 | 7.1678 | 1.9013 | 33.5519 | 9.1399 | 6.6674 | -0.39793 | 33.8979 | 8.6276 | 6.2937 | -1.9738 | 33.9504 | 8.3869 | 6.1181 | -1.462 | 30.0418 | 13.2606 | 9.6734 | 13.9317 | 30.147 | 13.1392 | 9.5849 | 13.2367 | 30.239 | 13.0344 | 9.5084 | 12.9598 | 30.3444 | 12.9534 | 9.4494 | 12.835 | 30.4809 | 12.8664 | 9.3859 | 12.6925 | 30.6752 | 12.5561 | 9.1595 | 12.4939 | 30.926 | 12.4632 | 9.0917 | 12.1894 | 31.2109 | 12.3923 | 9.04 | 11.8704 | 31.3964 | 12.2929 | 8.9675 | 11.4419 | 31.5625 | 12.1183 | 8.8402 | 11.0036 | 32.122 | 11.6496 | 8.4982 | 9.5113 | 32.6945 | 11.218 | 8.1834 | 7.892 | 33.1117 | 10.8668 | 7.9272 | 6.7482 | 33.4682 | 10.5139 | 7.6698 | 5.7292 | 33.6577 | 10.2535 | 7.4798 | 5.1679 | 30.0418 | 13.2606 | 9.6734 | 13.9317 | 30.1102 | 12.9657 | 9.4583 | 12.3415 | 30.2263 | 12.7493 | 9.3004 | 11.8137 | 30.3781 | 12.5543 | 9.1582 | 11.5805 | 30.5654 | 12.5075 | 9.1241 | 11.265 | 30.7805 | 12.2942 | 8.9685 | 10.8864 | 31.0415 | 12.0351 | 8.7794 | 10.3491 | 31.3683 | 11.5893 | 8.4542 | 9.3011 | 31.5932 | 11.425 | 8.3344 | 7.9123 | 31.8231 | 11.1852 | 8.1594 | 6.6626 | 32.5402 | 10.3315 | 7.5367 | 3.3359 | 33.2267 | 9.4863 | 6.9201 | 0.12675 | 33.7324 | 8.7612 | 6.3912 | -2.3838 | 34.1046 | 8.213 | 5.9913 | -4.1849 | 34.1878 | 7.9306 | 5.7852 | -3.9125
HIGHER WALTON | LEYLAND | PENWORTHAM WEST / STANAH | 358020 | 427270 | 23.2839 | 7.0248 | 5.0489 | 11.665 | 23.4288 | 6.4771 | 4.6552 | 8.6754 | 23.6669 | 5.7654 | 4.1437 | 6.4377 | 23.9519 | 5.1378 | 3.6926 | 4.7356 | 24.2969 | 4.3913 | 3.1561 | 2.9905 | 21.2362 | 3.4964 | 2.5129 | 1.2178 | 21.257 | 3.4998 | 2.5154 | 0.94727 | 20.7299 | 3.413 | 2.453 | 0.62803 | 19.9197 | 3.2796 | 2.3571 | 0.13037 | 18.9358 | 3.1176 | 2.2407 | -0.3774 | 13.3518 | 2.1983 | 1.5799 | -4.4318 | 8.7678 | 1.4435 | 1.0375 | -7.6399 | 5.0044 | 0.82393 | 0.59217 | -10.1367 | 9.6806 | 1.5938 | 1.1455 | -12.5883 | 14.7507 | 2.4286 | 1.7455 | -14.3734 | 23.2237 | 7.0248 | 5.0489 | 11.665 | 23.3198 | 6.8312 | 4.9097 | 10.4916 | 23.4542 | 6.6014 | 4.7446 | 9.5837 | 23.6107 | 6.374 | 4.5811 | 8.8778 | 23.8036 | 6.1062 | 4.3887 | 8.1457 | 24.0313 | 5.8839 | 4.2289 | 7.3777 | 24.3093 | 5.6594 | 4.0675 | 7.0505 | 24.5817 | 5.4947 | 3.9492 | 6.667 | 24.8514 | 5.3436 | 3.8406 | 6.2337 | 25.156 | 5.1688 | 3.7149 | 5.7777 | 26.0587 | 4.7226 | 3.3942 | 4.2989 | 26.2038 | 4.3143 | 3.1007 | 2.7247 | 23.4853 | 3.8667 | 2.7791 | 1.2152 | 26.4347 | 4.3523 | 3.1281 | -0.37464 | 28.5924 | 4.7075 | 3.3834 | -4.9197 | 23.3055 | 7.0248 | 5.0489 | 11.665 | 23.4475 | 6.3671 | 4.5761 | 8.2366 | 23.6987 | 5.5432 | 3.984 | 5.9519 | 24.0017 | 4.9117 | 3.5302 | 4.3158 | 24.3629 | 4.0744 | 2.9284 | 2.6402 | 21.1051 | 3.4748 | 2.4974 | 0.95339 | 20.2857 | 3.3399 | 2.4004 | 0.80366 | 19.6471 | 3.2347 | 2.3249 | 0.62865 | 18.7783 | 3.0917 | 2.2221 | 0.30512 | 17.8249 | 2.9347 | 2.1092 | -0.02605 | 11.5298 | 1.8983 | 1.3643 | -4.0375 | 4.6346 | 0.76305 | 0.54842 | -8.7113 | 0.73455 | 0.12094 | 0.08692 | -11.0085 | 4.8419 | 0.79718 | 0.57295 | -13.1874 | 11.2455 | 1.8515 | 1.3307 | -14.4402 | 23.3056 | 7.0248 | 5.0489 | 11.665 | 23.3645 | 6.5942 | 4.7394 | 9.4186 | 23.5323 | 5.8532 | 4.2068 | 7.3835 | 23.7387 | 5.2072 | 3.7425 | 5.7736 | 24.0194 | 4.4609 | 3.2062 | 4.1012 | 22.2108 | 3.6568 | 2.6282 | 2.3719 | 22.2527 | 3.6637 | 2.6332 | 2.003 | 18.7345 | 3.0845 | 2.2169 | -1.163 | 13.289 | 2.1879 | 1.5725 | -5.6776 | 11.6006 | 1.9099 | 1.3727 | -6.5152 | 6.5471 | 1.0779 | 0.77473 | -9.3001 | 2.2742 | 0.37443 | 0.26911 | -11.9996 | 0.39879 | 0.065658 | 0.04719 | -13.9617 | 13.1278 | 2.1614 | 1.5534 | -15.1579 | 12.6916 | 2.0896 | 1.5018 | -13.8769 | 23.2838 | 7.0248 | 5.0489 | 11.665 | 23.4014 | 6.6333 | 4.7675 | 9.5167 | 23.5781 | 5.9688 | 4.2899 | 7.4766 | 23.7665 | 5.3472 | 3.8431 | 5.8586 | 24.0009 | 4.6419 | 3.3362 | 4.2424 | 22.7447 | 3.7447 | 2.6914 | 2.5689 | 22.9752 | 3.7827 | 2.7187 | 2.3537 | 22.5737 | 3.7166 | 2.6712 | 2.0958 | 21.8572 | 3.5986 | 2.5864 | 1.6598 | 20.9572 | 3.4504 | 2.4799 | 1.196 | 16.2442 | 2.6745 | 1.9222 | -2.117 | 13.529 | 2.2274 | 1.6009 | -3.7721 | 11.2611 | 1.854 | 1.3325 | -4.8718 | 17.8214 | 2.9342 | 2.1088 | -5.7298 | 25.6577 | 4.2243 | 3.0361 | -5.8447 | 23.2838 | 7.0248 | 5.0489 | 11.665 | 23.38 | 6.3118 | 4.5364 | 7.926 | 23.6037 | 5.4903 | 3.946 | 5.5445 | 23.8738 | 4.8422 | 3.4802 | 3.8251 | 23.498 | 3.8688 | 2.7806 | 0.84705 | 18.2216 | 3.0001 | 2.1562 | -1.2312 | 17.7363 | 2.9201 | 2.0988 | -1.9486 | 13.7728 | 2.2676 | 1.6298 | -5.4907 | 7.9496 | 1.3088 | 0.94069 | -10.347 | 6.2098 | 1.0224 | 0.73481 | -11.2243 | 0.90049 | 0.14826 | 0.10656 | -14.2352 | 2.6844 | 0.44197 | 0.31765 | -17.2673 | 2.6844 | 0.44197 | 0.31765 | -19.5547 | 6.3809 | 1.0506 | 0.75507 | -21.047 | 5.4219 | 0.89268 | 0.64158 | -20.0119
HILL TOP T11 & T12 | KEARSLEY LOCAL | KEARSLEY | 373466 | 403748 | 20.5107 | 3.3769 | 2.4271 | 8.7742 | 19.0745 | 3.1405 | 2.2571 | 8.1826 | 17.4306 | 2.8698 | 2.0626 | 7.6876 | 15.7022 | 2.5853 | 1.8581 | 7.2488 | 13.5112 | 2.2245 | 1.5988 | 6.67 | 12.8392 | 2.1139 | 1.5193 | 6.0579 | 11.0418 | 1.8179 | 1.3066 | 5.4399 | 10.2771 | 1.6921 | 1.2161 | 4.7974 | 9.3896 | 1.5459 | 1.1111 | 4.0774 | 8.4526 | 1.3917 | 1.0002 | 3.3942 | 3.7336 | 0.61471 | 0.4418 | -0.0089811 | 2.6844 | 0.44197 | 0.31765 | -4.8753 | 2.6844 | 0.44197 | 0.31765 | -8.6693 | 2.6844 | 0.44197 | 0.31765 | -12.3929 | 2.6844 | 0.44197 | 0.31765 | -15.4718 | 20.5107 | 3.3769 | 2.4271 | 8.7742 | 19.8322 | 3.2652 | 2.3468 | 8.466 | 19.1994 | 3.161 | 2.2719 | 8.2537 | 18.5663 | 3.0568 | 2.197 | 8.0257 | 17.766 | 2.925 | 2.1023 | 7.6956 | 16.7669 | 2.7605 | 1.9841 | 7.3136 | 15.7978 | 2.601 | 1.8694 | 6.8066 | 14.5836 | 2.4011 | 1.7257 | 6.1386 | 13.4929 | 2.2215 | 1.5966 | 5.5483 | 12.2723 | 2.0205 | 1.4522 | 4.9091 | 8.4655 | 1.3938 | 1.0017 | 2.8049 | 4.5623 | 0.75114 | 0.53986 | 0.63657 | 0.2449 | 0.040322 | 0.02898 | -1.3786 | 2.6844 | 0.44197 | 0.31765 | -3.5046 | 2.6844 | 0.44197 | 0.31765 | -4.8197 | 20.5107 | 3.3769 | 2.4271 | 8.7742 | 18.832 | 3.1005 | 2.2284 | 8.166 | 16.8234 | 2.7698 | 1.9907 | 7.7104 | 14.4856 | 2.3849 | 1.7141 | 7.3514 | 13.6662 | 2.25 | 1.6171 | 6.8657 | 11.9123 | 1.9613 | 1.4096 | 6.3669 | 11.5272 | 1.8979 | 1.364 | 5.9079 | 10.7557 | 1.7708 | 1.2727 | 5.4027 | 9.6726 | 1.5925 | 1.1446 | 4.7801 | 8.5613 | 1.4096 | 1.0131 | 4.1859 | 3.6232 | 0.59654 | 0.42874 | 1.0821 | 2.6844 | 0.44197 | 0.31765 | -3.6716 | 2.6844 | 0.44197 | 0.31765 | -7.3986 | 2.6844 | 0.44197 | 0.31765 | -10.9946 | 2.6844 | 0.44197 | 0.31765 | -13.8672 | 20.5107 | 3.3769 | 2.4271 | 8.7742 | 19.6815 | 3.2404 | 2.3289 | 8.7557 | 17.9922 | 2.9623 | 2.129 | 8.4729 | 15.7449 | 2.5923 | 1.8631 | 8.1779 | 14.8948 | 2.4523 | 1.7625 | 7.6965 | 13.8919 | 2.2872 | 1.6439 | 7.139 | 13.4421 | 2.2131 | 1.5906 | 6.3621 | 11.4369 | 1.883 | 1.3534 | 4.8202 | 9.2283 | 1.5194 | 1.092 | 3.2766 | 6.9391 | 1.1425 | 0.82111 | 1.781 | 2.6844 | 0.44197 | 0.31765 | -2.6117 | 2.6844 | 0.44197 | 0.31765 | -7.0448 | 2.6844 | 0.44197 | 0.31765 | -10.3807 | 2.6844 | 0.44197 | 0.31765 | -12.5565 | 2.6844 | 0.44197 | 0.31765 | -11.7594 | 20.5107 | 3.3769 | 2.4271 | 8.7742 | 19.5367 | 3.2166 | 2.3118 | 8.4219 | 18.1443 | 2.9873 | 2.147 | 8.0527 | 16.631 | 2.7382 | 1.968 | 7.7577 | 14.6948 | 2.4194 | 1.7389 | 7.4057 | 14.1155 | 2.324 | 1.6703 | 6.9755 | 12.7227 | 2.0947 | 1.5055 | 6.4839 | 11.5744 | 1.9056 | 1.3696 | 5.9613 | 10.9442 | 1.8019 | 1.295 | 5.3793 | 10.1856 | 1.677 | 1.2053 | 4.7789 | 6.8993 | 1.1359 | 0.81641 | 2.5178 | 3.7863 | 0.62339 | 0.44804 | 0.03234 | 1.2195 | 0.20079 | 0.14431 | -1.6629 | 2.6844 | 0.44197 | 0.31765 | -3.0932 | 2.6844 | 0.44197 | 0.31765 | -3.8348 | 20.5107 | 3.3769 | 2.4271 | 8.7742 | 19.1495 | 3.1528 | 2.266 | 8.4765 | 17.1555 | 2.8245 | 2.03 | 8.007 | 15.0007 | 2.4698 | 1.7751 | 7.5438 | 13.7698 | 2.2671 | 1.6294 | 6.9176 | 12.803 | 2.1079 | 1.515 | 6.2782 | 12.1481 | 2.0001 | 1.4375 | 5.4042 | 9.9154 | 1.6325 | 1.1733 | 3.7206 | 7.5616 | 1.245 | 0.89477 | 2.0783 | 5.0985 | 0.83943 | 0.60332 | 0.48137 | 2.6844 | 0.44197 | 0.31765 | -4.3295 | 2.6844 | 0.44197 | 0.31765 | -9.0722 | 2.6844 | 0.44197 | 0.31765 | -12.7355 | 2.6844 | 0.44197 | 0.31765 | -15.2432 | 2.6844 | 0.44197 | 0.31765 | -14.8418
HILL TOP T13 | KEARSLEY LOCAL | KEARSLEY | 373476 | 403758 | 6.5112 | 6.5112 | 6.5112 | 3.3712 | 6.5492 | 6.5492 | 6.5492 | 3.1845 | 6.6129 | 6.6129 | 6.6129 | 3.1801 | 6.6901 | 6.6901 | 6.6901 | 3.0947 | 6.7868 | 6.7868 | 6.7868 | 2.9788 | 6.9042 | 6.9042 | 6.9042 | 2.8598 | 7.0296 | 7.0296 | 7.0296 | 2.7508 | 7.1786 | 7.1786 | 7.1786 | 2.6371 | 7.325 | 7.325 | 7.325 | 2.4644 | 7.4649 | 7.4649 | 7.4649 | 2.2975 | 7.9405 | 7.9405 | 7.9405 | 1.1641 | 8.4725 | 8.4725 | 8.4725 | -0.68712 | 8.8069 | 8.8069 | 8.8069 | -2.2225 | 9.0396 | 9.0396 | 9.0396 | -3.8732 | 9.1964 | 9.1964 | 9.1964 | -5.2505 | 6.4972 | 6.4972 | 6.4972 | 3.3712 | 6.5253 | 6.5253 | 6.5253 | 3.1886 | 6.5573 | 6.5573 | 6.5573 | 3.2412 | 6.596 | 6.596 | 6.596 | 3.1782 | 6.6486 | 6.6486 | 6.6486 | 3.1047 | 6.7172 | 6.7172 | 6.7172 | 3.0194 | 6.8016 | 6.8016 | 6.8016 | 2.8982 | 6.901 | 6.901 | 6.901 | 2.7261 | 6.9808 | 6.9808 | 6.9808 | 2.5472 | 7.0598 | 7.0598 | 7.0598 | 2.3658 | 7.3371 | 7.3371 | 7.3371 | 1.8065 | 7.6576 | 7.6576 | 7.6576 | 1.2043 | 7.9808 | 7.9808 | 7.9808 | 0.59679 | 8.3281 | 8.3281 | 8.3281 | -0.067302 | 8.5372 | 8.5372 | 8.5372 | -0.51899 | 6.5172 | 6.5172 | 6.5172 | 3.3712 | 6.5601 | 6.5601 | 6.5601 | 3.1976 | 6.6311 | 6.6311 | 6.6311 | 3.2063 | 6.7188 | 6.7188 | 6.7188 | 3.1457 | 6.827 | 6.827 | 6.827 | 3.0536 | 6.9421 | 6.9421 | 6.9421 | 2.9621 | 7.0656 | 7.0656 | 7.0656 | 2.8934 | 7.2193 | 7.2193 | 7.2193 | 2.8237 | 7.3419 | 7.3419 | 7.3419 | 2.7189 | 7.4511 | 7.4511 | 7.4511 | 2.6048 | 7.9194 | 7.9194 | 7.9194 | 1.6341 | 8.4767 | 8.4767 | 8.4767 | -0.11055 | 8.7857 | 8.7857 | 8.7857 | -1.5512 | 9.0077 | 9.0077 | 9.0077 | -3.0675 | 9.1305 | 9.1305 | 9.1305 | -4.2697 | 6.5172 | 6.5172 | 6.5172 | 3.3712 | 6.5147 | 6.5147 | 6.5147 | 3.3378 | 6.5503 | 6.5503 | 6.5503 | 3.3865 | 6.5988 | 6.5988 | 6.5988 | 3.3348 | 6.6733 | 6.6733 | 6.6733 | 3.2367 | 6.7919 | 6.7919 | 6.7919 | 3.1256 | 6.9506 | 6.9506 | 6.9506 | 2.9219 | 7.1508 | 7.1508 | 7.1508 | 2.3722 | 7.3371 | 7.3371 | 7.3371 | 1.7861 | 7.525 | 7.525 | 7.525 | 1.1912 | 8.0795 | 8.0795 | 8.0795 | -0.56879 | 8.5074 | 8.5074 | 8.5074 | -2.2088 | 8.7466 | 8.7466 | 8.7466 | -3.5119 | 8.8995 | 8.8995 | 8.8995 | -4.3734 | 8.8698 | 8.8698 | 8.8698 | -3.8202 | 6.5112 | 6.5112 | 6.5112 | 3.3712 | 6.5424 | 6.5424 | 6.5424 | 3.2027 | 6.5865 | 6.5865 | 6.5865 | 3.2204 | 6.6333 | 6.6333 | 6.6333 | 3.1696 | 6.6965 | 6.6965 | 6.6965 | 3.1188 | 6.7977 | 6.7977 | 6.7977 | 3.0491 | 6.9255 | 6.9255 | 6.9255 | 2.9651 | 7.0489 | 7.0489 | 7.0489 | 2.8741 | 7.1706 | 7.1706 | 7.1706 | 2.7139 | 7.3009 | 7.3009 | 7.3009 | 2.5534 | 7.688 | 7.688 | 7.688 | 1.9834 | 8.0552 | 8.0552 | 8.0552 | 1.3772 | 8.3078 | 8.3078 | 8.3078 | 0.97642 | 8.5003 | 8.5003 | 8.5003 | 0.63984 | 8.5921 | 8.5921 | 8.5921 | 0.47826 | 6.5112 | 6.5112 | 6.5112 | 3.3712 | 6.5253 | 6.5253 | 6.5253 | 3.3054 | 6.5833 | 6.5833 | 6.5833 | 3.3132 | 6.6588 | 6.6588 | 6.6588 | 3.217 | 6.7532 | 6.7532 | 6.7532 | 3.0798 | 6.8648 | 6.8648 | 6.8648 | 2.9444 | 7.0052 | 7.0052 | 7.0052 | 2.7117 | 7.1992 | 7.1992 | 7.1992 | 2.122 | 7.3767 | 7.3767 | 7.3767 | 1.5104 | 7.5465 | 7.5465 | 7.5465 | 0.88962 | 8.0915 | 8.0915 | 8.0915 | -0.97908 | 8.602 | 8.602 | 8.602 | -2.7312 | 8.8652 | 8.8652 | 8.8652 | -4.1498 | 9.0303 | 9.0303 | 9.0303 | -5.143 | 9.0122 | 9.0122 | 9.0122 | -4.7267
HINDLEY GREEN | ATHERTON | KEARSLEY | 363389 | 403254 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | -0.12449 | 2.1312 | 0.44197 | 0.31765 | -4.2074 | 1.6795 | 0.44197 | 0.31765 | -7.0212 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | -0.1447 | 1.0123 | 0.38425 | 0.31397 | -4.3185 | 1.6795 | 0.44197 | 0.31765 | -7.6978 | 1.6795 | 0.44197 | 0.31765 | -9.2944 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6634 | 0.44197 | 0.31765 | -1.9489 | 1.6795 | 0.44197 | 0.31765 | -5.2825 | 1.6795 | 0.44197 | 0.31765 | -7.0439 | 1.6795 | 0.44197 | 0.31765 | -6.2724 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | -0.25962 | 0.96756 | 0.36725 | 0.30008 | -5.5494 | 1.6795 | 0.44197 | 0.31765 | -9.2154 | 1.6795 | 0.44197 | 0.31765 | -11.3101 | 1.6795 | 0.44197 | 0.31765 | -10.9692
HOLLINWOOD | CHADDERTON | WHITEGATE | 390287 | 402592 | 26.0518 | 12.4663 | 9.094 | 18.568 | 26.1029 | 12.3089 | 8.9792 | 18.2106 | 26.1844 | 11.1209 | 8.1125 | 18.0471 | 26.2866 | 9.9572 | 7.2636 | 17.9675 | 26.3987 | 8.7902 | 6.4123 | 17.8688 | 26.5071 | 7.5811 | 5.5303 | 17.7581 | 26.6382 | 6.4744 | 4.723 | 17.6424 | 26.8034 | 6.4355 | 4.6946 | 17.5204 | 26.961 | 6.3658 | 4.6437 | 17.3622 | 27.0977 | 6.3925 | 4.6633 | 17.2131 | 27.5302 | 6.3164 | 4.6077 | 16.2642 | 27.9484 | 6.6863 | 4.8776 | 14.5315 | 28.2074 | 8.1158 | 5.9204 | 13.0876 | 28.4119 | 9.9749 | 7.2766 | 11.6606 | 28.5415 | 10.3426 | 7.5448 | 10.2696 | 26.0376 | 12.4663 | 9.094 | 18.568 | 26.0672 | 12.4051 | 9.0494 | 18.4299 | 26.1027 | 11.3363 | 8.2697 | 18.3098 | 26.1408 | 10.2624 | 7.4863 | 18.229 | 26.1924 | 9.1836 | 6.6993 | 18.1459 | 26.2585 | 8.0999 | 5.9088 | 18.0421 | 26.3407 | 6.9474 | 5.068 | 17.9112 | 26.4394 | 6.8795 | 5.0185 | 17.7527 | 26.5408 | 6.8158 | 4.9721 | 17.5923 | 26.6489 | 6.7523 | 4.9257 | 17.431 | 26.9451 | 6.5581 | 4.784 | 16.9331 | 27.2655 | 6.3621 | 4.641 | 16.2192 | 27.574 | 7.1705 | 5.2308 | 15.5384 | 27.8993 | 8.6808 | 6.3326 | 14.8111 | 28.1151 | 9.0847 | 6.6271 | 14.2924 | 26.0577 | 12.4663 | 9.094 | 18.568 | 26.1154 | 12.2759 | 8.9551 | 18.1598 | 26.207 | 11.0451 | 8.0572 | 17.9863 | 26.3239 | 9.8356 | 7.1749 | 17.9063 | 26.4398 | 8.5941 | 6.2693 | 17.7485 | 26.562 | 7.4921 | 5.4654 | 17.5796 | 26.709 | 6.3701 | 4.6469 | 17.4052 | 26.8919 | 6.2934 | 4.5909 | 17.2273 | 27.0101 | 6.2277 | 4.543 | 17.038 | 27.1262 | 6.2363 | 4.5493 | 16.86 | 27.5569 | 6.1522 | 4.488 | 16.2329 | 27.9954 | 6.4975 | 4.7398 | 14.6867 | 28.2711 | 7.895 | 5.7593 | 13.3546 | 28.4691 | 9.7139 | 7.0862 | 12.1018 | 28.5641 | 10.1045 | 7.3711 | 10.9849 | 26.0577 | 12.4663 | 9.094 | 18.568 | 26.0539 | 12.3448 | 9.0054 | 18.3919 | 26.1042 | 12.1539 | 8.8661 | 18.2902 | 26.1769 | 11.9079 | 8.6867 | 18.2487 | 26.2795 | 11.7574 | 8.5768 | 18.1178 | 26.3888 | 11.6641 | 8.5088 | 17.9574 | 26.5333 | 11.5454 | 8.4222 | 17.741 | 26.7101 | 11.4713 | 8.3681 | 17.3777 | 26.8729 | 11.383 | 8.3037 | 16.9866 | 27.0387 | 11.2622 | 8.2157 | 16.4115 | 27.465 | 11.311 | 8.2512 | 14.8093 | 27.8251 | 10.8135 | 7.8883 | 13.2321 | 28.063 | 10.4148 | 7.5975 | 11.9615 | 28.2144 | 10.244 | 7.4728 | 11.1993 | 28.2168 | 10.161 | 7.4123 | 11.6283 | 26.0518 | 12.4663 | 9.094 | 18.568 | 26.0946 | 12.3731 | 9.026 | 18.3749 | 26.1521 | 11.2106 | 8.178 | 18.2659 | 26.2118 | 10.0546 | 7.3347 | 18.2276 | 26.2906 | 8.9066 | 6.4972 | 18.1946 | 26.4002 | 7.7222 | 5.6332 | 18.1327 | 26.5248 | 6.5614 | 4.7865 | 18.0425 | 26.6673 | 6.5529 | 4.7802 | 17.9405 | 26.8015 | 6.4748 | 4.7232 | 17.7928 | 26.9408 | 6.5101 | 4.749 | 17.6459 | 27.3054 | 6.5159 | 4.7532 | 17.1611 | 27.6742 | 7.1198 | 5.1938 | 16.4845 | 27.9355 | 8.7483 | 6.3818 | 15.9142 | 28.1442 | 10.8209 | 7.8937 | 15.4128 | 28.2478 | 11.4261 | 8.3352 | 15.1527 | 26.0518 | 12.4663 | 9.094 | 18.568 | 26.0627 | 12.2837 | 8.9608 | 18.2163 | 26.1393 | 12.0709 | 8.8055 | 18.0452 | 26.2446 | 11.8132 | 8.6175 | 17.9586 | 26.3578 | 11.6717 | 8.5143 | 17.7888 | 26.4619 | 11.5637 | 8.4356 | 17.6121 | 26.5902 | 11.4438 | 8.3481 | 17.3848 | 26.7659 | 11.3571 | 8.2849 | 16.9911 | 26.9274 | 11.2452 | 8.2032 | 16.456 | 27.0901 | 11.1125 | 8.1064 | 15.818 | 27.5369 | 11.1281 | 8.1178 | 14.098 | 27.9018 | 10.6132 | 7.7422 | 12.4189 | 28.1517 | 10.1907 | 7.434 | 11.0279 | 28.3017 | 9.9987 | 7.2939 | 10.1311 | 28.3086 | 9.8857 | 7.2115 | 10.4131
HOLME RD | RIBBLE | PENWORTHAM EAST / ROCHDALE | 352311 | 429141 | 30.1782 | 7.9233 | 5.6947 | 12.5098 | 30.2789 | 7.7628 | 5.5793 | 11.9241 | 30.4163 | 7.5922 | 5.4567 | 11.7733 | 30.5921 | 7.4865 | 5.3807 | 11.7268 | 30.8088 | 7.3206 | 5.2615 | 11.6017 | 31.0592 | 6.9964 | 5.0285 | 11.4723 | 31.3521 | 6.9903 | 5.0241 | 11.3544 | 31.679 | 6.9109 | 4.967 | 11.2362 | 31.9195 | 6.7999 | 4.8872 | 11.0539 | 32.1504 | 6.7041 | 4.8184 | 10.9003 | 33.0088 | 6.1735 | 4.437 | 9.1167 | 34.0519 | 5.6605 | 4.0683 | 5.5644 | 33.8092 | 5.5664 | 4.0007 | 2.5508 | 33.7495 | 5.5566 | 3.9936 | -0.90861 | 30.3437 | 4.9959 | 3.5906 | -3.8782 | 30.1413 | 7.9233 | 5.6947 | 12.5098 | 30.2208 | 7.9122 | 5.6866 | 12.2614 | 30.2945 | 7.9077 | 5.6834 | 12.1338 | 30.3902 | 7.8388 | 5.6339 | 12.0188 | 30.5247 | 7.7461 | 5.5673 | 11.8371 | 30.6977 | 7.6176 | 5.4749 | 11.6097 | 30.9067 | 7.298 | 5.2452 | 11.3077 | 31.1441 | 7.1363 | 5.129 | 10.9483 | 31.2875 | 7.0044 | 5.0342 | 10.6758 | 31.4393 | 6.8752 | 4.9413 | 10.399 | 31.9205 | 6.5174 | 4.6842 | 9.5681 | 32.3531 | 6.2667 | 4.504 | 8.7192 | 32.7567 | 6.3526 | 4.5658 | 7.7308 | 33.1664 | 6.5345 | 4.6965 | 6.7508 | 33.4626 | 6.4457 | 4.6326 | 6.1111 | 30.1911 | 7.9233 | 5.6947 | 12.5098 | 30.3003 | 7.7083 | 5.5401 | 11.8691 | 30.4552 | 7.4958 | 5.3874 | 11.7389 | 30.6573 | 7.3008 | 5.2472 | 11.7469 | 30.9068 | 7.0919 | 5.0971 | 11.682 | 31.1957 | 6.8664 | 4.935 | 11.6232 | 31.5216 | 6.8558 | 4.9274 | 11.604 | 31.8617 | 6.7378 | 4.8426 | 11.5921 | 32.1237 | 6.6027 | 4.7455 | 11.5209 | 32.3755 | 6.4732 | 4.6524 | 11.4629 | 33.2809 | 5.8684 | 4.2178 | 9.8048 | 31.6373 | 5.2088 | 3.7437 | 6.4227 | 30.8715 | 5.0828 | 3.6531 | 3.5559 | 30.4759 | 5.0176 | 3.6063 | 0.47097 | 26.6905 | 4.3944 | 3.1583 | -2.0533 | 30.1912 | 7.9233 | 5.6947 | 12.5098 | 30.1856 | 7.8256 | 5.6244 | 12.4128 | 30.2524 | 7.7135 | 5.5438 | 12.4167 | 30.353 | 7.5692 | 5.4401 | 12.4433 | 30.511 | 7.3351 | 5.2719 | 12.3574 | 30.7611 | 7.0427 | 5.0617 | 12.2415 | 31.084 | 6.9611 | 5.0031 | 11.9263 | 31.4722 | 6.8832 | 4.9471 | 10.8996 | 31.786 | 6.7065 | 4.8201 | 9.8081 | 32.0961 | 6.5169 | 4.6839 | 8.7215 | 33.042 | 7.2906 | 5.2399 | 5.5494 | 34.009 | 6.4511 | 4.6366 | 2.4559 | 34.4705 | 5.6753 | 4.079 | -0.14933 | 29.8647 | 4.917 | 3.5339 | -1.9168 | 28.7629 | 4.7356 | 3.4036 | -0.76494 | 30.1781 | 7.9233 | 5.6947 | 12.5098 | 30.2606 | 7.8438 | 5.6375 | 12.1956 | 30.3487 | 7.7092 | 5.5407 | 12.1467 | 30.4492 | 7.6164 | 5.4741 | 12.1914 | 30.586 | 7.4846 | 5.3793 | 12.2068 | 30.8036 | 7.2 | 5.1748 | 12.1708 | 31.0926 | 7.1592 | 5.1455 | 12.0891 | 31.3972 | 7.0962 | 5.1002 | 12.0041 | 31.6016 | 6.9944 | 5.027 | 11.8432 | 31.807 | 6.8962 | 4.9565 | 11.6922 | 32.4811 | 6.5896 | 4.7361 | 11.0662 | 33.2015 | 6.4943 | 4.6676 | 9.8008 | 33.6098 | 6.7974 | 4.8854 | 8.877 | 33.9805 | 7.2719 | 5.2265 | 8.0328 | 34.1756 | 7.2049 | 5.1783 | 7.6292 | 30.1781 | 7.9233 | 5.6947 | 12.5098 | 30.2086 | 7.7248 | 5.552 | 12.0885 | 30.3347 | 7.5817 | 5.4491 | 11.9382 | 30.5075 | 7.4084 | 5.3246 | 11.8392 | 30.7232 | 7.1549 | 5.1424 | 11.6398 | 30.9684 | 6.8362 | 4.9133 | 11.4482 | 31.2645 | 6.7727 | 4.8677 | 11.0395 | 31.6684 | 6.6624 | 4.7884 | 9.8838 | 31.9943 | 6.4636 | 4.6455 | 8.698 | 32.313 | 6.2547 | 4.4954 | 7.5175 | 33.2558 | 6.9799 | 5.0166 | 4.0631 | 34.1479 | 6.087 | 4.3749 | 0.73765 | 31.9563 | 5.2614 | 3.7814 | -2.0881 | 27.0734 | 4.4574 | 3.2036 | -4.1211 | 25.608 | 4.2162 | 3.0302 | -3.2627
HOLT ST | BURY | KEARSLEY | 378620 | 416362 | 23.3947 | 19.2136 | 13.8092 | 8.9618 | 23.4914 | 19.0644 | 13.702 | 8.6112 | 23.6465 | 18.8562 | 13.5524 | 8.427 | 23.8649 | 18.6245 | 13.3858 | 8.2847 | 24.1455 | 18.221 | 13.0958 | 8.0525 | 24.483 | 17.7579 | 12.763 | 7.8063 | 24.787 | 17.3788 | 12.4905 | 7.5729 | 25.1746 | 17.5688 | 12.6271 | 7.3194 | 25.5512 | 17.5489 | 12.6127 | 6.9483 | 25.9469 | 17.4656 | 12.5529 | 6.3847 | 27.2947 | 16.8205 | 12.0892 | 3.5333 | 28.4163 | 15.8116 | 11.3641 | -0.54986 | 29.1153 | 14.8663 | 10.6847 | -3.8185 | 29.6822 | 14.8823 | 10.6962 | -7.144 | 30.0564 | 14.2567 | 10.2466 | -9.816 | 23.3464 | 19.2136 | 13.8092 | 8.9618 | 23.3967 | 19.1326 | 13.751 | 8.7821 | 23.4517 | 19.0595 | 13.6984 | 8.6537 | 23.5425 | 18.9731 | 13.6364 | 8.5065 | 23.6808 | 18.8366 | 13.5382 | 8.2868 | 23.8628 | 18.6767 | 13.4233 | 8.0195 | 24.0846 | 18.6324 | 13.3915 | 7.6777 | 24.3409 | 18.5079 | 13.302 | 7.2606 | 24.5498 | 18.3996 | 13.2242 | 6.8871 | 24.7832 | 18.2676 | 13.1293 | 6.498 | 25.5303 | 17.7877 | 12.7844 | 5.1245 | 26.3503 | 17.374 | 12.487 | 3.4758 | 27.1867 | 16.7536 | 12.0411 | 1.9025 | 28.087 | 16.3405 | 11.7442 | 0.23636 | 28.6586 | 15.9436 | 11.459 | -0.86056 | 23.4151 | 19.2136 | 13.8092 | 8.9618 | 23.5247 | 19.0336 | 13.6798 | 8.5999 | 23.7012 | 18.7421 | 13.4703 | 8.4464 | 23.9485 | 18.442 | 13.2546 | 8.3667 | 24.2623 | 17.9745 | 12.9186 | 8.2068 | 24.552 | 17.4401 | 12.5345 | 8.0478 | 24.8658 | 17.7275 | 12.7411 | 7.9329 | 25.2603 | 17.6892 | 12.7136 | 7.8175 | 25.6202 | 17.5037 | 12.5803 | 7.5291 | 25.9614 | 17.2211 | 12.3771 | 7.0451 | 27.3057 | 16.1581 | 11.6131 | 4.4444 | 28.4696 | 15.1189 | 10.8663 | 0.046423 | 29.2552 | 15.0811 | 10.8391 | -3.5427 | 29.8543 | 14.4516 | 10.3866 | -6.8954 | 30.1512 | 13.7593 | 9.8891 | -9.4761 | 23.4151 | 19.2136 | 13.8092 | 8.9618 | 23.4076 | 19.1057 | 13.7317 | 8.988 | 23.4857 | 18.8342 | 13.5365 | 8.9575 | 23.6211 | 18.4322 | 13.2476 | 8.923 | 23.8401 | 17.4013 | 12.5067 | 8.7664 | 24.19 | 17.9336 | 12.8892 | 8.5622 | 24.605 | 17.7113 | 12.7295 | 8.1637 | 25.1342 | 17.1458 | 12.323 | 7.0659 | 25.6178 | 16.7283 | 12.0229 | 5.8709 | 26.0357 | 16.4673 | 11.8353 | 4.6524 | 27.3451 | 16.5684 | 11.908 | 0.98949 | 28.3548 | 15.6795 | 11.2691 | -2.6461 | 29.0287 | 14.9195 | 10.7229 | -5.5578 | 29.4726 | 14.2533 | 10.2441 | -7.5768 | 29.4886 | 14.0701 | 10.1125 | -7.1723 | 23.3947 | 19.2136 | 13.8092 | 8.9618 | 23.4704 | 19.0996 | 13.7273 | 8.7459 | 23.5658 | 18.9146 | 13.5943 | 8.6514 | 23.6939 | 18.6921 | 13.4344 | 8.61 | 23.8784 | 18.2335 | 13.1047 | 8.534 | 24.1745 | 17.9274 | 12.8848 | 8.395 | 24.5151 | 17.4146 | 12.5162 | 8.206 | 24.8401 | 17.6638 | 12.6953 | 7.9979 | 25.1513 | 17.6705 | 12.7002 | 7.6781 | 25.4882 | 17.6456 | 12.6823 | 7.3384 | 26.6205 | 17.1798 | 12.3475 | 5.5142 | 27.6937 | 16.4842 | 11.8475 | 3.5368 | 28.4485 | 16.2082 | 11.6491 | 2.1509 | 28.9855 | 16.4037 | 11.7897 | 0.75376 | 29.202 | 16.0768 | 11.5547 | -0.29523 | 23.3947 | 19.2136 | 13.8092 | 8.9618 | 23.4336 | 19.06 | 13.6988 | 8.7754 | 23.5788 | 18.7021 | 13.4415 | 8.601 | 23.7901 | 18.3432 | 13.1837 | 8.4367 | 24.062 | 17.265 | 12.4087 | 8.1689 | 24.3841 | 17.8131 | 12.8027 | 7.9 | 24.7147 | 17.5787 | 12.6341 | 7.426 | 25.2301 | 17.0132 | 12.2277 | 6.215 | 25.7087 | 16.5451 | 11.8913 | 4.9266 | 26.104 | 16.2027 | 11.6452 | 3.6017 | 27.3996 | 16.3043 | 11.7182 | -0.37766 | 28.5127 | 15.3364 | 11.0226 | -4.4112 | 29.2575 | 14.5048 | 10.4249 | -7.7289 | 29.7469 | 13.7518 | 9.8837 | -10.1674 | 29.838 | 13.5749 | 9.7566 | -9.8067
HURST | HARTSHEAD-HEYROD | STALYBRIDGE | 394658 | 400360 | 23.4376 | 6.5083 | 4.7477 | 10.3595 | 23.5397 | 6.3863 | 4.6587 | 10.0305 | 23.6699 | 6.2961 | 4.5929 | 9.9645 | 23.7562 | 6.3832 | 4.6565 | 9.9366 | 23.8695 | 6.349 | 4.6315 | 9.7899 | 24.0044 | 6.2775 | 4.5793 | 9.6169 | 24.1659 | 6.1881 | 4.5141 | 9.4605 | 24.3539 | 6.0721 | 4.4295 | 9.3424 | 24.487 | 5.9786 | 4.3613 | 9.1574 | 24.6139 | 5.9568 | 4.3454 | 8.932 | 25.041 | 5.5623 | 4.0576 | 7.3219 | 25.5106 | 4.9897 | 3.6399 | 4.474 | 25.8502 | 4.482 | 3.2696 | 2.0694 | 26.1469 | 4.3166 | 3.1489 | -0.37028 | 26.1156 | 4.2362 | 3.0903 | -2.5364 | 23.4016 | 6.5083 | 4.7477 | 10.3595 | 23.4553 | 6.4659 | 4.7168 | 10.21 | 23.5047 | 6.421 | 4.684 | 10.166 | 23.573 | 6.3597 | 4.6393 | 10.1251 | 23.6792 | 6.2568 | 4.5642 | 10.0263 | 23.7628 | 6.12 | 4.4645 | 9.9056 | 23.8597 | 5.9702 | 4.3552 | 9.7275 | 23.9706 | 5.8809 | 4.29 | 9.5006 | 24.0585 | 5.8533 | 4.2699 | 9.2794 | 24.1503 | 5.8218 | 4.2469 | 9.0542 | 24.4407 | 5.6892 | 4.1502 | 8.3528 | 24.7319 | 5.562 | 4.0574 | 7.5943 | 24.9841 | 5.4432 | 3.9708 | 6.8549 | 25.2103 | 5.5994 | 4.0847 | 6.1153 | 25.3675 | 5.7523 | 4.1962 | 5.6422 | 23.4534 | 6.5083 | 4.7477 | 10.3595 | 23.5717 | 6.3543 | 4.6354 | 10.0041 | 23.6961 | 6.3236 | 4.613 | 9.9562 | 23.7998 | 6.3652 | 4.6434 | 9.9694 | 23.9347 | 6.3007 | 4.5963 | 9.8699 | 24.0949 | 6.2263 | 4.542 | 9.7619 | 24.285 | 6.0799 | 4.4352 | 9.6938 | 24.4647 | 6.0872 | 4.4405 | 9.6058 | 24.6082 | 6.0072 | 4.3822 | 9.4393 | 24.744 | 5.9345 | 4.3291 | 9.2694 | 25.1519 | 5.4797 | 3.9974 | 7.8239 | 25.5962 | 4.8772 | 3.5579 | 5.0991 | 25.9205 | 4.341 | 3.1667 | 2.7948 | 25.6041 | 4.1532 | 3.0297 | 0.46846 | 24.8677 | 4.0338 | 2.9426 | -1.5763 | 23.4534 | 6.5083 | 4.7477 | 10.3595 | 23.4525 | 6.4345 | 4.6939 | 10.4065 | 23.5348 | 6.4597 | 4.7123 | 10.4586 | 23.5878 | 6.5167 | 4.7538 | 10.4909 | 23.6666 | 6.4735 | 4.7223 | 10.3767 | 23.8028 | 6.3694 | 4.6464 | 10.225 | 23.9866 | 6.3395 | 4.6246 | 9.9267 | 24.2059 | 6.1124 | 4.4589 | 9.0765 | 24.3607 | 5.8721 | 4.2836 | 8.1812 | 24.5139 | 5.6508 | 4.1222 | 7.3009 | 24.9834 | 4.9865 | 3.6376 | 4.7431 | 25.463 | 4.3913 | 3.2034 | 2.2509 | 24.0237 | 3.8969 | 2.8427 | 0.16657 | 25.86 | 4.1947 | 3.06 | -1.1491 | 25.7228 | 4.1725 | 3.0438 | -0.38395 | 23.4376 | 6.5083 | 4.7477 | 10.3595 | 23.5228 | 6.4215 | 4.6844 | 10.1615 | 23.6213 | 6.329 | 4.6169 | 10.1641 | 23.6716 | 6.4441 | 4.7009 | 10.2266 | 23.7334 | 6.4464 | 4.7026 | 10.2512 | 23.8458 | 6.4031 | 4.671 | 10.2398 | 24.0046 | 6.3328 | 4.6197 | 10.1803 | 24.1829 | 6.2445 | 4.5552 | 10.1093 | 24.3164 | 6.1323 | 4.4734 | 9.9623 | 24.432 | 6.1279 | 4.4702 | 9.7638 | 24.8104 | 5.8765 | 4.2868 | 8.9166 | 25.205 | 5.6509 | 4.1223 | 7.9319 | 25.4575 | 5.448 | 3.9743 | 7.2152 | 25.6677 | 5.6189 | 4.0989 | 6.5513 | 25.7484 | 5.8271 | 4.2508 | 6.0501 | 23.4376 | 6.5083 | 4.7477 | 10.3595 | 23.4722 | 6.3933 | 4.6638 | 10.2163 | 23.5977 | 6.4041 | 4.6717 | 10.1595 | 23.6824 | 6.4394 | 4.6974 | 10.0996 | 23.797 | 6.3745 | 4.6501 | 9.8934 | 23.9302 | 6.2554 | 4.5632 | 9.678 | 24.0971 | 6.2128 | 4.5321 | 9.3083 | 24.3202 | 5.9691 | 4.3543 | 8.3727 | 24.4856 | 5.7173 | 4.1707 | 7.4005 | 24.6464 | 5.4819 | 3.999 | 6.4431 | 25.1203 | 4.7756 | 3.4837 | 3.6555 | 25.5406 | 4.1429 | 3.0222 | 0.96421 | 22.4596 | 3.6432 | 2.6576 | -1.3052 | 23.9057 | 3.8777 | 2.8288 | -2.8403 | 23.2661 | 3.774 | 2.7531 | -2.3261
HUTTON END & SKELTON C | PENRITH & SHAP | HARKER / HUTTON | 345810 | 538827 | 20.4338 | 20.4338 | 19.2703 | 19.8878 | 20.5058 | 20.5058 | 19.2364 | 19.7962 | 20.6111 | 20.6111 | 18.8829 | 19.6044 | 20.7401 | 20.7401 | 18.5244 | 19.4081 | 20.9232 | 20.9232 | 18.1444 | 19.1111 | 21.1836 | 21.1836 | 17.7648 | 18.8282 | 21.4086 | 21.4086 | 17.369 | 18.4081 | 21.6661 | 21.6661 | 17.2312 | 17.64 | 21.9711 | 21.9711 | 17.07 | 16.6873 | 22.3083 | 22.3083 | 16.8934 | 15.6082 | 23.4057 | 22.6603 | 16.2864 | 11.8877 | 24.3491 | 21.8558 | 15.7082 | 8.4734 | 24.9314 | 21.2469 | 15.2705 | 6.2863 | 25.3023 | 20.6634 | 14.8512 | 4.8452 | 25.5004 | 19.6278 | 14.1069 | 3.8394 | 20.4346 | 20.4346 | 19.2703 | 19.8878 | 20.5056 | 20.5056 | 19.244 | 19.7703 | 20.5831 | 20.5831 | 19.2002 | 19.5868 | 20.6736 | 20.6736 | 19.1469 | 19.3941 | 20.787 | 20.787 | 19.0837 | 19.1736 | 20.9318 | 20.9318 | 19.0195 | 18.9577 | 21.1156 | 21.1156 | 18.9316 | 18.6841 | 21.3444 | 21.3444 | 18.8581 | 18.355 | 21.5508 | 21.5508 | 18.7975 | 18.1061 | 21.7554 | 21.7554 | 18.7324 | 17.8267 | 22.368 | 22.368 | 18.4363 | 16.1633 | 23.1226 | 23.1226 | 18.0519 | 13.7622 | 23.9127 | 23.9127 | 17.6225 | 11.104 | 24.7516 | 23.8026 | 17.1074 | 8.0666 | 25.2887 | 23.1674 | 16.6509 | 5.9417 | 20.4335 | 20.4335 | 19.2703 | 19.8878 | 20.5018 | 20.5018 | 19.2187 | 19.8145 | 20.6041 | 20.6041 | 18.8213 | 19.6391 | 20.7378 | 20.7378 | 18.4223 | 19.4762 | 20.9084 | 20.9084 | 18.0165 | 19.2191 | 21.1434 | 21.1434 | 17.6204 | 18.9916 | 21.3424 | 21.3424 | 17.2089 | 18.6512 | 21.5576 | 21.5576 | 17.0596 | 18.0354 | 21.8068 | 21.8068 | 16.8892 | 17.2874 | 22.0898 | 22.0898 | 16.6987 | 16.4053 | 23.1389 | 22.2725 | 16.0077 | 12.8603 | 24.1864 | 21.2641 | 15.2829 | 9.0724 | 24.8842 | 20.3461 | 14.6231 | 6.4719 | 25.3066 | 18.9075 | 13.5892 | 4.8507 | 25.4771 | 18.0279 | 12.957 | 3.9532 | 20.4335 | 20.4335 | 19.2703 | 19.8878 | 20.4497 | 20.4497 | 19.2275 | 19.8849 | 20.5245 | 20.5245 | 18.8455 | 19.7027 | 20.6587 | 20.6587 | 18.4202 | 19.4894 | 20.8202 | 20.8202 | 18.015 | 19.2228 | 21.0588 | 21.0588 | 17.5745 | 18.9298 | 21.2568 | 21.2568 | 17.0453 | 18.4328 | 21.5262 | 21.5262 | 16.734 | 17.4831 | 21.8418 | 21.8418 | 16.3986 | 16.3212 | 22.1917 | 21.5755 | 15.5067 | 15.0293 | 23.2936 | 20.4653 | 14.7088 | 10.991 | 24.2039 | 19.5308 | 14.0372 | 7.695 | 24.7477 | 18.7577 | 13.4815 | 5.7098 | 25.04 | 18.1009 | 13.0095 | 4.7383 | 25.0717 | 17.7232 | 12.738 | 4.7788 | 20.4338 | 20.4338 | 19.2703 | 19.8878 | 20.4942 | 20.4942 | 19.2407 | 19.8064 | 20.5802 | 20.5802 | 18.8887 | 19.619 | 20.6763 | 20.6763 | 18.5324 | 19.4326 | 20.8098 | 20.8098 | 18.163 | 19.2106 | 21.0157 | 21.0157 | 17.8006 | 19.0567 | 21.2602 | 21.2602 | 17.4332 | 18.861 | 21.4673 | 21.4673 | 17.3224 | 18.3028 | 21.7077 | 21.7077 | 17.1894 | 17.5705 | 21.981 | 21.981 | 17.0412 | 16.7123 | 22.9598 | 22.9536 | 16.4972 | 13.4852 | 23.9077 | 22.2094 | 15.9624 | 10.2809 | 24.5343 | 21.5997 | 15.5241 | 8.176 | 24.9323 | 20.9751 | 15.0752 | 6.7939 | 25.0639 | 19.933 | 14.3263 | 6.2332 | 20.4338 | 20.4338 | 19.2703 | 19.8878 | 20.4696 | 20.4696 | 19.2246 | 19.8777 | 20.5697 | 20.5697 | 18.84 | 19.6804 | 20.7028 | 20.7028 | 18.4069 | 19.4055 | 20.8636 | 20.8636 | 17.9943 | 19.0817 | 21.0844 | 21.0844 | 17.5557 | 18.802 | 21.3207 | 21.3207 | 17.0461 | 18.441 | 21.5652 | 21.5652 | 16.7627 | 17.6648 | 21.8451 | 21.8451 | 16.4536 | 16.6763 | 22.1607 | 21.7428 | 15.627 | 15.5519 | 23.2609 | 20.5399 | 14.7624 | 11.5823 | 24.3013 | 19.5426 | 14.0456 | 7.8167 | 24.9857 | 18.6693 | 13.418 | 5.3151 | 25.3584 | 17.9567 | 12.9058 | 4.0231 | 25.4139 | 17.5582 | 12.6194 | 3.9724
HYDE | HYDE | STALYBRIDGE | 395215 | 395126 | 31.7276 | 10.4072 | 7.5919 | 10.9613 | 31.8141 | 9.989 | 7.2869 | 10.4024 | 31.9439 | 10.0702 | 7.3461 | 10.168 | 32.0909 | 9.9522 | 7.26 | 10.0232 | 32.263 | 9.7465 | 7.1099 | 9.776 | 32.4399 | 9.5393 | 6.9588 | 9.5086 | 32.6245 | 9.3929 | 6.852 | 9.26 | 32.8457 | 9.2738 | 6.7651 | 9.0285 | 33.0474 | 9.1399 | 6.6674 | 8.7342 | 33.2457 | 9.0186 | 6.579 | 8.4693 | 34.0128 | 8.4594 | 6.171 | 6.3826 | 34.6537 | 7.814 | 5.7002 | 2.5793 | 35.1058 | 7.4724 | 5.451 | -0.63162 | 35.4839 | 7.3698 | 5.3762 | -4.0451 | 35.7216 | 6.995 | 5.1028 | -7.0198 | 31.7024 | 10.4072 | 7.5919 | 10.9613 | 31.7987 | 10.3092 | 7.5204 | 10.6984 | 31.8974 | 10.2166 | 7.4529 | 10.4886 | 32.0016 | 10.096 | 7.3649 | 10.2854 | 32.1348 | 9.8894 | 7.2142 | 10.0239 | 32.3042 | 9.8179 | 7.162 | 9.7333 | 32.5121 | 9.6141 | 7.0134 | 9.35 | 32.7299 | 9.4414 | 6.8874 | 8.8557 | 32.8656 | 9.2699 | 6.7623 | 8.4946 | 32.9987 | 9.1199 | 6.6528 | 8.1299 | 33.4289 | 8.7094 | 6.3534 | 7.0058 | 33.8954 | 8.4554 | 6.1681 | 5.8207 | 34.3441 | 8.3582 | 6.0972 | 4.7052 | 34.8269 | 8.5142 | 6.211 | 3.4713 | 35.176 | 8.4279 | 6.1481 | 2.5588 | 31.7365 | 10.4072 | 7.5919 | 10.9613 | 31.8327 | 9.9318 | 7.2451 | 10.3632 | 31.9778 | 10.0224 | 7.3112 | 10.1443 | 32.1463 | 9.7627 | 7.1218 | 9.446 | 32.3257 | 9.4247 | 6.8752 | 8.4949 | 32.4985 | 9.0764 | 6.6211 | 7.5315 | 32.7008 | 8.8296 | 6.4411 | 6.6134 | 32.9412 | 8.6664 | 6.322 | 6.3192 | 33.1403 | 8.504 | 6.2036 | 5.9922 | 33.3349 | 8.3488 | 6.0904 | 5.6721 | 34.1022 | 7.7648 | 5.6643 | 3.8735 | 34.7726 | 7.0814 | 5.1658 | 0.31299 | 35.243 | 6.702 | 4.889 | -2.6447 | 35.6055 | 6.5676 | 4.791 | -5.7483 | 35.7862 | 6.1994 | 4.5224 | -8.3622 | 31.7365 | 10.4072 | 7.5919 | 10.9613 | 31.7127 | 10.026 | 7.3138 | 10.8487 | 31.7741 | 10.1821 | 7.4277 | 10.7701 | 31.8514 | 9.9377 | 7.2494 | 10.1302 | 31.9705 | 9.612 | 7.0118 | 9.2058 | 32.1642 | 9.287 | 6.7748 | 8.2408 | 32.3959 | 8.9782 | 6.5495 | 7.0801 | 32.688 | 8.7088 | 6.353 | 5.8038 | 32.9284 | 8.433 | 6.1518 | 4.4616 | 33.147 | 8.1957 | 5.9786 | 3.1248 | 33.785 | 8.4693 | 6.1783 | -0.30681 | 34.4008 | 7.618 | 5.5572 | -3.658 | 34.8158 | 6.891 | 5.0269 | -6.3493 | 35.0909 | 6.5613 | 4.7864 | -8.0828 | 35.0696 | 6.47 | 4.7198 | -7.0239 | 31.7276 | 10.4072 | 7.5919 | 10.9613 | 31.8026 | 10.0637 | 7.3413 | 10.7131 | 31.8955 | 10.1509 | 7.4049 | 10.5834 | 31.9842 | 10.0592 | 7.3381 | 10.5239 | 32.0926 | 9.8902 | 7.2148 | 10.4375 | 32.2662 | 9.7108 | 7.0839 | 10.3156 | 32.4287 | 9.5754 | 6.9851 | 10.1559 | 32.6158 | 9.4709 | 6.9089 | 9.964 | 32.7938 | 9.3369 | 6.8111 | 9.6631 | 32.9769 | 9.2118 | 6.7199 | 9.3621 | 33.5905 | 8.8285 | 6.4403 | 8.2811 | 34.2349 | 8.6222 | 6.2898 | 7.0241 | 34.6952 | 8.6821 | 6.3335 | 6.0234 | 35.0358 | 9.0638 | 6.6119 | 5.0733 | 35.1875 | 9.171 | 6.6901 | 4.6203 | 31.7276 | 10.4072 | 7.5919 | 10.9613 | 31.7468 | 9.957 | 7.2635 | 10.5763 | 31.8664 | 10.0979 | 7.3663 | 10.3515 | 32.0046 | 9.8253 | 7.1674 | 9.5917 | 32.1748 | 9.4792 | 6.9149 | 8.5565 | 32.3491 | 9.1395 | 6.6671 | 7.5129 | 32.5639 | 8.8115 | 6.4279 | 6.2575 | 32.9306 | 8.5208 | 6.2158 | 4.8566 | 33.163 | 8.2311 | 6.0045 | 3.4381 | 33.3734 | 7.978 | 5.8198 | 2.0242 | 34.0154 | 8.1858 | 5.9714 | -1.6556 | 34.6228 | 7.286 | 5.315 | -5.2309 | 35.0425 | 6.5112 | 4.7498 | -8.1578 | 35.3059 | 6.1244 | 4.4677 | -10.2062 | 35.296 | 5.9678 | 4.3535 | -9.5107
HYNDBURN RD | HUNCOAT | PADIHAM | 375688 | 428877 | 29.052 | 14.8239 | 10.8139 | 17.2013 | 29.0848 | 14.5709 | 10.6293 | 16.4824 | 29.1351 | 14.2056 | 10.3628 | 16.1285 | 29.1939 | 13.7602 | 10.0379 | 15.9221 | 29.2699 | 13.3838 | 9.7633 | 15.5468 | 29.3685 | 13.0473 | 9.5178 | 15.16 | 29.4969 | 12.8134 | 9.3472 | 15.0754 | 29.6632 | 12.741 | 9.2944 | 14.9832 | 29.8202 | 12.661 | 9.236 | 14.8589 | 29.9906 | 12.5842 | 9.18 | 14.7373 | 30.5221 | 12.2315 | 8.9227 | 13.8689 | 30.9364 | 11.8784 | 8.6651 | 12.3717 | 31.234 | 11.7262 | 8.5541 | 11.1258 | 31.4928 | 11.6024 | 8.4638 | 9.8433 | 31.6637 | 11.1432 | 8.1288 | 8.7311 | 29.0431 | 14.8239 | 10.8139 | 17.2013 | 29.0984 | 14.712 | 10.7322 | 16.8331 | 29.1682 | 14.5132 | 10.5871 | 16.5917 | 29.2489 | 14.3014 | 10.4327 | 16.4209 | 29.3501 | 14.0751 | 10.2676 | 16.1977 | 29.4752 | 13.8399 | 10.096 | 15.9503 | 29.6263 | 13.6028 | 9.9231 | 15.7635 | 29.7565 | 13.4695 | 9.8258 | 15.5375 | 29.8244 | 13.3652 | 9.7497 | 15.4183 | 29.899 | 13.2742 | 9.6833 | 15.2969 | 30.166 | 12.9385 | 9.4385 | 14.9137 | 30.4923 | 12.6186 | 9.2051 | 14.5022 | 30.8204 | 12.4854 | 9.108 | 14.1218 | 31.1817 | 12.4922 | 9.1129 | 13.7227 | 31.4057 | 12.2552 | 8.94 | 13.4366 | 29.0548 | 14.8239 | 10.8139 | 17.2013 | 29.0901 | 14.5077 | 10.5832 | 16.3697 | 29.1438 | 14.0244 | 10.2306 | 15.9965 | 29.2072 | 13.5189 | 9.8619 | 15.7893 | 29.2865 | 13.1427 | 9.5874 | 15.4151 | 29.3865 | 12.7655 | 9.3122 | 15.031 | 29.5139 | 12.5784 | 9.1758 | 14.9499 | 29.6758 | 12.4631 | 9.0917 | 14.8646 | 29.8169 | 12.3489 | 9.0083 | 14.7776 | 29.9706 | 12.2369 | 8.9266 | 14.6958 | 30.4557 | 11.7559 | 8.5758 | 13.9311 | 30.8795 | 11.2616 | 8.2152 | 12.5338 | 31.1871 | 10.9842 | 8.0129 | 11.3911 | 31.4281 | 10.6464 | 7.7664 | 10.2737 | 31.554 | 10.1548 | 7.4077 | 9.4257 | 29.0548 | 14.8239 | 10.8139 | 17.2013 | 29.0419 | 14.5916 | 10.6444 | 16.7138 | 29.0627 | 14.3011 | 10.4325 | 16.4291 | 29.0912 | 13.881 | 10.126 | 16.2569 | 29.1391 | 13.6367 | 9.9478 | 15.912 | 29.2204 | 13.4348 | 9.8005 | 15.5481 | 29.3397 | 13.2116 | 9.6377 | 15.3856 | 29.5033 | 12.9463 | 9.4441 | 14.9183 | 29.6736 | 12.8075 | 9.3429 | 14.4149 | 29.8574 | 12.6454 | 9.2247 | 13.9197 | 30.4348 | 12.7533 | 9.3034 | 12.4993 | 30.8974 | 12.1204 | 8.8417 | 11.1927 | 31.1429 | 11.4587 | 8.3589 | 10.0843 | 31.289 | 10.7838 | 7.8666 | 9.3433 | 31.2339 | 10.4795 | 7.6447 | 10.1399 | 29.052 | 14.8239 | 10.8139 | 17.2013 | 29.0814 | 14.6295 | 10.672 | 16.6082 | 29.1208 | 14.2851 | 10.4208 | 16.2889 | 29.1614 | 13.8446 | 10.0995 | 16.1099 | 29.2151 | 13.4709 | 9.8268 | 15.7929 | 29.2979 | 13.141 | 9.5862 | 15.4603 | 29.4128 | 12.9096 | 9.4174 | 15.4018 | 29.5524 | 12.8415 | 9.3677 | 15.3197 | 29.6787 | 12.7628 | 9.3103 | 15.196 | 29.8194 | 12.6834 | 9.2523 | 15.0658 | 30.3138 | 12.4258 | 9.0644 | 14.6095 | 30.6864 | 12.3081 | 8.9786 | 14.1294 | 30.9032 | 12.3581 | 9.0151 | 13.8055 | 31.0616 | 12.5361 | 9.1449 | 13.5506 | 31.0943 | 12.3808 | 9.0317 | 13.5776 | 29.052 | 14.8239 | 10.8139 | 17.2013 | 29.0589 | 14.4985 | 10.5764 | 16.3498 | 29.1047 | 14.1697 | 10.3366 | 15.9666 | 29.1607 | 13.7416 | 10.0243 | 15.7489 | 29.2324 | 13.4957 | 9.8449 | 15.3609 | 29.3222 | 13.2893 | 9.6943 | 14.9676 | 29.4418 | 13.0691 | 9.5337 | 14.7788 | 29.6112 | 12.7802 | 9.323 | 14.273 | 29.7641 | 12.6414 | 9.2217 | 13.7631 | 29.9306 | 12.4729 | 9.0988 | 13.2616 | 30.496 | 12.5509 | 9.1557 | 11.8078 | 31.0334 | 11.8932 | 8.6759 | 10.4446 | 31.3553 | 11.1996 | 8.1699 | 9.1928 | 31.525 | 10.4802 | 7.6451 | 8.3076 | 31.4875 | 10.1453 | 7.4008 | 8.9391
INDIA ST | LOWER DARWEN | ROCHDALE | 369485 | 421865 | 29.6985 | 15.1501 | 11.0518 | 18.3993 | 29.7493 | 14.8659 | 10.8444 | 17.5965 | 29.8256 | 14.8462 | 10.8301 | 17.2655 | 29.9235 | 14.7717 | 10.7758 | 17.0413 | 30.0508 | 14.6262 | 10.6696 | 16.7578 | 30.2039 | 14.5385 | 10.6056 | 16.4579 | 30.3894 | 14.6965 | 10.7209 | 16.1269 | 30.6239 | 14.6705 | 10.7019 | 15.789 | 31.2655 | 14.5421 | 10.6083 | 14.9641 | 31.4654 | 14.4178 | 10.5176 | 14.5967 | 33.9719 | 13.635 | 9.9465 | 10.7242 | 34.6054 | 13.1662 | 9.6046 | 8.0068 | 35.4737 | 12.7905 | 9.3305 | 5.3418 | 35.8327 | 12.3229 | 8.9894 | 3.0002 | 35.9841 | 11.8151 | 8.619 | 0.97681 | 29.6707 | 15.1501 | 11.0518 | 18.3993 | 29.7251 | 15.048 | 10.9773 | 18.0566 | 29.7759 | 15.3913 | 11.2278 | 17.9124 | 29.8384 | 15.4497 | 11.2704 | 17.7956 | 29.9255 | 15.3636 | 11.2075 | 17.6275 | 30.0369 | 15.2824 | 11.1483 | 17.4282 | 30.1739 | 15.0231 | 10.9592 | 17.167 | 30.3134 | 14.9143 | 10.8798 | 16.8299 | 30.8566 | 14.7613 | 10.7682 | 16.1447 | 30.9649 | 14.6864 | 10.7135 | 15.8974 | 31.3063 | 14.4146 | 10.5152 | 15.1482 | 31.6777 | 14.2219 | 10.3747 | 14.4086 | 32.0366 | 13.9421 | 10.1705 | 13.7517 | 32.41 | 14.138 | 10.3135 | 13.0629 | 32.6639 | 14.355 | 10.4717 | 12.6341 | 29.7057 | 15.1501 | 11.0518 | 18.3993 | 29.7632 | 14.8378 | 10.8239 | 17.5187 | 29.8498 | 14.653 | 10.6891 | 17.1671 | 29.9627 | 14.6269 | 10.6701 | 16.9521 | 30.1079 | 14.5439 | 10.6096 | 16.6817 | 30.2811 | 14.6508 | 10.6876 | 16.3936 | 30.4895 | 14.7009 | 10.7241 | 16.0984 | 30.7508 | 14.6046 | 10.6539 | 15.8029 | 31.397 | 14.4279 | 10.5249 | 15.0331 | 31.6046 | 14.2768 | 10.4147 | 14.7052 | 34.1405 | 13.4479 | 9.8101 | 10.9403 | 36.0517 | 12.6793 | 9.2494 | 7.1461 | 36.4456 | 12.2453 | 8.9328 | 5.0192 | 36.7218 | 11.7189 | 8.5488 | 2.8275 | 36.8515 | 11.242 | 8.2009 | 1.004 | 29.7057 | 15.1501 | 11.0518 | 18.3993 | 29.6896 | 14.9296 | 10.891 | 17.9366 | 29.724 | 14.8334 | 10.8208 | 17.6969 | 29.7775 | 14.8884 | 10.8609 | 17.5303 | 29.8687 | 14.9973 | 10.9403 | 17.2864 | 30.0166 | 14.9591 | 10.9125 | 16.9904 | 30.6593 | 14.8347 | 10.8217 | 16.0567 | 32.7793 | 14.4218 | 10.5205 | 13.1566 | 32.9879 | 14.1834 | 10.3466 | 12.1109 | 33.9891 | 13.931 | 10.1625 | 10.276 | 35.0879 | 13.3957 | 9.772 | 6.7797 | 35.7426 | 12.6667 | 9.2402 | 4.277 | 36.1602 | 12.0124 | 8.7629 | 2.2389 | 36.3649 | 11.4963 | 8.3864 | 0.92144 | 36.3398 | 11.4298 | 8.3379 | 1.9538 | 29.6985 | 15.1501 | 11.0518 | 18.3993 | 29.7408 | 14.9288 | 10.8903 | 17.7172 | 29.7917 | 14.8624 | 10.8419 | 17.4391 | 29.8495 | 14.8158 | 10.8079 | 17.2691 | 29.9318 | 14.6906 | 10.7166 | 17.0751 | 30.0632 | 14.6516 | 10.6882 | 16.8519 | 30.242 | 14.8222 | 10.8126 | 16.5972 | 30.4477 | 14.8212 | 10.8119 | 16.3181 | 31.0596 | 14.6905 | 10.7165 | 15.4998 | 31.2353 | 14.5787 | 10.635 | 15.1211 | 33.6748 | 13.9291 | 10.1611 | 12.0157 | 34.252 | 13.8137 | 10.0769 | 11.1107 | 35.0714 | 13.7591 | 10.037 | 10.0504 | 35.3325 | 13.6831 | 9.9816 | 9.5106 | 35.4438 | 13.4654 | 9.8228 | 9.3408 | 29.6985 | 15.1501 | 11.0518 | 18.3993 | 29.7059 | 14.8602 | 10.8403 | 17.5974 | 29.7755 | 14.6931 | 10.7184 | 17.232 | 29.8708 | 14.7173 | 10.7361 | 16.9796 | 29.996 | 14.8265 | 10.8157 | 16.6575 | 30.1433 | 14.828 | 10.8168 | 16.3135 | 30.7717 | 14.6675 | 10.6998 | 15.3296 | 32.8985 | 14.2349 | 10.3842 | 12.3498 | 33.106 | 13.9787 | 10.1972 | 11.2444 | 34.1038 | 13.7217 | 10.0098 | 9.3503 | 35.194 | 13.1772 | 9.6126 | 5.7147 | 35.8292 | 12.3861 | 9.0355 | 3.0505 | 36.293 | 11.7034 | 8.5375 | 0.80501 | 36.5063 | 11.1334 | 8.1216 | -0.78634 | 36.4924 | 11.0112 | 8.0325 | -0.061186
INGLETON | KENDAL (PARKSIDE RD) | HARKER / HUTTON | 368913 | 472337 | 12.5694 | 12.5694 | 12.5694 | 9.7753 | 12.6214 | 12.6214 | 12.6214 | 9.6705 | 12.6744 | 12.6744 | 12.6744 | 9.6058 | 12.732 | 12.732 | 12.732 | 9.5503 | 12.7917 | 12.7917 | 12.7917 | 9.4734 | 12.8617 | 12.8617 | 12.8617 | 9.3949 | 12.9428 | 12.9428 | 12.9428 | 9.3281 | 13.0167 | 13.0167 | 13.0167 | 9.2638 | 13.0738 | 13.0738 | 13.0738 | 9.1958 | 13.1285 | 13.1285 | 13.1285 | 9.1196 | 13.3691 | 13.3691 | 13.3691 | 8.5796 | 13.5929 | 13.5929 | 13.5929 | 7.8494 | 13.6949 | 13.6949 | 13.6949 | 7.3197 | 13.7756 | 13.7756 | 13.7756 | 6.8832 | 13.8127 | 13.8127 | 13.8127 | 6.5875 | 12.5602 | 12.5602 | 12.5602 | 9.7753 | 12.603 | 12.603 | 12.603 | 9.6972 | 12.6418 | 12.6418 | 12.6418 | 9.6331 | 12.6882 | 12.6882 | 12.6882 | 9.5665 | 12.7296 | 12.7296 | 12.7296 | 9.488 | 12.7803 | 12.7803 | 12.7803 | 9.4038 | 12.8336 | 12.8336 | 12.8336 | 9.3003 | 12.8894 | 12.8894 | 12.8894 | 9.1674 | 12.9326 | 12.9326 | 12.9326 | 9.0883 | 12.9784 | 12.9784 | 12.9784 | 9.0099 | 13.1187 | 13.1187 | 13.1187 | 8.7141 | 13.2556 | 13.2556 | 13.2556 | 8.4204 | 13.3771 | 13.3771 | 13.3771 | 8.1612 | 13.5067 | 13.5067 | 13.5067 | 7.8369 | 13.6015 | 13.6015 | 13.6015 | 7.6449 | 12.5723 | 12.5723 | 12.5723 | 9.7753 | 12.6196 | 12.6196 | 12.6196 | 9.6636 | 12.673 | 12.673 | 12.673 | 9.6016 | 12.7324 | 12.7324 | 12.7324 | 9.5525 | 12.7937 | 12.7937 | 12.7937 | 9.4844 | 12.8652 | 12.8652 | 12.8652 | 9.417 | 12.9481 | 12.9481 | 12.9481 | 9.3635 | 13.0188 | 13.0188 | 13.0188 | 9.3165 | 13.0742 | 13.0742 | 13.0742 | 9.268 | 13.1277 | 13.1277 | 13.1277 | 9.2266 | 13.3792 | 13.3792 | 13.3792 | 8.5119 | 13.591 | 13.591 | 13.591 | 7.7063 | 13.6887 | 13.6887 | 13.6887 | 7.1112 | 13.7645 | 13.7645 | 13.7645 | 6.6162 | 13.801 | 13.801 | 13.801 | 6.2881 | 12.5724 | 12.5724 | 12.5724 | 9.7753 | 12.6062 | 12.6062 | 12.6062 | 9.7274 | 12.6398 | 12.6398 | 12.6398 | 9.6867 | 12.6829 | 12.6829 | 12.6829 | 9.6432 | 12.7394 | 12.7394 | 12.7394 | 9.5837 | 12.8066 | 12.8066 | 12.8066 | 9.5214 | 12.8897 | 12.8897 | 12.8897 | 9.436 | 12.987 | 12.987 | 12.987 | 9.2484 | 13.0743 | 13.0743 | 13.0743 | 9.0491 | 13.1585 | 13.1585 | 13.1585 | 8.8556 | 13.342 | 13.342 | 13.342 | 8.2684 | 13.4903 | 13.4903 | 13.4903 | 7.608 | 13.5949 | 13.5949 | 13.5949 | 7.0783 | 13.6616 | 13.6616 | 13.6616 | 6.7091 | 13.6532 | 13.6532 | 13.6532 | 6.6972 | 12.5694 | 12.5694 | 12.5694 | 9.7753 | 12.6107 | 12.6107 | 12.6107 | 9.6877 | 12.6498 | 12.6498 | 12.6498 | 9.631 | 12.6962 | 12.6962 | 12.6962 | 9.586 | 12.7376 | 12.7376 | 12.7376 | 9.5376 | 12.7942 | 12.7942 | 12.7942 | 9.4883 | 12.8658 | 12.8658 | 12.8658 | 9.4383 | 12.9412 | 12.9412 | 12.9412 | 9.3821 | 12.9961 | 12.9961 | 12.9961 | 9.3134 | 13.0526 | 13.0526 | 13.0526 | 9.2461 | 13.2405 | 13.2405 | 13.2405 | 8.9674 | 13.4398 | 13.4398 | 13.4398 | 8.3702 | 13.5775 | 13.5775 | 13.5775 | 7.9472 | 13.6589 | 13.6589 | 13.6589 | 7.5958 | 13.6813 | 13.6813 | 13.6813 | 7.4214 | 12.5694 | 12.5694 | 12.5694 | 9.7753 | 12.6074 | 12.6074 | 12.6074 | 9.6833 | 12.6556 | 12.6556 | 12.6556 | 9.6168 | 12.7122 | 12.7122 | 12.7122 | 9.5495 | 12.7671 | 12.7671 | 12.7671 | 9.467 | 12.8303 | 12.8303 | 12.8303 | 9.3863 | 12.9043 | 12.9043 | 12.9043 | 9.2812 | 12.9992 | 12.9992 | 12.9992 | 9.0655 | 13.0823 | 13.0823 | 13.0823 | 8.8507 | 13.1672 | 13.1672 | 13.1672 | 8.6419 | 13.4134 | 13.4134 | 13.4134 | 7.9873 | 13.5725 | 13.5725 | 13.5725 | 7.3619 | 13.6797 | 13.6797 | 13.6797 | 6.8775 | 13.751 | 13.751 | 13.751 | 6.5565 | 13.7463 | 13.7463 | 13.7463 | 6.5794
IRLAM | CARRINGTON BSP | CARRINGTON | 371680 | 393360 | 29.8225 | 11.9663 | 8.7293 | 10.5774 | 29.8782 | 11.8148 | 8.6187 | 9.5622 | 29.9882 | 11.8292 | 8.6293 | 9.2697 | 30.1288 | 11.8143 | 8.6184 | 9.1618 | 30.3303 | 11.7397 | 8.5639 | 8.9199 | 30.6214 | 11.6534 | 8.501 | 8.6132 | 31.0333 | 11.5338 | 8.4137 | 8.2681 | 31.5331 | 11.4249 | 8.3343 | 7.8863 | 32.0686 | 11.2803 | 8.2288 | 7.374 | 32.6119 | 11.1514 | 8.1348 | 6.8367 | 34.2961 | 10.511 | 7.6677 | 3.9617 | 35.8019 | 9.8068 | 7.1539 | -0.29864 | 36.7022 | 9.4309 | 6.8797 | -3.5696 | 37.3479 | 9.2261 | 6.7303 | -6.7838 | 37.7363 | 8.7391 | 6.3751 | -9.5309 | 29.8118 | 11.9663 | 8.7293 | 10.5774 | 29.8724 | 11.9032 | 8.6832 | 10.2653 | 29.9702 | 11.8606 | 8.6521 | 10.0651 | 30.0769 | 11.8137 | 8.6179 | 9.9093 | 30.2121 | 11.7389 | 8.5634 | 9.7096 | 30.3916 | 11.6236 | 8.4793 | 9.4674 | 30.6231 | 11.5641 | 8.4359 | 9.1457 | 30.9098 | 11.4285 | 8.3369 | 8.7523 | 31.1677 | 11.3105 | 8.2508 | 8.391 | 31.4612 | 11.1766 | 8.1532 | 7.9988 | 32.5409 | 10.7372 | 7.8326 | 6.6251 | 33.7569 | 10.4648 | 7.6339 | 5.0277 | 34.8824 | 10.2531 | 7.4795 | 3.1453 | 36.0826 | 10.1513 | 7.4052 | 0.88794 | 36.8234 | 9.8373 | 7.1762 | -0.57542 | 29.8271 | 11.9663 | 8.7293 | 10.5774 | 29.8857 | 11.8012 | 8.6088 | 9.438 | 29.998 | 11.8032 | 8.6102 | 9.1439 | 30.1366 | 11.7669 | 8.5838 | 9.09 | 30.3264 | 11.6728 | 8.5151 | 8.9079 | 30.5909 | 11.5738 | 8.443 | 8.6783 | 30.9555 | 11.464 | 8.3629 | 8.4504 | 31.3862 | 11.3565 | 8.2844 | 8.2061 | 31.8259 | 11.219 | 8.1841 | 7.8805 | 32.3298 | 11.0827 | 8.0846 | 7.5012 | 33.9608 | 10.4547 | 7.6266 | 4.9662 | 35.5651 | 9.5938 | 6.9985 | 0.63674 | 36.5776 | 9.2232 | 6.7282 | -2.679 | 37.2883 | 8.975 | 6.5471 | -5.5032 | 37.6459 | 8.4873 | 6.1913 | -7.9264 | 29.8271 | 11.9663 | 8.7293 | 10.5774 | 29.7898 | 11.9359 | 8.7071 | 10.0711 | 29.8532 | 12.0118 | 8.7625 | 9.9244 | 29.9487 | 11.9633 | 8.7271 | 9.8835 | 30.1134 | 11.8652 | 8.6555 | 9.6788 | 30.3921 | 11.7426 | 8.5661 | 9.394 | 30.807 | 11.5712 | 8.441 | 8.8923 | 31.375 | 11.296 | 8.2402 | 7.711 | 31.999 | 11.1088 | 8.1037 | 6.3973 | 32.4895 | 10.8535 | 7.9175 | 5.0238 | 33.9753 | 10.9451 | 7.9843 | 0.92803 | 35.2757 | 10.0882 | 7.3592 | -2.7833 | 36.085 | 9.3504 | 6.821 | -5.7059 | 36.5707 | 8.7773 | 6.4029 | -7.4168 | 36.6048 | 8.72 | 6.3611 | -6.5006 | 29.8225 | 11.9663 | 8.7293 | 10.5774 | 29.8685 | 11.9172 | 8.6934 | 10.1671 | 29.9509 | 11.9652 | 8.7284 | 10.0382 | 30.0424 | 11.9688 | 8.7311 | 10.0268 | 30.1797 | 11.9315 | 8.7038 | 9.9817 | 30.4102 | 11.8818 | 8.6676 | 9.8674 | 30.75 | 11.7959 | 8.605 | 9.6701 | 31.1886 | 11.703 | 8.5372 | 9.3982 | 31.6145 | 11.5802 | 8.4476 | 8.9725 | 32.1007 | 11.4553 | 8.3565 | 8.5019 | 33.5092 | 11.0209 | 8.0396 | 6.7337 | 34.8801 | 10.6271 | 7.7523 | 4.2372 | 35.7323 | 10.558 | 7.7019 | 2.5535 | 36.3129 | 10.7241 | 7.8231 | 1.3785 | 36.5128 | 10.6645 | 7.7796 | 0.99751 | 29.8225 | 11.9663 | 8.7293 | 10.5774 | 29.8088 | 11.8468 | 8.6421 | 9.5583 | 29.9047 | 11.887 | 8.6714 | 9.237 | 30.0308 | 11.8205 | 8.6229 | 9.1081 | 30.2089 | 11.7116 | 8.5434 | 8.8302 | 30.4565 | 11.5755 | 8.4442 | 8.5092 | 30.8063 | 11.4003 | 8.3164 | 7.9719 | 31.3028 | 11.0918 | 8.0913 | 6.7492 | 31.8643 | 10.9246 | 7.9694 | 5.4418 | 32.4781 | 10.6695 | 7.7833 | 4.0698 | 34.3384 | 10.7241 | 7.8231 | -0.1917 | 35.7951 | 9.7993 | 7.1484 | -4.2541 | 36.7633 | 8.981 | 6.5515 | -7.5933 | 37.3357 | 8.3441 | 6.0869 | -9.6636 | 37.4089 | 8.2437 | 6.0136 | -9.0072
JAMES ST | CARLISLE | HARKER / HUTTON | 340034 | 555418 | 31.7945 | 9.6368 | 6.9262 | 9.4696 | 31.8518 | 9.3858 | 6.7457 | 8.9042 | 31.9548 | 9.0572 | 6.5096 | 8.538 | 32.0669 | 8.7331 | 6.2767 | 8.2261 | 32.2037 | 8.3683 | 6.0145 | 7.8697 | 32.3813 | 8.0233 | 5.7665 | 7.492 | 32.6105 | 7.7113 | 5.5422 | 7.1282 | 32.9071 | 7.4747 | 5.3722 | 6.7538 | 33.2015 | 7.325 | 5.2646 | 6.3388 | 33.5167 | 7.1499 | 5.1388 | 5.9352 | 34.5306 | 6.3901 | 4.5927 | 3.8261 | 34.0496 | 5.606 | 4.0291 | 0.80272 | 30.4418 | 5.012 | 3.6022 | -1.8792 | 27.1348 | 4.4675 | 3.2109 | -4.8041 | 22.1336 | 3.6441 | 2.6191 | -7.1093 | 31.7743 | 9.6368 | 6.9262 | 9.4696 | 31.8626 | 9.499 | 6.8271 | 9.1275 | 31.9841 | 9.2095 | 6.619 | 8.8015 | 32.1153 | 8.8988 | 6.3957 | 8.5244 | 32.2652 | 8.56 | 6.1523 | 8.233 | 32.4542 | 8.2167 | 5.9055 | 7.901 | 32.6869 | 7.8695 | 5.6559 | 7.489 | 32.9657 | 7.6435 | 5.4935 | 6.9866 | 33.1 | 7.4607 | 5.3622 | 6.7102 | 33.2513 | 7.2738 | 5.2278 | 6.4302 | 33.8036 | 6.7321 | 4.8385 | 5.5941 | 34.4626 | 6.2023 | 4.4577 | 4.7493 | 35.123 | 5.8625 | 4.2135 | 4.0332 | 34.7274 | 5.7176 | 4.1094 | 3.352 | 32.9692 | 5.4281 | 3.9013 | 2.9716 | 31.8005 | 9.6368 | 6.9262 | 9.4696 | 31.8621 | 9.3183 | 6.6973 | 8.8356 | 31.9718 | 8.8809 | 6.3829 | 8.4589 | 32.093 | 8.4352 | 6.0626 | 8.1462 | 32.2376 | 8.021 | 5.7648 | 7.7924 | 32.4204 | 7.5784 | 5.4468 | 7.4201 | 32.6519 | 7.2666 | 5.2227 | 7.0639 | 32.9462 | 7.0326 | 5.0545 | 6.7024 | 33.212 | 6.7741 | 4.8687 | 6.3512 | 33.497 | 6.5192 | 4.6855 | 6.0165 | 33.4668 | 5.5101 | 3.9602 | 4.0926 | 27.6444 | 4.5514 | 3.2712 | 1.242 | 22.4884 | 3.7025 | 2.6611 | -1.1242 | 17.0943 | 2.8144 | 2.0228 | -3.7783 | 11.4269 | 1.8814 | 1.3522 | -5.695 | 31.8005 | 9.6368 | 6.9262 | 9.4696 | 31.7755 | 9.4132 | 6.7654 | 9.2115 | 31.8271 | 9.1655 | 6.5874 | 8.9589 | 31.8857 | 8.7935 | 6.3201 | 8.7217 | 31.9741 | 8.5962 | 6.1783 | 8.4329 | 32.1263 | 8.2487 | 5.9285 | 8.1015 | 32.3463 | 7.9318 | 5.7007 | 7.5868 | 32.642 | 7.5267 | 5.4096 | 6.4843 | 32.951 | 7.0785 | 5.0875 | 5.3233 | 33.2818 | 6.5914 | 4.7373 | 4.1799 | 34.3115 | 5.6925 | 4.0913 | 0.81476 | 27.7416 | 4.5674 | 3.2827 | -2.2987 | 21.2458 | 3.498 | 2.5141 | -4.7147 | 15.5351 | 2.5577 | 1.8383 | -6.0642 | 12.4719 | 2.0534 | 1.4758 | -4.5061 | 31.7945 | 9.6368 | 6.9262 | 9.4696 | 31.8445 | 9.4584 | 6.7979 | 9.0979 | 31.9257 | 9.1453 | 6.5729 | 8.7964 | 32.0014 | 8.8318 | 6.3476 | 8.5495 | 32.0943 | 8.4904 | 6.1022 | 8.3204 | 32.2419 | 8.1658 | 5.8689 | 8.0603 | 32.4473 | 7.861 | 5.6499 | 7.7579 | 32.6948 | 7.6376 | 5.4893 | 7.4144 | 32.9334 | 7.4867 | 5.3808 | 7.0048 | 33.1956 | 7.3087 | 5.2529 | 6.5864 | 34.0979 | 6.6958 | 4.8124 | 5.3024 | 34.9422 | 6.2612 | 4.5001 | 4.2904 | 35.4711 | 6.0347 | 4.3372 | 3.664 | 35.7952 | 5.9534 | 4.2788 | 3.2076 | 33.8142 | 5.5673 | 4.0013 | 3.3372 | 31.7945 | 9.6368 | 6.9262 | 9.4696 | 31.8028 | 9.3319 | 6.707 | 8.9528 | 31.8972 | 9.0588 | 6.5107 | 8.5822 | 32.0039 | 8.6911 | 6.2464 | 8.2458 | 32.1332 | 8.4498 | 6.0731 | 7.8658 | 32.2954 | 8.0959 | 5.8187 | 7.4778 | 32.5092 | 7.7634 | 5.5797 | 6.9135 | 32.8113 | 7.3454 | 5.2793 | 5.7289 | 33.094 | 6.9004 | 4.9594 | 4.5436 | 33.3981 | 6.3805 | 4.5858 | 3.3778 | 33.0414 | 5.44 | 3.9098 | -0.23924 | 25.9657 | 4.2751 | 3.0726 | -3.4959 | 19.2338 | 3.1667 | 2.276 | -6.0888 | 13.2574 | 2.1827 | 1.5688 | -7.6792 | 9.8925 | 1.6287 | 1.1706 | -6.414
KAY ST | HUNCOAT | PADIHAM | 373863 | 427594 | 28.6973 | 14.6998 | 10.7233 | 18.0374 | 28.7955 | 14.5681 | 10.6272 | 17.8481 | 28.9079 | 14.3216 | 10.4474 | 17.7353 | 29.0431 | 14.099 | 10.285 | 17.6417 | 29.2111 | 13.6884 | 9.9855 | 17.4488 | 29.4074 | 13.2558 | 9.6699 | 17.2522 | 29.6306 | 12.9211 | 9.4258 | 17.0888 | 29.8757 | 12.7711 | 9.3163 | 16.9356 | 30.0784 | 12.6595 | 9.235 | 16.7245 | 30.2779 | 12.5633 | 9.1648 | 16.5301 | 30.9158 | 12.0614 | 8.7986 | 14.7237 | 31.6302 | 11.4692 | 8.3666 | 11.7044 | 32.1953 | 11.1242 | 8.1149 | 9.1848 | 32.6673 | 10.8645 | 7.9255 | 6.4649 | 32.9587 | 10.3744 | 7.568 | 4.2865 | 28.6642 | 14.6998 | 10.7233 | 18.0374 | 28.7594 | 14.5988 | 10.6496 | 17.8893 | 28.8125 | 14.4174 | 10.5173 | 17.7695 | 28.8794 | 14.2633 | 10.4049 | 17.6471 | 28.9731 | 14.1015 | 10.2868 | 17.4804 | 29.0934 | 13.9045 | 10.1431 | 17.2821 | 29.238 | 13.5696 | 9.8989 | 17.0298 | 29.4022 | 13.4185 | 9.7886 | 16.7281 | 29.5161 | 13.3525 | 9.7405 | 16.4766 | 29.6385 | 13.2698 | 9.6801 | 16.2106 | 30.0444 | 12.8715 | 9.3896 | 15.4052 | 30.4257 | 12.6523 | 9.2297 | 14.6273 | 30.8097 | 12.6075 | 9.197 | 13.8519 | 31.2115 | 12.6028 | 9.1936 | 13.0701 | 31.4623 | 12.2324 | 8.9234 | 12.5997 | 28.7074 | 14.6998 | 10.7233 | 18.0374 | 28.8113 | 14.5283 | 10.5982 | 17.8486 | 28.9333 | 14.1472 | 10.3202 | 17.7564 | 29.0862 | 13.967 | 10.1888 | 17.7013 | 29.2761 | 13.4965 | 9.8455 | 17.5695 | 29.4959 | 13.0377 | 9.5108 | 17.4304 | 29.721 | 12.749 | 9.3002 | 17.3437 | 29.9933 | 12.5801 | 9.177 | 17.2792 | 30.2084 | 12.4595 | 9.0891 | 17.1482 | 30.3876 | 12.3346 | 8.9979 | 16.9203 | 30.9452 | 11.7628 | 8.5808 | 15.2743 | 31.6741 | 11.0996 | 8.097 | 12.3764 | 32.2489 | 10.6888 | 7.7973 | 9.9559 | 32.6523 | 10.3502 | 7.5503 | 7.4845 | 32.909 | 9.8125 | 7.1581 | 5.633 | 28.7074 | 14.6998 | 10.7233 | 18.0374 | 28.7365 | 14.5833 | 10.6383 | 18.086 | 28.8085 | 14.4045 | 10.5079 | 18.0726 | 28.896 | 14.3053 | 10.4355 | 18.0486 | 29.0229 | 14.0102 | 10.2203 | 17.9222 | 29.2195 | 13.7263 | 10.0132 | 17.7568 | 29.4739 | 13.4266 | 9.7945 | 17.4271 | 29.7867 | 13.0839 | 9.5445 | 16.4825 | 30.0515 | 12.755 | 9.3046 | 15.4886 | 30.3165 | 12.4527 | 9.0841 | 14.5014 | 31.1258 | 12.4033 | 9.048 | 11.6571 | 31.8447 | 11.6245 | 8.4799 | 8.9622 | 32.2368 | 10.8871 | 7.942 | 6.7392 | 32.5103 | 10.2384 | 7.4688 | 5.3256 | 32.4654 | 10.1284 | 7.3885 | 6.4953 | 28.6972 | 14.6998 | 10.7233 | 18.0374 | 28.7805 | 14.6005 | 10.6508 | 17.8875 | 28.8607 | 14.3851 | 10.4938 | 17.8195 | 28.9421 | 14.1685 | 10.3357 | 17.7951 | 29.0504 | 13.8166 | 10.0791 | 17.7562 | 29.2182 | 13.4011 | 9.7759 | 17.6674 | 29.4365 | 13.0493 | 9.5192 | 17.5455 | 29.6406 | 12.9117 | 9.4189 | 17.4154 | 29.7998 | 12.7994 | 9.337 | 17.2121 | 29.9669 | 12.699 | 9.2637 | 17.0057 | 30.5516 | 12.3769 | 9.0288 | 16.1302 | 31.0582 | 12.1537 | 8.866 | 15.069 | 31.3678 | 12.1479 | 8.8618 | 14.3183 | 31.6377 | 12.3876 | 9.0366 | 13.6837 | 31.7466 | 12.2617 | 8.9447 | 13.4763 | 28.6972 | 14.6998 | 10.7233 | 18.0374 | 28.7582 | 14.5342 | 10.6025 | 17.977 | 28.8644 | 14.3324 | 10.4553 | 17.8739 | 28.9965 | 14.2 | 10.3587 | 17.7422 | 29.1616 | 13.8786 | 10.1242 | 17.5151 | 29.3515 | 13.5847 | 9.9098 | 17.2921 | 29.5823 | 13.2809 | 9.6882 | 16.897 | 29.9 | 12.9202 | 9.4251 | 15.8515 | 30.1692 | 12.5809 | 9.1776 | 14.7808 | 30.4366 | 12.2652 | 8.9473 | 13.7176 | 31.2436 | 12.152 | 8.8647 | 10.6353 | 32.0028 | 11.3239 | 8.2606 | 7.7116 | 32.4884 | 10.5387 | 7.6879 | 5.2537 | 32.7656 | 9.8085 | 7.1552 | 3.5403 | 32.7426 | 9.6545 | 7.0429 | 4.3742
KENDAL | KENDAL (PARKSIDE RD) | HARKER / HUTTON | 351915 | 491858 | 27.6386 | 9.6051 | 6.9034 | 8.1496 | 27.7913 | 9.3446 | 6.7161 | 7.2125 | 27.9622 | 8.9417 | 6.4266 | 6.7857 | 28.1754 | 8.5314 | 6.1317 | 6.473 | 28.444 | 7.9992 | 5.7491 | 6.0046 | 28.7624 | 7.5455 | 5.4231 | 5.4722 | 29.1052 | 7.1229 | 5.1194 | 4.9652 | 29.5168 | 6.9734 | 5.0119 | 4.4836 | 29.8605 | 6.8008 | 4.8879 | 3.9862 | 30.1992 | 6.627 | 4.763 | 3.542 | 31.2584 | 5.8391 | 4.1967 | 0.95036 | 29.4722 | 4.8524 | 3.4875 | -3.3188 | 24.0925 | 3.9666 | 2.8509 | -6.8806 | 18.7428 | 3.0859 | 2.2179 | -10.6546 | 13.9419 | 2.2954 | 1.6498 | -14.0767 | 27.6088 | 9.6051 | 6.9034 | 8.1496 | 27.7417 | 9.4408 | 6.7853 | 7.5905 | 27.8726 | 9.3287 | 6.7047 | 7.2548 | 28.0328 | 9.1753 | 6.5944 | 6.9274 | 28.2439 | 8.9748 | 6.4503 | 6.5129 | 28.5044 | 8.7559 | 6.293 | 6.0906 | 28.8183 | 8.4098 | 6.0443 | 5.5543 | 29.182 | 8.1266 | 5.8407 | 4.8773 | 29.379 | 7.9246 | 5.6955 | 4.4534 | 29.5908 | 7.7769 | 5.5894 | 4.0333 | 30.2539 | 7.3166 | 5.2586 | 2.7664 | 30.9596 | 6.9015 | 4.9602 | 1.5071 | 31.5861 | 6.4825 | 4.6591 | 0.2951 | 32.1895 | 6.1075 | 4.3895 | -1.0771 | 32.5893 | 5.743 | 4.1276 | -2.1194 | 27.6509 | 9.6051 | 6.9034 | 8.1496 | 27.8013 | 9.3028 | 6.6861 | 7.1331 | 27.9813 | 8.8386 | 6.3525 | 6.7174 | 28.2106 | 8.3664 | 6.0131 | 6.4549 | 28.4993 | 7.8324 | 5.6293 | 6.0389 | 28.8405 | 7.3941 | 5.3143 | 5.5683 | 29.2035 | 6.9801 | 5.0168 | 5.1557 | 29.6473 | 6.7878 | 4.8785 | 4.7694 | 29.9986 | 6.5837 | 4.7319 | 4.3925 | 30.349 | 6.3837 | 4.5881 | 4.0477 | 31.5028 | 5.4745 | 3.9346 | 1.7534 | 26.7037 | 4.3966 | 3.1599 | -2.2808 | 20.784 | 3.4219 | 2.4594 | -5.6315 | 14.9613 | 2.4633 | 1.7704 | -9.1403 | 9.9168 | 1.6327 | 1.1735 | -12.2407 | 27.6511 | 9.6051 | 6.9034 | 8.1496 | 27.6744 | 9.4351 | 6.7812 | 7.7959 | 27.7661 | 9.0516 | 6.5056 | 7.5382 | 27.8968 | 8.5209 | 6.1241 | 7.2916 | 28.0959 | 8.0586 | 5.7918 | 6.8797 | 28.397 | 7.6356 | 5.4879 | 6.3906 | 28.7598 | 7.0381 | 5.0584 | 5.6984 | 29.177 | 6.5129 | 4.681 | 4.2318 | 29.5401 | 6.0005 | 4.3126 | 2.7185 | 29.9054 | 5.5261 | 3.9717 | 1.2222 | 26.4736 | 4.3587 | 3.1327 | -2.9429 | 20.2925 | 3.341 | 2.4012 | -6.7595 | 14.8752 | 2.4491 | 1.7602 | -9.7784 | 11.0921 | 1.8262 | 1.3125 | -11.6823 | 9.6474 | 1.5884 | 1.1416 | -10.5471 | 27.6385 | 9.6051 | 6.9034 | 8.1496 | 27.7636 | 9.4019 | 6.7573 | 7.4417 | 27.8821 | 9.0213 | 6.4838 | 7.0936 | 28.016 | 8.6324 | 6.2043 | 6.8611 | 28.1951 | 8.1462 | 5.8548 | 6.5719 | 28.4597 | 7.7055 | 5.5381 | 6.2278 | 28.8063 | 7.3027 | 5.2486 | 5.8523 | 29.1593 | 7.1781 | 5.1591 | 5.4431 | 29.4439 | 7.0131 | 5.0404 | 4.9524 | 29.7381 | 6.8376 | 4.9143 | 4.4771 | 30.7139 | 6.2588 | 4.4983 | 2.9958 | 31.7084 | 5.7741 | 4.15 | 1.5041 | 32.4109 | 5.3458 | 3.8421 | 0.47158 | 30.1304 | 4.9607 | 3.5654 | -0.56762 | 28.6126 | 4.7108 | 3.3858 | -1.1242 | 27.6385 | 9.6051 | 6.9034 | 8.1496 | 27.6956 | 9.3413 | 6.7138 | 7.3808 | 27.8461 | 8.9177 | 6.4093 | 6.9512 | 28.0471 | 8.3515 | 6.0024 | 6.5751 | 28.3025 | 7.878 | 5.6621 | 6.0424 | 28.5992 | 7.4395 | 5.3469 | 5.4675 | 28.9338 | 6.8174 | 4.8998 | 4.669 | 29.3637 | 6.2655 | 4.5032 | 3.0656 | 29.7205 | 5.7405 | 4.1258 | 1.4716 | 30.0811 | 5.2516 | 3.7744 | -0.10881 | 24.4989 | 4.0336 | 2.899 | -4.5499 | 17.9672 | 2.9582 | 2.1261 | -8.5964 | 12.231 | 2.0137 | 1.4473 | -11.8466 | 8.1082 | 1.335 | 0.95946 | -14.0391 | 6.3389 | 1.0437 | 0.7501 | -13.2368
KESWICK | STAINBURN & SIDDICK | HARKER / HUTTON | 327022 | 523784 | 18.0412 | 18.0412 | 18.0412 | 8.1079 | 18.1223 | 18.1223 | 18.1223 | 7.9147 | 18.235 | 18.235 | 18.235 | 7.7555 | 18.3732 | 18.3732 | 18.3732 | 7.6351 | 18.5284 | 18.5284 | 18.5284 | 7.4795 | 18.6653 | 18.6653 | 18.6653 | 7.3226 | 18.7569 | 18.7569 | 18.7569 | 7.2001 | 18.8641 | 18.8641 | 18.8641 | 7.0899 | 18.9401 | 18.9401 | 18.9401 | 6.9631 | 19.0109 | 19.0109 | 19.0109 | 6.8558 | 19.2513 | 19.2513 | 19.2513 | 6.0488 | 19.5259 | 19.5259 | 18.9086 | 4.6261 | 19.7237 | 19.7237 | 18.5698 | 3.4745 | 19.857 | 19.857 | 18.2107 | 2.3573 | 19.9074 | 19.9074 | 17.7977 | 1.4071 | 18.0439 | 18.0439 | 18.0439 | 8.1079 | 18.1411 | 18.1411 | 18.1411 | 7.9529 | 18.2467 | 18.2467 | 18.2467 | 7.763 | 18.3718 | 18.3718 | 18.3718 | 7.5792 | 18.5376 | 18.5376 | 18.5376 | 7.3794 | 18.7264 | 18.7264 | 18.7264 | 7.1701 | 18.8452 | 18.8452 | 18.8452 | 6.9152 | 18.9871 | 18.9871 | 18.9871 | 6.6001 | 19.0386 | 19.0386 | 19.0386 | 6.437 | 19.09 | 19.09 | 19.09 | 6.2763 | 19.2288 | 19.2288 | 19.2288 | 5.8157 | 19.3546 | 19.3546 | 19.0617 | 5.3926 | 19.4616 | 19.4616 | 18.8784 | 5.022 | 19.5677 | 19.5677 | 18.7157 | 4.602 | 19.6409 | 19.6409 | 18.5111 | 4.2855 | 18.0403 | 18.0403 | 18.0403 | 8.1079 | 18.1213 | 18.1213 | 18.1213 | 7.9101 | 18.2325 | 18.2325 | 18.2325 | 7.7589 | 18.3687 | 18.3687 | 18.3687 | 7.6608 | 18.5209 | 18.5209 | 18.5209 | 7.5242 | 18.6818 | 18.6818 | 18.6818 | 7.3886 | 18.8039 | 18.8039 | 18.8039 | 7.296 | 18.9272 | 18.9272 | 18.9272 | 7.219 | 19.0112 | 19.0112 | 19.0112 | 7.1563 | 19.0892 | 19.0892 | 19.0892 | 7.0952 | 19.3502 | 19.3502 | 18.8682 | 6.4545 | 19.6419 | 19.6419 | 18.4039 | 5.1903 | 19.8392 | 19.8392 | 17.9504 | 4.182 | 19.92 | 19.92 | 17.4551 | 3.2359 | 19.9395 | 19.9395 | 16.9551 | 2.4877 | 18.0403 | 18.0403 | 18.0403 | 8.1079 | 18.0609 | 18.0609 | 18.0609 | 8.0325 | 18.1085 | 18.1085 | 18.1085 | 7.9306 | 18.1731 | 18.1731 | 18.1731 | 7.8415 | 18.2602 | 18.2602 | 18.2602 | 7.7304 | 18.388 | 18.388 | 18.388 | 7.6141 | 18.5326 | 18.5326 | 18.5326 | 7.4441 | 18.6833 | 18.6833 | 18.6833 | 7.0145 | 18.8251 | 18.8251 | 18.8251 | 6.561 | 18.94 | 18.94 | 18.94 | 6.106 | 19.1877 | 19.1877 | 18.6866 | 4.819 | 19.4154 | 19.4154 | 18.22 | 3.6093 | 19.5679 | 19.5679 | 17.7751 | 2.7031 | 19.6406 | 19.6406 | 17.3327 | 2.2557 | 19.6068 | 19.6068 | 17.0566 | 2.8974 | 18.0412 | 18.0412 | 18.0412 | 8.1079 | 18.1113 | 18.1113 | 18.1113 | 7.9872 | 18.1913 | 18.1913 | 18.1913 | 7.8498 | 18.2819 | 18.2819 | 18.2819 | 7.7501 | 18.3903 | 18.3903 | 18.3903 | 7.6602 | 18.5427 | 18.5427 | 18.5427 | 7.5749 | 18.6875 | 18.6875 | 18.6875 | 7.4882 | 18.7851 | 18.7851 | 18.7851 | 7.3777 | 18.8551 | 18.8551 | 18.8551 | 7.226 | 18.9239 | 18.9239 | 18.9239 | 7.0771 | 19.1427 | 19.1427 | 19.1427 | 6.5528 | 19.3727 | 19.3727 | 19.1295 | 5.9361 | 19.5316 | 19.5316 | 18.9129 | 5.5411 | 19.6622 | 19.6622 | 18.6769 | 5.1938 | 19.7122 | 19.7122 | 18.4114 | 5.1657 | 18.0412 | 18.0412 | 18.0412 | 8.1079 | 18.1064 | 18.1064 | 18.1064 | 7.9432 | 18.2171 | 18.2171 | 18.2171 | 7.7773 | 18.3565 | 18.3565 | 18.3565 | 7.6243 | 18.5124 | 18.5124 | 18.5124 | 7.4503 | 18.6596 | 18.6596 | 18.6596 | 7.2825 | 18.7594 | 18.7594 | 18.7594 | 7.0553 | 18.8981 | 18.8981 | 18.8981 | 6.5509 | 19.0031 | 19.0031 | 19.0031 | 6.0621 | 19.1028 | 19.1028 | 19.0327 | 5.5729 | 19.3868 | 19.3868 | 18.5672 | 4.1887 | 19.6223 | 19.6223 | 18.0823 | 2.9017 | 19.7571 | 19.7571 | 17.6222 | 1.9228 | 19.8268 | 19.8268 | 17.1657 | 1.3867 | 19.7916 | 19.7916 | 16.8744 | 1.9261
KINGSWAY | BELFIELD | ROCHDALE | 391636 | 411724 | 46.7778 | 9.4132 | 6.7655 | 40.2531 | 46.8008 | 9.0908 | 6.5337 | 38.6702 | 46.8586 | 8.851 | 6.3614 | 37.9751 | 46.8989 | 8.5272 | 6.1286 | 37.6222 | 46.9375 | 8.2195 | 5.9075 | 37.2821 | 46.9857 | 8.1096 | 5.8286 | 36.934 | 47.047 | 8.0056 | 5.7538 | 36.8764 | 47.1282 | 7.8988 | 5.677 | 36.8002 | 47.2574 | 7.8618 | 5.6505 | 36.6579 | 47.4002 | 7.819 | 5.6197 | 36.5045 | 46.4332 | 7.6449 | 5.4945 | 35.975 | 45.1607 | 7.4354 | 5.3439 | 35.4527 | 44.1263 | 7.2651 | 5.2215 | 35.0956 | 43.8115 | 7.2132 | 5.1843 | 34.8135 | 43.679 | 7.1914 | 5.1686 | 34.6366 | 46.7784 | 9.4132 | 6.7655 | 40.2531 | 46.7934 | 9.3196 | 6.6982 | 39.8491 | 46.8413 | 9.2787 | 6.6688 | 39.7016 | 46.8763 | 9.2447 | 6.6444 | 39.6615 | 46.8952 | 9.1926 | 6.6069 | 39.6408 | 46.9211 | 9.1471 | 6.5742 | 39.6173 | 46.9517 | 8.9539 | 6.4353 | 39.5907 | 46.9829 | 8.9159 | 6.4081 | 39.5606 | 47.0562 | 8.8661 | 6.3722 | 39.4627 | 47.136 | 8.8159 | 6.3362 | 39.358 | 47.4173 | 8.711 | 6.2608 | 39.0034 | 47.7567 | 8.6326 | 6.2044 | 38.5131 | 48.0999 | 8.4721 | 6.0891 | 37.7723 | 48.4574 | 8.2854 | 5.9549 | 36.9867 | 48.7004 | 8.144 | 5.8533 | 36.4831 | 46.7762 | 9.4132 | 6.7655 | 40.2531 | 46.7946 | 9.0391 | 6.4966 | 38.4099 | 46.8496 | 8.762 | 6.2974 | 37.6627 | 46.8883 | 8.3909 | 6.0307 | 37.3109 | 46.9179 | 8.1735 | 5.8744 | 36.9749 | 46.9527 | 7.9728 | 5.7302 | 36.6342 | 46.9952 | 7.9249 | 5.6958 | 36.588 | 47.0503 | 7.8319 | 5.629 | 36.5284 | 47.1432 | 7.7807 | 5.5921 | 36.4256 | 47.1068 | 7.7558 | 5.5742 | 36.3136 | 45.986 | 7.5712 | 5.4416 | 35.8681 | 44.6112 | 7.3449 | 5.2789 | 35.3771 | 43.5701 | 7.1735 | 5.1557 | 35.0519 | 43.415 | 7.148 | 5.1374 | 34.8583 | 43.3948 | 7.1446 | 5.135 | 34.8349 | 46.7762 | 9.4132 | 6.7655 | 40.2531 | 46.7871 | 9.1373 | 6.5671 | 38.9342 | 46.8345 | 8.8826 | 6.3841 | 38.2988 | 46.8728 | 8.5138 | 6.1191 | 37.9507 | 46.9084 | 8.2999 | 5.9653 | 37.6156 | 46.9518 | 8.1269 | 5.8409 | 37.2682 | 47.0176 | 7.954 | 5.7167 | 37.1967 | 47.1262 | 7.7793 | 5.5911 | 37.0723 | 46.3603 | 7.6329 | 5.4859 | 36.8993 | 45.8257 | 7.5449 | 5.4226 | 36.7179 | 44.65 | 7.3513 | 5.2835 | 36.1767 | 43.5286 | 7.1666 | 5.1508 | 35.7357 | 42.8242 | 7.0507 | 5.0675 | 35.4671 | 43.4877 | 7.1599 | 5.146 | 35.3687 | 43.4692 | 7.1569 | 5.1438 | 35.5339 | 46.7778 | 9.4132 | 6.7655 | 40.2531 | 46.7958 | 9.2317 | 6.635 | 39.4658 | 46.8479 | 9.0299 | 6.49 | 38.938 | 46.8803 | 8.7093 | 6.2596 | 38.5958 | 46.9053 | 8.3956 | 6.0341 | 38.2722 | 46.9412 | 8.3017 | 5.9666 | 37.9389 | 46.9904 | 8.2014 | 5.8945 | 37.8936 | 47.0539 | 8.0983 | 5.8204 | 37.8345 | 47.1599 | 8.0666 | 5.7977 | 37.7136 | 47.2797 | 8.0277 | 5.7697 | 37.5808 | 47.6959 | 7.8944 | 5.6738 | 37.1335 | 47.1482 | 7.7626 | 5.5791 | 36.7151 | 46.4258 | 7.6437 | 5.4936 | 36.3606 | 46.4261 | 7.6437 | 5.4937 | 36.0727 | 46.7517 | 7.6973 | 5.5322 | 36.0309 | 46.7778 | 9.4132 | 6.7655 | 40.2531 | 46.797 | 8.995 | 6.4649 | 38.1501 | 46.856 | 8.7038 | 6.2556 | 37.3492 | 46.9003 | 8.3389 | 5.9933 | 36.994 | 46.9363 | 8.1181 | 5.8346 | 36.6553 | 46.9782 | 7.9424 | 5.7084 | 36.3122 | 47.0383 | 7.7663 | 5.5818 | 36.2502 | 46.1123 | 7.592 | 5.4566 | 36.136 | 45.2303 | 7.4468 | 5.3522 | 35.9779 | 44.7142 | 7.3619 | 5.2911 | 35.8106 | 43.5152 | 7.1644 | 5.1492 | 35.2717 | 42.3245 | 6.9684 | 5.0083 | 34.7802 | 41.5487 | 6.8407 | 4.9165 | 34.4571 | 42.1547 | 6.9405 | 4.9882 | 34.3277 | 42.083 | 6.9287 | 4.9798 | 34.4854
KINKRY HILL | - | HARKER / HUTTON | 350800 | 575111 | 3.13 | 3.13 | 3.13 | 2.286 | 3.1488 | 3.1488 | 3.1488 | 1.8909 | 3.1773 | 3.1773 | 3.1773 | 1.7982 | 3.2137 | 3.2137 | 3.2137 | 1.7724 | 3.2362 | 3.2362 | 3.2362 | 1.7413 | 3.2515 | 3.2515 | 3.2515 | 1.7097 | 3.2662 | 3.2662 | 3.2662 | 1.6822 | 3.2837 | 3.2837 | 3.2837 | 1.6573 | 3.2981 | 3.2981 | 3.2981 | 1.627 | 3.3117 | 3.3117 | 3.3117 | 1.6012 | 3.3538 | 3.3538 | 3.3538 | 1.4611 | 3.3971 | 3.3971 | 3.3971 | 1.2492 | 3.427 | 3.427 | 3.427 | 1.0999 | 3.4489 | 3.4489 | 3.4489 | 1.0017 | 3.4613 | 3.4613 | 3.4613 | 0.94898 | 3.1301 | 3.1301 | 3.1301 | 2.286 | 3.145 | 3.145 | 3.145 | 2.2371 | 3.1615 | 3.1615 | 3.1615 | 2.2019 | 3.1863 | 3.1863 | 3.1863 | 2.1685 | 3.2213 | 3.2213 | 3.2213 | 2.1296 | 3.245 | 3.245 | 3.245 | 2.0895 | 3.2593 | 3.2593 | 3.2593 | 2.0428 | 3.2733 | 3.2733 | 3.2733 | 1.9905 | 3.2841 | 3.2841 | 3.2841 | 1.9519 | 3.2951 | 3.2951 | 3.2951 | 1.9128 | 3.3271 | 3.3271 | 3.3271 | 1.7739 | 3.3553 | 3.3553 | 3.3553 | 1.6485 | 3.3784 | 3.3784 | 3.3784 | 1.544 | 3.3964 | 3.3964 | 3.3964 | 1.4391 | 3.4074 | 3.4074 | 3.4074 | 1.3674 | 3.129 | 3.129 | 3.129 | 2.286 | 3.147 | 3.147 | 3.147 | 1.8304 | 3.174 | 3.174 | 3.174 | 1.7301 | 3.2079 | 3.2079 | 3.2079 | 1.7107 | 3.2405 | 3.2405 | 3.2405 | 1.6865 | 3.2502 | 3.2502 | 3.2502 | 1.6635 | 3.2574 | 3.2574 | 3.2574 | 1.6469 | 3.2628 | 3.2628 | 3.2628 | 1.6354 | 3.2707 | 3.2707 | 3.2707 | 1.6203 | 3.2774 | 3.2774 | 3.2774 | 1.5643 | 3.3018 | 3.3018 | 3.3018 | 1.3154 | 3.332 | 3.332 | 3.332 | 1.0711 | 3.3511 | 3.3511 | 3.3511 | 0.90763 | 3.3611 | 3.3611 | 3.3611 | 0.8021 | 3.364 | 3.364 | 3.364 | 0.75011 | 3.129 | 3.129 | 3.129 | 2.286 | 3.1356 | 3.1356 | 3.1356 | 1.9693 | 3.1485 | 3.1485 | 3.1485 | 1.8985 | 3.1668 | 3.1668 | 3.1668 | 1.8771 | 3.1903 | 3.1903 | 3.1903 | 1.8559 | 3.2239 | 3.2239 | 3.2239 | 1.832 | 3.2327 | 3.2327 | 3.2327 | 1.8073 | 3.2408 | 3.2408 | 3.2408 | 1.7716 | 3.2536 | 3.2536 | 3.2536 | 1.7272 | 3.2658 | 3.2658 | 3.2658 | 1.682 | 3.2993 | 3.2993 | 3.2993 | 1.55 | 3.3296 | 3.3296 | 3.3296 | 1.3122 | 3.3472 | 3.3472 | 3.3472 | 1.156 | 3.3501 | 3.3501 | 3.3501 | 1.0573 | 3.331 | 3.331 | 3.331 | 1.0522 | 3.13 | 3.13 | 3.13 | 2.286 | 3.1456 | 3.1456 | 3.1456 | 2.2134 | 3.1646 | 3.1646 | 3.1646 | 2.1803 | 3.1873 | 3.1873 | 3.1873 | 2.1598 | 3.2144 | 3.2144 | 3.2144 | 2.1395 | 3.2394 | 3.2394 | 3.2394 | 2.1193 | 3.2541 | 3.2541 | 3.2541 | 2.0999 | 3.2699 | 3.2699 | 3.2699 | 2.0828 | 3.2828 | 3.2828 | 3.2828 | 2.0573 | 3.2954 | 3.2954 | 3.2954 | 2.0233 | 3.3351 | 3.3351 | 3.3351 | 1.8172 | 3.3759 | 3.3759 | 3.3759 | 1.5913 | 3.4038 | 3.4038 | 3.4038 | 1.4365 | 3.4257 | 3.4257 | 3.4257 | 1.313 | 3.4328 | 3.4328 | 3.4328 | 1.2611 | 3.13 | 3.13 | 3.13 | 2.286 | 3.1471 | 3.1471 | 3.1471 | 1.7695 | 3.1756 | 3.1756 | 3.1756 | 1.6525 | 3.213 | 3.213 | 3.213 | 1.6155 | 3.2362 | 3.2362 | 3.2362 | 1.5793 | 3.2517 | 3.2517 | 3.2517 | 1.5446 | 3.2673 | 3.2673 | 3.2673 | 1.508 | 3.2878 | 3.2878 | 3.2878 | 1.4545 | 3.3049 | 3.3049 | 3.3049 | 1.397 | 3.3212 | 3.3212 | 3.3212 | 1.3394 | 3.3668 | 3.3668 | 3.3668 | 1.1793 | 3.4076 | 3.4076 | 3.4076 | 1.0206 | 3.434 | 3.434 | 3.434 | 0.912 | 3.4484 | 3.4484 | 3.4484 | 0.87606 | 3.4456 | 3.4456 | 3.4456 | 0.9037
KIRKBY LONSDALE | KENDAL (PARKSIDE RD) | HARKER / HUTTON | 359833 | 478813 | 13.0953 | 13.0953 | 13.0953 | 6.8412 | 13.1656 | 13.1656 | 13.1656 | 6.7037 | 13.2532 | 13.2532 | 13.2532 | 6.5959 | 13.3426 | 13.3426 | 13.3426 | 6.5132 | 13.4495 | 13.4495 | 13.4495 | 6.4115 | 13.572 | 13.572 | 13.572 | 6.3092 | 13.7117 | 13.7117 | 13.7117 | 6.2208 | 13.8815 | 13.8815 | 13.8815 | 6.1365 | 14.0008 | 14.0008 | 14.0008 | 6.0317 | 14.1098 | 14.1098 | 14.1098 | 5.939 | 14.4129 | 14.4129 | 14.4129 | 5.4429 | 14.6923 | 14.6923 | 14.6923 | 4.6497 | 14.8783 | 14.8783 | 14.8783 | 3.9434 | 15.0255 | 15.0255 | 15.0255 | 3.2091 | 15.0928 | 15.0928 | 14.3968 | 2.5635 | 13.0816 | 13.0816 | 13.0816 | 6.8412 | 13.1402 | 13.1402 | 13.1402 | 6.7218 | 13.2068 | 13.2068 | 13.2068 | 6.5991 | 13.2967 | 13.2967 | 13.2967 | 6.4808 | 13.3834 | 13.3834 | 13.3834 | 6.3471 | 13.4798 | 13.4798 | 13.4798 | 6.2023 | 13.5927 | 13.5927 | 13.5927 | 6.0265 | 13.719 | 13.719 | 13.719 | 5.8125 | 13.8061 | 13.8061 | 13.8061 | 5.6765 | 13.8965 | 13.8965 | 13.8965 | 5.5418 | 14.1218 | 14.1218 | 14.1218 | 5.1516 | 14.3217 | 14.3217 | 14.3217 | 4.7859 | 14.4963 | 14.4963 | 14.4963 | 4.4624 | 14.6679 | 14.6679 | 14.6679 | 4.1099 | 14.7794 | 14.7794 | 14.7794 | 3.8534 | 13.0989 | 13.0989 | 13.0989 | 6.8412 | 13.174 | 13.174 | 13.174 | 6.7022 | 13.2717 | 13.2717 | 13.2717 | 6.6022 | 13.3734 | 13.3734 | 13.3734 | 6.5381 | 13.4962 | 13.4962 | 13.4962 | 6.4541 | 13.6379 | 13.6379 | 13.6379 | 6.3724 | 13.8008 | 13.8008 | 13.8008 | 6.3126 | 13.9881 | 13.9881 | 13.9881 | 6.2604 | 14.1129 | 14.1129 | 14.1129 | 6.2048 | 14.2254 | 14.2254 | 14.2254 | 6.1386 | 14.5107 | 14.5107 | 14.5107 | 5.6242 | 14.791 | 14.791 | 14.791 | 4.8116 | 14.9855 | 14.9855 | 14.9855 | 4.1824 | 15.0836 | 15.0836 | 14.4376 | 3.5647 | 15.0983 | 15.0983 | 14.0607 | 3.0463 | 13.0989 | 13.0989 | 13.0989 | 6.8412 | 13.1186 | 13.1186 | 13.1186 | 6.8058 | 13.1729 | 13.1729 | 13.1729 | 6.7456 | 13.2473 | 13.2473 | 13.2473 | 6.6991 | 13.3225 | 13.3225 | 13.3225 | 6.6355 | 13.4368 | 13.4368 | 13.4368 | 6.5659 | 13.5721 | 13.5721 | 13.5721 | 6.4724 | 13.7169 | 13.7169 | 13.7169 | 6.2571 | 13.8308 | 13.8308 | 13.8308 | 5.9838 | 13.9425 | 13.9425 | 13.9425 | 5.677 | 14.2551 | 14.2551 | 14.2551 | 4.8036 | 14.5694 | 14.5694 | 14.5694 | 3.9742 | 14.7745 | 14.7745 | 14.2721 | 3.3608 | 14.8535 | 14.8535 | 13.9788 | 3.0218 | 14.8271 | 14.8271 | 13.7696 | 3.3361 | 13.0953 | 13.0953 | 13.0953 | 6.8412 | 13.1545 | 13.1545 | 13.1545 | 6.7254 | 13.229 | 13.229 | 13.229 | 6.6325 | 13.2897 | 13.2897 | 13.2897 | 6.5689 | 13.3652 | 13.3652 | 13.3652 | 6.5067 | 13.4748 | 13.4748 | 13.4748 | 6.44 | 13.6142 | 13.6142 | 13.6142 | 6.3682 | 13.7685 | 13.7685 | 13.7685 | 6.2866 | 13.8824 | 13.8824 | 13.8824 | 6.1719 | 13.9885 | 13.9885 | 13.9885 | 6.0603 | 14.2908 | 14.2908 | 14.2908 | 5.6932 | 14.5561 | 14.5561 | 14.5561 | 5.2881 | 14.7222 | 14.7222 | 14.7222 | 5.0172 | 14.8582 | 14.8582 | 14.8582 | 4.7738 | 14.919 | 14.919 | 14.919 | 4.6848 | 13.0953 | 13.0953 | 13.0953 | 6.8412 | 13.1508 | 13.1508 | 13.1508 | 6.7403 | 13.2388 | 13.2388 | 13.2388 | 6.6334 | 13.3287 | 13.3287 | 13.3287 | 6.5406 | 13.4356 | 13.4356 | 13.4356 | 6.4326 | 13.5571 | 13.5571 | 13.5571 | 6.3285 | 13.6975 | 13.6975 | 13.6975 | 6.1956 | 13.8757 | 13.8757 | 13.8757 | 5.9277 | 13.9985 | 13.9985 | 13.9985 | 5.661 | 14.1117 | 14.1117 | 14.1117 | 5.3915 | 14.4196 | 14.4196 | 14.4196 | 4.542 | 14.7029 | 14.7029 | 14.579 | 3.6882 | 14.8896 | 14.8896 | 14.1754 | 3.0387 | 14.9678 | 14.9678 | 13.8792 | 2.6449 | 14.9414 | 14.9414 | 13.7156 | 2.8806
KIRKBY MOOR | ULVERSTON | HARKER / HUTTON | 326099 | 483011 | 2.5909 | 2.5909 | 2.5909 | 2.5909 | 2.6131 | 2.6131 | 2.6131 | 2.6131 | 2.6486 | 2.6486 | 2.6486 | 2.6486 | 2.697 | 2.697 | 2.697 | 2.697 | 2.7562 | 2.7562 | 2.7562 | 2.7562 | 2.8244 | 2.8244 | 2.8244 | 2.8244 | 2.9022 | 2.9022 | 2.9022 | 2.9022 | 2.9851 | 2.9851 | 2.9851 | 2.9851 | 3.0404 | 3.0404 | 3.0404 | 3.0404 | 3.0914 | 3.0914 | 3.0914 | 3.0914 | 3.3154 | 3.3154 | 3.3154 | 3.3154 | 3.4816 | 3.4816 | 3.4816 | 3.4816 | 3.5978 | 3.5978 | 3.5978 | 3.2263 | 3.6854 | 3.6854 | 3.6854 | 2.8712 | 3.7392 | 3.7392 | 3.7392 | 2.6398 | 2.5779 | 2.5779 | 2.5779 | 2.5779 | 2.5995 | 2.5995 | 2.5995 | 2.5995 | 2.6185 | 2.6185 | 2.6185 | 2.6185 | 2.6436 | 2.6436 | 2.6436 | 2.6436 | 2.6779 | 2.6779 | 2.6779 | 2.6779 | 2.7208 | 2.7208 | 2.7208 | 2.7208 | 2.7707 | 2.7707 | 2.7707 | 2.7707 | 2.8265 | 2.8265 | 2.8265 | 2.8265 | 2.8621 | 2.8621 | 2.8621 | 2.8621 | 2.8998 | 2.8998 | 2.8998 | 2.8998 | 3.0188 | 3.0188 | 3.0188 | 3.0188 | 3.1184 | 3.1184 | 3.1184 | 3.1184 | 3.2219 | 3.2219 | 3.2219 | 3.2219 | 3.3357 | 3.3357 | 3.3357 | 3.3357 | 3.4051 | 3.4051 | 3.4051 | 3.4051 | 2.5937 | 2.5937 | 2.5937 | 2.5937 | 2.6183 | 2.6183 | 2.6183 | 2.6183 | 2.6581 | 2.6581 | 2.6581 | 2.6581 | 2.7131 | 2.7131 | 2.7131 | 2.7131 | 2.7808 | 2.7808 | 2.7808 | 2.7808 | 2.8594 | 2.8594 | 2.8594 | 2.8594 | 2.9328 | 2.9328 | 2.9328 | 2.9328 | 3.0014 | 3.0014 | 3.0014 | 3.0014 | 3.0587 | 3.0587 | 3.0587 | 3.0587 | 3.1111 | 3.1111 | 3.1111 | 3.1111 | 3.2842 | 3.2842 | 3.2842 | 3.2842 | 3.446 | 3.446 | 3.446 | 3.3968 | 3.5649 | 3.5649 | 3.5649 | 2.9012 | 3.6313 | 3.6313 | 3.6313 | 2.5191 | 3.6458 | 3.6458 | 3.6458 | 2.279 | 2.5937 | 2.5937 | 2.5937 | 2.5937 | 2.6064 | 2.6064 | 2.6064 | 2.6064 | 2.6284 | 2.6284 | 2.6284 | 2.6284 | 2.6607 | 2.6607 | 2.6607 | 2.6607 | 2.7056 | 2.7056 | 2.7056 | 2.7056 | 2.7735 | 2.7735 | 2.7735 | 2.7735 | 2.857 | 2.857 | 2.857 | 2.857 | 2.9518 | 2.9518 | 2.9518 | 2.9518 | 3.028 | 3.028 | 3.028 | 3.028 | 3.1035 | 3.1035 | 3.1035 | 3.1035 | 3.3134 | 3.3134 | 3.3134 | 3.3134 | 3.4721 | 3.4721 | 3.4721 | 3.4721 | 3.5544 | 3.5544 | 3.5544 | 3.0346 | 3.5876 | 3.5876 | 3.5876 | 2.7169 | 3.5406 | 3.5406 | 3.5406 | 2.7149 | 2.5909 | 2.5909 | 2.5909 | 2.5909 | 2.61 | 2.61 | 2.61 | 2.61 | 2.6351 | 2.6351 | 2.6351 | 2.6351 | 2.6672 | 2.6672 | 2.6672 | 2.6672 | 2.7082 | 2.7082 | 2.7082 | 2.7082 | 2.7686 | 2.7686 | 2.7686 | 2.7686 | 2.8418 | 2.8418 | 2.8418 | 2.8418 | 2.8954 | 2.8954 | 2.8954 | 2.8954 | 2.9457 | 2.9457 | 2.9457 | 2.9457 | 2.9974 | 2.9974 | 2.9974 | 2.9974 | 3.1866 | 3.1866 | 3.1866 | 3.1866 | 3.3964 | 3.3964 | 3.3964 | 3.3964 | 3.5058 | 3.5058 | 3.5058 | 3.5058 | 3.5937 | 3.5937 | 3.5937 | 3.3503 | 3.6348 | 3.6348 | 3.6348 | 3.1987 | 2.5909 | 2.5909 | 2.5909 | 2.5909 | 2.612 | 2.612 | 2.612 | 2.612 | 2.6475 | 2.6475 | 2.6475 | 2.6475 | 2.6967 | 2.6967 | 2.6967 | 2.6967 | 2.7559 | 2.7559 | 2.7559 | 2.7559 | 2.8236 | 2.8236 | 2.8236 | 2.8236 | 2.9018 | 2.9018 | 2.9018 | 2.9018 | 3.001 | 3.001 | 3.001 | 3.001 | 3.0814 | 3.0814 | 3.0814 | 3.0814 | 3.1599 | 3.1599 | 3.1599 | 3.1599 | 3.3659 | 3.3659 | 3.3659 | 3.3659 | 3.5324 | 3.5324 | 3.5324 | 3.3778 | 3.6473 | 3.6473 | 3.6473 | 2.9478 | 3.7214 | 3.7214 | 3.7214 | 2.6762 | 3.7321 | 3.7321 | 3.7321 | 2.6795
KIRKBY STEPHEN | PENRITH & SHAP | HARKER / HUTTON | 376579 | 509136 | 18.3969 | 18.3969 | 18.3969 | 12.3716 | 18.482 | 18.482 | 18.482 | 11.6667 | 18.5702 | 18.5702 | 18.5702 | 11.4523 | 18.6845 | 18.6845 | 18.6845 | 11.3416 | 18.8296 | 18.8296 | 18.8296 | 11.1623 | 19.0051 | 19.0051 | 19.0051 | 10.9692 | 19.1739 | 19.1739 | 19.1739 | 10.7955 | 19.2972 | 19.2972 | 19.2972 | 10.607 | 19.4006 | 19.4006 | 19.4006 | 10.4074 | 19.4992 | 19.4992 | 19.4992 | 10.2212 | 19.8632 | 19.8632 | 19.8632 | 9.2476 | 20.2899 | 20.2899 | 20.2899 | 7.7695 | 20.6077 | 20.6077 | 20.6077 | 6.6114 | 20.8968 | 20.8968 | 20.8968 | 5.5802 | 21.1352 | 21.1352 | 20.5524 | 4.6512 | 18.3804 | 18.3804 | 18.3804 | 12.3716 | 18.4774 | 18.4774 | 18.4774 | 12.1933 | 18.5687 | 18.5687 | 18.5687 | 12.0362 | 18.6827 | 18.6827 | 18.6827 | 11.8718 | 18.8258 | 18.8258 | 18.8258 | 11.6803 | 18.9984 | 18.9984 | 18.9984 | 11.499 | 19.2045 | 19.2045 | 19.2045 | 11.2773 | 19.4476 | 19.4476 | 19.4476 | 10.8518 | 19.548 | 19.548 | 19.548 | 10.7225 | 19.6617 | 19.6617 | 19.6617 | 10.5883 | 19.9447 | 19.9447 | 19.9447 | 10.1612 | 20.1737 | 20.1737 | 20.1737 | 9.5815 | 20.3725 | 20.3725 | 20.3725 | 9.0035 | 20.5668 | 20.5668 | 20.5668 | 8.2992 | 20.697 | 20.697 | 20.697 | 7.7253 | 18.4005 | 18.4005 | 18.4005 | 12.3716 | 18.4792 | 18.4792 | 18.4792 | 11.5777 | 18.5664 | 18.5664 | 18.5664 | 11.3567 | 18.6809 | 18.6809 | 18.6809 | 11.2655 | 18.8254 | 18.8254 | 18.8254 | 11.1072 | 18.9986 | 18.9986 | 18.9986 | 10.94 | 19.1638 | 19.1638 | 19.1638 | 10.8029 | 19.2811 | 19.2811 | 19.2811 | 10.6759 | 19.3787 | 19.3787 | 19.3787 | 10.558 | 19.4728 | 19.4728 | 19.4728 | 10.4234 | 19.8291 | 19.8291 | 19.8291 | 9.5724 | 20.2604 | 20.2604 | 20.2604 | 8.0118 | 20.5829 | 20.5829 | 20.5687 | 6.8238 | 20.8663 | 20.8663 | 20.0143 | 5.9233 | 21.0868 | 21.0868 | 19.5254 | 5.3253 | 18.4006 | 18.4006 | 18.4006 | 12.3716 | 18.4491 | 18.4491 | 18.4491 | 11.8666 | 18.5045 | 18.5045 | 18.5045 | 11.7058 | 18.5839 | 18.5839 | 18.5839 | 11.583 | 18.6942 | 18.6942 | 18.6942 | 11.4243 | 18.8513 | 18.8513 | 18.8513 | 11.2557 | 18.9788 | 18.9788 | 18.9788 | 11.0297 | 19.1226 | 19.1226 | 19.1226 | 10.5735 | 19.2654 | 19.2654 | 19.2654 | 10.0844 | 19.4092 | 19.4092 | 19.4092 | 9.5891 | 19.8381 | 19.8381 | 19.8381 | 8.1584 | 20.2445 | 20.2445 | 20.2445 | 6.8462 | 20.5379 | 20.5379 | 20.4003 | 5.9147 | 20.7393 | 20.7393 | 19.915 | 5.46 | 20.7541 | 20.7541 | 19.5782 | 5.9061 | 18.3967 | 18.3967 | 18.3967 | 12.3716 | 18.4675 | 18.4675 | 18.4675 | 12.1854 | 18.5352 | 18.5352 | 18.5352 | 12.0629 | 18.6181 | 18.6181 | 18.6181 | 11.9605 | 18.7237 | 18.7237 | 18.7237 | 11.8428 | 18.8665 | 18.8665 | 18.8665 | 11.7394 | 19.0478 | 19.0478 | 19.0478 | 11.6363 | 19.2008 | 19.2008 | 19.2008 | 11.5129 | 19.2938 | 19.2938 | 19.2938 | 11.3379 | 19.3891 | 19.3891 | 19.3891 | 11.1563 | 19.6958 | 19.6958 | 19.6958 | 10.4722 | 20.0132 | 20.0132 | 20.0132 | 9.5768 | 20.2337 | 20.2337 | 20.2337 | 8.716 | 20.4207 | 20.4207 | 20.4207 | 8.0161 | 20.5072 | 20.5072 | 20.5072 | 7.6614 | 18.3967 | 18.3967 | 18.3967 | 12.3716 | 18.459 | 18.459 | 18.459 | 11.5337 | 18.5391 | 18.5391 | 18.5391 | 11.2786 | 18.6466 | 18.6466 | 18.6466 | 11.108 | 18.7798 | 18.7798 | 18.7798 | 10.9034 | 18.9375 | 18.9375 | 18.9375 | 10.6988 | 19.1267 | 19.1267 | 19.1267 | 10.4396 | 19.3411 | 19.3411 | 19.3411 | 9.9474 | 19.4979 | 19.4979 | 19.4979 | 9.4421 | 19.651 | 19.651 | 19.651 | 8.9248 | 20.1052 | 20.1052 | 20.1052 | 7.3951 | 20.5306 | 20.5306 | 20.5306 | 5.9606 | 20.8415 | 20.8415 | 20.2448 | 4.9107 | 21.0489 | 21.0489 | 19.7424 | 4.3331 | 21.0739 | 21.0739 | 19.3907 | 4.6644
KIRKBY THORE | PENRITH & SHAP | HARKER / HUTTON | 364439 | 526672 | 30.0204 | 26.5659 | 19.0934 | 18.0192 | 30.0794 | 26.4218 | 18.9899 | 17.4437 | 30.1911 | 26.31 | 18.9095 | 17.3034 | 30.2702 | 26.2107 | 18.8382 | 17.2452 | 30.345 | 26.0817 | 18.7454 | 17.095 | 30.4303 | 25.9503 | 18.651 | 16.9277 | 30.5328 | 25.8242 | 18.5604 | 16.7725 | 30.6664 | 25.7367 | 18.4975 | 16.6229 | 30.8091 | 25.6436 | 18.4306 | 16.4366 | 30.9587 | 25.5553 | 18.3671 | 16.2691 | 31.3961 | 25.2249 | 18.1296 | 15.5197 | 31.7424 | 24.8757 | 17.8786 | 14.5005 | 31.9457 | 24.5402 | 17.6375 | 13.7173 | 32.0483 | 24.1656 | 17.3683 | 13.13 | 32.1366 | 23.7542 | 17.0726 | 12.48 | 30.0149 | 26.5659 | 19.0934 | 18.0192 | 30.0701 | 26.5186 | 19.0594 | 17.8704 | 30.1523 | 26.4628 | 19.0194 | 17.767 | 30.2488 | 26.3941 | 18.9699 | 17.6525 | 30.3449 | 26.3138 | 18.9123 | 17.5308 | 30.4309 | 26.2368 | 18.8569 | 17.4341 | 30.5227 | 26.1047 | 18.7619 | 17.3084 | 30.6336 | 26.022 | 18.7025 | 17.1431 | 30.7059 | 25.9488 | 18.6499 | 16.994 | 30.7846 | 25.8744 | 18.5965 | 16.8441 | 31.0618 | 25.6547 | 18.4385 | 16.3855 | 31.3782 | 25.4618 | 18.2999 | 15.9286 | 31.6922 | 25.2491 | 18.147 | 15.4358 | 32.0219 | 24.9576 | 17.9375 | 14.761 | 32.6597 | 24.5357 | 17.6343 | 13.6887 | 30.0234 | 26.5659 | 19.0934 | 18.0192 | 30.0855 | 26.3823 | 18.9614 | 17.3745 | 30.2013 | 26.2109 | 18.8383 | 17.2311 | 30.2868 | 26.0605 | 18.7302 | 17.1972 | 30.3667 | 25.896 | 18.6119 | 17.0684 | 30.4502 | 25.742 | 18.5013 | 16.9264 | 30.5549 | 25.5977 | 18.3976 | 16.8096 | 30.6891 | 25.4774 | 18.3111 | 16.6695 | 30.8159 | 25.3529 | 18.2216 | 16.5222 | 30.9484 | 25.2344 | 18.1365 | 16.3943 | 31.3444 | 24.8026 | 17.8261 | 15.7792 | 32.1202 | 24.2537 | 17.4316 | 14.4355 | 32.3416 | 23.7976 | 17.1038 | 13.7703 | 32.4196 | 23.2981 | 16.7448 | 13.3634 | 32.4375 | 22.8238 | 16.4039 | 12.962 | 30.0234 | 26.5659 | 19.0934 | 18.0192 | 30.0272 | 26.437 | 19.0008 | 17.6547 | 30.0884 | 26.3009 | 18.903 | 17.5624 | 30.1564 | 26.1076 | 18.764 | 17.4617 | 30.2412 | 25.9407 | 18.6441 | 17.2961 | 30.8311 | 25.6494 | 18.4347 | 16.5886 | 30.9014 | 25.3976 | 18.2537 | 16.4076 | 31.0047 | 25.1475 | 18.074 | 16.091 | 31.1106 | 24.8949 | 17.8925 | 15.7418 | 31.2254 | 24.6606 | 17.724 | 15.3994 | 31.6278 | 24.1365 | 17.3474 | 14.376 | 32.022 | 23.6603 | 17.0051 | 13.4447 | 32.1921 | 23.2362 | 16.7003 | 12.9266 | 32.2308 | 22.802 | 16.3882 | 12.8707 | 32.1317 | 22.5115 | 16.1795 | 13.4343 | 30.0204 | 26.5659 | 19.0934 | 18.0192 | 30.069 | 26.5051 | 19.0497 | 17.8572 | 30.1497 | 26.4079 | 18.9799 | 17.7878 | 30.2339 | 26.3102 | 18.9096 | 17.7311 | 30.2861 | 26.1931 | 18.8255 | 17.6313 | 30.3643 | 26.0805 | 18.7446 | 17.5486 | 30.4545 | 25.9703 | 18.6653 | 17.4678 | 30.5638 | 25.8942 | 18.6107 | 17.3735 | 30.6798 | 25.8067 | 18.5478 | 17.213 | 30.8047 | 25.7205 | 18.4858 | 17.0528 | 31.2264 | 25.4248 | 18.2733 | 16.4662 | 31.5878 | 25.1502 | 18.076 | 15.8173 | 31.8184 | 24.8853 | 17.8856 | 15.3934 | 31.9524 | 24.5506 | 17.645 | 15.0137 | 32.0359 | 24.2106 | 17.4006 | 14.7354 | 30.0204 | 26.5659 | 19.0934 | 18.0192 | 30.0564 | 26.3801 | 18.9599 | 17.3764 | 30.1649 | 26.2268 | 18.8497 | 17.203 | 30.2502 | 26.0282 | 18.707 | 17.0811 | 30.3227 | 25.8576 | 18.5844 | 16.9029 | 30.9071 | 25.5651 | 18.3742 | 16.1926 | 30.9715 | 25.3142 | 18.1938 | 16.0168 | 31.0771 | 25.0627 | 18.0131 | 15.6951 | 31.1726 | 24.8132 | 17.8337 | 15.3638 | 31.2765 | 24.5781 | 17.6647 | 15.0154 | 31.6763 | 24.0446 | 17.2813 | 13.9454 | 32.0956 | 23.555 | 16.9294 | 12.9343 | 32.2977 | 23.0909 | 16.5959 | 12.3124 | 32.3491 | 22.6497 | 16.2788 | 12.1516 | 32.2552 | 22.3321 | 16.0505 | 12.5875
KIRKHALL LANE | ATHERTON | KEARSLEY | 365510 | 401069 | 20.6371 | 11.9039 | 8.5556 | 8.7581 | 20.719 | 11.6025 | 8.3389 | 7.5002 | 20.8291 | 11.4786 | 8.2499 | 7.141 | 20.972 | 11.3161 | 8.1331 | 7.0059 | 21.1635 | 11.0801 | 7.9635 | 6.7796 | 21.3795 | 10.8246 | 7.7799 | 6.5411 | 21.6159 | 10.6561 | 7.6587 | 6.3227 | 21.8527 | 10.5145 | 7.557 | 6.1337 | 22.0074 | 10.3596 | 7.4456 | 5.9168 | 22.1528 | 10.2496 | 7.3666 | 5.7259 | 22.5549 | 9.9529 | 7.1534 | 4.2832 | 22.9256 | 9.326 | 6.7028 | 1.6234 | 23.2035 | 8.9549 | 6.4361 | -0.60786 | 23.4563 | 8.9968 | 6.4661 | -2.9679 | 23.6368 | 8.4587 | 6.0794 | -5.1717 | 20.6076 | 11.9039 | 8.5556 | 8.7581 | 20.6632 | 11.7784 | 8.4654 | 8.3081 | 20.7012 | 11.7114 | 8.4172 | 8.1465 | 20.7496 | 11.5962 | 8.3344 | 8.05 | 20.8227 | 11.4638 | 8.2393 | 7.9109 | 20.9115 | 11.301 | 8.1222 | 7.7563 | 21.0246 | 11.0283 | 7.9262 | 7.5397 | 21.1669 | 10.9113 | 7.8421 | 7.2298 | 21.2903 | 10.8076 | 7.7676 | 6.9461 | 21.4167 | 10.7014 | 7.6913 | 6.6616 | 21.803 | 10.4077 | 7.4802 | 5.8095 | 22.1899 | 10.1954 | 7.3277 | 4.9305 | 22.5165 | 9.9548 | 7.1547 | 4.0787 | 22.7553 | 9.8953 | 7.1119 | 3.1308 | 22.9385 | 10.1425 | 7.2896 | 2.4627 | 20.646 | 11.9039 | 8.5556 | 8.7581 | 20.7366 | 11.5749 | 8.3191 | 7.3281 | 20.8618 | 11.3936 | 8.1888 | 6.9512 | 21.0269 | 11.2023 | 8.0513 | 6.8487 | 21.2466 | 10.921 | 7.8492 | 6.5365 | 21.4965 | 10.6114 | 7.6266 | 6.2182 | 21.7749 | 10.3324 | 7.4261 | 5.9387 | 22.0098 | 10.2917 | 7.3969 | 5.6907 | 22.1547 | 10.2214 | 7.3463 | 5.4205 | 22.2636 | 10.1222 | 7.275 | 5.1669 | 22.6702 | 9.6835 | 6.9597 | 3.7973 | 23.0554 | 9.0987 | 6.5394 | 1.296 | 23.3335 | 8.6219 | 6.1967 | -0.79653 | 23.5737 | 8.6369 | 6.2075 | -2.9978 | 23.726 | 8.1029 | 5.8237 | -5.0287 | 20.646 | 11.9039 | 8.5556 | 8.7581 | 20.6447 | 11.682 | 8.3961 | 7.9606 | 20.7103 | 11.5717 | 8.3168 | 7.733 | 20.8118 | 11.3784 | 8.1779 | 7.6542 | 20.9744 | 11.0796 | 7.9631 | 7.34 | 21.2039 | 10.6384 | 7.646 | 6.9952 | 21.4931 | 10.6534 | 7.6568 | 6.5361 | 21.7044 | 10.4388 | 7.5025 | 5.6267 | 21.8748 | 10.2599 | 7.374 | 4.6831 | 22.0397 | 10.0651 | 7.234 | 3.7489 | 22.458 | 9.9553 | 7.1551 | 1.2673 | 22.82 | 9.3039 | 6.6869 | -1.1123 | 23.0799 | 8.7542 | 6.2918 | -3.0349 | 23.2688 | 8.3522 | 6.0029 | -4.2944 | 23.2731 | 8.2616 | 5.9377 | -3.7561 | 20.6371 | 11.9039 | 8.5556 | 8.7581 | 20.7056 | 11.7004 | 8.4093 | 7.9895 | 20.7829 | 11.609 | 8.3436 | 7.7611 | 20.869 | 11.4696 | 8.2434 | 7.6976 | 20.9846 | 11.272 | 8.1014 | 7.6082 | 21.1543 | 11.0364 | 7.9321 | 7.4911 | 21.3704 | 10.8861 | 7.824 | 7.3565 | 21.6092 | 10.7563 | 7.7308 | 7.2153 | 21.806 | 10.6064 | 7.623 | 7.0016 | 21.9663 | 10.4412 | 7.5043 | 6.7949 | 22.3075 | 10.3185 | 7.4161 | 6.0645 | 22.6724 | 10.0383 | 7.2147 | 5.1614 | 22.9279 | 9.9926 | 7.1818 | 4.5202 | 23.1347 | 10.3774 | 7.4585 | 3.8199 | 23.2367 | 10.1778 | 7.315 | 3.3571 | 20.6371 | 11.9039 | 8.5556 | 8.7581 | 20.6576 | 11.5825 | 8.3246 | 7.3494 | 20.7611 | 11.4071 | 8.1985 | 6.9375 | 20.911 | 11.1939 | 8.0453 | 6.7787 | 21.1126 | 10.8843 | 7.8228 | 6.3921 | 21.3363 | 10.443 | 7.5056 | 6.0013 | 21.614 | 10.4436 | 7.5061 | 5.4838 | 21.8409 | 10.2073 | 7.3362 | 4.4927 | 22.0253 | 10.0162 | 7.1988 | 3.4837 | 22.2006 | 9.8073 | 7.0487 | 2.4844 | 22.6085 | 9.6546 | 6.939 | -0.1886 | 22.9434 | 8.9709 | 6.4475 | -2.7144 | 23.1833 | 8.3904 | 6.0304 | -4.7812 | 23.348 | 7.9517 | 5.7151 | -6.2242 | 23.3557 | 7.8172 | 5.6184 | -5.9066
KITT GREEN | ORRELL | WASHWAY FARM / KIRKBY | 354934 | 405497 | 30.9539 | 13.2088 | 9.6356 | 13.3197 | 31.0101 | 13.0382 | 9.5112 | 12.6303 | 31.0575 | 12.8991 | 9.4097 | 12.1005 | 31.1204 | 12.7947 | 9.3336 | 11.7346 | 31.2315 | 12.5943 | 9.1874 | 11.294 | 31.3688 | 12.3763 | 9.0283 | 10.7574 | 31.5278 | 12.1495 | 8.8629 | 10.2232 | 31.7122 | 12.035 | 8.7794 | 10.0724 | 36.353 | 11.1658 | 8.1453 | 5.327 | 36.42 | 11.0859 | 8.087 | 5.1173 | 40.9991 | 9.8947 | 7.2181 | -0.2379 | 41.9599 | 9.4029 | 6.8593 | -2.3328 | 43.4766 | 8.9349 | 6.5179 | -4.8057 | 44.2699 | 8.86 | 6.4632 | -6.3719 | 44.0805 | 8.6936 | 6.3419 | -7.2936 | 30.9546 | 13.2088 | 9.6356 | 13.3197 | 31.0051 | 13.1606 | 9.6005 | 13.1629 | 31.0427 | 13.1031 | 9.5585 | 13.0242 | 31.0852 | 13.0524 | 9.5216 | 12.9682 | 31.1465 | 12.9986 | 9.4823 | 12.9345 | 31.2254 | 12.944 | 9.4425 | 12.8979 | 31.3264 | 12.7172 | 9.277 | 12.8335 | 31.4452 | 12.6599 | 9.2352 | 12.7444 | 31.5638 | 12.607 | 9.1966 | 12.5322 | 31.6941 | 12.5488 | 9.1542 | 12.306 | 32.1559 | 12.3279 | 8.993 | 11.3945 | 32.6983 | 12.146 | 8.8603 | 10.3316 | 34.0463 | 11.823 | 8.6247 | 8.4337 | 34.6094 | 11.7863 | 8.5979 | 7.2562 | 34.935 | 11.8183 | 8.6213 | 6.5501 | 30.9537 | 13.2088 | 9.6356 | 13.3197 | 31.0105 | 13.0151 | 9.4943 | 12.5426 | 31.0567 | 12.8626 | 9.3831 | 12.0059 | 31.1172 | 12.7443 | 9.2968 | 11.6762 | 31.2222 | 12.5291 | 9.1398 | 11.2658 | 31.3489 | 12.3032 | 8.975 | 10.766 | 31.4923 | 12.1005 | 8.8271 | 10.2899 | 31.6535 | 11.9741 | 8.7349 | 10.2057 | 36.2095 | 11.1227 | 8.1139 | 5.6769 | 36.2373 | 11.05 | 8.0609 | 5.6092 | 41.5653 | 9.7223 | 7.0923 | -0.32097 | 42.5432 | 9.264 | 6.758 | -2.2816 | 43.2664 | 8.8831 | 6.4801 | -3.8436 | 43.981 | 8.8603 | 6.4634 | -5.2132 | 43.6963 | 8.757 | 6.3881 | -5.8122 | 30.9537 | 13.2088 | 9.6356 | 13.3197 | 30.9221 | 13.0917 | 9.5502 | 12.9094 | 30.9351 | 12.982 | 9.4702 | 12.4508 | 30.9744 | 12.8626 | 9.3831 | 12.1187 | 31.0683 | 12.6267 | 9.211 | 11.6905 | 31.2028 | 12.3911 | 9.0392 | 11.1585 | 31.4022 | 11.8535 | 8.647 | 10.5393 | 41.6054 | 9.814 | 7.1592 | 0.043561 | 41.5872 | 9.4989 | 6.9293 | -0.2381 | 41.624 | 9.2032 | 6.7136 | -0.61481 | 42.282 | 8.7361 | 6.3729 | -2.3972 | 43.1671 | 8.3449 | 6.0875 | -4.2621 | 43.6679 | 7.9948 | 5.8321 | -5.597 | 43.9057 | 8.0068 | 5.8408 | -6.2453 | 43.2884 | 8.1275 | 5.9289 | -4.9752 | 30.9539 | 13.2088 | 9.6356 | 13.3197 | 31.0004 | 13.1286 | 9.5771 | 13.076 | 31.0281 | 13.0104 | 9.4909 | 12.6542 | 31.0522 | 12.9228 | 9.427 | 12.352 | 31.0957 | 12.7544 | 9.3042 | 12.0691 | 31.1732 | 12.5647 | 9.1658 | 11.702 | 31.2894 | 12.3608 | 9.0171 | 11.3056 | 31.4357 | 12.2597 | 8.9433 | 11.2366 | 36.0427 | 11.4031 | 8.3184 | 6.5639 | 36.0829 | 11.3312 | 8.266 | 6.4094 | 40.4328 | 10.2398 | 7.4698 | 1.5953 | 40.9629 | 9.9698 | 7.2729 | 0.58011 | 42.1019 | 9.7056 | 7.0801 | -0.85085 | 42.5027 | 9.8751 | 7.2037 | -1.3571 | 42.1308 | 10.0183 | 7.3082 | -0.86049 | 30.9539 | 13.2088 | 9.6356 | 13.3197 | 30.9396 | 13.0179 | 9.4964 | 12.5599 | 30.9786 | 12.8856 | 9.3999 | 12.0035 | 31.0464 | 12.7582 | 9.3069 | 11.6383 | 31.1615 | 12.5214 | 9.1342 | 11.1838 | 31.2951 | 12.2814 | 8.9591 | 10.6429 | 31.4842 | 11.7447 | 8.5676 | 10.0165 | 41.6861 | 9.6945 | 7.072 | -0.48662 | 41.6596 | 9.3816 | 6.8437 | -0.75987 | 41.6875 | 9.0868 | 6.6287 | -1.1256 | 42.365 | 8.587 | 6.2641 | -2.9624 | 43.3277 | 8.1873 | 5.9725 | -5.0224 | 43.834 | 7.7627 | 5.6628 | -6.5634 | 44.1453 | 7.7649 | 5.6644 | -7.3809 | 43.5341 | 7.8628 | 5.7358 | -6.2345
KNOTT MILL | BLOOM ST | SOUTH MANCHESTER | 383136 | 397725 | 29.6815 | 7.2251 | 5.2706 | 14.1552 | 29.7838 | 6.4987 | 4.7407 | 9.7838 | 29.9163 | 6.1397 | 4.4788 | 8.5621 | 30.0609 | 6.0287 | 4.3979 | 8.1762 | 30.2114 | 5.9145 | 4.3145 | 7.8036 | 30.3744 | 5.8231 | 4.2479 | 7.4192 | 30.5497 | 5.6951 | 4.1545 | 7.041 | 30.7529 | 5.5591 | 4.0553 | 6.6446 | 30.9264 | 5.4003 | 3.9395 | 6.1986 | 31.0956 | 5.244 | 3.8254 | 5.7669 | 29.9392 | 4.8564 | 3.5427 | 4.3798 | 27.5798 | 4.4737 | 3.2635 | 2.8007 | 25.8792 | 4.1979 | 3.0623 | 1.6726 | 28.8602 | 4.6814 | 3.415 | 0.50725 | 32.0056 | 5.1916 | 3.7872 | -0.6863 | 29.6678 | 7.2251 | 5.2706 | 14.1552 | 29.7733 | 7.0313 | 5.1293 | 12.6676 | 29.8948 | 6.8411 | 4.9905 | 12.0735 | 30.0288 | 6.9127 | 5.0427 | 11.7117 | 30.1763 | 6.862 | 5.0057 | 11.3432 | 30.34 | 6.7449 | 4.9203 | 10.9729 | 30.4831 | 6.4142 | 4.6791 | 10.5693 | 30.6493 | 6.2789 | 4.5803 | 10.095 | 30.7945 | 6.152 | 4.4878 | 9.649 | 30.9441 | 6.0291 | 4.3981 | 9.1917 | 31.3739 | 5.6779 | 4.142 | 7.9031 | 31.7716 | 5.4114 | 3.9475 | 6.6676 | 32.0777 | 5.2228 | 3.81 | 5.6557 | 32.4113 | 5.5701 | 4.0633 | 4.5469 | 32.7503 | 5.8612 | 4.2757 | 3.4515 | 29.6867 | 7.2251 | 5.2706 | 14.1552 | 29.7996 | 6.3611 | 4.6404 | 9.0796 | 29.9461 | 5.9754 | 4.3589 | 7.6846 | 30.1095 | 5.8448 | 4.2637 | 7.2677 | 30.2822 | 5.7168 | 4.1703 | 6.8531 | 30.4709 | 5.5897 | 4.0776 | 6.421 | 30.6775 | 5.4469 | 3.9734 | 6.0061 | 30.9167 | 5.2861 | 3.8561 | 5.5567 | 31.1132 | 5.1066 | 3.7252 | 5.0888 | 30.4341 | 4.9367 | 3.6013 | 4.6084 | 27.5559 | 4.4698 | 3.2607 | 3.0487 | 24.8581 | 4.0322 | 2.9414 | 1.3553 | 22.8938 | 3.7136 | 2.709 | 0.15394 | 25.5509 | 4.1446 | 3.0234 | -1.1019 | 28.3946 | 4.6059 | 3.3599 | -2.3681 | 29.6867 | 7.2251 | 5.2706 | 14.1552 | 29.7398 | 6.6092 | 4.8213 | 10.5855 | 29.8403 | 6.3331 | 4.6199 | 9.5377 | 29.9512 | 6.2291 | 4.544 | 9.1851 | 30.0754 | 6.1033 | 4.4523 | 8.8184 | 30.2356 | 5.9985 | 4.3758 | 8.4096 | 30.4171 | 5.8788 | 4.2885 | 7.9925 | 30.6124 | 5.7095 | 4.165 | 7.4786 | 30.7848 | 5.5387 | 4.0404 | 6.9195 | 30.9567 | 5.3021 | 3.8678 | 6.3411 | 29.5561 | 4.7943 | 3.4974 | 4.6798 | 27.0386 | 4.3859 | 3.1995 | 3.0834 | 25.9674 | 4.2122 | 3.0727 | 1.9887 | 32.7256 | 5.3268 | 3.8858 | 0.95354 | 30.8089 | 4.9975 | 3.6456 | 0.02006 | 29.6815 | 7.2251 | 5.2706 | 14.1552 | 29.7779 | 6.7976 | 4.9587 | 11.4634 | 29.8914 | 6.4896 | 4.734 | 10.6113 | 30.0077 | 6.3872 | 4.6594 | 10.2694 | 30.1301 | 6.2825 | 4.583 | 9.9457 | 30.2843 | 6.2125 | 4.532 | 9.5956 | 30.4619 | 6.0917 | 4.4438 | 9.2529 | 30.6529 | 5.9644 | 4.3509 | 8.8926 | 30.8153 | 5.8089 | 4.2375 | 8.4588 | 30.9782 | 5.6527 | 4.1236 | 8.0231 | 31.4572 | 5.2954 | 3.8629 | 6.7472 | 30.7346 | 4.9854 | 3.6368 | 5.4843 | 29.349 | 4.7607 | 3.4729 | 4.5728 | 32.6278 | 5.2926 | 3.8608 | 3.5765 | 32.973 | 5.8613 | 4.2757 | 2.5725 | 29.6815 | 7.2251 | 5.2706 | 14.1552 | 29.7579 | 6.2453 | 4.5559 | 8.5084 | 29.8913 | 5.8936 | 4.2993 | 6.9853 | 30.0406 | 5.7716 | 4.2103 | 6.5631 | 30.1981 | 5.6375 | 4.1125 | 6.135 | 30.3676 | 5.5237 | 4.0295 | 5.6918 | 30.5506 | 5.3916 | 3.9331 | 5.2291 | 30.7669 | 5.2082 | 3.7993 | 4.6537 | 30.9486 | 5.0291 | 3.6687 | 4.0513 | 29.5026 | 4.7856 | 3.491 | 3.4293 | 26.2001 | 4.2499 | 3.1003 | 1.6358 | 23.5844 | 3.8256 | 2.7907 | -0.025741 | 22.4202 | 3.6368 | 2.653 | -1.1792 | 29.1857 | 4.7342 | 3.4535 | -2.2866 | 27.0154 | 4.3822 | 3.1967 | -3.3405
LAMBERHEAD | ORRELL | WASHWAY FARM / KIRKBY | 355516 | 404030 | 22.8585 | 10.2896 | 7.5061 | 16.95 | 23.0181 | 9.9996 | 7.2946 | 15.5979 | 23.1231 | 9.8337 | 7.1736 | 15.1086 | 23.2444 | 9.7102 | 7.0834 | 14.8867 | 23.3967 | 9.5192 | 6.9441 | 14.6088 | 23.5629 | 9.3229 | 6.8009 | 14.3439 | 23.7396 | 9.1678 | 6.6878 | 14.1431 | 23.9428 | 9.034 | 6.5902 | 13.9845 | 24.108 | 8.8506 | 6.4564 | 13.7413 | 24.2679 | 8.8048 | 6.423 | 13.5185 | 24.9052 | 8.3589 | 6.0977 | 11.7462 | 25.7365 | 7.8817 | 5.7496 | 8.482 | 26.3954 | 7.9525 | 5.8013 | 5.6923 | 27.0266 | 12.7803 | 9.3231 | 2.7747 | 27.5467 | 12.2725 | 8.9526 | 0.20862 | 22.8808 | 10.2896 | 7.5061 | 16.95 | 23.0037 | 10.2096 | 7.4478 | 16.6727 | 23.0618 | 10.1344 | 7.3929 | 16.4448 | 23.133 | 10.0518 | 7.3327 | 16.2731 | 23.2249 | 9.9568 | 7.2634 | 16.0941 | 23.3363 | 9.8492 | 7.1848 | 15.8964 | 23.4685 | 9.6045 | 7.0063 | 15.6545 | 23.624 | 9.4987 | 6.9291 | 15.3501 | 23.7165 | 9.394 | 6.8528 | 15.0376 | 23.8133 | 9.2895 | 6.7766 | 14.7232 | 24.115 | 9.0004 | 6.5656 | 13.8061 | 24.4152 | 8.805 | 6.4232 | 12.9365 | 24.7033 | 8.6977 | 6.3448 | 12.0761 | 25.0066 | 11.6647 | 8.5092 | 11.2134 | 25.2226 | 14.754 | 10.7628 | 10.5939 | 22.8492 | 10.2896 | 7.5061 | 16.95 | 22.9999 | 9.9531 | 7.2606 | 15.4185 | 23.142 | 9.7517 | 7.1138 | 14.9137 | 23.2763 | 9.6134 | 7.0128 | 14.7404 | 23.4435 | 9.4156 | 6.8686 | 14.5093 | 23.6268 | 9.2225 | 6.7277 | 14.298 | 23.8235 | 9.0635 | 6.6117 | 14.166 | 24.0511 | 8.9238 | 6.5098 | 14.0892 | 24.2302 | 8.7466 | 6.3805 | 13.967 | 24.4006 | 8.6992 | 6.3459 | 13.8357 | 25.0782 | 8.2223 | 5.9981 | 12.3374 | 25.9609 | 7.7116 | 5.6255 | 9.3413 | 26.6596 | 7.8114 | 5.6983 | 6.7983 | 27.3174 | 12.6615 | 9.2364 | 4.1861 | 27.8462 | 12.2046 | 8.9031 | 1.9787 | 22.8492 | 10.2896 | 7.5061 | 16.95 | 22.9028 | 10.05 | 7.3313 | 15.9264 | 22.9999 | 9.9059 | 7.2262 | 15.5606 | 23.1299 | 9.7768 | 7.1321 | 15.3991 | 23.2682 | 9.5778 | 6.9869 | 15.1609 | 23.4363 | 9.4709 | 6.9089 | 14.9076 | 23.6559 | 9.1383 | 6.6663 | 14.5164 | 23.9818 | 8.8132 | 6.4291 | 13.5267 | 24.2763 | 8.6894 | 6.3388 | 12.4742 | 24.5646 | 8.8127 | 6.4288 | 11.4156 | 25.4224 | 13.1596 | 9.5998 | 8.3779 | 26.2677 | 12.5618 | 9.1637 | 5.4991 | 26.9231 | 11.9985 | 8.7527 | 3.1317 | 27.405 | 11.719 | 8.5488 | 1.6841 | 27.4042 | 11.737 | 8.562 | 2.8189 | 22.8585 | 10.2896 | 7.5061 | 16.95 | 22.9906 | 10.1697 | 7.4187 | 16.5349 | 23.0886 | 10.0475 | 7.3295 | 16.2758 | 23.1675 | 9.9414 | 7.2521 | 16.1402 | 23.2622 | 9.7794 | 7.1339 | 16.032 | 23.3938 | 9.6092 | 7.0098 | 15.9063 | 23.5547 | 9.4677 | 6.9066 | 15.7821 | 23.7295 | 9.3409 | 6.814 | 15.6613 | 23.8741 | 9.1599 | 6.682 | 15.4227 | 24.0201 | 9.1107 | 6.6461 | 15.1847 | 24.4921 | 8.8332 | 6.4437 | 14.3878 | 24.9905 | 8.7521 | 6.3845 | 13.4952 | 25.3515 | 9.1705 | 6.6898 | 12.7562 | 25.666 | 14.4528 | 10.5431 | 12.1518 | 25.8461 | 14.3925 | 10.4991 | 11.9938 | 22.8585 | 10.2896 | 7.5061 | 16.95 | 22.9928 | 9.9227 | 7.2385 | 15.2537 | 23.1119 | 9.7416 | 7.1064 | 14.6792 | 23.242 | 9.5967 | 7.0007 | 14.4223 | 23.4021 | 9.3826 | 6.8445 | 14.0979 | 23.5747 | 9.2718 | 6.7636 | 13.7881 | 23.7887 | 8.9297 | 6.5141 | 13.3351 | 24.1314 | 8.5831 | 6.2612 | 12.2487 | 24.437 | 8.4455 | 6.1609 | 11.124 | 24.7337 | 8.5566 | 6.2419 | 9.9957 | 25.6024 | 12.8631 | 9.3835 | 6.7534 | 26.426 | 12.2246 | 8.9177 | 3.681 | 27.074 | 11.6233 | 8.479 | 1.1215 | 27.5438 | 11.3 | 8.2432 | -0.56338 | 27.5641 | 11.2745 | 8.2246 | 0.30451
LANCASTER | LANCASTER | HEYSHAM | 348644 | 463628 | 24.3418 | 4.0077 | 2.8804 | 6.8757 | 22.3239 | 3.6755 | 2.6416 | 5.3012 | 19.9253 | 3.2806 | 2.3578 | 3.2429 | 19.5084 | 3.2119 | 2.3085 | 3.1531 | 18.2606 | 3.0065 | 2.1608 | 2.9582 | 16.5854 | 2.7307 | 1.9626 | 2.7312 | 14.0921 | 2.3202 | 1.6675 | 2.5215 | 12.7952 | 2.1066 | 1.5141 | 2.3408 | 11.3206 | 1.8638 | 1.3396 | 1.9819 | 10.5099 | 1.7304 | 1.2437 | 1.6547 | 8.6792 | 1.429 | 1.027 | -0.41934 | 7.2209 | 1.1889 | 0.85446 | -4.943 | 12.828 | 2.112 | 1.518 | -7.6445 | 21.8073 | 3.5904 | 2.5805 | -10.1817 | 22.9135 | 3.7725 | 2.7114 | -12.523 | 24.3418 | 4.0077 | 2.8804 | 6.8757 | 23.466 | 3.8635 | 2.7768 | 6.2831 | 22.9585 | 3.7799 | 2.7167 | 6.0341 | 21.8492 | 3.5973 | 2.5855 | 5.8415 | 20.6671 | 3.4027 | 2.4456 | 5.6166 | 19.4239 | 3.198 | 2.2985 | 5.3811 | 17.1511 | 2.8238 | 2.0295 | 5.0744 | 16.3067 | 2.6848 | 1.9296 | 4.6752 | 15.4774 | 2.5482 | 1.8315 | 4.2363 | 14.6487 | 2.4118 | 1.7334 | 3.7983 | 13.3154 | 2.1923 | 1.5756 | 2.499 | 13.1099 | 2.1584 | 1.5513 | 0.081649 | 17.1804 | 2.8286 | 2.033 | -1.1753 | 23.4636 | 3.8631 | 2.7765 | -2.4685 | 24.2686 | 3.9956 | 2.8717 | -4.2851 | 24.3418 | 4.0077 | 2.8804 | 6.8757 | 21.7995 | 3.5891 | 2.5796 | 5.1038 | 19.5915 | 3.2256 | 2.3183 | 3.0929 | 18.6971 | 3.0783 | 2.2125 | 3.0701 | 17.3279 | 2.8529 | 2.0504 | 2.9403 | 15.5911 | 2.567 | 1.8449 | 2.7886 | 12.0825 | 1.9893 | 1.4297 | 1.5492 | 10.7964 | 1.7776 | 1.2776 | 1.5586 | 9.4136 | 1.5499 | 1.1139 | 1.4001 | 8.7469 | 1.4401 | 1.035 | 1.2358 | 5.5529 | 0.91425 | 0.65709 | -1.4909 | 4.3953 | 0.72365 | 0.5201 | -4.8354 | 9.5659 | 1.575 | 1.1319 | -7.2159 | 18.2182 | 2.9995 | 2.1558 | -9.1631 | 19.1698 | 3.1562 | 2.2684 | -11.0351 | 24.3418 | 4.0077 | 2.8804 | 6.8757 | 22.6365 | 3.7269 | 2.6786 | 5.901 | 22.3165 | 3.6742 | 2.6407 | 5.6544 | 18.7563 | 3.0881 | 2.2195 | 2.7198 | 17.6328 | 2.9031 | 2.0865 | 2.6748 | 17.0415 | 2.8058 | 2.0166 | 2.5682 | 14.5217 | 2.3909 | 1.7184 | 2.3062 | 12.6651 | 2.0852 | 1.4987 | 1.4698 | 11.1986 | 1.8438 | 1.3252 | 0.43738 | 10.3333 | 1.7013 | 1.2228 | -0.61191 | 27.708 | 4.5619 | 3.2787 | -3.9534 | 23.149 | 3.8113 | 2.7393 | -6.8655 | 19.5514 | 3.219 | 2.3135 | -9.0338 | 19.3421 | 3.1845 | 2.2888 | -10.0326 | 18.7023 | 3.0792 | 2.2131 | -8.728 | 24.3418 | 4.0077 | 2.8804 | 6.8757 | 22.9657 | 3.7811 | 2.7176 | 5.9398 | 20.7832 | 3.4218 | 2.4593 | 4.0349 | 20.4843 | 3.3726 | 2.4239 | 4.0376 | 19.4385 | 3.2004 | 2.3002 | 4.028 | 17.9788 | 2.9601 | 2.1275 | 3.9797 | 15.5983 | 2.5681 | 1.8458 | 3.8953 | 14.378 | 2.3672 | 1.7014 | 3.7779 | 12.8939 | 2.1229 | 1.5258 | 3.4292 | 12.023 | 1.9795 | 1.4227 | 3.0824 | 11.2128 | 1.8461 | 1.3268 | 1.8429 | 11.9512 | 1.9677 | 1.4142 | -0.65583 | 19.3544 | 3.1866 | 2.2902 | -1.7103 | 30.0452 | 4.9467 | 3.5553 | -2.7753 | 33.2652 | 5.4769 | 3.9363 | -3.1886 | 24.3418 | 4.0077 | 2.8804 | 6.8757 | 21.8457 | 3.5967 | 2.585 | 5.1415 | 21.2366 | 3.4964 | 2.513 | 4.6782 | 17.5407 | 2.8879 | 2.0756 | 1.6347 | 16.2778 | 2.68 | 1.9262 | 1.4926 | 15.6341 | 2.574 | 1.85 | 1.3241 | 13.0085 | 2.1418 | 1.5393 | 0.9867 | 11.0678 | 1.8222 | 1.3097 | 0.048401 | 9.5547 | 1.5731 | 1.1306 | -1.0536 | 8.6335 | 1.4214 | 1.0216 | -2.1734 | 25.7192 | 4.2345 | 3.0434 | -5.7685 | 20.8639 | 3.4351 | 2.4689 | -8.9404 | 16.9726 | 2.7944 | 2.0084 | -11.3627 | 16.4768 | 2.7128 | 1.9497 | -12.6369 | 15.5523 | 2.5606 | 1.8403 | -11.6181
LANGLEY | CHADDERTON | WHITEGATE | 386421 | 406330 | 30.8631 | 12.7545 | 9.1669 | 13.4621 | 30.9774 | 12.2619 | 8.8128 | 10.8132 | 31.1217 | 11.9647 | 8.5993 | 9.9773 | 31.2942 | 11.7779 | 8.465 | 9.5728 | 31.5049 | 11.5616 | 8.3096 | 8.9769 | 31.6752 | 11.3247 | 8.1393 | 8.3433 | 31.868 | 11.0897 | 7.9704 | 7.7328 | 32.0948 | 10.9189 | 7.8476 | 7.1803 | 32.2825 | 10.7501 | 7.7263 | 6.6091 | 32.4653 | 10.6 | 7.6184 | 6.0643 | 33.0545 | 9.9773 | 7.1709 | 3.3654 | 33.6482 | 9.232 | 6.6352 | -0.65762 | 34.0605 | 8.8058 | 6.3289 | -3.6654 | 34.4522 | 8.5411 | 6.1386 | -6.5056 | 34.783 | 8.1456 | 5.8544 | -9.1069 | 30.8385 | 12.7545 | 9.1669 | 13.4621 | 30.9249 | 12.5801 | 9.0416 | 12.5447 | 31.0097 | 12.4096 | 8.919 | 12.1871 | 31.1061 | 12.246 | 8.8014 | 11.969 | 31.2316 | 12.0817 | 8.6833 | 11.7027 | 31.3854 | 11.9432 | 8.5838 | 11.4479 | 31.5705 | 11.6723 | 8.3891 | 11.097 | 31.7865 | 11.5276 | 8.2851 | 10.5619 | 31.9264 | 11.4091 | 8.2 | 10.0761 | 32.0726 | 11.2797 | 8.1069 | 9.561 | 32.495 | 10.8818 | 7.8209 | 7.9561 | 32.8685 | 10.5142 | 7.5567 | 6.216 | 33.213 | 10.2893 | 7.3951 | 4.5155 | 33.5854 | 10.1922 | 7.3253 | 2.5214 | 33.8872 | 9.9327 | 7.1388 | 1.0143 | 30.8735 | 12.7545 | 9.1669 | 13.4621 | 31.0145 | 12.1619 | 8.741 | 10.3395 | 31.1951 | 11.7949 | 8.4773 | 9.3235 | 31.4142 | 11.5798 | 8.3226 | 8.8156 | 31.6243 | 11.3197 | 8.1357 | 8.1142 | 31.8318 | 11.0364 | 7.9321 | 7.3663 | 32.0716 | 10.7576 | 7.7317 | 6.6506 | 32.3516 | 10.5505 | 7.5829 | 5.9711 | 32.5778 | 10.3461 | 7.4359 | 5.2816 | 32.7996 | 10.1463 | 7.2923 | 4.5851 | 33.4164 | 9.3742 | 6.7374 | 1.463 | 34.0372 | 8.5469 | 6.1428 | -2.6028 | 34.4798 | 8.0788 | 5.8064 | -5.3879 | 34.8814 | 7.8138 | 5.6159 | -7.8166 | 35.1841 | 7.5638 | 5.4363 | -9.6273 | 30.8735 | 12.7545 | 9.1669 | 13.4621 | 30.8991 | 12.3711 | 8.8914 | 11.4557 | 31.0043 | 12.1478 | 8.7309 | 10.6818 | 31.1405 | 12.0044 | 8.6278 | 10.1872 | 31.3344 | 11.7925 | 8.4755 | 9.4769 | 31.5249 | 11.5483 | 8.3 | 8.706 | 31.7439 | 11.2658 | 8.097 | 7.7986 | 32.0031 | 10.9512 | 7.8708 | 6.3862 | 32.229 | 10.6259 | 7.6371 | 4.9788 | 32.4545 | 10.3034 | 7.4053 | 3.602 | 33.1479 | 9.7867 | 7.0339 | -0.32426 | 33.7775 | 8.9662 | 6.4442 | -3.8482 | 34.1576 | 8.3583 | 6.0073 | -6.0747 | 34.4592 | 8.1436 | 5.853 | -7.3688 | 34.6242 | 7.8926 | 5.6725 | -7.5407 | 30.8631 | 12.7545 | 9.1669 | 13.4621 | 30.966 | 12.4562 | 8.9525 | 11.8123 | 31.0756 | 12.2046 | 8.7717 | 11.2068 | 31.1917 | 12.0312 | 8.6471 | 10.8934 | 31.3385 | 11.862 | 8.5255 | 10.5255 | 31.5399 | 11.6745 | 8.3907 | 10.1174 | 31.7261 | 11.4745 | 8.2469 | 9.689 | 31.9319 | 11.3204 | 8.1362 | 9.2298 | 32.1016 | 11.1529 | 8.0158 | 8.6531 | 32.2726 | 10.9948 | 7.9022 | 8.0699 | 32.8187 | 10.5253 | 7.5647 | 6.16 | 33.3477 | 10.1429 | 7.2899 | 4.0516 | 33.6866 | 10.0169 | 7.1993 | 2.5723 | 34.0238 | 9.9942 | 7.183 | 0.99788 | 34.2882 | 9.8806 | 7.1014 | -0.4641 | 30.8631 | 12.7545 | 9.1669 | 13.4621 | 30.9196 | 12.1504 | 8.7328 | 10.257 | 31.0753 | 11.8648 | 8.5275 | 9.1779 | 31.271 | 11.7088 | 8.4153 | 8.5855 | 31.4876 | 11.4771 | 8.2488 | 7.7934 | 31.6722 | 11.2199 | 8.064 | 6.9689 | 31.8892 | 10.9212 | 7.8493 | 5.992 | 32.1689 | 10.5908 | 7.6118 | 4.4868 | 32.4034 | 10.251 | 7.3676 | 3.0084 | 32.6344 | 9.917 | 7.1276 | 1.5595 | 33.3283 | 9.3244 | 6.7016 | -2.593 | 33.9371 | 8.484 | 6.0976 | -6.3012 | 34.3182 | 7.8455 | 5.6387 | -8.7048 | 34.6159 | 7.5889 | 5.4543 | -10.2093 | 34.8007 | 7.2897 | 5.2392 | -10.6439
LANGROYD RD | NELSON | PADIHAM | 389077 | 440584 | 29.5871 | 13.0968 | 9.554 | 15.188 | 29.6865 | 13.1299 | 9.5781 | 15.0485 | 29.7686 | 13.1755 | 9.6114 | 14.967 | 29.877 | 13.1322 | 9.5798 | 14.8918 | 30.0175 | 12.5686 | 9.1686 | 14.717 | 30.1839 | 12.8681 | 9.3871 | 14.5238 | 30.3797 | 12.7491 | 9.3003 | 14.3571 | 30.6206 | 12.6608 | 9.2359 | 14.2101 | 30.8153 | 12.5161 | 9.1303 | 14.0278 | 30.9503 | 12.387 | 9.0361 | 13.8743 | 31.365 | 11.8691 | 8.6583 | 12.2111 | 31.8241 | 11.1781 | 8.1542 | 8.9609 | 32.1622 | 10.5714 | 7.7117 | 6.2156 | 32.4585 | 9.8886 | 7.2136 | 3.3115 | 32.6469 | 9.2747 | 6.7658 | 0.96942 | 29.5543 | 13.0968 | 9.554 | 15.188 | 29.6312 | 13.0936 | 9.5516 | 15.0502 | 29.6922 | 12.9327 | 9.4342 | 14.9422 | 29.7596 | 12.7681 | 9.3142 | 14.8294 | 29.8459 | 12.6561 | 9.2324 | 14.6705 | 29.9581 | 12.5603 | 9.1626 | 14.4868 | 30.0956 | 12.2099 | 8.9069 | 14.2349 | 30.2539 | 12.1533 | 8.8657 | 13.9027 | 30.3565 | 12.1476 | 8.8615 | 13.6527 | 30.4636 | 12.144 | 8.8589 | 13.4022 | 30.8084 | 12.0736 | 8.8075 | 12.6456 | 31.1512 | 11.9891 | 8.7459 | 11.8927 | 31.4415 | 11.8514 | 8.6454 | 11.2104 | 31.7134 | 11.2523 | 8.2084 | 10.4941 | 31.8882 | 11.5792 | 8.4468 | 10.0357 | 29.6021 | 13.0968 | 9.554 | 15.188 | 29.6975 | 13.1398 | 9.5853 | 15.0613 | 29.7894 | 13.1847 | 9.618 | 15.0005 | 29.9135 | 13.0096 | 9.4903 | 14.9623 | 30.0739 | 12.6295 | 9.213 | 14.826 | 30.2644 | 12.7866 | 9.3277 | 14.678 | 30.4904 | 12.6818 | 9.2512 | 14.5773 | 30.7687 | 12.5074 | 9.1239 | 14.4994 | 30.9141 | 12.3409 | 9.0026 | 14.4017 | 31.0494 | 12.2204 | 8.9146 | 14.3178 | 31.4974 | 11.7348 | 8.5604 | 12.872 | 31.9898 | 10.9869 | 8.0148 | 9.8094 | 32.3497 | 10.319 | 7.5276 | 7.2288 | 32.6578 | 9.5578 | 6.9723 | 4.5298 | 32.8416 | 9.0305 | 6.5876 | 2.4098 | 29.6021 | 13.0968 | 9.554 | 15.188 | 29.613 | 13.2069 | 9.6343 | 15.3698 | 29.6493 | 13.3209 | 9.7174 | 15.3977 | 29.7088 | 13.2991 | 9.7015 | 15.3984 | 29.8099 | 13.0268 | 9.5029 | 15.2779 | 29.972 | 12.8717 | 9.3897 | 15.1242 | 30.1872 | 12.9719 | 9.4628 | 14.7842 | 30.4573 | 12.7607 | 9.3087 | 13.7503 | 30.6804 | 12.3937 | 9.041 | 12.6867 | 30.8324 | 12.0688 | 8.804 | 11.6424 | 31.2882 | 11.0967 | 8.0949 | 8.6578 | 31.7477 | 10.4058 | 7.5909 | 5.7922 | 32.0772 | 9.7276 | 7.0962 | 3.4623 | 32.3103 | 9.2807 | 6.7701 | 2.0459 | 32.2953 | 9.3507 | 6.8212 | 3.3659 | 29.587 | 13.0968 | 9.554 | 15.188 | 29.6742 | 13.1446 | 9.5888 | 15.0805 | 29.7259 | 13.2013 | 9.6301 | 15.0379 | 29.7865 | 13.1797 | 9.6144 | 15.031 | 29.8729 | 12.6501 | 9.2281 | 14.9981 | 30.0125 | 12.9751 | 9.4652 | 14.935 | 30.2015 | 12.8806 | 9.3962 | 14.8385 | 30.4144 | 12.7916 | 9.3313 | 14.7124 | 30.5841 | 12.6531 | 9.2303 | 14.5108 | 30.7373 | 12.5103 | 9.1261 | 14.3113 | 31.1272 | 12.1434 | 8.8584 | 13.5763 | 31.5251 | 11.9179 | 8.6939 | 12.7263 | 31.7935 | 11.7068 | 8.5399 | 12.1549 | 32.0233 | 11.4276 | 8.3362 | 11.6319 | 32.1226 | 11.1594 | 8.1407 | 11.5232 | 29.587 | 13.0968 | 9.554 | 15.188 | 29.626 | 13.1948 | 9.6254 | 15.2935 | 29.6977 | 13.2832 | 9.6899 | 15.2397 | 29.8016 | 13.2429 | 9.6605 | 15.1503 | 29.9395 | 12.9585 | 9.453 | 14.9456 | 30.1 | 12.7702 | 9.3157 | 14.7322 | 30.2989 | 12.8749 | 9.3921 | 14.3185 | 30.5803 | 12.6271 | 9.2113 | 13.1844 | 30.8134 | 12.2392 | 8.9283 | 12.0498 | 31.0066 | 11.9104 | 8.6884 | 10.9329 | 31.4743 | 10.9088 | 7.9578 | 7.7211 | 31.9131 | 10.1705 | 7.4192 | 4.6537 | 32.2315 | 9.4501 | 6.8937 | 2.0869 | 32.4521 | 8.9075 | 6.4979 | 0.33614 | 32.4545 | 8.9321 | 6.5158 | 1.2753
LEIGH | ATHERTON | KEARSLEY | 365863 | 399907 | 19.1629 | 19.1629 | 19.1629 | 11.9483 | 19.177 | 19.177 | 19.177 | 11.1036 | 19.1914 | 19.1914 | 19.1914 | 10.9025 | 19.2088 | 19.2088 | 19.2088 | 10.8794 | 19.2361 | 19.2361 | 19.2361 | 10.827 | 19.2702 | 19.2702 | 19.2702 | 10.7682 | 19.3112 | 19.3112 | 19.3112 | 10.7206 | 19.3611 | 19.3611 | 19.3611 | 10.6798 | 19.4014 | 19.4014 | 19.4014 | 10.6162 | 19.4413 | 19.4413 | 19.4413 | 10.5607 | 19.6134 | 19.6134 | 19.6134 | 9.9161 | 19.8419 | 19.8419 | 19.6088 | 8.6471 | 20.0189 | 20.0189 | 19.5223 | 7.57 | 20.1886 | 20.1886 | 19.7059 | 6.4183 | 20.3108 | 20.3108 | 19.5844 | 5.4754 | 19.1605 | 19.1605 | 19.1605 | 11.9483 | 19.1793 | 19.1793 | 19.1793 | 11.6609 | 19.1979 | 19.1979 | 19.1979 | 11.5562 | 19.2199 | 19.2199 | 19.2199 | 11.5101 | 19.2502 | 19.2502 | 19.2502 | 11.4557 | 19.2879 | 19.2879 | 19.2879 | 11.3985 | 19.3357 | 19.3357 | 19.3357 | 11.3187 | 19.3934 | 19.3934 | 19.3934 | 11.211 | 19.416 | 19.416 | 19.416 | 11.1295 | 19.44 | 19.44 | 19.44 | 11.0442 | 19.521 | 19.521 | 19.521 | 10.7845 | 19.6114 | 19.6114 | 19.6114 | 10.5146 | 19.6979 | 19.6979 | 19.6979 | 10.2667 | 19.7883 | 19.7883 | 19.7883 | 10.0038 | 19.8503 | 19.8503 | 19.8503 | 9.8205 | 19.1639 | 19.1639 | 19.1639 | 11.9483 | 19.1796 | 19.1796 | 19.1796 | 10.9764 | 19.1959 | 19.1959 | 19.1959 | 10.7546 | 19.2162 | 19.2162 | 19.2162 | 10.7442 | 19.2466 | 19.2466 | 19.2466 | 10.7023 | 19.284 | 19.284 | 19.284 | 10.6553 | 19.3293 | 19.3293 | 19.3293 | 10.6271 | 19.3836 | 19.3836 | 19.3836 | 10.6046 | 19.4249 | 19.4249 | 19.4249 | 10.5767 | 19.4652 | 19.4652 | 19.4652 | 10.5477 | 19.6445 | 19.6445 | 19.6445 | 9.9843 | 19.8856 | 19.8856 | 19.5607 | 8.783 | 20.0729 | 20.0729 | 19.4133 | 7.7709 | 20.2473 | 20.2473 | 19.5796 | 6.6866 | 20.3483 | 20.3483 | 19.4531 | 5.8522 | 19.1639 | 19.1639 | 19.1639 | 11.9483 | 19.1447 | 19.1447 | 19.1447 | 11.3564 | 19.1449 | 19.1449 | 19.1449 | 11.2205 | 19.1494 | 19.1494 | 19.1494 | 11.2254 | 19.1663 | 19.1663 | 19.1663 | 11.1906 | 19.1955 | 19.1955 | 19.1955 | 11.1446 | 19.2432 | 19.2432 | 19.2432 | 11.026 | 19.3258 | 19.3258 | 19.3258 | 10.6306 | 19.4026 | 19.4026 | 19.4026 | 10.2211 | 19.4794 | 19.4794 | 19.4794 | 9.8112 | 19.7108 | 19.7108 | 19.7108 | 8.6334 | 19.9327 | 19.9327 | 19.7738 | 7.4996 | 20.0992 | 20.0992 | 19.5974 | 6.5653 | 20.2093 | 20.2093 | 19.539 | 5.9892 | 20.1686 | 20.1686 | 19.5228 | 6.535 | 19.1629 | 19.1629 | 19.1629 | 11.9483 | 19.175 | 19.175 | 19.175 | 11.4424 | 19.1839 | 19.1839 | 19.1839 | 11.3199 | 19.1921 | 19.1921 | 19.1921 | 11.3183 | 19.207 | 19.207 | 19.207 | 11.3144 | 19.2325 | 19.2325 | 19.2325 | 11.3041 | 19.2691 | 19.2691 | 19.2691 | 11.2842 | 19.3118 | 19.3118 | 19.3118 | 11.2543 | 19.3463 | 19.3463 | 19.3463 | 11.1885 | 19.382 | 19.382 | 19.382 | 11.1227 | 19.5043 | 19.5043 | 19.5043 | 10.8786 | 19.6335 | 19.6335 | 19.6335 | 10.5953 | 19.7254 | 19.7254 | 19.7254 | 10.4049 | 19.8031 | 19.8031 | 19.8031 | 10.2331 | 19.8417 | 19.8417 | 19.8417 | 10.2074 | 19.1629 | 19.1629 | 19.1629 | 11.9483 | 19.1512 | 19.1512 | 19.1512 | 10.9345 | 19.1619 | 19.1619 | 19.1619 | 10.6912 | 19.1788 | 19.1788 | 19.1788 | 10.6675 | 19.2065 | 19.2065 | 19.2065 | 10.6062 | 19.2396 | 19.2396 | 19.2396 | 10.542 | 19.2884 | 19.2884 | 19.2884 | 10.4005 | 19.3774 | 19.3774 | 19.3774 | 9.9757 | 19.4553 | 19.4553 | 19.4553 | 9.5486 | 19.5327 | 19.5327 | 19.5327 | 9.1201 | 19.7661 | 19.7661 | 19.7661 | 7.8784 | 19.99 | 19.99 | 19.6637 | 6.6893 | 20.1633 | 20.1633 | 19.4773 | 5.6825 | 20.2837 | 20.2837 | 19.4059 | 4.9977 | 20.2508 | 20.2508 | 19.3611 | 5.4111
LEVENSHULME | LONGSIGHT | BREDBURY | 387494 | 394155 | 24.1024 | 14.2947 | 10.4278 | 6.525 | 24.239 | 13.904 | 10.1428 | 5.199 | 24.4006 | 13.6614 | 9.9658 | 4.7275 | 24.535 | 13.4007 | 9.7756 | 4.4529 | 24.7194 | 13.1019 | 9.5576 | 4.0329 | 24.9364 | 12.7414 | 9.2947 | 3.5854 | 25.1845 | 12.3798 | 9.0309 | 3.1659 | 25.4733 | 12.0408 | 8.7836 | 2.7335 | 25.7231 | 11.8245 | 8.6258 | 2.2466 | 25.9776 | 11.7392 | 8.5636 | 1.7785 | 26.779 | 11.0942 | 8.093 | -0.80645 | 27.5367 | 10.3239 | 7.5311 | -4.6256 | 28.0502 | 9.7689 | 7.1263 | -7.4183 | 28.4542 | 9.3591 | 6.8274 | -9.8194 | 28.6868 | 9.095 | 6.6347 | -11.2258 | 24.0721 | 14.2947 | 10.4278 | 6.525 | 24.1914 | 14.0885 | 10.2774 | 6.126 | 24.3056 | 13.9729 | 10.193 | 5.9202 | 24.4017 | 13.7409 | 10.0238 | 5.741 | 24.5137 | 13.4781 | 9.8321 | 5.4942 | 24.6483 | 13.1846 | 9.618 | 5.2373 | 24.8194 | 12.8052 | 9.3412 | 4.896 | 25.0279 | 12.6695 | 9.2422 | 4.4574 | 25.14 | 12.5496 | 9.1548 | 4.121 | 25.2643 | 12.4176 | 9.0585 | 3.72 | 25.6998 | 12.0485 | 8.7892 | 2.4973 | 26.1987 | 11.7573 | 8.5768 | 1.2785 | 26.6826 | 11.4942 | 8.3849 | 0.1706 | 27.1596 | 11.3147 | 8.2539 | -0.93659 | 27.4742 | 11.0793 | 8.0822 | -1.6284 | 24.1138 | 14.2947 | 10.4278 | 6.525 | 24.2743 | 13.8608 | 10.1113 | 4.9116 | 24.4713 | 13.5191 | 9.862 | 4.285 | 24.6558 | 13.2182 | 9.6425 | 3.8923 | 24.8887 | 12.8744 | 9.3917 | 3.2898 | 25.157 | 12.4508 | 9.0827 | 2.6572 | 25.4389 | 11.9796 | 8.739 | 2.0652 | 25.752 | 11.7387 | 8.5632 | 1.4674 | 26.0092 | 11.4012 | 8.317 | 0.73346 | 26.2745 | 11.2678 | 8.2197 | 0.076454 | 27.1908 | 10.4597 | 7.6302 | -2.9179 | 28.103 | 9.6291 | 7.0243 | -6.6991 | 28.7317 | 9.0778 | 6.6222 | -9.1342 | 29.2171 | 8.7042 | 6.3496 | -10.9174 | 29.4686 | 8.561 | 6.2451 | -11.2713 | 24.1139 | 14.2947 | 10.4278 | 6.525 | 24.1511 | 14.0206 | 10.2279 | 5.6409 | 24.2578 | 13.8741 | 10.121 | 5.1931 | 24.4072 | 13.6688 | 9.9712 | 4.8482 | 24.575 | 13.4611 | 9.8197 | 4.2608 | 24.8026 | 13.1773 | 9.6127 | 3.6165 | 25.0858 | 12.9024 | 9.4121 | 2.772 | 25.3962 | 12.4873 | 9.1093 | 1.2194 | 25.6815 | 12.0759 | 8.8092 | -0.37783 | 25.9756 | 11.7133 | 8.5447 | -1.8276 | 26.8804 | 10.6132 | 7.7422 | -5.6841 | 27.693 | 9.9411 | 7.2519 | -8.7216 | 28.2217 | 9.4045 | 6.8605 | -10.4947 | 28.5973 | 9.1436 | 6.6701 | -10.9412 | 28.7198 | 9.1457 | 6.6716 | -9.5333 | 24.1023 | 14.2947 | 10.4278 | 6.525 | 24.2196 | 14.0158 | 10.2244 | 5.8477 | 24.3354 | 13.8441 | 10.0991 | 5.5492 | 24.4485 | 13.5999 | 9.921 | 5.3685 | 24.5659 | 13.3438 | 9.7341 | 5.143 | 24.7293 | 13.014 | 9.4935 | 4.8918 | 24.9398 | 12.6767 | 9.2475 | 4.605 | 25.1838 | 12.3539 | 9.012 | 4.2572 | 25.4007 | 12.1287 | 8.8477 | 3.7877 | 25.6318 | 12.0503 | 8.7905 | 3.3044 | 26.4129 | 11.5864 | 8.4521 | 1.6999 | 27.1144 | 11.2185 | 8.1838 | 0.10173 | 27.6068 | 10.9699 | 8.0024 | -1.0202 | 28.0084 | 10.8296 | 7.9001 | -2.0668 | 28.2207 | 10.7534 | 7.8445 | -2.5578 | 24.1023 | 14.2947 | 10.4278 | 6.525 | 24.1777 | 13.8984 | 10.1387 | 5.0391 | 24.3455 | 13.6985 | 9.9928 | 4.3847 | 24.5231 | 13.4549 | 9.8152 | 3.9298 | 24.7462 | 13.235 | 9.6547 | 3.2427 | 24.9886 | 12.9351 | 9.436 | 2.5313 | 25.2606 | 12.6476 | 9.2262 | 1.6033 | 25.59 | 12.2131 | 8.9093 | -0.059837 | 25.8697 | 11.7982 | 8.6066 | -1.7302 | 26.1574 | 11.4108 | 8.324 | -3.2567 | 27.065 | 10.2873 | 7.5045 | -7.3876 | 27.8975 | 9.5097 | 6.9372 | -10.7776 | 28.4627 | 8.9201 | 6.5071 | -12.8302 | 28.8588 | 8.605 | 6.2772 | -13.579 | 29.0222 | 8.551 | 6.2379 | -12.4794
LEYLAND NATIONAL | STAINBURN & SIDDICK | HARKER / HUTTON | 301973 | 525948 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 7.7436 | 1.2749 | 0.91631 | 7.7436 | 12.2041 | 2.3546 | 1.6923 | 12.2041 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 3.8973 | 0.64166 | 0.46118 | 3.8973 | 8.2111 | 1.3519 | 0.97163 | 8.2111 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 11.035 | 3.406 | 2.448 | 11.035 | 11.4302 | 2.74 | 1.9693 | 11.4302 | 11.7014 | 2.1948 | 1.5774 | 11.7014 | 10.5037 | 1.7294 | 1.2429 | 10.5037 | 8.8607 | 1.4588 | 1.0485 | 8.8607 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 11.1497 | 1.8357 | 1.3194 | 11.1497 | 11.738 | 2.5542 | 1.8358 | 11.738 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 11.2288 | 3.3623 | 2.4165 | 11.2288 | 11.658 | 2.7485 | 1.9754 | 11.658 | 11.9626 | 2.1919 | 1.5754 | 11.9626 | 10.2429 | 1.6864 | 1.2121 | 10.2429 | 8.2852 | 1.3641 | 0.9804 | 8.2852
LITTLE HULTON | KEARSLEY LOCAL | KEARSLEY | 372024 | 403826 | 22.1288 | 12.8753 | 9.2537 | 8.1851 | 22.2024 | 12.6314 | 9.0784 | 6.9155 | 22.2647 | 12.3175 | 8.8528 | 6.2744 | 22.363 | 12.2386 | 8.7961 | 5.8743 | 22.5385 | 12.0006 | 8.6251 | 5.2644 | 22.763 | 11.7615 | 8.4532 | 4.543 | 23.0381 | 11.3414 | 8.1513 | 3.8294 | 23.3683 | 11.0868 | 7.9683 | 3.1687 | 23.7102 | 10.8838 | 7.8224 | 2.5886 | 24.0775 | 10.6869 | 7.6809 | 2.1204 | 25.4102 | 9.9265 | 7.1344 | -0.52832 | 26.4215 | 8.953 | 6.4347 | -4.6728 | 27.0978 | 8.1431 | 5.8526 | -7.9917 | 27.616 | 7.3015 | 5.2478 | -11.1083 | 27.9823 | 6.4836 | 4.6599 | -14.2036 | 22.1226 | 12.8753 | 9.2537 | 8.1851 | 22.1819 | 12.7813 | 9.1862 | 7.7173 | 22.2175 | 12.7336 | 9.1519 | 7.5383 | 22.2695 | 12.6735 | 9.1087 | 7.4142 | 22.3532 | 12.5726 | 9.0362 | 7.2303 | 22.4595 | 12.3758 | 8.8947 | 7.0243 | 22.6036 | 12.318 | 8.8532 | 6.7226 | 22.7933 | 12.1951 | 8.7649 | 6.2736 | 22.9545 | 12.1365 | 8.7227 | 5.8759 | 23.1366 | 12.0352 | 8.6499 | 5.4643 | 23.822 | 11.688 | 8.4004 | 4.1338 | 24.6812 | 11.3008 | 8.1221 | 2.469 | 25.565 | 10.8066 | 7.7669 | 0.69896 | 26.5254 | 10.193 | 7.3259 | -1.3111 | 27.1669 | 9.6983 | 6.9704 | -2.5768 | 22.1315 | 12.8753 | 9.2537 | 8.1851 | 22.2065 | 12.5744 | 9.0375 | 6.7527 | 22.2711 | 12.3354 | 8.8657 | 6.1006 | 22.3704 | 12.1466 | 8.73 | 5.7424 | 22.5439 | 11.9266 | 8.5719 | 5.1814 | 22.7607 | 11.587 | 8.3278 | 4.521 | 23.0216 | 11.1678 | 8.0265 | 3.8996 | 23.3276 | 10.8639 | 7.8081 | 3.3402 | 23.6327 | 10.707 | 7.6953 | 2.8718 | 23.9658 | 10.5029 | 7.5486 | 2.5033 | 25.2894 | 9.6971 | 6.9695 | 0.12608 | 26.409 | 8.7327 | 6.2763 | -3.9258 | 27.197 | 7.9046 | 5.6812 | -7.1524 | 27.7754 | 6.9654 | 5.0062 | -10.1471 | 28.1311 | 6.2143 | 4.4663 | -13.0692 | 22.1315 | 12.8753 | 9.2537 | 8.1851 | 22.0921 | 12.7125 | 9.1367 | 7.4683 | 22.1153 | 12.5259 | 9.0026 | 6.9779 | 22.1857 | 12.32 | 8.8546 | 6.6383 | 22.3427 | 12.0537 | 8.6633 | 6.0612 | 22.5678 | 11.6058 | 8.3413 | 5.3573 | 22.8903 | 11.1409 | 8.0072 | 4.4909 | 23.3917 | 10.6782 | 7.6747 | 3.012 | 23.8555 | 10.2829 | 7.3905 | 1.5688 | 24.2142 | 9.9077 | 7.1209 | 0.21274 | 25.3393 | 8.8091 | 6.3313 | -3.7957 | 26.3291 | 7.8929 | 5.6728 | -7.5784 | 26.9771 | 7.1667 | 5.1509 | -10.5006 | 27.3924 | 6.5811 | 4.73 | -12.1637 | 27.4564 | 6.4866 | 4.6621 | -11.4928 | 22.1288 | 12.8753 | 9.2537 | 8.1851 | 22.1893 | 12.7297 | 9.1491 | 7.425 | 22.2298 | 12.4616 | 8.9564 | 6.922 | 22.2825 | 12.3877 | 8.9033 | 6.6374 | 22.3768 | 12.1902 | 8.7613 | 6.2993 | 22.5228 | 12.0334 | 8.6486 | 5.8566 | 22.7259 | 11.6561 | 8.3775 | 5.3682 | 22.9814 | 11.4331 | 8.2172 | 4.8374 | 23.2627 | 11.2229 | 8.0661 | 4.3008 | 23.5762 | 11.0671 | 7.9541 | 3.8468 | 24.6948 | 10.508 | 7.5523 | 2.2765 | 25.8302 | 9.9469 | 7.149 | 0.23428 | 26.4944 | 9.4927 | 6.8226 | -1.2007 | 26.9571 | 8.9975 | 6.4667 | -2.4204 | 27.1799 | 8.6046 | 6.1843 | -3.0934 | 22.1288 | 12.8753 | 9.2537 | 8.1851 | 22.1046 | 12.5911 | 9.0494 | 6.8668 | 22.1525 | 12.3726 | 8.8925 | 6.1873 | 22.2496 | 12.1448 | 8.7287 | 5.7612 | 22.4235 | 11.8368 | 8.5074 | 5.1085 | 22.6351 | 11.4271 | 8.2129 | 4.3608 | 22.9259 | 10.9164 | 7.8459 | 3.4414 | 23.4032 | 10.4386 | 7.5024 | 1.8945 | 23.8706 | 10.0297 | 7.2085 | 0.4131 | 24.2322 | 9.6483 | 6.9345 | -0.98328 | 25.3542 | 8.5128 | 6.1183 | -5.1851 | 26.4346 | 7.5193 | 5.4043 | -9.2471 | 27.1876 | 6.7506 | 4.8518 | -12.4572 | 27.6612 | 6.1105 | 4.3918 | -14.413 | 27.7872 | 5.9602 | 4.2837 | -14.0281
LITTLE SALKELD | PENRITH & SHAP | HARKER / HUTTON | 356221 | 537513 | 15.8554 | 15.8554 | 15.8554 | 8.9416 | 15.9632 | 15.9632 | 15.9632 | 8.7748 | 16.1046 | 16.1046 | 16.1046 | 8.6554 | 16.1913 | 16.1913 | 16.1913 | 8.5566 | 16.2562 | 16.2562 | 16.2562 | 8.3737 | 16.3281 | 16.3281 | 16.3281 | 8.1695 | 16.4062 | 16.4062 | 16.4062 | 7.9846 | 16.4979 | 16.4979 | 16.4979 | 7.819 | 16.5812 | 16.5812 | 16.5812 | 7.6438 | 16.6619 | 16.6619 | 16.6619 | 7.497 | 16.9427 | 16.9427 | 16.5903 | 6.6298 | 17.2574 | 17.2574 | 16.3074 | 5.3824 | 17.4868 | 17.4868 | 16.0428 | 4.4753 | 17.6806 | 17.6806 | 15.7538 | 3.8617 | 17.8394 | 17.8394 | 15.4511 | 3.3344 | 15.8478 | 15.8478 | 15.8478 | 8.9416 | 15.925 | 15.925 | 15.925 | 8.8202 | 16.0009 | 16.0009 | 16.0009 | 8.6696 | 16.1104 | 16.1104 | 16.1104 | 8.5076 | 16.2578 | 16.2578 | 16.2578 | 8.3227 | 16.3367 | 16.3367 | 16.3367 | 8.1834 | 16.4291 | 16.4291 | 16.4291 | 8.0167 | 16.5303 | 16.5303 | 16.5303 | 7.8179 | 16.5869 | 16.5869 | 16.5869 | 7.6553 | 16.6456 | 16.6456 | 16.6456 | 7.4845 | 16.8273 | 16.8273 | 16.8273 | 6.967 | 17.0035 | 17.0035 | 17.0035 | 6.4797 | 17.17 | 17.17 | 17.1617 | 5.9217 | 17.3542 | 17.3542 | 16.9268 | 5.1022 | 17.4693 | 17.4693 | 16.6365 | 4.2855 | 15.8594 | 15.8594 | 15.8594 | 8.9416 | 15.9644 | 15.9644 | 15.9644 | 8.7736 | 16.1033 | 16.1033 | 16.1033 | 8.6657 | 16.1921 | 16.1921 | 16.1921 | 8.5924 | 16.2564 | 16.2564 | 16.2564 | 8.4393 | 16.327 | 16.327 | 16.327 | 8.2731 | 16.4035 | 16.4035 | 16.4035 | 8.1367 | 16.4923 | 16.4923 | 16.4923 | 8.0273 | 16.5726 | 16.5726 | 16.5726 | 7.8308 | 16.6492 | 16.6492 | 16.5754 | 7.517 | 16.9251 | 16.9251 | 16.1697 | 6.3052 | 17.2423 | 17.2423 | 15.7528 | 4.9275 | 17.4742 | 17.4742 | 15.3636 | 3.9157 | 17.6635 | 17.6635 | 14.9433 | 3.2416 | 17.8096 | 17.8096 | 14.5575 | 2.7172 | 15.8594 | 15.8594 | 15.8594 | 8.9416 | 15.916 | 15.916 | 15.916 | 8.8839 | 15.9985 | 15.9985 | 15.9985 | 8.7881 | 16.1056 | 16.1056 | 16.1056 | 8.6208 | 16.1541 | 16.1541 | 16.1541 | 8.4375 | 16.217 | 16.217 | 16.217 | 8.2435 | 16.2965 | 16.2965 | 16.2965 | 8.0321 | 16.4016 | 16.4016 | 16.4016 | 7.7157 | 16.5066 | 16.5066 | 16.3468 | 7.3572 | 16.6109 | 16.6109 | 16.1549 | 6.9911 | 16.9234 | 16.9234 | 15.746 | 5.9343 | 17.2235 | 17.2235 | 15.3538 | 4.7088 | 17.4322 | 17.4322 | 14.9724 | 3.8847 | 17.5687 | 17.5687 | 14.5842 | 3.4593 | 17.5829 | 17.5829 | 14.2642 | 3.5212 | 15.8553 | 15.8553 | 15.8553 | 8.9416 | 15.9431 | 15.9431 | 15.9431 | 8.8374 | 16.0396 | 16.0396 | 16.0396 | 8.7241 | 16.1565 | 16.1565 | 16.1565 | 8.6182 | 16.1992 | 16.1992 | 16.1992 | 8.4949 | 16.2583 | 16.2583 | 16.2583 | 8.41 | 16.3322 | 16.3322 | 16.3322 | 8.3332 | 16.4132 | 16.4132 | 16.4132 | 8.2512 | 16.4858 | 16.4858 | 16.4858 | 8.1185 | 16.5599 | 16.5599 | 16.5599 | 7.9855 | 16.8085 | 16.8085 | 16.6974 | 7.325 | 17.0723 | 17.0723 | 16.43 | 6.1462 | 17.2557 | 17.2557 | 16.1808 | 5.3176 | 17.4142 | 17.4142 | 15.8804 | 4.559 | 17.4946 | 17.4946 | 15.5914 | 4.0877 | 15.8553 | 15.8553 | 15.8553 | 8.9416 | 15.9417 | 15.9417 | 15.9417 | 8.8084 | 16.0779 | 16.0779 | 16.0779 | 8.6607 | 16.1739 | 16.1739 | 16.1739 | 8.4422 | 16.2419 | 16.2419 | 16.2419 | 8.2109 | 16.3142 | 16.3142 | 16.3142 | 7.9789 | 16.3998 | 16.3998 | 16.3998 | 7.7255 | 16.5222 | 16.5222 | 16.5024 | 7.3535 | 16.6381 | 16.6381 | 16.2893 | 6.9591 | 16.7518 | 16.7518 | 16.0938 | 6.5572 | 17.0876 | 17.0876 | 15.6679 | 5.3804 | 17.3998 | 17.3998 | 15.2908 | 4.2983 | 17.6191 | 17.6191 | 14.8555 | 3.6046 | 17.7569 | 17.7569 | 14.542 | 3.4123 | 17.7783 | 17.7783 | 14.2531 | 3.566
LITTLEBOROUGH | BELFIELD | ROCHDALE | 393221 | 416124 | 24.3799 | 10.5064 | 7.6643 | 7.4275 | 24.4298 | 10.3024 | 7.5155 | 6.8046 | 24.4978 | 10.0847 | 7.3567 | 6.5699 | 24.5734 | 10.0777 | 7.3515 | 6.4622 | 24.6664 | 9.9204 | 7.2368 | 6.2899 | 24.7761 | 9.7501 | 7.1126 | 6.1072 | 24.907 | 9.5842 | 6.9916 | 5.9433 | 25.0683 | 9.4302 | 6.8792 | 5.7872 | 25.2007 | 9.3274 | 6.8042 | 5.5549 | 25.3279 | 9.2216 | 6.727 | 5.3451 | 25.7443 | 8.7639 | 6.3931 | 3.7249 | 26.1921 | 8.0303 | 5.858 | 0.77203 | 26.5196 | 7.5555 | 5.5117 | -1.7136 | 26.812 | 7.0034 | 5.1089 | -4.4035 | 27.0114 | 6.445 | 4.7015 | -6.6764 | 24.3698 | 10.5064 | 7.6643 | 7.4275 | 24.4239 | 10.3933 | 7.5818 | 7.1486 | 24.4868 | 10.3228 | 7.5303 | 6.9766 | 24.559 | 10.2373 | 7.468 | 6.847 | 24.6551 | 10.1558 | 7.4085 | 6.6833 | 24.7784 | 10.093 | 7.3627 | 6.4946 | 24.9278 | 9.8838 | 7.2101 | 6.2432 | 25.0987 | 9.7835 | 7.1369 | 5.913 | 25.1926 | 9.6831 | 7.0637 | 5.6 | 25.2793 | 9.5869 | 6.9935 | 5.2842 | 25.5498 | 9.28 | 6.7697 | 4.3338 | 25.821 | 8.9564 | 6.5336 | 3.3677 | 26.0627 | 8.851 | 6.4567 | 2.4583 | 26.308 | 8.5812 | 6.2599 | 1.4551 | 26.4888 | 8.2785 | 6.0391 | 0.73007 | 24.3842 | 10.5064 | 7.6643 | 7.4275 | 24.4391 | 10.2705 | 7.4922 | 6.7418 | 24.5141 | 10.0086 | 7.3011 | 6.5146 | 24.6004 | 9.9488 | 7.2575 | 6.1788 | 24.706 | 9.7391 | 7.1046 | 5.7784 | 24.8307 | 9.5101 | 6.9375 | 5.3741 | 24.9804 | 9.3092 | 6.791 | 5.071 | 25.1634 | 9.137 | 6.6653 | 4.9903 | 25.3037 | 9.0357 | 6.5914 | 4.8596 | 25.437 | 8.9249 | 6.5106 | 4.7311 | 25.8778 | 8.3593 | 6.098 | 3.3627 | 26.3522 | 7.8144 | 5.7005 | 0.63064 | 26.6947 | 7.269 | 5.3026 | -1.6552 | 26.9852 | 6.6284 | 4.8353 | -4.1016 | 27.1614 | 6.0683 | 4.4268 | -6.0908 | 24.3842 | 10.5064 | 7.6643 | 7.4275 | 24.3506 | 10.3503 | 7.5504 | 7.1928 | 24.3746 | 10.1897 | 7.4333 | 7.0824 | 24.4062 | 10.0905 | 7.3609 | 6.7799 | 24.4628 | 9.861 | 7.1935 | 6.3852 | 24.5587 | 9.5735 | 6.9837 | 5.9625 | 24.6906 | 9.1472 | 6.6728 | 5.4536 | 24.8596 | 8.9696 | 6.5432 | 4.5968 | 25.0062 | 8.7239 | 6.364 | 3.6866 | 25.1505 | 8.5009 | 6.2013 | 2.7765 | 25.59 | 7.8764 | 5.7457 | 0.14381 | 26.0339 | 7.2587 | 5.2951 | -2.4338 | 26.3475 | 6.7156 | 4.8989 | -4.5157 | 26.5787 | 6.2701 | 4.574 | -5.8841 | 26.6011 | 6.238 | 4.5506 | -4.9997 | 24.3799 | 10.5064 | 7.6643 | 7.4275 | 24.4231 | 10.3537 | 7.5529 | 7.0355 | 24.4703 | 10.1666 | 7.4164 | 6.8829 | 24.5141 | 10.1562 | 7.4088 | 6.8405 | 24.5728 | 10.0293 | 7.3162 | 6.7844 | 24.6686 | 9.8841 | 7.2103 | 6.6947 | 24.7993 | 9.7295 | 7.0976 | 6.5778 | 24.9446 | 9.5785 | 6.9874 | 6.451 | 25.0608 | 9.4766 | 6.913 | 6.2236 | 25.1765 | 9.3706 | 6.8357 | 6.0026 | 25.5479 | 9.0552 | 6.6057 | 5.2301 | 25.9352 | 8.6972 | 6.3445 | 4.175 | 26.2157 | 8.5294 | 6.2221 | 3.4055 | 26.4616 | 8.3084 | 6.0608 | 2.7019 | 26.5979 | 8.0927 | 5.9035 | 2.3179 | 24.3799 | 10.5064 | 7.6643 | 7.4275 | 24.3711 | 10.2844 | 7.5023 | 6.8847 | 24.4304 | 10.1036 | 7.3704 | 6.645 | 24.5038 | 9.9821 | 7.2818 | 6.2541 | 24.5969 | 9.7332 | 7.1002 | 5.7784 | 24.7041 | 9.4346 | 6.8824 | 5.3005 | 24.8387 | 8.991 | 6.5588 | 4.7225 | 25.0307 | 8.8029 | 6.4216 | 3.7717 | 25.1868 | 8.5364 | 6.2272 | 2.7919 | 25.3382 | 8.3098 | 6.0619 | 1.8119 | 25.7828 | 7.6442 | 5.5763 | -1.0359 | 26.2032 | 6.9895 | 5.0988 | -3.7971 | 26.5026 | 6.4096 | 4.6757 | -6.0655 | 26.7123 | 5.9197 | 4.3184 | -7.6765 | 26.7403 | 5.8374 | 4.2583 | -7.072
LONGFORD BRIDGE | STRETFORD | SOUTH MANCHESTER | 380056 | 395083 | 30.266 | 7.6523 | 5.5822 | 15.7246 | 30.3783 | 7.3946 | 5.3942 | 14.4981 | 30.5025 | 7.1767 | 5.2353 | 13.5012 | 30.6402 | 7.0001 | 5.1065 | 12.858 | 30.7605 | 6.8523 | 4.9986 | 12.4218 | 30.9 | 6.6654 | 4.8623 | 11.965 | 31.0322 | 6.4891 | 4.7337 | 11.5246 | 31.1758 | 6.3365 | 4.6224 | 11.1192 | 31.2881 | 6.1788 | 4.5074 | 10.7106 | 31.3956 | 6.0402 | 4.4063 | 10.3255 | 31.8682 | 5.5988 | 4.0842 | 8.5176 | 31.7845 | 5.1558 | 3.7611 | 5.7785 | 30.9929 | 5.0274 | 3.6674 | 3.7073 | 31.7166 | 5.1447 | 3.753 | 1.7918 | 31.1099 | 5.0463 | 3.6812 | 0.43486 | 30.2329 | 7.6523 | 5.5822 | 15.7246 | 30.2944 | 7.5616 | 5.5161 | 15.311 | 30.3436 | 7.4532 | 5.437 | 15.0308 | 30.4176 | 7.3399 | 5.3544 | 14.8489 | 30.522 | 7.2048 | 5.2558 | 14.6222 | 30.6261 | 7.1225 | 5.1957 | 14.4077 | 30.7551 | 6.882 | 5.0203 | 14.1402 | 30.9091 | 6.7928 | 4.9552 | 13.8154 | 30.9987 | 6.7129 | 4.897 | 13.5462 | 31.096 | 6.6362 | 4.841 | 13.2662 | 31.3532 | 6.4233 | 4.6857 | 12.5163 | 31.598 | 6.2793 | 4.5806 | 11.8019 | 31.8263 | 6.2983 | 4.5945 | 11.0843 | 32.0644 | 6.515 | 4.7526 | 10.2782 | 32.2446 | 6.5217 | 4.7575 | 9.6753 | 30.2782 | 7.6523 | 5.5822 | 15.7246 | 30.4383 | 7.3402 | 5.3546 | 14.2521 | 30.6001 | 7.0277 | 5.1266 | 12.843 | 30.732 | 6.764 | 4.9342 | 11.8225 | 30.8775 | 6.5392 | 4.7702 | 11.0044 | 31.021 | 6.2829 | 4.5833 | 10.1629 | 31.1817 | 6.0295 | 4.3984 | 9.3473 | 31.3612 | 5.7922 | 4.2253 | 8.5524 | 31.5007 | 5.5611 | 4.0567 | 7.7632 | 31.6362 | 5.3273 | 3.8862 | 6.9746 | 28.6145 | 4.6415 | 3.3859 | 4.0289 | 24.7401 | 4.0131 | 2.9275 | 0.52674 | 23.2536 | 3.772 | 2.7516 | -1.95 | 24.2506 | 3.9337 | 2.8696 | -3.2343 | 24.2849 | 3.9393 | 2.8736 | -3.7045 | 30.2782 | 7.6523 | 5.5822 | 15.7246 | 30.3256 | 7.4647 | 5.4454 | 14.8845 | 30.4489 | 7.2266 | 5.2717 | 13.6203 | 30.5315 | 6.9921 | 5.1006 | 12.6221 | 30.6394 | 6.8074 | 4.9659 | 11.8022 | 30.7957 | 6.6019 | 4.816 | 10.9399 | 30.9835 | 6.3592 | 4.639 | 9.9426 | 31.2294 | 6.105 | 4.4535 | 8.4701 | 31.4281 | 5.8416 | 4.2614 | 7.0215 | 31.6258 | 5.587 | 4.0757 | 5.6105 | 32.1797 | 5.6807 | 4.144 | 1.9072 | 30.4742 | 4.9432 | 3.606 | -1.1327 | 27.1903 | 4.4105 | 3.2174 | -3.106 | 26.5978 | 4.3144 | 3.1473 | -3.3641 | 26.4678 | 4.2933 | 3.1319 | -2.3461 | 30.266 | 7.6523 | 5.5822 | 15.7246 | 30.3662 | 7.5009 | 5.4718 | 14.9975 | 30.4638 | 7.3154 | 5.3365 | 14.135 | 30.5728 | 7.1538 | 5.2186 | 13.5622 | 30.654 | 7.0332 | 5.1306 | 13.2606 | 30.776 | 6.8703 | 5.0118 | 12.9411 | 30.8891 | 6.7133 | 4.8972 | 12.6086 | 31.009 | 6.574 | 4.7957 | 12.2589 | 31.1085 | 6.4153 | 4.6799 | 11.8542 | 31.2098 | 6.2755 | 4.5779 | 11.4449 | 31.5482 | 5.9712 | 4.3559 | 10.3902 | 31.9074 | 5.8347 | 4.2563 | 9.3454 | 32.1681 | 5.9522 | 4.3421 | 8.5779 | 32.4152 | 6.3134 | 4.6055 | 7.8239 | 32.575 | 6.4191 | 4.6826 | 7.3493 | 30.266 | 7.6523 | 5.5822 | 15.7246 | 30.3433 | 7.349 | 5.361 | 14.3121 | 30.5094 | 7.0689 | 5.1567 | 12.871 | 30.6287 | 6.8185 | 4.974 | 11.7932 | 30.7722 | 6.6209 | 4.8298 | 10.9021 | 30.9223 | 6.4068 | 4.6737 | 9.9938 | 31.0969 | 6.1521 | 4.4878 | 8.9373 | 31.373 | 5.8821 | 4.2909 | 7.3846 | 31.5885 | 5.609 | 4.0917 | 5.8776 | 31.7916 | 5.3427 | 3.8974 | 4.4072 | 32.3316 | 5.3953 | 3.9358 | 0.53413 | 28.5167 | 4.6257 | 3.3744 | -2.6474 | 25.0391 | 4.0616 | 2.9629 | -4.7722 | 24.2136 | 3.9277 | 2.8652 | -5.2188 | 23.94 | 3.8833 | 2.8328 | -4.3231
LONGRIDGE | PRESTON EAST | PENWORTHAM EAST / ROCHDALE | 360581 | 437001 | 29.9914 | 15.0037 | 10.945 | 15.3677 | 30.0896 | 14.7329 | 10.7475 | 14.0878 | 30.2114 | 14.5406 | 10.6072 | 13.71 | 30.3644 | 14.4308 | 10.5271 | 13.5398 | 30.5581 | 14.2554 | 10.3991 | 13.2757 | 30.7349 | 13.9591 | 10.183 | 12.995 | 30.9199 | 13.7884 | 10.0584 | 12.7235 | 31.1518 | 13.7517 | 10.0317 | 12.4564 | 31.3737 | 13.6438 | 9.9529 | 12.1648 | 31.5733 | 13.4997 | 9.8478 | 11.8985 | 32.1258 | 12.9711 | 9.4623 | 10.3503 | 32.7066 | 12.3969 | 9.0434 | 7.865 | 33.1039 | 11.9376 | 8.7083 | 5.9083 | 33.3706 | 11.3815 | 8.3027 | 3.9624 | 33.5367 | 11.13 | 8.1192 | 2.179 | 29.9688 | 15.0037 | 10.945 | 15.3677 | 30.0513 | 14.8858 | 10.859 | 14.8454 | 30.1381 | 14.7033 | 10.7259 | 14.588 | 30.2442 | 14.4505 | 10.5414 | 14.3834 | 30.3819 | 14.425 | 10.5228 | 14.1418 | 30.5509 | 14.3801 | 10.4901 | 13.915 | 30.7562 | 14.0255 | 10.2314 | 13.6058 | 30.9309 | 13.9544 | 10.1795 | 13.1614 | 31.0462 | 13.8824 | 10.127 | 12.84 | 31.1708 | 13.8004 | 10.0672 | 12.5196 | 31.6049 | 13.482 | 9.8349 | 11.5511 | 32.0962 | 13.1942 | 9.625 | 10.5259 | 32.5678 | 12.8648 | 9.3847 | 9.4618 | 33.0144 | 12.525 | 9.1368 | 8.174 | 33.2924 | 12.2814 | 8.9591 | 7.2028 | 30.0013 | 15.0037 | 10.945 | 15.3677 | 30.1029 | 14.6677 | 10.6999 | 13.9198 | 30.2343 | 14.4183 | 10.5179 | 13.5268 | 30.4027 | 14.2272 | 10.3786 | 13.386 | 30.614 | 14.0112 | 10.221 | 13.1512 | 30.7731 | 13.5352 | 9.8737 | 12.9055 | 30.967 | 13.6674 | 9.9702 | 12.6886 | 31.2076 | 13.5305 | 9.8703 | 12.4775 | 31.4042 | 13.365 | 9.7496 | 12.2662 | 31.5461 | 13.183 | 9.6168 | 12.0648 | 32.0843 | 12.6063 | 9.1961 | 10.7506 | 32.6899 | 11.9172 | 8.6934 | 8.4132 | 33.1245 | 11.3718 | 8.2955 | 6.5696 | 33.4434 | 10.8658 | 7.9265 | 4.7826 | 33.5764 | 10.3704 | 7.5651 | 3.1727 | 30.0013 | 15.0037 | 10.945 | 15.3677 | 30.0166 | 14.7788 | 10.7809 | 14.5353 | 30.0871 | 14.5829 | 10.638 | 14.2659 | 30.1878 | 14.3627 | 10.4774 | 14.1138 | 30.3368 | 14.098 | 10.2843 | 13.8868 | 30.5614 | 13.9268 | 10.1594 | 13.6479 | 30.7554 | 13.8799 | 10.1252 | 13.3045 | 30.9814 | 13.6586 | 9.9637 | 12.5661 | 31.1836 | 13.4129 | 9.7845 | 11.794 | 31.3943 | 13.1196 | 9.5705 | 11.0221 | 32.0427 | 12.6412 | 9.2216 | 8.79 | 32.544 | 11.9354 | 8.7067 | 6.5897 | 32.8622 | 11.4098 | 8.3233 | 4.9709 | 33.0602 | 10.9675 | 8.0007 | 3.9698 | 33.0727 | 10.6726 | 7.7855 | 4.4515 | 29.9914 | 15.0037 | 10.945 | 15.3677 | 30.0732 | 14.8285 | 10.8172 | 14.5518 | 30.1611 | 14.6607 | 10.6948 | 14.2591 | 30.2621 | 14.5545 | 10.6173 | 14.1057 | 30.3958 | 14.3969 | 10.5023 | 13.9239 | 30.5925 | 14.1201 | 10.3004 | 13.7521 | 30.778 | 13.966 | 10.188 | 13.5615 | 30.9768 | 13.9391 | 10.1684 | 13.3211 | 31.1651 | 13.8282 | 10.0875 | 13.0014 | 31.3649 | 13.6832 | 9.9817 | 12.6835 | 31.9301 | 13.2325 | 9.6529 | 11.5601 | 32.4236 | 12.8697 | 9.3883 | 10.1929 | 32.7681 | 12.6039 | 9.1944 | 9.2737 | 33.0408 | 12.3764 | 9.0284 | 8.3906 | 33.1535 | 12.2788 | 8.9572 | 7.864 | 29.9914 | 15.0037 | 10.945 | 15.3677 | 30.0313 | 14.6648 | 10.6978 | 13.9391 | 30.1415 | 14.448 | 10.5396 | 13.515 | 30.2888 | 14.2186 | 10.3723 | 13.2972 | 30.4737 | 13.9453 | 10.1729 | 13.0078 | 30.653 | 13.7215 | 10.0097 | 12.7205 | 30.8266 | 13.6737 | 9.9747 | 12.317 | 31.0628 | 13.4432 | 9.8066 | 11.5079 | 31.2808 | 13.1893 | 9.6214 | 10.7027 | 31.508 | 12.8818 | 9.3971 | 9.8953 | 32.1508 | 12.3978 | 9.044 | 7.5248 | 32.6818 | 11.5883 | 8.4535 | 5.1687 | 33.0375 | 11.0629 | 8.0703 | 3.3891 | 33.2524 | 10.5896 | 7.725 | 2.203 | 33.2733 | 10.2577 | 7.4829 | 2.4897
LONGSIGHT | LONGSIGHT | BREDBURY | 385535 | 396037 | 27.4295 | 11.9257 | 8.6997 | 9.2165 | 27.5758 | 11.3281 | 8.2637 | 6.519 | 27.7504 | 9.4186 | 6.8707 | 5.1765 | 27.9508 | 7.8029 | 5.6921 | 4.8271 | 28.187 | 6.0945 | 4.4458 | 4.389 | 26.1984 | 4.2496 | 3.1001 | 3.9253 | 15.2979 | 2.4815 | 1.8102 | 3.4827 | 13.9188 | 2.2578 | 1.647 | 3.0746 | 12.6464 | 2.0514 | 1.4964 | 2.6333 | 11.9445 | 1.9375 | 1.4134 | 2.2118 | 9.8508 | 1.5979 | 1.1656 | 0.14076 | 11.907 | 1.9314 | 1.409 | -2.7963 | 23.1548 | 3.7559 | 2.7399 | -4.9128 | 31.164 | 6.089 | 4.4418 | -6.7871 | 31.3236 | 6.5826 | 4.8019 | -8.1851 | 27.41 | 11.9257 | 8.6997 | 9.2165 | 27.5566 | 11.7209 | 8.5502 | 8.51 | 27.7208 | 9.8387 | 7.1772 | 8.1327 | 27.9091 | 8.3414 | 6.085 | 7.8591 | 28.1402 | 6.7111 | 4.8956 | 7.5545 | 28.4227 | 5.027 | 3.6671 | 7.2393 | 19.2022 | 3.1148 | 2.2722 | 6.8461 | 18.1486 | 2.9439 | 2.1475 | 6.3499 | 17.2367 | 2.796 | 2.0396 | 5.9699 | 16.347 | 2.6516 | 1.9343 | 5.5697 | 13.8091 | 2.24 | 1.634 | 4.384 | 11.8995 | 1.9302 | 1.4081 | 3.208 | 18.6355 | 3.0229 | 2.2051 | 2.1438 | 30.1531 | 4.8911 | 3.568 | 1.0492 | 30.9556 | 5.2516 | 3.831 | 0.26883 | 27.4379 | 11.9257 | 8.6997 | 9.2165 | 27.5986 | 11.2235 | 8.1874 | 6.1255 | 27.7949 | 9.2865 | 6.7744 | 4.6288 | 28.0245 | 7.6019 | 5.5455 | 4.1884 | 28.2935 | 5.8415 | 4.2613 | 3.6459 | 24.4364 | 3.9638 | 2.8915 | 3.0716 | 13.3028 | 2.1578 | 1.5741 | 2.53 | 11.7319 | 1.903 | 1.3882 | 2.002 | 10.2649 | 1.6651 | 1.2146 | 1.4836 | 9.2783 | 1.505 | 1.0979 | 0.94274 | 6.2901 | 1.0203 | 0.7443 | -1.4853 | 7.7306 | 1.254 | 0.91475 | -4.4701 | 18.6792 | 3.0299 | 2.2103 | -6.3876 | 31.4344 | 5.3579 | 3.9085 | -7.7836 | 31.4937 | 5.9697 | 4.3548 | -8.2662 | 27.438 | 11.9257 | 8.6997 | 9.2165 | 27.4804 | 11.3963 | 8.3134 | 7.0267 | 27.5921 | 11.1429 | 8.1286 | 5.7526 | 27.7274 | 11.0161 | 8.0361 | 5.3681 | 27.9107 | 10.8034 | 7.8809 | 4.8552 | 28.1743 | 10.5501 | 7.6961 | 4.2833 | 28.5043 | 10.2918 | 7.5077 | 3.601 | 28.8905 | 9.9626 | 7.2675 | 2.492 | 29.1629 | 9.6599 | 7.0467 | 1.3844 | 29.3807 | 9.3469 | 6.8184 | 0.2901 | 30.0329 | 8.4933 | 6.1958 | -2.7668 | 30.545 | 7.7678 | 5.6665 | -5.2834 | 30.8466 | 7.2281 | 5.2728 | -6.7214 | 30.9972 | 6.7979 | 4.959 | -7.191 | 30.9189 | 6.6397 | 4.8435 | -6.4131 | 27.4294 | 11.9257 | 8.6997 | 9.2165 | 27.5564 | 11.5155 | 8.4004 | 7.3774 | 27.6907 | 9.6259 | 7.0219 | 6.2472 | 27.8288 | 8.0432 | 5.8674 | 5.9885 | 27.995 | 6.3764 | 4.6515 | 5.7264 | 28.2067 | 4.5754 | 3.3377 | 5.4412 | 17.4088 | 2.8239 | 2.06 | 5.132 | 16.0778 | 2.608 | 1.9025 | 4.7863 | 14.8121 | 2.4027 | 1.7527 | 4.3451 | 14.0684 | 2.282 | 1.6647 | 3.8933 | 12.6865 | 2.0579 | 1.5012 | 2.4264 | 16.5092 | 2.678 | 1.9535 | 0.96961 | 29.1005 | 4.7204 | 3.4435 | -0.053331 | 30.7051 | 7.2559 | 5.293 | -0.98836 | 30.8193 | 7.9361 | 5.7893 | -1.4895 | 27.4294 | 11.9257 | 8.6997 | 9.2165 | 27.5092 | 11.187 | 8.1608 | 6.0831 | 27.6801 | 10.8974 | 7.9495 | 4.5386 | 27.8846 | 10.7372 | 7.8326 | 4.0513 | 28.1263 | 10.499 | 7.6589 | 3.446 | 28.4014 | 10.2344 | 7.4659 | 2.8164 | 28.7243 | 9.9641 | 7.2687 | 2.0651 | 29.0629 | 9.6158 | 7.0146 | 0.86261 | 29.3383 | 9.3018 | 6.7855 | -0.29747 | 29.5531 | 8.9771 | 6.5487 | -1.4469 | 30.2219 | 8.0859 | 5.8986 | -4.6952 | 30.7724 | 7.3203 | 5.34 | -7.3746 | 31.1017 | 6.7431 | 4.919 | -8.9796 | 31.2733 | 6.2766 | 4.5787 | -9.6452 | 31.2274 | 6.0776 | 4.4336 | -9.0785
LOSTOCK | WESTHOUGHTON | KEARSLEY | 365293 | 409079 | 38.6119 | 6.8779 | 4.9433 | 15.7727 | 37.5295 | 6.179 | 4.4409 | 13.4093 | 34.0313 | 5.603 | 4.027 | 13.0597 | 33.083 | 5.4469 | 3.9148 | 12.8385 | 31.4781 | 5.1826 | 3.7249 | 12.626 | 29.3994 | 4.8404 | 3.4789 | 12.4067 | 28.5342 | 4.6979 | 3.3765 | 12.1927 | 27.9479 | 4.6014 | 3.3071 | 11.9485 | 27.1984 | 4.478 | 3.2184 | 11.5308 | 26.6161 | 4.3821 | 3.1495 | 11.123 | 24.3793 | 4.0139 | 2.8848 | 9.3264 | 22.3855 | 3.6856 | 2.6489 | 6.7808 | 23.0862 | 3.801 | 2.7318 | 4.8063 | 39.5156 | 6.5059 | 4.6759 | 2.8883 | 38.6811 | 6.3685 | 4.5772 | 1.3989 | 38.5734 | 6.8779 | 4.9433 | 15.7727 | 38.6221 | 6.4438 | 4.6313 | 14.8401 | 37.3313 | 6.1463 | 4.4175 | 14.8727 | 35.271 | 5.8071 | 4.1737 | 14.7647 | 33.7499 | 5.5567 | 3.9937 | 14.6912 | 32.238 | 5.3077 | 3.8148 | 14.6026 | 30.7363 | 5.0605 | 3.6371 | 14.4786 | 30.2716 | 4.984 | 3.5821 | 14.2991 | 29.571 | 4.8686 | 3.4992 | 13.8895 | 29.0065 | 4.7757 | 3.4324 | 13.4704 | 27.3405 | 4.5014 | 3.2352 | 12.2142 | 25.9172 | 4.2671 | 3.0668 | 10.5242 | 25.371 | 4.1771 | 3.0022 | 8.8906 | 34.8032 | 5.7301 | 4.1183 | 7.2518 | 43.2015 | 7.2955 | 5.2434 | 6.2634 | 38.6198 | 6.8779 | 4.9433 | 15.7727 | 37.0722 | 6.1037 | 4.3868 | 13.0845 | 34.1813 | 5.6277 | 4.0447 | 12.669 | 32.4511 | 5.3428 | 3.84 | 12.4441 | 30.5259 | 5.0258 | 3.6122 | 12.2334 | 28.3617 | 4.6695 | 3.3561 | 12.0191 | 27.4873 | 4.5256 | 3.2526 | 11.8111 | 26.8207 | 4.4158 | 3.1737 | 11.5788 | 26.0473 | 4.2885 | 3.0822 | 11.2503 | 25.4443 | 4.1892 | 3.0109 | 10.9421 | 23.1015 | 3.8035 | 2.7336 | 9.4187 | 20.9426 | 3.448 | 2.4782 | 7.1256 | 21.8243 | 3.5932 | 2.5825 | 5.4164 | 38.8523 | 6.3967 | 4.5975 | 3.9037 | 37.9274 | 6.2445 | 4.488 | 2.9681 | 38.6198 | 6.8779 | 4.9433 | 15.7727 | 38.0626 | 6.2667 | 4.504 | 13.8988 | 35.7444 | 5.885 | 4.2297 | 13.7042 | 34.0052 | 5.5987 | 4.0239 | 13.5498 | 31.7927 | 5.2344 | 3.7621 | 13.3873 | 29.6396 | 4.8799 | 3.5073 | 13.1662 | 27.7303 | 4.5656 | 3.2814 | 12.8195 | 27.8495 | 4.5852 | 3.2955 | 12.1172 | 27.863 | 4.5874 | 3.2971 | 11.3102 | 28.7118 | 4.7272 | 3.3975 | 10.5167 | 41.2551 | 7.5953 | 5.4589 | 8.2314 | 42.1715 | 6.9657 | 5.0064 | 6.0627 | 39.4233 | 6.4907 | 4.665 | 4.5048 | 38.09 | 6.2712 | 4.5073 | 3.6784 | 37.8682 | 6.2347 | 4.481 | 4.6069 | 38.6119 | 6.8779 | 4.9433 | 15.7727 | 38.5481 | 6.3467 | 4.5615 | 14.2807 | 35.8283 | 5.8989 | 4.2396 | 14.1603 | 34.408 | 5.665 | 4.0716 | 14.0325 | 33.0416 | 5.44 | 3.9099 | 13.9514 | 31.1306 | 5.1254 | 3.6837 | 13.8171 | 30.2836 | 4.986 | 3.5835 | 13.6423 | 29.7559 | 4.8991 | 3.5211 | 13.4488 | 29.0464 | 4.7823 | 3.4371 | 13.0665 | 28.482 | 4.6894 | 3.3703 | 12.6765 | 26.9276 | 4.4334 | 3.1864 | 11.4351 | 26.427 | 4.351 | 3.1271 | 10.1294 | 28.2268 | 4.6473 | 3.3401 | 9.275 | 43.0483 | 7.7381 | 5.5615 | 8.4613 | 43.1713 | 7.8056 | 5.6101 | 8.1933 | 38.6119 | 6.8779 | 4.9433 | 15.7727 | 36.8729 | 6.0708 | 4.3632 | 12.8852 | 34.3285 | 5.6519 | 4.0622 | 12.4153 | 32.3943 | 5.3335 | 3.8333 | 12.1685 | 30.0526 | 4.9479 | 3.5562 | 11.9317 | 27.9344 | 4.5992 | 3.3055 | 11.6974 | 26.1792 | 4.3102 | 3.0978 | 11.3529 | 26.1171 | 4.3 | 3.0905 | 10.6076 | 26.0401 | 4.2873 | 3.0814 | 9.7605 | 26.8388 | 4.4188 | 3.1759 | 8.9323 | 41.3417 | 7.2502 | 5.2109 | 6.5522 | 40.1004 | 6.6022 | 4.7451 | 4.313 | 37.0842 | 6.1056 | 4.3882 | 2.6747 | 35.6544 | 5.8702 | 4.219 | 1.7803 | 35.2985 | 5.8116 | 4.1769 | 2.6047
LOWER DARWEN | LOWER DARWEN | ROCHDALE | 369695 | 424981 | 29.4961 | 13.5743 | 9.9023 | 17.8392 | 29.5181 | 13.4744 | 9.8294 | 17.0132 | 29.5799 | 13.4049 | 9.7787 | 16.585 | 29.6499 | 13.3515 | 9.7397 | 16.3557 | 29.7342 | 13.2789 | 9.6868 | 16.278 | 29.8393 | 13.0786 | 9.5407 | 16.2005 | 29.9704 | 12.7967 | 9.335 | 16.1259 | 30.1415 | 12.7484 | 9.2998 | 16.0422 | 30.3259 | 12.756 | 9.3053 | 15.8697 | 30.522 | 12.727 | 9.2842 | 15.6975 | 31.1681 | 12.5116 | 9.127 | 15.0906 | 31.7754 | 12.3557 | 9.0133 | 14.4478 | 32.1786 | 12.4312 | 9.0684 | 13.9701 | 32.3801 | 12.5841 | 9.1799 | 13.5551 | 32.3983 | 12.5355 | 9.1445 | 13.3209 | 29.4822 | 13.5743 | 9.9023 | 17.8392 | 29.4944 | 13.5837 | 9.9091 | 17.5517 | 29.527 | 13.6842 | 9.9824 | 17.4061 | 29.5551 | 13.7198 | 10.0084 | 17.3667 | 29.5864 | 13.661 | 9.9655 | 17.3628 | 29.6278 | 13.5898 | 9.9136 | 17.3545 | 29.6802 | 13.4605 | 9.8193 | 17.339 | 29.7442 | 13.3761 | 9.7577 | 17.3165 | 29.8257 | 13.3384 | 9.7302 | 17.2021 | 29.9174 | 13.2797 | 9.6874 | 17.0858 | 30.2511 | 13.0886 | 9.548 | 16.7326 | 30.6466 | 12.9903 | 9.4763 | 16.3788 | 31.0496 | 13.0511 | 9.5206 | 16.0646 | 31.4795 | 12.8876 | 9.4013 | 15.7554 | 31.7614 | 13.139 | 9.5847 | 15.5714 | 29.4987 | 13.5743 | 9.9023 | 17.8392 | 29.526 | 13.4272 | 9.7949 | 16.844 | 29.5934 | 13.3097 | 9.7092 | 16.3612 | 29.6709 | 13.1934 | 9.6244 | 16.0997 | 29.7626 | 13.0654 | 9.531 | 15.9926 | 29.8741 | 12.8241 | 9.355 | 15.8874 | 30.0097 | 12.7185 | 9.2779 | 15.7863 | 30.1843 | 12.714 | 9.2747 | 15.6789 | 30.3548 | 12.6511 | 9.2288 | 15.5209 | 30.5359 | 12.5898 | 9.1841 | 15.3682 | 31.1853 | 12.2934 | 8.9679 | 14.8047 | 31.8138 | 12.1086 | 8.8331 | 14.1891 | 31.9882 | 12.138 | 8.8545 | 13.8365 | 32.0561 | 12.3318 | 8.9959 | 13.6153 | 31.9932 | 12.2972 | 8.9706 | 13.6473 | 29.4987 | 13.5743 | 9.9023 | 17.8392 | 29.5061 | 13.4814 | 9.8345 | 17.1498 | 29.5512 | 13.4189 | 9.7889 | 16.7347 | 29.603 | 13.3185 | 9.7157 | 16.4884 | 29.6723 | 13.1073 | 9.5616 | 16.3937 | 29.7807 | 12.7988 | 9.3365 | 16.2902 | 29.9309 | 12.9272 | 9.4302 | 16.1523 | 30.1378 | 12.9048 | 9.4139 | 15.9119 | 30.3495 | 12.8206 | 9.3525 | 15.6131 | 30.5726 | 12.7219 | 9.2805 | 15.3193 | 31.262 | 13.1776 | 9.6129 | 14.5373 | 31.8713 | 12.847 | 9.3717 | 13.9615 | 32.0443 | 12.6357 | 9.2176 | 13.6563 | 32.0251 | 12.4987 | 9.1176 | 13.621 | 31.8436 | 12.3828 | 9.0331 | 14.134 | 29.4961 | 13.5743 | 9.9023 | 17.8392 | 29.5129 | 13.5269 | 9.8677 | 17.2763 | 29.5599 | 13.4664 | 9.8236 | 16.9045 | 29.6054 | 13.4284 | 9.7958 | 16.6943 | 29.6592 | 13.3738 | 9.756 | 16.6473 | 29.7443 | 13.1781 | 9.6132 | 16.5923 | 29.8615 | 12.8851 | 9.3995 | 16.5262 | 30.0033 | 12.8636 | 9.3838 | 16.4507 | 30.1554 | 12.8746 | 9.3919 | 16.2858 | 30.3215 | 12.8466 | 9.3714 | 16.1172 | 30.8892 | 12.6792 | 9.2493 | 15.6503 | 31.4441 | 12.6459 | 9.225 | 15.3225 | 31.7431 | 12.8241 | 9.355 | 15.1316 | 31.9192 | 13.0961 | 9.5534 | 15.0461 | 31.9415 | 13.1203 | 9.5711 | 15.2022 | 29.4961 | 13.5743 | 9.9023 | 17.8392 | 29.5114 | 13.3927 | 9.7698 | 16.7262 | 29.572 | 13.3198 | 9.7166 | 16.2204 | 29.6418 | 13.2124 | 9.6383 | 15.9521 | 29.7228 | 13.0055 | 9.4874 | 15.8393 | 29.8206 | 12.7369 | 9.2914 | 15.7302 | 29.9491 | 12.7735 | 9.3181 | 15.5907 | 30.1419 | 12.7601 | 9.3083 | 15.341 | 30.3378 | 12.6774 | 9.248 | 15.0403 | 30.5448 | 12.5753 | 9.1735 | 14.7455 | 31.2206 | 13.0222 | 9.4995 | 13.9485 | 31.8547 | 12.6849 | 9.2535 | 13.3443 | 32.1952 | 12.4539 | 9.0849 | 13.0075 | 32.2137 | 12.3143 | 8.9831 | 12.95 | 32.0679 | 12.2303 | 8.9219 | 13.4427
LYONS RD | BARTON | CARRINGTON | 378253 | 397241 | 25.3133 | 10.8673 | 7.9275 | 15.0999 | 25.3581 | 10.2173 | 7.4534 | 11.1317 | 25.4169 | 9.9147 | 7.2326 | 10.0252 | 25.4921 | 9.7185 | 7.0895 | 9.5495 | 25.584 | 9.5266 | 6.9496 | 9.1077 | 25.6945 | 9.347 | 6.8185 | 8.6576 | 25.8293 | 9.1848 | 6.7002 | 8.1982 | 25.9995 | 9.073 | 6.6186 | 7.7132 | 26.1693 | 8.9337 | 6.517 | 7.114 | 26.3562 | 8.7923 | 6.4138 | 6.5024 | 30.4049 | 7.827 | 5.7097 | 1.0652 | 30.1423 | 4.8894 | 3.5667 | -16.9883 | 28.9352 | 4.6936 | 3.4239 | -18.2936 | 30.9883 | 5.0266 | 3.6668 | -20.3092 | 34.1147 | 5.5337 | 4.0368 | -21.2611 | 25.3138 | 10.8673 | 7.9275 | 15.0999 | 25.3802 | 10.7133 | 7.8152 | 14.1473 | 25.456 | 10.5781 | 7.7166 | 13.8106 | 25.5497 | 10.4735 | 7.6403 | 13.7151 | 25.6603 | 10.3606 | 7.5579 | 13.6577 | 25.7953 | 10.2587 | 7.4836 | 13.59 | 25.9352 | 10.0362 | 7.3213 | 13.5137 | 26.0234 | 9.9857 | 7.2844 | 13.4296 | 26.1213 | 9.9355 | 7.2478 | 13.2447 | 26.2423 | 9.8778 | 7.2057 | 13.0498 | 26.6774 | 9.707 | 7.0811 | 12.4248 | 27.1015 | 9.5842 | 6.9916 | 11.7531 | 27.5228 | 9.5183 | 6.9435 | 11.1182 | 27.9596 | 9.9907 | 7.2881 | 10.4527 | 28.2363 | 10.4521 | 7.6247 | 9.9836 | 25.3131 | 10.8673 | 7.9275 | 15.0999 | 25.3573 | 10.1083 | 7.3738 | 10.5086 | 25.4146 | 9.7552 | 7.1163 | 9.2764 | 25.4865 | 9.5499 | 6.9665 | 8.8024 | 25.5721 | 9.3601 | 6.8281 | 8.3659 | 25.6721 | 9.189 | 6.7032 | 7.9253 | 25.7907 | 9.0096 | 6.5724 | 7.4808 | 25.9379 | 8.8929 | 6.4873 | 7.0172 | 26.0808 | 8.7444 | 6.3789 | 6.4868 | 26.242 | 8.6086 | 6.2799 | 5.9461 | 15.3939 | 2.497 | 1.8216 | -31.3566 | 13.7077 | 2.2235 | 1.622 | -32.4481 | 12.7053 | 2.0609 | 1.5034 | -33.3324 | 14.5173 | 2.3549 | 1.7178 | -35.1843 | 19.0214 | 3.0855 | 2.2508 | -34.907 | 25.3131 | 10.8673 | 7.9275 | 15.0999 | 25.3347 | 10.3254 | 7.5322 | 11.7719 | 25.3643 | 10.1119 | 7.3765 | 10.8161 | 25.4079 | 9.9606 | 7.2661 | 10.3628 | 25.4695 | 9.8207 | 7.1641 | 9.9421 | 25.5593 | 9.6783 | 7.0602 | 9.4994 | 25.6793 | 9.5529 | 6.9687 | 9.0185 | 29.7036 | 8.7671 | 6.3954 | 4.5323 | 29.7287 | 8.6339 | 6.2983 | 4.0405 | 29.7875 | 8.489 | 6.1926 | 3.5223 | 30.2006 | 8.009 | 5.8424 | 1.7787 | 30.6515 | 7.6378 | 5.5717 | 0.042273 | 30.9172 | 7.4249 | 5.4164 | -1.4222 | 31.141 | 8.2948 | 6.0509 | -3.0293 | 31.1056 | 8.0198 | 5.8503 | -4.3728 | 25.3133 | 10.8673 | 7.9275 | 15.0999 | 25.3531 | 10.5377 | 7.6871 | 13.0656 | 25.3996 | 10.3004 | 7.514 | 12.367 | 25.456 | 10.118 | 7.3809 | 11.9175 | 25.5262 | 9.9283 | 7.2426 | 11.5114 | 25.6223 | 9.7561 | 7.1169 | 11.0863 | 25.7444 | 9.6031 | 7.0053 | 10.6414 | 25.8885 | 9.4943 | 6.926 | 10.1801 | 26.0249 | 9.3592 | 6.8274 | 9.6108 | 26.1789 | 9.2228 | 6.7279 | 9.0259 | 30.1618 | 8.2983 | 6.0535 | 3.7244 | 33.4706 | 5.4293 | 3.9606 | -14.1223 | 32.5726 | 5.2836 | 3.8543 | -15.2483 | 34.6455 | 5.6198 | 4.0996 | -17.0331 | 38.5554 | 6.2541 | 4.5622 | -17.6399 | 25.3133 | 10.8673 | 7.9275 | 15.0999 | 25.3577 | 10.0068 | 7.2998 | 9.886 | 25.4157 | 9.717 | 7.0884 | 8.5256 | 25.4892 | 9.5582 | 6.9725 | 8.0452 | 25.5764 | 9.417 | 6.8695 | 7.6038 | 25.6779 | 9.2786 | 6.7686 | 7.1593 | 25.8034 | 9.1506 | 6.6752 | 6.6845 | 29.8371 | 8.3596 | 6.0982 | 2.198 | 29.8468 | 8.2278 | 6.0021 | 1.7179 | 29.8905 | 8.0844 | 5.8975 | 1.2116 | 30.308 | 7.6079 | 5.5499 | -0.54172 | 30.8266 | 7.2151 | 5.2634 | -2.3436 | 31.1646 | 6.9806 | 5.0923 | -3.8779 | 31.4278 | 7.8587 | 5.7328 | -5.5206 | 31.4031 | 7.5597 | 5.5147 | -6.8744
MANCHESTER UNIVERSITY | LONGSIGHT | BREDBURY | 384762 | 396769 | 31.7868 | 10.9527 | 7.9898 | 12.9891 | 31.7932 | 10.6798 | 7.7908 | 12.2493 | 31.8583 | 10.3072 | 7.519 | 11.9325 | 31.8904 | 9.9293 | 7.2433 | 11.556 | 31.8966 | 9.5763 | 6.9858 | 11.2549 | 31.899 | 9.409 | 6.8637 | 10.9678 | 31.8951 | 9.156 | 6.6792 | 10.6185 | 31.8902 | 9.0318 | 6.5886 | 10.6526 | 31.9358 | 8.9109 | 6.5004 | 10.5462 | 31.9771 | 8.8159 | 6.4311 | 10.4515 | 32.0823 | 8.6632 | 6.3197 | 10.1958 | 32.1631 | 8.5408 | 6.2304 | 9.975 | 32.2014 | 8.5312 | 6.2234 | 9.8605 | 32.2031 | 8.6534 | 6.3125 | 9.8346 | 32.144 | 8.7323 | 6.3701 | 9.9765 | 31.7882 | 10.9527 | 7.9898 | 12.9891 | 31.797 | 10.8454 | 7.9116 | 12.6871 | 31.8617 | 10.595 | 7.7289 | 12.768 | 31.8953 | 10.2862 | 7.5036 | 12.7015 | 31.907 | 10.0402 | 7.3242 | 12.7103 | 31.9167 | 9.7517 | 7.1137 | 12.7293 | 31.9254 | 9.3694 | 6.8348 | 12.759 | 31.9331 | 9.3129 | 6.7936 | 12.7965 | 32.0036 | 9.243 | 6.7426 | 12.6246 | 32.0718 | 9.1981 | 6.7099 | 12.4607 | 32.2564 | 9.183 | 6.6989 | 12.0229 | 32.4109 | 9.2271 | 6.7311 | 11.659 | 32.5309 | 9.2919 | 6.7783 | 11.3771 | 32.646 | 9.3808 | 6.8431 | 11.1004 | 32.7315 | 9.3826 | 6.8445 | 10.8904 | 31.7861 | 10.9527 | 7.9898 | 12.9891 | 31.7849 | 10.6516 | 7.7702 | 12.1674 | 31.8467 | 10.2226 | 7.4572 | 11.8336 | 31.8684 | 9.7504 | 7.1128 | 11.4534 | 31.8696 | 9.4431 | 6.8886 | 11.1509 | 31.8676 | 9.3452 | 6.8172 | 10.8629 | 31.8568 | 9.0625 | 6.611 | 10.5117 | 31.8453 | 8.9358 | 6.5185 | 10.5444 | 31.8524 | 8.8392 | 6.4481 | 10.4945 | 31.8706 | 8.755 | 6.3866 | 10.4646 | 31.9032 | 8.6188 | 6.2873 | 10.4126 | 31.9101 | 8.5249 | 6.2188 | 10.4097 | 31.873 | 8.543 | 6.232 | 10.5232 | 31.7723 | 8.7022 | 6.3481 | 10.814 | 31.5826 | 8.8608 | 6.4638 | 11.3653 | 31.7861 | 10.9527 | 7.9898 | 12.9891 | 31.7777 | 10.7205 | 7.8205 | 12.3332 | 31.8327 | 10.4073 | 7.592 | 12.0383 | 31.8472 | 10.1529 | 7.4064 | 11.6643 | 31.8431 | 9.9814 | 7.2813 | 11.3668 | 31.84 | 10.0176 | 7.3077 | 11.0794 | 31.8296 | 9.9048 | 7.2254 | 10.7203 | 31.8181 | 9.803 | 7.1511 | 10.7264 | 31.8254 | 9.7166 | 7.0881 | 10.6497 | 31.8444 | 9.6225 | 7.0195 | 10.5921 | 31.8772 | 9.39 | 6.8499 | 10.4952 | 31.8831 | 9.2364 | 6.7379 | 10.4947 | 31.8451 | 9.137 | 6.6653 | 10.6118 | 31.7402 | 9.1258 | 6.6572 | 10.9411 | 31.5362 | 9.1605 | 6.6825 | 11.6002 | 31.7868 | 10.9527 | 7.9898 | 12.9891 | 31.7915 | 10.8032 | 7.8808 | 12.6436 | 31.852 | 10.4552 | 7.6269 | 12.4112 | 31.878 | 10.0761 | 7.3504 | 12.0418 | 31.8787 | 9.7341 | 7.1009 | 11.7497 | 31.8804 | 9.5544 | 6.9698 | 11.467 | 31.8784 | 9.3112 | 6.7924 | 11.1173 | 31.8728 | 9.1874 | 6.7021 | 11.1517 | 31.9168 | 9.0625 | 6.611 | 11.0455 | 31.9572 | 8.9631 | 6.5384 | 10.9495 | 32.0598 | 8.833 | 6.4436 | 10.7196 | 32.1367 | 8.7664 | 6.395 | 10.5679 | 32.1715 | 8.8064 | 6.4241 | 10.5197 | 32.1699 | 8.9924 | 6.5598 | 10.5698 | 32.102 | 9.1301 | 6.6603 | 10.8113 | 31.7868 | 10.9527 | 7.9898 | 12.9891 | 31.7837 | 10.6299 | 7.7543 | 12.0923 | 31.8461 | 10.2597 | 7.4843 | 11.7428 | 31.8691 | 10.0229 | 7.3116 | 11.3612 | 31.8721 | 9.8779 | 7.2058 | 11.0576 | 31.8722 | 9.8931 | 7.2169 | 10.7689 | 31.8651 | 9.7729 | 7.1292 | 10.4095 | 31.8602 | 9.6706 | 7.0546 | 10.4115 | 31.873 | 9.5834 | 6.991 | 10.3306 | 31.897 | 9.4892 | 6.9222 | 10.2694 | 31.9424 | 9.2557 | 6.7519 | 10.1658 | 31.9541 | 9.1006 | 6.6387 | 10.1646 | 31.9203 | 8.9983 | 6.5642 | 10.2812 | 31.818 | 8.9843 | 6.5539 | 10.6112 | 31.6188 | 9.013 | 6.5748 | 11.2667
MARPLE | HAZEL GROVE | BREDBURY | 395671 | 388643 | 6.0896 | 6.0896 | 6.0896 | 0.31064 | 6.1109 | 6.1109 | 6.1109 | 0.13726 | 6.138 | 6.138 | 6.138 | -0.013055 | 6.1713 | 6.1713 | 6.1713 | -0.13435 | 6.2135 | 6.2135 | 6.2135 | -0.28279 | 6.2623 | 6.2623 | 6.2623 | -0.44094 | 6.3197 | 6.3197 | 6.3197 | -0.52349 | 6.3901 | 6.3901 | 6.3901 | -0.60667 | 6.4435 | 6.4435 | 6.4435 | -0.70709 | 6.4937 | 6.4937 | 6.4937 | -0.79806 | 6.659 | 6.659 | 6.659 | -1.4353 | 6.8461 | 6.8461 | 6.8461 | -2.5722 | 6.9897 | 6.9897 | 6.9897 | -3.5488 | 7.1289 | 7.1289 | 7.1289 | -4.6757 | 7.2355 | 7.2355 | 7.2355 | -5.6649 | 6.0822 | 6.0822 | 6.0822 | 0.31064 | 6.1028 | 6.1028 | 6.1028 | 0.25122 | 6.1232 | 6.1232 | 6.1232 | 0.17828 | 6.1479 | 6.1479 | 6.1479 | 0.10458 | 6.1821 | 6.1821 | 6.1821 | 0.012089 | 6.2251 | 6.2251 | 6.2251 | -0.085645 | 6.2778 | 6.2778 | 6.2778 | -0.19175 | 6.3391 | 6.3391 | 6.3391 | -0.33721 | 6.3708 | 6.3708 | 6.3708 | -0.45957 | 6.4034 | 6.4034 | 6.4034 | -0.58342 | 6.5031 | 6.5031 | 6.5031 | -0.95489 | 6.6007 | 6.6007 | 6.6007 | -1.3296 | 6.6876 | 6.6876 | 6.6876 | -1.6918 | 6.7787 | 6.7787 | 6.7787 | -2.0993 | 6.8521 | 6.8521 | 6.8521 | -2.3931 | 6.0923 | 6.0923 | 6.0923 | 0.31064 | 6.1162 | 6.1162 | 6.1162 | 0.1227 | 6.1472 | 6.1472 | 6.1472 | -0.023207 | 6.1865 | 6.1865 | 6.1865 | -0.13102 | 6.2361 | 6.2361 | 6.2361 | -0.26715 | 6.2936 | 6.2936 | 6.2936 | -0.41292 | 6.362 | 6.362 | 6.362 | -0.51182 | 6.4455 | 6.4455 | 6.4455 | -0.61128 | 6.5067 | 6.5067 | 6.5067 | -0.72098 | 6.5639 | 6.5639 | 6.5639 | -0.82697 | 6.7495 | 6.7495 | 6.7495 | -1.4097 | 6.9539 | 6.9539 | 6.9539 | -2.4857 | 7.1089 | 7.1089 | 7.1089 | -3.4048 | 7.2338 | 7.2338 | 7.2338 | -4.4655 | 7.2996 | 7.2996 | 7.2996 | -5.38 | 6.0923 | 6.0923 | 6.0923 | 0.31064 | 6.0806 | 6.0806 | 6.0806 | 0.27461 | 6.09 | 6.09 | 6.09 | 0.16931 | 6.1057 | 6.1057 | 6.1057 | 0.074506 | 6.134 | 6.134 | 6.134 | -0.057782 | 6.1803 | 6.1803 | 6.1803 | -0.20108 | 6.2423 | 6.2423 | 6.2423 | -0.36778 | 6.3199 | 6.3199 | 6.3199 | -0.75057 | 6.382 | 6.382 | 6.382 | -1.1502 | 6.4424 | 6.4424 | 6.4424 | -1.5524 | 6.6263 | 6.6263 | 6.6263 | -2.6351 | 6.8215 | 6.8215 | 6.8215 | -3.6974 | 6.9679 | 6.9679 | 6.9679 | -4.5681 | 7.0912 | 7.0912 | 7.0912 | -5.1983 | 7.0957 | 7.0957 | 7.0957 | -4.9486 | 6.0896 | 6.0896 | 6.0896 | 0.31064 | 6.1078 | 6.1078 | 6.1078 | 0.25286 | 6.1252 | 6.1252 | 6.1252 | 0.13988 | 6.1438 | 6.1438 | 6.1438 | 0.042853 | 6.1708 | 6.1708 | 6.1708 | -0.065882 | 6.2139 | 6.2139 | 6.2139 | -0.1853 | 6.2721 | 6.2721 | 6.2721 | -0.24791 | 6.336 | 6.336 | 6.336 | -0.3135 | 6.3833 | 6.3833 | 6.3833 | -0.40651 | 6.4298 | 6.4298 | 6.4298 | -0.49619 | 6.5767 | 6.5767 | 6.5767 | -0.80505 | 6.7349 | 6.7349 | 6.7349 | -1.1782 | 6.8546 | 6.8546 | 6.8546 | -1.4434 | 6.9705 | 6.9705 | 6.9705 | -1.716 | 7.0488 | 7.0488 | 7.0488 | -1.9195 | 6.0896 | 6.0896 | 6.0896 | 0.31064 | 6.0875 | 6.0875 | 6.0875 | 0.18798 | 6.1112 | 6.1112 | 6.1112 | 0.039241 | 6.1439 | 6.1439 | 6.1439 | -0.089668 | 6.1867 | 6.1867 | 6.1867 | -0.25328 | 6.235 | 6.235 | 6.235 | -0.42407 | 6.2951 | 6.2951 | 6.2951 | -0.6197 | 6.3803 | 6.3803 | 6.3803 | -1.0298 | 6.4473 | 6.4473 | 6.4473 | -1.4488 | 6.5114 | 6.5114 | 6.5114 | -1.8712 | 6.6956 | 6.6956 | 6.6956 | -3.0252 | 6.8728 | 6.8728 | 6.8728 | -4.1446 | 7.006 | 7.006 | 7.006 | -5.0759 | 7.1141 | 7.1141 | 7.1141 | -5.7902 | 7.1534 | 7.1534 | 7.1534 | -5.6431
MARTON | BLACKPOOL | PENWORTHAM WEST / STANAH | 333341 | 433485 | 24.0512 | 9.0963 | 6.6356 | 14.9072 | 24.127 | 8.6129 | 6.283 | 13.6171 | 24.2189 | 8.5876 | 6.2645 | 13.1167 | 24.3467 | 8.4602 | 6.1716 | 12.8318 | 24.5464 | 8.3198 | 6.0692 | 12.4804 | 24.768 | 8.0772 | 5.8922 | 12.1139 | 24.9966 | 7.893 | 5.7579 | 11.7599 | 25.2343 | 7.7071 | 5.6222 | 11.4171 | 25.416 | 7.553 | 5.5098 | 11.0654 | 25.5883 | 7.4115 | 5.4066 | 10.7348 | 26.4301 | 6.813 | 4.97 | 9.0213 | 26.9379 | 6.0072 | 4.3821 | 5.8786 | 27.3164 | 5.3197 | 3.8806 | 3.21 | 27.6646 | 4.5661 | 3.3309 | 0.31427 | 23.3902 | 3.7941 | 2.7678 | -2.2887 | 24.0399 | 9.0963 | 6.6356 | 14.9072 | 24.0962 | 8.7218 | 6.3624 | 14.5417 | 24.147 | 8.7958 | 6.4164 | 14.2772 | 24.214 | 8.7486 | 6.382 | 14.0548 | 24.3075 | 8.6425 | 6.3046 | 13.7978 | 24.3915 | 8.5072 | 6.2059 | 13.5014 | 24.502 | 8.1241 | 5.9264 | 13.1327 | 24.6479 | 7.9524 | 5.8012 | 12.6871 | 24.7419 | 7.8411 | 5.72 | 12.4975 | 24.8423 | 7.7375 | 5.6444 | 12.3053 | 25.1769 | 7.4 | 5.3982 | 11.7261 | 25.5496 | 7.1517 | 5.217 | 11.1581 | 26.0177 | 6.9765 | 5.0892 | 10.6024 | 26.6066 | 6.8093 | 4.9673 | 10.0005 | 27.1025 | 6.579 | 4.7993 | 9.5413 | 24.056 | 9.0963 | 6.6356 | 14.9072 | 24.1381 | 8.59 | 6.2663 | 13.4193 | 24.2382 | 8.4897 | 6.1931 | 12.887 | 24.3786 | 8.2923 | 6.0491 | 12.6047 | 24.5925 | 8.012 | 5.8446 | 11.6495 | 24.8304 | 7.6577 | 5.5862 | 10.6811 | 25.0787 | 7.3353 | 5.351 | 9.7257 | 25.3388 | 7.0171 | 5.1189 | 8.7857 | 25.5331 | 6.7199 | 4.9021 | 7.8656 | 25.7155 | 6.4512 | 4.7061 | 6.9699 | 26.4457 | 5.8065 | 4.2358 | 5.3865 | 26.9567 | 4.9315 | 3.5974 | 2.3828 | 25.9411 | 4.2079 | 3.0696 | -0.14062 | 20.9388 | 3.3965 | 2.4777 | -2.8291 | 15.7636 | 2.557 | 1.8653 | -5.1605 | 24.056 | 9.0963 | 6.6356 | 14.9072 | 24.0549 | 8.7278 | 6.3668 | 14.0146 | 24.1227 | 8.7212 | 6.362 | 13.6199 | 24.2692 | 8.5692 | 6.2511 | 13.3404 | 24.4948 | 8.2776 | 6.0384 | 12.3746 | 24.7675 | 7.9629 | 5.8089 | 11.3713 | 25.1783 | 7.5969 | 5.5419 | 10.1817 | 25.5936 | 7.1235 | 5.1965 | 8.4067 | 25.7878 | 6.6624 | 4.8601 | 6.5991 | 25.9521 | 6.1691 | 4.5003 | 4.8082 | 26.4472 | 5.4828 | 3.9996 | 1.756 | 26.9249 | 4.6033 | 3.3581 | -1.1055 | 23.6696 | 3.8394 | 2.8008 | -3.4066 | 19.8044 | 3.2125 | 2.3435 | -4.8514 | 19.3133 | 3.1328 | 2.2853 | -3.9023 | 24.0512 | 9.0963 | 6.6356 | 14.9072 | 24.1138 | 8.7834 | 6.4074 | 14.3524 | 24.182 | 8.8043 | 6.4226 | 14.0108 | 24.2614 | 8.6958 | 6.3435 | 13.7932 | 24.3707 | 8.5917 | 6.2675 | 13.5698 | 24.5071 | 8.381 | 6.1139 | 13.3231 | 24.6658 | 8.2076 | 5.9873 | 13.0397 | 24.8451 | 8.0305 | 5.8582 | 12.7386 | 24.9958 | 7.8817 | 5.7496 | 12.4183 | 25.1523 | 7.7408 | 5.6468 | 12.0969 | 25.7418 | 7.358 | 5.3675 | 11.3331 | 26.4594 | 7.0654 | 5.1541 | 10.454 | 26.8106 | 6.8445 | 4.993 | 9.8287 | 27.0143 | 6.6065 | 4.8193 | 9.2152 | 27.0893 | 6.3238 | 4.6131 | 8.9394 | 24.0512 | 9.0963 | 6.6356 | 14.9072 | 24.0693 | 8.5679 | 6.2501 | 13.3699 | 24.1672 | 8.5076 | 6.2061 | 12.8011 | 24.3502 | 8.3293 | 6.0761 | 12.4401 | 24.6058 | 8.0154 | 5.8471 | 11.4001 | 24.8795 | 7.6929 | 5.6119 | 10.3534 | 25.28 | 7.3152 | 5.3364 | 9.1245 | 25.8169 | 6.8234 | 4.9776 | 7.2786 | 25.9903 | 6.351 | 4.6329 | 5.4343 | 26.1613 | 5.8407 | 4.2607 | 3.6094 | 26.6718 | 5.1206 | 3.7354 | 0.46613 | 25.9719 | 4.2129 | 3.0733 | -2.4695 | 21.0951 | 3.4218 | 2.4962 | -4.8603 | 17.05 | 2.7657 | 2.0175 | -6.4268 | 16.3575 | 2.6533 | 1.9356 | -5.6448
MARYPORT | STAINBURN & SIDDICK | HARKER / HUTTON | 303716 | 535313 | 22.7391 | 17.3101 | 12.4411 | 17.3203 | 22.8345 | 17.2142 | 12.3722 | 17.0873 | 22.9488 | 16.7546 | 12.0419 | 16.8811 | 23.094 | 16.291 | 11.7086 | 16.7087 | 23.2743 | 15.7776 | 11.3397 | 16.4581 | 23.485 | 15.2639 | 10.9705 | 16.206 | 23.7245 | 14.7633 | 10.6107 | 16.0071 | 23.9887 | 14.6239 | 10.5105 | 15.8212 | 24.2049 | 14.4743 | 10.403 | 15.5722 | 24.4166 | 14.3262 | 10.2965 | 15.3537 | 25.0858 | 13.7595 | 9.8892 | 13.798 | 25.7529 | 13.0438 | 9.3748 | 11.0641 | 26.2192 | 12.3106 | 8.8479 | 8.8355 | 26.594 | 11.3815 | 8.1801 | 6.6177 | 26.8324 | 10.4009 | 7.4753 | 4.8011 | 22.7116 | 17.3101 | 12.4411 | 17.3203 | 22.7978 | 17.2469 | 12.3957 | 17.1365 | 22.8754 | 17.1682 | 12.3391 | 16.9551 | 22.9628 | 17.0724 | 12.2703 | 16.78 | 23.0793 | 16.9419 | 12.1765 | 16.5658 | 23.2262 | 16.806 | 12.0788 | 16.3421 | 23.4023 | 16.659 | 11.9732 | 16.0559 | 23.6057 | 16.5094 | 11.8657 | 15.6845 | 23.7222 | 16.3794 | 11.7722 | 15.3752 | 23.8454 | 16.2442 | 11.6751 | 15.0684 | 24.2435 | 15.8559 | 11.396 | 14.1626 | 24.6148 | 15.4982 | 11.1389 | 13.3002 | 24.9495 | 15.1541 | 10.8915 | 12.5396 | 25.2871 | 14.732 | 10.5882 | 11.7206 | 25.5176 | 14.2018 | 10.2071 | 11.1883 | 22.7511 | 17.3101 | 12.4411 | 17.3203 | 22.8518 | 17.1858 | 12.3518 | 17.0914 | 22.981 | 16.6655 | 11.9778 | 16.9097 | 23.1484 | 16.1445 | 11.6034 | 16.7816 | 23.3564 | 15.5889 | 11.204 | 16.5775 | 23.6001 | 15.0451 | 10.8132 | 16.3807 | 23.8526 | 14.5145 | 10.4319 | 16.2567 | 24.1559 | 14.3366 | 10.304 | 16.1568 | 24.3651 | 14.1498 | 10.1697 | 16.0154 | 24.5453 | 13.981 | 10.0484 | 15.884 | 25.361 | 13.276 | 9.5417 | 14.5833 | 26.1163 | 12.3615 | 8.8845 | 12.0733 | 26.6502 | 11.4286 | 8.214 | 10.0404 | 27.0692 | 9.9134 | 7.1249 | 8.0594 | 27.2641 | 9.0619 | 6.513 | 6.4788 | 22.7511 | 17.3101 | 12.4411 | 17.3203 | 22.7796 | 17.2266 | 12.3811 | 17.3232 | 22.8436 | 16.7509 | 12.0392 | 17.2125 | 22.9323 | 16.2336 | 11.6674 | 17.1031 | 23.0638 | 15.6819 | 11.2709 | 16.9249 | 23.2684 | 15.1009 | 10.8533 | 16.7288 | 23.5312 | 14.4247 | 10.3673 | 16.4131 | 23.812 | 14.0033 | 10.0645 | 15.576 | 24.0469 | 13.5874 | 9.7655 | 14.6922 | 24.2811 | 13.1833 | 9.4751 | 13.8185 | 24.9999 | 12.0065 | 8.6293 | 11.3128 | 25.7127 | 11.0101 | 7.9131 | 8.9381 | 26.207 | 10.1337 | 7.2833 | 7.0973 | 26.5755 | 9.2312 | 6.6347 | 6.0397 | 26.6646 | 8.9028 | 6.3986 | 7.1659 | 22.7391 | 17.3101 | 12.4411 | 17.3203 | 22.8242 | 17.2273 | 12.3816 | 17.1325 | 22.906 | 16.7772 | 12.0581 | 16.964 | 22.9987 | 16.3263 | 11.734 | 16.8459 | 23.1193 | 15.8387 | 11.3836 | 16.7217 | 23.3029 | 15.3486 | 11.0314 | 16.5873 | 23.5446 | 14.8577 | 10.6785 | 16.4334 | 23.8023 | 14.7155 | 10.5763 | 16.2203 | 23.9962 | 14.5558 | 10.4616 | 15.9026 | 24.1935 | 14.3931 | 10.3446 | 15.5865 | 24.8315 | 13.9058 | 9.9944 | 14.507 | 25.4832 | 13.4526 | 9.6686 | 13.3094 | 25.95 | 12.9859 | 9.3333 | 12.4967 | 26.3322 | 12.2622 | 8.813 | 11.7542 | 26.5044 | 11.5011 | 8.2661 | 11.5941 | 22.7391 | 17.3101 | 12.4411 | 17.3203 | 22.7994 | 17.2044 | 12.3652 | 17.2132 | 22.9089 | 16.7103 | 12.0101 | 17.0053 | 23.0542 | 16.1746 | 11.625 | 16.7944 | 23.2335 | 15.6059 | 11.2163 | 16.5228 | 23.4402 | 15.013 | 10.7901 | 16.2635 | 23.6811 | 14.3263 | 10.2966 | 15.8759 | 23.9756 | 13.884 | 9.9787 | 14.9341 | 24.2178 | 13.4627 | 9.6759 | 13.9756 | 24.4559 | 13.0442 | 9.3751 | 13.0289 | 25.17 | 11.8244 | 8.4984 | 10.2993 | 25.8375 | 10.7988 | 7.7613 | 7.718 | 26.3044 | 9.863 | 7.0888 | 5.6882 | 26.6288 | 8.9493 | 6.432 | 4.4038 | 26.7126 | 8.5478 | 6.1435 | 5.2591
MEDIPARK | ALTRINCHAM | CARRINGTON | 380478 | 387812 | 38.7601 | 11.0536 | 7.9444 | 33.8593 | 38.7612 | 10.9067 | 7.8389 | 33.6539 | 38.771 | 10.7881 | 7.7536 | 33.5647 | 38.7757 | 10.6915 | 7.6842 | 33.5461 | 38.777 | 10.537 | 7.5731 | 33.5475 | 38.7778 | 10.3916 | 7.4686 | 33.5529 | 38.7782 | 10.2446 | 7.363 | 33.5633 | 38.778 | 10.0515 | 7.2242 | 33.5771 | 38.7818 | 10.1508 | 7.2956 | 33.5515 | 38.7849 | 10.1793 | 7.316 | 33.5293 | 38.7935 | 10.1313 | 7.2816 | 33.4443 | 38.801 | 9.9763 | 7.1702 | 33.3339 | 38.8037 | 9.7393 | 6.9998 | 33.2562 | 38.8005 | 9.6652 | 6.9465 | 33.1951 | 38.7896 | 9.5179 | 6.8407 | 33.18 | 38.7601 | 11.0536 | 7.9444 | 33.8593 | 38.7641 | 11.0148 | 7.9165 | 33.8359 | 38.7775 | 10.9749 | 7.8879 | 33.7796 | 38.7868 | 10.9238 | 7.8512 | 33.7559 | 38.7933 | 10.8803 | 7.8199 | 33.7538 | 38.8007 | 10.821 | 7.7773 | 33.7542 | 38.808 | 10.5978 | 7.6168 | 33.7561 | 38.8139 | 10.5492 | 7.5819 | 33.7582 | 38.8226 | 10.4988 | 7.5457 | 33.713 | 38.8308 | 10.4498 | 7.5105 | 33.6705 | 38.8524 | 10.3169 | 7.415 | 33.5573 | 38.8672 | 10.2914 | 7.3966 | 33.4628 | 38.8788 | 10.221 | 7.3461 | 33.3907 | 38.8902 | 9.9216 | 7.1309 | 33.3194 | 38.8979 | 9.9732 | 7.1679 | 33.2655 | 38.7601 | 11.0536 | 7.9444 | 33.8593 | 38.762 | 10.8802 | 7.8198 | 33.6196 | 38.772 | 10.7252 | 7.7084 | 33.5233 | 38.7777 | 10.5848 | 7.6075 | 33.5039 | 38.7794 | 10.3835 | 7.4628 | 33.3244 | 38.7804 | 10.1654 | 7.3061 | 33.1489 | 38.7812 | 9.9581 | 7.1571 | 32.9784 | 38.7814 | 10.0358 | 7.2129 | 32.8112 | 38.7836 | 10.045 | 7.2196 | 32.6224 | 38.7834 | 10.0068 | 7.1921 | 32.439 | 38.7813 | 9.8678 | 7.0922 | 32.2949 | 38.7773 | 9.6618 | 6.9441 | 32.251 | 38.7681 | 9.5284 | 6.8483 | 32.2435 | 38.7485 | 9.3667 | 6.732 | 32.2805 | 38.7165 | 9.235 | 6.6374 | 32.3928 | 38.7601 | 11.0536 | 7.9444 | 33.8593 | 38.7599 | 10.9018 | 7.8353 | 33.6896 | 38.7683 | 10.7262 | 7.7091 | 33.6085 | 38.7724 | 10.4445 | 7.5067 | 33.5893 | 38.7723 | 10.1466 | 7.2926 | 33.4106 | 38.7713 | 10.2442 | 7.3627 | 33.2365 | 38.7704 | 10.2621 | 7.3756 | 33.0602 | 38.7699 | 10.1784 | 7.3154 | 32.8666 | 38.774 | 10.0127 | 7.1964 | 32.6479 | 38.7756 | 9.9583 | 7.1572 | 32.4345 | 38.7765 | 9.7277 | 6.9915 | 32.24 | 38.7722 | 9.5132 | 6.8373 | 32.197 | 38.7626 | 9.3382 | 6.7115 | 32.1919 | 38.7406 | 9.2045 | 6.6155 | 32.2649 | 38.7017 | 9.1284 | 6.5608 | 32.4762 | 38.7601 | 11.0536 | 7.9444 | 33.8593 | 38.7612 | 10.9626 | 7.879 | 33.8217 | 38.7709 | 10.8538 | 7.8008 | 33.7665 | 38.7755 | 10.7639 | 7.7362 | 33.7487 | 38.7763 | 10.6168 | 7.6305 | 33.7537 | 38.7763 | 10.4749 | 7.5285 | 33.7631 | 38.7761 | 10.3269 | 7.4222 | 33.7753 | 38.7757 | 10.143 | 7.2899 | 33.7884 | 38.7795 | 10.218 | 7.3439 | 33.7611 | 38.7828 | 10.2549 | 7.3704 | 33.7364 | 38.7899 | 10.246 | 7.364 | 33.6762 | 38.793 | 10.1559 | 7.2993 | 33.6364 | 38.7918 | 10.0384 | 7.2148 | 33.6263 | 38.7853 | 9.9922 | 7.1816 | 33.6424 | 38.7696 | 9.8994 | 7.1149 | 33.7233 | 38.7601 | 11.0536 | 7.9444 | 33.8593 | 38.7614 | 10.8569 | 7.803 | 33.5871 | 38.7713 | 10.6732 | 7.6711 | 33.4836 | 38.7771 | 10.3881 | 7.4661 | 33.4625 | 38.7789 | 10.0936 | 7.2545 | 33.2817 | 38.78 | 10.1815 | 7.3177 | 33.1052 | 38.7812 | 10.1942 | 7.3268 | 32.9264 | 38.783 | 10.1111 | 7.267 | 32.7301 | 38.7871 | 9.9606 | 7.1589 | 32.5115 | 38.7887 | 9.8813 | 7.1019 | 32.298 | 38.7898 | 9.6483 | 6.9344 | 32.1035 | 38.7856 | 9.4314 | 6.7785 | 32.0604 | 38.7762 | 9.2554 | 6.6521 | 32.055 | 38.7544 | 9.1186 | 6.5537 | 32.1276 | 38.7159 | 9.0081 | 6.4743 | 32.3384
MELLING | KENDAL (PARKSIDE RD) | HARKER / HUTTON | 360144 | 471643 | 6.6002 | 6.6002 | 6.6002 | 3.75 | 6.6347 | 6.6347 | 6.6347 | 3.634 | 6.6912 | 6.6912 | 6.6912 | 3.586 | 6.7535 | 6.7535 | 6.7535 | 3.5516 | 6.7894 | 6.7894 | 6.7894 | 3.496 | 6.824 | 6.824 | 6.824 | 3.4392 | 6.8618 | 6.8618 | 6.8618 | 3.391 | 6.9066 | 6.9066 | 6.9066 | 3.3454 | 6.9409 | 6.9409 | 6.9409 | 3.2771 | 6.9725 | 6.9725 | 6.9725 | 3.2168 | 7.0839 | 7.0839 | 7.0839 | 2.9046 | 7.2174 | 7.2174 | 7.2174 | 2.4109 | 7.3085 | 7.3085 | 7.3085 | 2.0193 | 7.3579 | 7.3579 | 7.3579 | 1.6585 | 7.383 | 7.383 | 7.383 | 1.3406 | 6.587 | 6.587 | 6.587 | 3.75 | 6.6084 | 6.6084 | 6.6084 | 3.6976 | 6.6335 | 6.6335 | 6.6335 | 3.6483 | 6.6698 | 6.6698 | 6.6698 | 3.5905 | 6.7208 | 6.7208 | 6.7208 | 3.5158 | 6.7858 | 6.7858 | 6.7858 | 3.4344 | 6.8573 | 6.8573 | 6.8573 | 3.3361 | 6.9072 | 6.9072 | 6.9072 | 3.1485 | 6.9284 | 6.9284 | 6.9284 | 3.0986 | 6.9497 | 6.9497 | 6.9497 | 3.0336 | 7.0126 | 7.0126 | 7.0126 | 2.7924 | 7.0696 | 7.0696 | 7.0696 | 2.586 | 7.1196 | 7.1196 | 7.1196 | 2.4186 | 7.1721 | 7.1721 | 7.1721 | 2.2614 | 7.2122 | 7.2122 | 7.2122 | 2.1566 | 6.6066 | 6.6066 | 6.6066 | 3.75 | 6.646 | 6.646 | 6.646 | 3.6247 | 6.7112 | 6.7112 | 6.7112 | 3.5807 | 6.7665 | 6.7665 | 6.7665 | 3.5568 | 6.8009 | 6.8009 | 6.8009 | 3.5133 | 6.8401 | 6.8401 | 6.8401 | 3.471 | 6.8838 | 6.8838 | 6.8838 | 3.4421 | 6.9357 | 6.9357 | 6.9357 | 3.4173 | 6.9735 | 6.9735 | 6.9735 | 3.3633 | 7.0081 | 7.0081 | 7.0081 | 3.221 | 7.128 | 7.128 | 7.128 | 2.7289 | 7.2683 | 7.2683 | 7.2683 | 2.1519 | 7.3477 | 7.3477 | 7.3477 | 1.7195 | 7.3911 | 7.3911 | 7.3911 | 1.3532 | 7.3872 | 7.3872 | 7.3872 | 1.0911 | 6.6066 | 6.6066 | 6.6066 | 3.75 | 6.6166 | 6.6166 | 6.6166 | 3.7066 | 6.6486 | 6.6486 | 6.6486 | 3.6881 | 6.6962 | 6.6962 | 6.6962 | 3.6696 | 6.742 | 6.742 | 6.742 | 3.6346 | 6.7724 | 6.7724 | 6.7724 | 3.5956 | 6.8095 | 6.8095 | 6.8095 | 3.5381 | 6.8585 | 6.8585 | 6.8585 | 3.3955 | 6.9064 | 6.9064 | 6.9064 | 3.2401 | 6.9528 | 6.9528 | 6.9528 | 3.087 | 7.0882 | 7.0882 | 7.0882 | 2.6515 | 7.1843 | 7.1843 | 7.1843 | 2.1956 | 7.2483 | 7.2483 | 7.2483 | 1.79 | 7.2898 | 7.2898 | 7.2898 | 1.5024 | 7.2478 | 7.2478 | 7.2478 | 1.5051 | 6.6002 | 6.6002 | 6.6002 | 3.75 | 6.6284 | 6.6284 | 6.6284 | 3.7049 | 6.666 | 6.666 | 6.666 | 3.6768 | 6.713 | 6.713 | 6.713 | 3.6545 | 6.76 | 6.76 | 6.76 | 3.6254 | 6.7921 | 6.7921 | 6.7921 | 3.5933 | 6.8282 | 6.8282 | 6.8282 | 3.5566 | 6.8681 | 6.8681 | 6.8681 | 3.5171 | 6.8991 | 6.8991 | 6.8991 | 3.4612 | 6.9293 | 6.9293 | 6.9293 | 3.3982 | 7.0254 | 7.0254 | 7.0254 | 3.1843 | 7.128 | 7.128 | 7.128 | 2.8166 | 7.2007 | 7.2007 | 7.2007 | 2.5198 | 7.2642 | 7.2642 | 7.2642 | 2.2591 | 7.2947 | 7.2947 | 7.2947 | 2.1217 | 6.6002 | 6.6002 | 6.6002 | 3.75 | 6.6256 | 6.6256 | 6.6256 | 3.6441 | 6.681 | 6.681 | 6.681 | 3.5927 | 6.7454 | 6.7454 | 6.7454 | 3.5452 | 6.7829 | 6.7829 | 6.7829 | 3.4829 | 6.8177 | 6.8177 | 6.8177 | 3.4231 | 6.8599 | 6.8599 | 6.8599 | 3.3415 | 6.922 | 6.922 | 6.922 | 3.1658 | 6.9728 | 6.9728 | 6.9728 | 2.9891 | 7.021 | 7.021 | 7.021 | 2.8153 | 7.154 | 7.154 | 7.154 | 2.3203 | 7.2399 | 7.2399 | 7.2399 | 1.8565 | 7.296 | 7.296 | 7.296 | 1.495 | 7.3279 | 7.3279 | 7.3279 | 1.2745 | 7.3211 | 7.3211 | 7.3211 | 1.4137
MERESIDE | PEEL | PENWORTHAM WEST / STANAH | 334431 | 434843 | 29.0402 | 13.7493 | 10.0299 | 19.1488 | 29.0825 | 13.436 | 9.8014 | 18.2114 | 29.143 | 13.4182 | 9.7884 | 17.9252 | 29.2164 | 13.3556 | 9.7428 | 17.8082 | 29.2744 | 13.2154 | 9.6405 | 17.6769 | 29.3386 | 13.0777 | 9.54 | 17.5376 | 29.4163 | 13.0021 | 9.4849 | 17.397 | 29.5121 | 12.9352 | 9.4361 | 17.2505 | 29.5965 | 12.8646 | 9.3845 | 17.0673 | 29.6823 | 12.8117 | 9.346 | 16.8937 | 29.9555 | 12.603 | 9.1937 | 16.1057 | 30.219 | 12.3704 | 9.024 | 14.9505 | 30.3993 | 12.2551 | 8.9399 | 14.0363 | 30.5444 | 14.7706 | 10.7749 | 13.0551 | 30.6415 | 17.408 | 12.6989 | 12.169 | 29.0277 | 13.7493 | 10.0299 | 19.1488 | 29.0829 | 13.5415 | 9.8783 | 18.9024 | 29.1429 | 13.3516 | 9.7398 | 18.7605 | 29.2141 | 13.4017 | 9.7764 | 18.6718 | 29.2912 | 13.4631 | 9.8212 | 18.581 | 29.3659 | 13.4468 | 9.8093 | 18.4762 | 29.4566 | 13.1975 | 9.6274 | 18.3424 | 29.5637 | 13.1892 | 9.6213 | 18.1691 | 29.6129 | 13.168 | 9.6059 | 17.9834 | 29.6655 | 13.1419 | 9.5869 | 17.7962 | 29.8411 | 13.0146 | 9.494 | 17.2355 | 30.0322 | 12.8601 | 9.3813 | 16.6758 | 30.2135 | 12.8182 | 9.3507 | 16.1662 | 30.4024 | 14.8409 | 10.8263 | 15.6195 | 30.5348 | 16.9259 | 12.3472 | 15.2263 | 29.0439 | 13.7493 | 10.0299 | 19.1488 | 29.0903 | 13.4175 | 9.7879 | 18.0668 | 29.1568 | 13.3486 | 9.7376 | 17.7556 | 29.2312 | 13.2729 | 9.6824 | 17.6381 | 29.2891 | 13.1227 | 9.5728 | 17.5076 | 29.3575 | 12.9979 | 9.4818 | 17.3697 | 29.44 | 12.9186 | 9.4239 | 17.23 | 29.5405 | 12.8355 | 9.3633 | 17.0865 | 29.6232 | 12.775 | 9.3192 | 16.9313 | 29.7062 | 12.7141 | 9.2747 | 16.7881 | 29.9846 | 12.4769 | 9.1017 | 16.0887 | 30.2689 | 12.2141 | 8.91 | 15.0258 | 30.4667 | 12.087 | 8.8173 | 14.1997 | 30.6167 | 14.5901 | 10.6433 | 13.3587 | 30.7032 | 17.2246 | 12.5651 | 12.6608 | 29.0439 | 13.7493 | 10.0299 | 19.1488 | 29.0433 | 13.4812 | 9.8344 | 18.4576 | 29.0727 | 13.4431 | 9.8066 | 18.2437 | 29.1129 | 13.323 | 9.719 | 18.1601 | 29.1725 | 13.1662 | 9.6046 | 18.0538 | 29.2279 | 13.0279 | 9.5037 | 17.9193 | 29.3015 | 12.8916 | 9.4043 | 17.7299 | 29.3918 | 12.7782 | 9.3215 | 17.3943 | 29.4776 | 12.6871 | 9.2551 | 17.0318 | 29.5656 | 12.591 | 9.1849 | 16.6758 | 29.8392 | 12.3281 | 8.9932 | 15.6222 | 30.0991 | 12.1821 | 8.8867 | 14.5299 | 30.272 | 12.5559 | 9.1594 | 13.714 | 30.3925 | 17.3576 | 12.6621 | 13.2143 | 30.4213 | 17.2057 | 12.5513 | 13.4479 | 29.0402 | 13.7493 | 10.0299 | 19.1488 | 29.0776 | 13.524 | 9.8656 | 18.7293 | 29.123 | 13.5157 | 9.8595 | 18.5548 | 29.1722 | 13.4663 | 9.8234 | 18.4797 | 29.228 | 13.3365 | 9.7288 | 18.4114 | 29.2837 | 13.2005 | 9.6295 | 18.318 | 29.3581 | 13.128 | 9.5767 | 18.2052 | 29.4419 | 13.0629 | 9.5292 | 18.0848 | 29.5132 | 12.9934 | 9.4785 | 17.9131 | 29.5878 | 12.9404 | 9.4399 | 17.742 | 29.8365 | 12.7694 | 9.3151 | 17.1905 | 30.0893 | 12.6231 | 9.2084 | 16.5886 | 30.2674 | 12.588 | 9.1827 | 16.1799 | 30.4103 | 15.1956 | 11.085 | 15.8129 | 30.4883 | 17.948 | 13.0928 | 15.6309 | 29.0402 | 13.7493 | 10.0299 | 19.1488 | 29.0594 | 13.3992 | 9.7746 | 17.9991 | 29.1164 | 13.3479 | 9.7371 | 17.6699 | 29.189 | 13.2177 | 9.6421 | 17.5394 | 29.2448 | 13.0602 | 9.5272 | 17.3928 | 29.3064 | 12.9192 | 9.4244 | 17.2423 | 29.3821 | 12.7861 | 9.3272 | 17.0422 | 29.4829 | 12.6632 | 9.2377 | 16.6748 | 29.5692 | 12.5692 | 9.1691 | 16.29 | 29.6568 | 12.4702 | 9.0969 | 15.9144 | 29.9321 | 12.201 | 8.9005 | 14.8311 | 30.1944 | 12.0514 | 8.7913 | 13.742 | 30.3741 | 12.4192 | 9.0596 | 12.903 | 30.4917 | 17.217 | 12.5595 | 12.3826 | 30.5227 | 17.1002 | 12.4744 | 12.5736
MIDDLETON JUNCTION | CHADDERTON | WHITEGATE | 388606 | 405292 | 30.9609 | 13.0495 | 9.379 | 13.227 | 31.0263 | 12.9002 | 9.2716 | 12.748 | 31.128 | 10.921 | 7.8492 | 12.7618 | 31.234 | 8.9294 | 6.4177 | 12.7255 | 31.321 | 6.8992 | 4.9586 | 12.6161 | 29.5755 | 4.8694 | 3.4997 | 12.4839 | 17.3435 | 2.8555 | 2.0523 | 12.3496 | 16.7851 | 2.7635 | 1.9862 | 12.2168 | 16.2038 | 2.6678 | 1.9174 | 12.0101 | 16.2039 | 2.6679 | 1.9174 | 11.7262 | 15.4529 | 2.5442 | 1.8286 | 9.9639 | 19.6133 | 3.2292 | 2.3209 | 7.1765 | 33.6135 | 5.9497 | 4.2762 | 4.8869 | 33.9651 | 9.2388 | 6.6401 | 2.3932 | 34.2151 | 9.8603 | 7.0868 | 0.046124 | 30.9408 | 13.0495 | 9.379 | 13.227 | 30.9956 | 12.9887 | 9.3352 | 12.9739 | 31.0618 | 11.0538 | 7.9446 | 13.0032 | 31.1381 | 9.0839 | 6.5288 | 12.9259 | 31.24 | 7.1103 | 5.1103 | 12.8161 | 31.079 | 5.1169 | 3.6776 | 12.6869 | 18.3569 | 3.0223 | 2.1722 | 12.5021 | 17.7577 | 2.9237 | 2.1013 | 12.2602 | 17.2161 | 2.8345 | 2.0372 | 12.0113 | 16.6769 | 2.7457 | 1.9734 | 11.7567 | 15.0708 | 2.4813 | 1.7834 | 10.9558 | 13.562 | 2.2329 | 1.6048 | 9.9258 | 23.5742 | 3.8813 | 2.7896 | 8.9076 | 33.321 | 6.4691 | 4.6495 | 7.8257 | 33.5982 | 6.9116 | 4.9675 | 7.0741 | 30.9694 | 13.0495 | 9.379 | 13.227 | 31.0432 | 12.8749 | 9.2535 | 12.7241 | 31.1582 | 10.8558 | 7.8023 | 12.7518 | 31.2556 | 8.8233 | 6.3415 | 12.7552 | 31.3463 | 6.7894 | 4.8797 | 12.6859 | 28.8817 | 4.7551 | 3.4176 | 12.6006 | 16.6236 | 2.7369 | 1.9671 | 12.5376 | 16.0053 | 2.6351 | 1.8939 | 12.4788 | 15.3327 | 2.5244 | 1.8143 | 12.3642 | 15.1514 | 2.4946 | 1.7929 | 12.1299 | 14.3343 | 2.36 | 1.6962 | 10.5745 | 18.794 | 3.0943 | 2.2239 | 7.9154 | 33.6506 | 5.7941 | 4.1643 | 5.7373 | 33.9997 | 9.0394 | 6.4968 | 3.527 | 34.2125 | 9.6839 | 6.96 | 1.536 | 30.9694 | 13.0495 | 9.379 | 13.227 | 30.9486 | 12.9688 | 9.321 | 13.1268 | 30.9991 | 12.8956 | 9.2683 | 13.2474 | 31.0699 | 12.7698 | 9.1779 | 13.2625 | 31.1352 | 12.6293 | 9.0769 | 13.1761 | 31.2364 | 12.4826 | 8.9715 | 13.0543 | 31.3669 | 12.2494 | 8.8039 | 12.7815 | 31.555 | 12.0219 | 8.6404 | 11.9753 | 31.7475 | 11.8913 | 8.5465 | 11.1104 | 31.9494 | 11.752 | 8.4464 | 10.2358 | 32.5755 | 11.5989 | 8.3364 | 7.6692 | 33.1182 | 10.9264 | 7.853 | 5.169 | 33.4852 | 10.3493 | 7.4383 | 3.1339 | 33.7306 | 9.8777 | 7.0993 | 1.8038 | 33.7327 | 9.815 | 7.0542 | 2.5675 | 30.9609 | 13.0495 | 9.379 | 13.227 | 31.0165 | 12.9709 | 9.3224 | 12.9892 | 31.0862 | 11.0203 | 7.9205 | 13.0836 | 31.1601 | 9.045 | 6.5008 | 13.1103 | 31.2283 | 7.0427 | 5.0617 | 13.1157 | 30.5742 | 5.0338 | 3.6179 | 13.0834 | 18.3975 | 3.029 | 2.177 | 13.0141 | 17.9019 | 2.9474 | 2.1184 | 12.924 | 17.3399 | 2.8549 | 2.0519 | 12.7351 | 17.4235 | 2.8687 | 2.0618 | 12.5452 | 17.5225 | 2.8849 | 2.0735 | 11.5088 | 23.5608 | 3.8791 | 2.788 | 10.353 | 33.1981 | 6.8733 | 4.94 | 9.5388 | 33.461 | 10.5384 | 7.5741 | 8.8237 | 33.5855 | 11.539 | 8.2933 | 8.4692 | 30.9609 | 13.0495 | 9.379 | 13.227 | 30.9668 | 12.9109 | 9.2793 | 12.9446 | 31.0594 | 12.8112 | 9.2077 | 12.9711 | 31.1568 | 12.6645 | 9.1022 | 12.9116 | 31.2414 | 12.5116 | 8.9923 | 12.7585 | 31.3315 | 12.36 | 8.8834 | 12.594 | 31.4537 | 12.1193 | 8.7104 | 12.2661 | 31.646 | 11.8913 | 8.5465 | 11.3893 | 31.833 | 11.74 | 8.4377 | 10.4755 | 32.0283 | 11.588 | 8.3285 | 9.5506 | 32.6544 | 11.3865 | 8.1837 | 6.8049 | 33.2462 | 10.6843 | 7.679 | 4.1325 | 33.6453 | 10.0725 | 7.2393 | 1.9077 | 33.9036 | 9.56 | 6.871 | 0.34682 | 33.9195 | 9.4547 | 6.7952 | 0.88809
MIDWAY | EGREMONT | HARKER / HUTTON | 304525 | 501993 | 17.7299 | 17.7299 | 17.7299 | 12.1984 | 17.8385 | 17.8385 | 17.8385 | 12.0367 | 17.9574 | 17.9574 | 17.9574 | 11.9304 | 18.0864 | 18.0864 | 18.0864 | 11.8419 | 18.2315 | 18.2315 | 18.2315 | 11.7015 | 18.3729 | 18.3729 | 18.3506 | 11.5542 | 18.5398 | 18.5398 | 18.2632 | 11.4268 | 18.7467 | 18.7467 | 18.187 | 11.3323 | 18.9282 | 18.9282 | 18.1091 | 11.2247 | 19.0657 | 19.0657 | 18.0335 | 11.1333 | 19.4036 | 19.4036 | 17.7978 | 10.3912 | 19.7053 | 19.7053 | 17.5373 | 9.0792 | 19.9064 | 19.9064 | 17.2987 | 8.1095 | 20.0466 | 20.0466 | 17.0084 | 7.3156 | 20.1052 | 20.1052 | 16.7206 | 6.6158 | 17.7195 | 17.7195 | 17.7195 | 12.1984 | 17.7877 | 17.7877 | 17.7877 | 12.0757 | 17.8512 | 17.8512 | 17.8512 | 11.9826 | 17.9356 | 17.9356 | 17.9356 | 11.8828 | 18.0498 | 18.0498 | 18.0498 | 11.7526 | 18.1623 | 18.1623 | 18.1623 | 11.6127 | 18.2685 | 18.2685 | 18.2685 | 11.4406 | 18.3903 | 18.3903 | 18.3903 | 11.2374 | 18.4758 | 18.4758 | 18.4758 | 11.1169 | 18.5688 | 18.5688 | 18.4408 | 10.9948 | 18.894 | 18.894 | 18.3212 | 10.6266 | 19.2468 | 19.2468 | 18.2071 | 10.2577 | 19.5601 | 19.5601 | 18.0941 | 9.9054 | 19.7227 | 19.7227 | 17.9827 | 9.5156 | 19.8047 | 19.8047 | 17.8544 | 9.2336 | 17.7339 | 17.7339 | 17.7339 | 12.1984 | 17.8468 | 17.8468 | 17.8468 | 12.0312 | 17.9667 | 17.9667 | 17.9667 | 11.9351 | 18.1051 | 18.1051 | 18.1051 | 11.8686 | 18.2568 | 18.2568 | 18.2568 | 11.7524 | 18.4088 | 18.4088 | 18.2902 | 11.6342 | 18.5879 | 18.5879 | 18.196 | 11.5467 | 18.8106 | 18.8106 | 18.1113 | 11.4972 | 18.9768 | 18.9768 | 18.0249 | 11.44 | 19.1015 | 19.1015 | 17.94 | 11.3909 | 19.402 | 19.402 | 17.5958 | 10.162 | 19.7276 | 19.7276 | 17.2653 | 8.7241 | 19.9416 | 19.9416 | 16.9507 | 7.6492 | 20.0874 | 20.0874 | 16.5532 | 6.7696 | 20.1448 | 20.1448 | 16.2196 | 6.185 | 17.734 | 17.734 | 17.734 | 12.1984 | 17.7964 | 17.7964 | 17.7964 | 12.1815 | 17.879 | 17.879 | 17.879 | 12.1328 | 17.9717 | 17.9717 | 17.9717 | 12.0694 | 18.0939 | 18.0939 | 18.0939 | 11.9673 | 18.2493 | 18.2493 | 18.2122 | 11.8506 | 18.4261 | 18.4261 | 17.6828 | 11.6836 | 18.6343 | 18.6343 | 17.06 | 11.331 | 18.7925 | 18.7925 | 17.4014 | 10.9552 | 18.9235 | 18.9235 | 17.4571 | 10.5847 | 19.2881 | 19.2881 | 17.2096 | 9.5076 | 19.5909 | 19.5909 | 17.0083 | 8.484 | 19.7871 | 19.7871 | 17.0144 | 7.6143 | 19.9073 | 19.9073 | 16.8612 | 6.9767 | 19.8734 | 19.8734 | 16.6381 | 7.0373 | 17.7299 | 17.7299 | 17.7299 | 12.1984 | 17.8194 | 17.8194 | 17.8194 | 12.067 | 17.9025 | 17.9025 | 17.9025 | 11.9819 | 17.9938 | 17.9938 | 17.9938 | 11.9214 | 18.0999 | 18.0999 | 18.0999 | 11.8482 | 18.2329 | 18.2329 | 18.2329 | 11.7678 | 18.386 | 18.386 | 18.3023 | 11.6707 | 18.5618 | 18.5618 | 18.2263 | 11.5743 | 18.7129 | 18.7129 | 18.1463 | 11.4464 | 18.8703 | 18.8703 | 18.0662 | 11.3174 | 19.2518 | 19.2518 | 17.8634 | 10.8275 | 19.5533 | 19.5533 | 17.6477 | 9.8667 | 19.741 | 19.741 | 17.43 | 9.0711 | 19.8849 | 19.8849 | 17.1461 | 8.4009 | 19.9072 | 19.9072 | 16.8992 | 8.1265 | 17.7299 | 17.7299 | 17.7299 | 12.1984 | 17.8077 | 17.8077 | 17.8077 | 12.0933 | 17.9198 | 17.9198 | 17.9198 | 11.8286 | 18.0448 | 18.0448 | 18.0448 | 11.551 | 18.1871 | 18.1871 | 18.1871 | 11.2393 | 18.3182 | 18.3182 | 18.0926 | 10.9307 | 18.4746 | 18.4746 | 17.5387 | 10.567 | 18.6793 | 18.6793 | 16.888 | 9.9998 | 18.8572 | 18.8572 | 17.2041 | 9.4317 | 19.0205 | 19.0205 | 17.2293 | 8.8692 | 19.3774 | 19.3774 | 16.9833 | 7.6944 | 19.6821 | 19.6821 | 16.7334 | 6.5637 | 19.8863 | 19.8863 | 16.7445 | 5.6974 | 20.0068 | 20.0068 | 16.6076 | 5.2143 | 19.9992 | 19.9992 | 16.5107 | 5.6154
MILNROW | CASTLETON | ROCHDALE | 392351 | 413056 | 28.8071 | 10.9049 | 7.955 | 17.0934 | 28.9015 | 10.7062 | 7.81 | 16.3155 | 28.9865 | 10.4883 | 7.651 | 16.0337 | 29.1049 | 10.2868 | 7.5041 | 15.9066 | 29.3088 | 10.1404 | 7.3973 | 15.7207 | 29.5269 | 9.9865 | 7.285 | 15.5253 | 29.7128 | 9.8257 | 7.1677 | 15.3548 | 29.8742 | 9.6896 | 7.0685 | 15.2067 | 30.025 | 9.5996 | 7.0028 | 14.9965 | 30.1775 | 9.5039 | 6.9329 | 14.8004 | 30.7274 | 9.0768 | 6.6214 | 13.3235 | 31.3496 | 8.4659 | 6.1758 | 10.6579 | 31.743 | 7.9686 | 5.813 | 8.4012 | 31.9947 | 7.5807 | 5.53 | 5.9962 | 32.1465 | 7.1795 | 5.2373 | 3.8285 | 28.8057 | 10.9049 | 7.955 | 17.0934 | 28.8738 | 10.8425 | 7.9094 | 16.8321 | 28.9141 | 10.76 | 7.8493 | 16.6598 | 28.9655 | 10.6619 | 7.7777 | 16.5422 | 29.0358 | 10.5521 | 7.6976 | 16.4172 | 29.1007 | 10.4228 | 7.6033 | 16.2863 | 29.191 | 10.222 | 7.4568 | 16.1131 | 29.3316 | 10.1374 | 7.3951 | 15.8753 | 29.4615 | 10.068 | 7.3445 | 15.6295 | 29.5961 | 10.0049 | 7.2984 | 15.3807 | 30.0255 | 9.7477 | 7.1108 | 14.6225 | 30.4132 | 9.5731 | 6.9834 | 13.8285 | 30.7331 | 9.3766 | 6.8401 | 13.0307 | 31.0796 | 9.0525 | 6.6037 | 12.111 | 31.328 | 9.0575 | 6.6073 | 11.4071 | 28.8077 | 10.9049 | 7.955 | 17.0934 | 28.905 | 10.6776 | 7.7892 | 16.2202 | 28.9913 | 10.4184 | 7.6001 | 15.9318 | 29.1127 | 10.2461 | 7.4744 | 15.7154 | 29.318 | 10.0316 | 7.3179 | 15.4377 | 29.5371 | 9.8189 | 7.1627 | 15.1544 | 29.7408 | 9.612 | 7.0118 | 14.8506 | 29.9318 | 9.4845 | 6.9188 | 14.7537 | 30.0917 | 9.3804 | 6.8428 | 14.6302 | 30.2422 | 9.2839 | 6.7724 | 14.4994 | 30.8092 | 8.8085 | 6.4257 | 13.2145 | 31.4765 | 8.1898 | 5.9743 | 10.7148 | 31.823 | 7.7198 | 5.6315 | 8.6223 | 32.054 | 7.3263 | 5.3445 | 6.4438 | 32.1678 | 6.9234 | 5.0505 | 4.5476 | 28.8077 | 10.9049 | 7.955 | 17.0934 | 28.8332 | 10.7589 | 7.8484 | 16.5989 | 28.9022 | 10.5457 | 7.6929 | 16.399 | 29.042 | 10.3953 | 7.5832 | 16.1783 | 29.2709 | 10.2021 | 7.4423 | 15.8814 | 29.4701 | 9.9776 | 7.2785 | 15.5644 | 29.6265 | 9.6779 | 7.0599 | 15.0635 | 29.85 | 9.3262 | 6.8033 | 14.2633 | 30.0351 | 9.0834 | 6.6262 | 13.4178 | 30.2237 | 8.9628 | 6.5383 | 12.5643 | 30.803 | 8.3692 | 6.1052 | 10.0956 | 31.3559 | 7.7965 | 5.6874 | 7.7173 | 31.6462 | 7.339 | 5.3537 | 5.8009 | 31.8172 | 7.1237 | 5.1966 | 4.5873 | 31.8008 | 7.1034 | 5.1818 | 5.2917 | 28.8071 | 10.9049 | 7.955 | 17.0934 | 28.8856 | 10.7751 | 7.8603 | 16.7025 | 28.9546 | 10.5889 | 7.7245 | 16.5205 | 29.0329 | 10.4048 | 7.5901 | 16.4452 | 29.1363 | 10.2975 | 7.5119 | 16.3734 | 29.2541 | 10.151 | 7.405 | 16.2864 | 29.3892 | 10.0055 | 7.2989 | 16.1894 | 29.5463 | 9.8768 | 7.205 | 16.0774 | 29.7133 | 9.786 | 7.1388 | 15.8694 | 29.8871 | 9.6908 | 7.0693 | 15.6591 | 30.4377 | 9.3943 | 6.853 | 14.9191 | 30.9007 | 9.0915 | 6.6321 | 14.0565 | 31.228 | 8.9088 | 6.4989 | 13.4571 | 31.4951 | 8.87 | 6.4706 | 12.8746 | 31.6397 | 8.7993 | 6.419 | 12.5596 | 28.8071 | 10.9049 | 7.955 | 17.0934 | 28.8449 | 10.6802 | 7.791 | 16.225 | 28.9329 | 10.4376 | 7.6141 | 15.9072 | 29.0948 | 10.2826 | 7.501 | 15.6312 | 29.3416 | 10.0693 | 7.3454 | 15.2839 | 29.5501 | 9.8379 | 7.1766 | 14.9323 | 29.6963 | 9.536 | 6.9564 | 14.39 | 29.9232 | 9.173 | 6.6916 | 13.5337 | 30.1154 | 8.9615 | 6.5373 | 12.6516 | 30.3006 | 8.7918 | 6.4135 | 11.7609 | 30.873 | 8.179 | 5.9665 | 9.1643 | 31.4138 | 7.5729 | 5.5244 | 6.6548 | 31.7615 | 7.0893 | 5.1716 | 4.5889 | 31.9325 | 6.8392 | 4.9891 | 3.1847 | 31.9227 | 6.7813 | 4.9468 | 3.6877
MINTSFEET | KENDAL (PARKSIDE RD) | HARKER / HUTTON | 351827 | 494315 | 15.9393 | 2.6243 | 1.8861 | 9.1835 | 13.0959 | 2.1561 | 1.5497 | 6.8417 | 11.7999 | 1.9428 | 1.3963 | 6.1697 | 10.8704 | 1.7897 | 1.2863 | 5.8572 | 9.6435 | 1.5877 | 1.1411 | 5.4928 | 9.0307 | 1.4868 | 1.0686 | 5.0747 | 7.7385 | 1.2741 | 0.91571 | 4.3396 | 6.829 | 1.1243 | 0.80809 | 3.9456 | 5.8155 | 0.95747 | 0.68815 | 3.4697 | 4.5618 | 0.75106 | 0.5398 | 2.7973 | 0.87844 | 0.14463 | 0.10395 | 0.87844 | 2.6844 | 0.44197 | 0.31765 | -5.5633 | 2.6844 | 0.44197 | 0.31765 | -8.5038 | 5.2727 | 0.8681 | 0.62392 | -14.0797 | 25.8572 | 4.2572 | 3.0597 | -15.9053 | 15.9393 | 2.6243 | 1.8861 | 9.1835 | 14.8143 | 2.4391 | 1.753 | 8.3186 | 14.1743 | 2.3337 | 1.6773 | 8.0185 | 13.3627 | 2.2001 | 1.5812 | 7.739 | 12.4837 | 2.0553 | 1.4772 | 7.4239 | 11.3228 | 1.8642 | 1.3398 | 7.0007 | 9.6564 | 1.5899 | 1.1427 | 6.4592 | 8.316 | 1.3692 | 0.98404 | 5.8297 | 6.946 | 1.1436 | 0.82194 | 5.3917 | 6.0786 | 1.0008 | 0.71929 | 4.9679 | 3.8272 | 0.63013 | 0.45288 | 3.6789 | 1.2501 | 0.20582 | 0.14793 | 1.2501 | 2.6844 | 0.44197 | 0.31765 | 1.0393 | 12.5946 | 2.0736 | 1.4903 | -3.4802 | 29.4502 | 4.8488 | 3.4849 | -4.2432 | 15.9393 | 2.6243 | 1.8861 | 9.1835 | 12.5992 | 2.0744 | 1.4909 | 6.4977 | 10.9553 | 1.8037 | 1.2964 | 5.7663 | 9.303 | 1.5317 | 1.1008 | 5.4533 | 8.8705 | 1.4605 | 1.0497 | 5.091 | 7.8426 | 1.2912 | 0.92803 | 4.6773 | 6.3686 | 1.0485 | 0.7536 | 3.9544 | 5.2667 | 0.86713 | 0.62322 | 3.5668 | 3.8757 | 0.63811 | 0.45862 | 2.863 | 2.8854 | 0.47506 | 0.34144 | 2.5605 | 2.6844 | 0.44197 | 0.31765 | -9.3872 | 2.6844 | 0.44197 | 0.31765 | -12.2527 | 2.6844 | 0.44197 | 0.31765 | -14.2046 | 2.6844 | 0.44197 | 0.31765 | -15.2639 | 21.0202 | 3.4608 | 2.4874 | -16.416 | 15.9393 | 2.6243 | 1.8861 | 9.1835 | 13.608 | 2.2404 | 1.6103 | 7.3724 | 12.4036 | 2.0422 | 1.4677 | 6.8341 | 6.624 | 1.0906 | 0.78383 | 1.7217 | 6.058 | 0.9974 | 0.71685 | 1.6978 | 4.5007 | 0.741 | 0.53257 | 1.1631 | 2.4564 | 0.40443 | 0.29067 | 0.54154 | 0.10485 | 0.017263 | 0.012407 | -0.20623 | 2.6844 | 0.44197 | 0.31765 | -1.5358 | 2.6844 | 0.44197 | 0.31765 | -2.6806 | 2.6844 | 0.44197 | 0.31765 | -5.8321 | 2.6844 | 0.44197 | 0.31765 | -8.1833 | 2.6844 | 0.44197 | 0.31765 | -9.9806 | 27.317 | 4.4975 | 3.2325 | -10.7614 | 27.0333 | 4.4508 | 3.1989 | -9.4757 | 15.9393 | 2.6243 | 1.8861 | 9.1835 | 14.2126 | 2.34 | 1.6818 | 7.8626 | 13.1779 | 2.1696 | 1.5594 | 7.4028 | 12.3336 | 2.0306 | 1.4595 | 7.1602 | 11.1992 | 1.8439 | 1.3252 | 6.9335 | 10.8384 | 1.7845 | 1.2825 | 6.645 | 9.6668 | 1.5916 | 1.1439 | 5.9893 | 8.8261 | 1.4532 | 1.0444 | 5.6479 | 7.8359 | 1.2901 | 0.92724 | 5.1905 | 6.5556 | 1.0793 | 0.77574 | 4.5103 | 3.6925 | 0.60793 | 0.43693 | 3.2907 | 2.6844 | 0.44197 | 0.31765 | -1.5204 | 2.6844 | 0.44197 | 0.31765 | -2.7723 | 14.15 | 2.3297 | 1.6744 | -6.5472 | 33.566 | 6.1211 | 4.3994 | -6.3366 | 15.9393 | 2.6243 | 1.8861 | 9.1835 | 12.3886 | 2.0397 | 1.466 | 6.2966 | 10.8976 | 1.7942 | 1.2895 | 5.5085 | 5.0265 | 0.82758 | 0.5948 | 0.31338 | 4.3223 | 0.71164 | 0.51147 | 0.21908 | 2.7066 | 0.44562 | 0.32028 | -0.34044 | 0.6364 | 0.10478 | 0.075307 | -0.97513 | 2.6844 | 0.44197 | 0.31765 | -1.7735 | 2.6844 | 0.44197 | 0.31765 | -3.1368 | 2.6844 | 0.44197 | 0.31765 | -4.3115 | 2.6844 | 0.44197 | 0.31765 | -7.7705 | 2.6844 | 0.44197 | 0.31765 | -10.5129 | 2.6844 | 0.44197 | 0.31765 | -12.5752 | 23.8989 | 3.9348 | 2.828 | -13.5692 | 23.3698 | 3.8477 | 2.7654 | -12.503
MONSALL | STUART ST | STALYBRIDGE | 386332 | 401003 | 24.2656 | 7.9775 | 5.8195 | 10.3632 | 24.283 | 7.6441 | 5.5763 | 9.1958 | 24.3008 | 6.7548 | 4.9275 | 8.8947 | 24.3098 | 5.971 | 4.3557 | 8.8255 | 24.3281 | 5.1114 | 3.7287 | 8.5235 | 24.352 | 4.2527 | 3.1023 | 8.2025 | 20.9628 | 3.4004 | 2.4805 | 7.9003 | 20.3624 | 3.303 | 2.4095 | 7.6323 | 19.6695 | 3.1906 | 2.3275 | 7.357 | 18.9721 | 3.0775 | 2.245 | 7.1034 | 16.4515 | 2.6686 | 1.9467 | 5.7127 | 13.6584 | 2.2155 | 1.6162 | 3.7541 | 11.3079 | 1.8343 | 1.3381 | 2.2596 | 9.2148 | 1.4947 | 1.0904 | 0.91685 | 7.2327 | 1.1732 | 0.85584 | 0.078578 | 24.2652 | 7.9775 | 5.8195 | 10.3632 | 24.2809 | 7.8611 | 5.7346 | 10.2057 | 24.3048 | 7.7802 | 5.6756 | 10.1158 | 24.3223 | 7.6829 | 5.6045 | 10.0705 | 24.3415 | 7.5817 | 5.5308 | 10.0216 | 24.3652 | 7.4566 | 5.4395 | 9.9816 | 24.4004 | 7.2588 | 5.2952 | 9.906 | 24.4472 | 7.1936 | 5.2477 | 9.789 | 24.4655 | 7.1317 | 5.2025 | 9.7 | 24.4847 | 7.0908 | 5.1726 | 9.6043 | 24.5388 | 6.9377 | 5.061 | 9.3352 | 24.5942 | 6.8175 | 4.9733 | 9.0479 | 24.6443 | 6.6972 | 4.8855 | 8.7675 | 24.6951 | 6.5999 | 4.8146 | 8.4546 | 24.7294 | 6.4548 | 4.7087 | 8.2139 | 24.2658 | 7.9775 | 5.8195 | 10.3632 | 24.3029 | 7.5756 | 5.5263 | 8.9395 | 24.3418 | 6.659 | 4.8576 | 8.5103 | 24.375 | 5.8188 | 4.2447 | 8.345 | 24.4192 | 4.9325 | 3.5982 | 7.9352 | 24.4711 | 4.0311 | 2.9406 | 7.4977 | 19.4104 | 3.1486 | 2.2968 | 7.0984 | 18.5632 | 3.0111 | 2.1966 | 6.7124 | 17.6659 | 2.8656 | 2.0904 | 6.3497 | 16.83 | 2.73 | 1.9915 | 5.9756 | 13.7144 | 2.2246 | 1.6228 | 4.2831 | 10.4348 | 1.6926 | 1.2347 | 2.3532 | 8.3259 | 1.3505 | 0.9852 | 1.1195 | 6.2475 | 1.0134 | 0.73927 | 0.28325 | 6.1336 | 0.99493 | 0.72579 | 0.27539 | 24.2658 | 7.9775 | 5.8195 | 10.3632 | 24.2433 | 7.7097 | 5.6241 | 9.5139 | 24.2682 | 6.8738 | 5.0143 | 9.1921 | 24.2927 | 6.0592 | 4.4201 | 9.0259 | 24.3308 | 5.2047 | 3.7967 | 8.6072 | 24.3748 | 4.3416 | 3.1671 | 8.1709 | 21.2403 | 3.4454 | 2.5134 | 7.6348 | 19.6157 | 3.1819 | 2.3211 | 6.6701 | 18.0232 | 2.9235 | 2.1327 | 5.7476 | 15.8445 | 2.5701 | 1.8749 | 4.8552 | 12.3452 | 2.0025 | 1.4608 | 2.5565 | 9.7718 | 1.5851 | 1.1563 | 1.0262 | 8.0513 | 1.306 | 0.95271 | 0.1955 | 7.0456 | 1.1429 | 0.83371 | 0.17658 | 7.2682 | 1.179 | 0.86005 | 1.3057 | 24.2656 | 7.9775 | 5.8195 | 10.3632 | 24.2823 | 7.8356 | 5.716 | 10.0794 | 24.2993 | 6.9898 | 5.099 | 9.958 | 24.3046 | 6.21 | 4.5301 | 9.9127 | 24.3114 | 5.3685 | 3.9163 | 9.7071 | 24.3215 | 4.5429 | 3.314 | 9.5031 | 22.7395 | 3.6886 | 2.6908 | 9.2801 | 22.1939 | 3.6001 | 2.6262 | 9.017 | 21.5081 | 3.4888 | 2.545 | 8.7014 | 20.7597 | 3.3674 | 2.4565 | 8.3891 | 18.8422 | 3.0564 | 2.2296 | 7.5238 | 17.61 | 2.8565 | 2.0838 | 6.9732 | 16.4137 | 2.6625 | 1.9422 | 6.62 | 15.5468 | 2.5218 | 1.8397 | 6.2912 | 15.0552 | 2.4421 | 1.7815 | 6.2334 | 24.2656 | 7.9775 | 5.8195 | 10.3632 | 24.2485 | 7.5678 | 5.5206 | 8.9716 | 24.2796 | 6.7016 | 4.8887 | 8.5263 | 24.3112 | 5.8758 | 4.2863 | 8.3427 | 24.3566 | 5.0265 | 3.6668 | 7.9052 | 24.4075 | 4.1496 | 3.0271 | 7.4492 | 20.0101 | 3.2458 | 2.3678 | 6.8822 | 18.3363 | 2.9743 | 2.1697 | 5.8901 | 16.7624 | 2.719 | 1.9835 | 4.9567 | 14.5995 | 2.3682 | 1.7276 | 4.0493 | 11.065 | 1.7948 | 1.3093 | 1.6856 | 8.3082 | 1.3477 | 0.98311 | 0.094389 | 6.5275 | 1.0588 | 0.7724 | -0.81671 | 5.3816 | 0.87296 | 0.63681 | -0.96313 | 5.4203 | 0.87923 | 0.64139 | -0.0018892
MONTON | BARTON | CARRINGTON | 376321 | 399494 | 23.4216 | 10.9698 | 8.0023 | 11.513 | 23.496 | 10.7955 | 7.8751 | 10.7166 | 23.6072 | 10.5897 | 7.725 | 10.1953 | 23.745 | 10.4026 | 7.5886 | 9.8547 | 23.9179 | 10.1965 | 7.4382 | 9.4543 | 24.1224 | 9.9903 | 7.2878 | 9.0075 | 24.3337 | 9.7611 | 7.1206 | 8.5329 | 24.5766 | 9.5291 | 6.9513 | 8.0462 | 24.8104 | 9.4686 | 6.9072 | 7.5155 | 25.0548 | 9.3357 | 6.8103 | 6.9935 | 25.7807 | 8.8219 | 6.4355 | 4.901 | 26.3874 | 8.2527 | 6.0202 | 2.3451 | 26.7843 | 7.9011 | 5.7638 | 0.64704 | 27.0805 | 7.6372 | 5.5713 | -0.77298 | 27.2492 | 7.3931 | 5.3932 | -1.7172 | 23.4026 | 10.9698 | 8.0023 | 11.513 | 23.4673 | 10.9064 | 7.9561 | 11.2309 | 23.5423 | 10.7812 | 7.8648 | 11.0161 | 23.6251 | 10.6367 | 7.7593 | 10.8115 | 23.7283 | 10.4814 | 7.646 | 10.5659 | 23.8525 | 10.3505 | 7.5505 | 10.3138 | 24.0042 | 10.0811 | 7.354 | 10.0007 | 24.1859 | 9.9661 | 7.2701 | 9.5764 | 24.3132 | 9.8615 | 7.1938 | 9.1911 | 24.4541 | 9.7593 | 7.1193 | 8.7889 | 24.9454 | 9.4262 | 6.8762 | 7.556 | 25.4667 | 9.1326 | 6.6621 | 6.3274 | 25.9437 | 8.8922 | 6.4867 | 5.2132 | 26.4471 | 8.7457 | 6.3799 | 4.0937 | 26.7756 | 8.5594 | 6.2439 | 3.3912 | 23.4279 | 10.9698 | 8.0023 | 11.513 | 23.5162 | 10.7554 | 7.8459 | 10.569 | 23.6446 | 10.4998 | 7.6595 | 9.9765 | 23.8038 | 10.2887 | 7.5055 | 9.5924 | 23.9996 | 10.0551 | 7.3351 | 9.1454 | 24.2277 | 9.8032 | 7.1513 | 8.6135 | 24.4622 | 9.4887 | 6.9219 | 8.0929 | 24.7285 | 9.409 | 6.8637 | 7.5577 | 24.9615 | 9.2646 | 6.7584 | 6.998 | 25.1874 | 9.0915 | 6.6321 | 6.4211 | 25.9234 | 8.3977 | 6.126 | 4.1348 | 26.6063 | 7.7989 | 5.6892 | 1.5385 | 27.0595 | 7.4285 | 5.419 | -0.062489 | 27.3737 | 7.1303 | 5.2014 | -1.2276 | 27.5068 | 6.9511 | 5.0707 | -1.6853 | 23.4279 | 10.9698 | 8.0023 | 11.513 | 23.4514 | 10.8427 | 7.9096 | 10.9466 | 23.5313 | 10.7243 | 7.8232 | 10.4668 | 23.6374 | 10.546 | 7.6931 | 10.1273 | 23.7808 | 10.3608 | 7.5581 | 9.703 | 23.9715 | 10.1667 | 7.4165 | 9.2352 | 24.2167 | 10.0345 | 7.32 | 8.6239 | 24.5069 | 9.7591 | 7.1191 | 7.7091 | 24.7581 | 9.5124 | 6.9392 | 6.7761 | 25.0196 | 9.27 | 6.7623 | 5.8466 | 25.7833 | 8.5642 | 6.2475 | 3.1774 | 26.3908 | 7.9702 | 5.8141 | 0.91382 | 26.7671 | 7.5498 | 5.5075 | -0.35202 | 27.0065 | 7.2844 | 5.3139 | -0.93589 | 27.0593 | 7.1893 | 5.2445 | -0.56841 | 23.4216 | 10.9698 | 8.0023 | 11.513 | 23.4863 | 10.8765 | 7.9342 | 11.078 | 23.5732 | 10.6941 | 7.8012 | 10.6658 | 23.6703 | 10.5324 | 7.6833 | 10.3948 | 23.7917 | 10.3491 | 7.5495 | 10.1083 | 23.9601 | 10.171 | 7.4196 | 9.7978 | 24.1726 | 9.9566 | 7.2632 | 9.4098 | 24.4096 | 9.7741 | 7.1301 | 8.991 | 24.6059 | 9.6684 | 7.0529 | 8.5009 | 24.817 | 9.5442 | 6.9624 | 7.9975 | 25.4995 | 9.1297 | 6.66 | 6.3698 | 26.0963 | 8.743 | 6.3779 | 4.7678 | 26.4883 | 8.5214 | 6.2163 | 3.779 | 26.7828 | 8.3773 | 6.1111 | 2.9566 | 26.9246 | 8.2313 | 6.0046 | 2.4918 | 23.4216 | 10.9698 | 8.0023 | 11.513 | 23.4699 | 10.7613 | 7.8502 | 10.6028 | 23.585 | 10.6027 | 7.7345 | 9.9851 | 23.7321 | 10.4039 | 7.5895 | 9.5554 | 23.9135 | 10.2046 | 7.4441 | 9.0507 | 24.118 | 10.0002 | 7.295 | 8.5025 | 24.3521 | 9.8544 | 7.1886 | 7.8328 | 24.6185 | 9.5633 | 6.9763 | 6.8386 | 24.8653 | 9.307 | 6.7894 | 5.8493 | 25.1246 | 9.055 | 6.6055 | 4.8661 | 25.9059 | 8.3189 | 6.0685 | 2.0148 | 26.5476 | 7.6893 | 5.6093 | -0.41943 | 26.9663 | 7.239 | 5.2807 | -1.8472 | 27.2259 | 6.9717 | 5.0858 | -2.5736 | 27.299 | 6.8232 | 4.9774 | -2.3666
MOORSIDE | RIBBLE | PENWORTHAM EAST / ROCHDALE | 349331 | 435746 | 14.15 | 12.6309 | 9.214 | 11.6847 | 14.239 | 12.046 | 8.7874 | 8.0361 | 14.3743 | 11.4481 | 8.3512 | 7.2336 | 14.5297 | 10.908 | 7.9572 | 7.0474 | 14.7159 | 10.3479 | 7.5486 | 6.8255 | 14.9327 | 9.7104 | 7.0836 | 6.6011 | 15.1881 | 8.9446 | 6.5249 | 6.3915 | 15.406 | 8.6283 | 6.2942 | 6.1808 | 15.569 | 8.4693 | 6.1782 | 5.8958 | 15.7267 | 8.4978 | 6.199 | 5.6139 | 16.2131 | 8.1773 | 5.9652 | 4.4819 | 16.6917 | 7.6869 | 5.6075 | 2.9614 | 17.0232 | 7.9689 | 5.8132 | 1.8679 | 17.302 | 8.134 | 5.9336 | 0.87133 | 17.5062 | 7.7599 | 5.6607 | -0.02006 | 14.1138 | 12.6309 | 9.214 | 11.6847 | 14.1632 | 12.4324 | 9.0693 | 10.1866 | 14.2263 | 12.3386 | 9.0008 | 9.797 | 14.3098 | 12.2649 | 8.9471 | 9.6333 | 14.4131 | 12.1752 | 8.8817 | 9.4427 | 14.5421 | 12.0532 | 8.7927 | 9.2482 | 14.6861 | 11.8198 | 8.6224 | 8.9964 | 14.8515 | 11.7427 | 8.5661 | 8.6485 | 14.9889 | 11.5937 | 8.4575 | 8.3175 | 15.135 | 11.5564 | 8.4302 | 7.9744 | 15.6105 | 11.2872 | 8.2338 | 6.9437 | 16.1054 | 11.1174 | 8.11 | 5.9218 | 16.5422 | 11.1057 | 8.1015 | 4.9995 | 16.9924 | 11.035 | 8.0499 | 3.9675 | 17.2887 | 10.7273 | 7.8254 | 3.2921 | 14.1658 | 12.6309 | 9.214 | 11.6847 | 14.2633 | 11.9317 | 8.704 | 7.4707 | 14.4115 | 11.2432 | 8.2018 | 6.588 | 14.5892 | 10.6782 | 7.7896 | 6.4409 | 14.803 | 10.096 | 7.3649 | 6.2588 | 15.033 | 9.3725 | 6.8371 | 6.0816 | 15.1929 | 8.3239 | 6.0722 | 5.9359 | 15.3779 | 8.4862 | 6.1906 | 5.7993 | 15.5308 | 8.4314 | 6.1506 | 5.6128 | 15.6774 | 8.2967 | 6.0523 | 5.4248 | 16.1436 | 7.7749 | 5.6717 | 4.5446 | 16.6169 | 7.6155 | 5.5554 | 3.217 | 16.9461 | 7.6768 | 5.6001 | 2.2898 | 17.2127 | 7.694 | 5.6126 | 1.5018 | 17.3934 | 7.631 | 5.5667 | 0.85795 | 14.1658 | 12.6309 | 9.214 | 11.6847 | 14.1945 | 12.147 | 8.8611 | 8.7848 | 14.2814 | 11.586 | 8.4518 | 8.1619 | 14.3872 | 11.0428 | 8.0556 | 8.0327 | 14.531 | 10.4415 | 7.6169 | 7.869 | 14.7032 | 9.8023 | 7.1506 | 7.6889 | 14.836 | 9.1492 | 6.6742 | 7.4755 | 14.9872 | 8.7744 | 6.4008 | 7.0978 | 15.1377 | 8.7598 | 6.3902 | 6.6599 | 15.2868 | 8.7541 | 6.386 | 6.2136 | 15.7382 | 9.3447 | 6.8168 | 4.9333 | 16.1824 | 8.8706 | 6.471 | 3.686 | 16.4826 | 8.4997 | 6.2004 | 2.871 | 16.7071 | 8.1519 | 5.9467 | 2.448 | 16.7866 | 7.9975 | 5.8341 | 2.7598 | 14.15 | 12.6309 | 9.214 | 11.6847 | 14.2236 | 12.1769 | 8.8829 | 8.8327 | 14.3203 | 11.6267 | 8.4815 | 8.1914 | 14.4259 | 11.1044 | 8.1005 | 8.0438 | 14.5529 | 10.5832 | 7.7203 | 7.8914 | 14.7448 | 9.9388 | 7.2502 | 7.7294 | 14.9957 | 9.1935 | 6.7065 | 7.5595 | 15.2672 | 8.8979 | 6.4909 | 7.3703 | 15.4128 | 8.664 | 6.3202 | 7.0777 | 15.5587 | 8.7376 | 6.374 | 6.7838 | 16.0236 | 8.4722 | 6.1804 | 5.798 | 16.4973 | 8.1234 | 5.9259 | 4.7209 | 16.832 | 8.4782 | 6.1847 | 3.9733 | 17.1192 | 8.7452 | 6.3795 | 3.3307 | 17.2769 | 8.6529 | 6.3122 | 3.0213 | 14.15 | 12.6309 | 9.214 | 11.6847 | 14.2129 | 11.8373 | 8.6351 | 6.9761 | 14.3436 | 11.1835 | 8.1582 | 5.9793 | 14.4976 | 10.6483 | 7.7678 | 5.7731 | 14.6812 | 10.0137 | 7.3048 | 5.5403 | 14.8919 | 9.3751 | 6.839 | 5.3146 | 15.1402 | 8.7063 | 6.3511 | 5.0488 | 15.3595 | 8.3438 | 6.0867 | 4.5952 | 15.5341 | 8.2745 | 6.0361 | 4.1055 | 15.7041 | 8.2743 | 6.036 | 3.609 | 16.206 | 8.8199 | 6.434 | 2.1489 | 16.6754 | 8.309 | 6.0613 | 0.73305 | 16.9966 | 7.9145 | 5.7735 | -0.21819 | 17.2241 | 7.5303 | 5.4933 | -0.76879 | 17.3182 | 7.3639 | 5.3719 | -0.57998
MORTON PARK & PIRELLI | CARLISLE | HARKER / HUTTON | 337826 | 553939 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 1.6391 | 0.44197 | 0.31765 | 1.6391 | 1.6795 | 0.44197 | 0.31765 | 1.4477 | 1.6795 | 0.44197 | 0.31765 | -0.77774 | 1.6795 | 0.44197 | 0.31765 | -3.0528 | 1.6795 | 0.44197 | 0.31765 | -5.3469 | 1.6795 | 0.44197 | 0.31765 | -8.1167 | 1.6795 | 0.44197 | 0.31765 | -10.3556 | 1.6795 | 0.44197 | 0.31765 | -12.6928 | 1.6795 | 0.44197 | 0.31765 | -15.0011 | 1.6795 | 0.44197 | 0.31765 | -24.235 | 1.6795 | 0.44197 | 0.31765 | -35.1232 | 1.6795 | 0.44197 | 0.31765 | -44.056 | 1.6795 | 0.44197 | 0.31765 | -47.2572 | 1.6795 | 0.44197 | 0.31765 | -49.9012 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0.51038 | 0.19372 | 0.15829 | 0.51038 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 0.71855 | 1.6795 | 0.44197 | 0.31765 | -1.5549 | 1.6795 | 0.44197 | 0.31765 | -3.9408 | 1.6795 | 0.44197 | 0.31765 | -6.3824 | 1.6795 | 0.44197 | 0.31765 | -8.8229 | 1.6795 | 0.44197 | 0.31765 | -16.1156 | 1.6795 | 0.44197 | 0.31765 | -23.3916 | 1.6795 | 0.44197 | 0.31765 | -31.9189 | 1.6795 | 0.44197 | 0.31765 | -36.5688 | 1.6795 | 0.44197 | 0.31765 | -37.1292 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0.80805 | 0.3067 | 0.25061 | 0.80805 | 1.6795 | 0.44197 | 0.31765 | 0.21854 | 1.6795 | 0.44197 | 0.31765 | -2.008 | 1.6795 | 0.44197 | 0.31765 | -4.2804 | 1.6795 | 0.44197 | 0.31765 | -6.5701 | 1.6795 | 0.44197 | 0.31765 | -9.3232 | 1.6795 | 0.44197 | 0.31765 | -13.459 | 1.6795 | 0.44197 | 0.31765 | -15.656 | 1.6795 | 0.44197 | 0.31765 | -17.825 | 1.6795 | 0.44197 | 0.31765 | -29.8088 | 1.6795 | 0.44197 | 0.31765 | -39.9932 | 1.6795 | 0.44197 | 0.31765 | -48.2529 | 1.6795 | 0.44197 | 0.31765 | -50.7466 | 1.6795 | 0.44197 | 0.31765 | -52.8872 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.4734 | 0.44197 | 0.31765 | 2.4734 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 0.27957 | 1.6795 | 0.44197 | 0.31765 | -6.1205 | 1.6795 | 0.44197 | 0.31765 | -11.5714 | 1.6795 | 0.44197 | 0.31765 | -15.2544 | 1.6795 | 0.44197 | 0.31765 | -17.8931 | 1.6795 | 0.44197 | 0.31765 | -20.5935 | 1.6795 | 0.44197 | 0.31765 | -23.3052 | 1.6795 | 0.44197 | 0.31765 | -31.9846 | 1.6795 | 0.44197 | 0.31765 | -41.1234 | 1.6795 | 0.44197 | 0.31765 | -49.699 | 1.6795 | 0.44197 | 0.31765 | -50.8978 | 1.6795 | 0.44197 | 0.31765 | -49.3186 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 1.3398 | 0.44197 | 0.31765 | 1.3398 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.2907 | 1.6795 | 0.44197 | 0.31765 | -0.86265 | 1.6795 | 0.44197 | 0.31765 | -3.5371 | 1.6795 | 0.44197 | 0.31765 | -5.7185 | 1.6795 | 0.44197 | 0.31765 | -8.049 | 1.6795 | 0.44197 | 0.31765 | -10.3748 | 1.6795 | 0.44197 | 0.31765 | -18.859 | 1.6795 | 0.44197 | 0.31765 | -27.4833 | 1.6795 | 0.44197 | 0.31765 | -34.2668 | 1.6795 | 0.44197 | 0.31765 | -35.1033 | 1.6795 | 0.44197 | 0.31765 | -35.1441 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0.26106 | 0.099087 | 0.080964 | 0.26106 | 1.6795 | 0.44197 | 0.31765 | -0.75593 | 1.6795 | 0.44197 | 0.31765 | -3.5974 | 1.6795 | 0.44197 | 0.31765 | -10.0673 | 1.6795 | 0.44197 | 0.31765 | -15.5464 | 1.6795 | 0.44197 | 0.31765 | -19.2476 | 1.6795 | 0.44197 | 0.31765 | -21.9433 | 1.6795 | 0.44197 | 0.31765 | -24.6861 | 1.6795 | 0.44197 | 0.31765 | -27.4871 | 1.6795 | 0.44197 | 0.31765 | -36.6598 | 1.6795 | 0.44197 | 0.31765 | -46.0183 | 1.6795 | 0.44197 | 0.31765 | -54.7987 | 1.6795 | 0.44197 | 0.31765 | -56.2149 | 1.6795 | 0.44197 | 0.31765 | -54.8675
MOSLEY RD | STRETFORD | SOUTH MANCHESTER | 379058 | 396289 | 22.296 | 11.9538 | 8.7201 | 10.4778 | 22.3435 | 11.6199 | 8.4766 | 8.5831 | 22.4371 | 10.8025 | 7.8802 | 7.8491 | 22.5466 | 10.0701 | 7.346 | 7.4594 | 22.6918 | 9.3385 | 6.8123 | 7.0917 | 22.8588 | 8.5038 | 6.2034 | 6.695 | 23.0606 | 7.7406 | 5.6467 | 6.2602 | 23.3268 | 7.6578 | 5.5863 | 5.7667 | 23.6559 | 7.518 | 5.4843 | 5.1405 | 24.0219 | 7.3708 | 5.3769 | 4.4785 | 25.1917 | 6.9424 | 5.0644 | 2.392 | 26.5332 | 6.5706 | 4.7932 | 0.21484 | 29.0105 | 6.1827 | 4.5102 | -3.0722 | 29.3918 | 7.7558 | 5.6577 | -4.3289 | 29.5698 | 9.2248 | 6.7293 | -5.4287 | 22.2962 | 11.9538 | 8.7201 | 10.4778 | 22.3383 | 11.8768 | 8.664 | 10.0347 | 22.4189 | 11.2039 | 8.1731 | 9.7682 | 22.495 | 10.5616 | 7.7045 | 9.6271 | 22.5761 | 9.895 | 7.2182 | 9.5142 | 22.6834 | 9.1891 | 6.7033 | 9.3772 | 22.8226 | 8.3749 | 6.1094 | 9.2152 | 22.9724 | 8.3101 | 6.0621 | 9.0255 | 23.1632 | 8.2379 | 6.0094 | 8.7919 | 23.375 | 8.1652 | 5.9564 | 8.5356 | 24.1261 | 7.9266 | 5.7823 | 7.6428 | 25.3785 | 7.591 | 5.5375 | 6.2304 | 27.7902 | 7.3041 | 5.3282 | 3.3398 | 28.7067 | 8.2789 | 6.0394 | 0.95837 | 29.2853 | 9.3675 | 6.8334 | -0.55215 | 22.296 | 11.9538 | 8.7201 | 10.4778 | 22.3396 | 11.5571 | 8.4307 | 8.2872 | 22.4272 | 10.6979 | 7.804 | 7.4953 | 22.523 | 9.9458 | 7.2554 | 7.11 | 22.642 | 9.2001 | 6.7113 | 6.7543 | 22.8172 | 8.3659 | 6.1028 | 6.3787 | 22.9865 | 7.6476 | 5.5788 | 5.977 | 23.2062 | 7.5433 | 5.5027 | 5.531 | 23.4683 | 7.4022 | 5.3998 | 5.0038 | 23.7679 | 7.2527 | 5.2907 | 4.4435 | 26.7463 | 6.5032 | 4.744 | 0.59179 | 28.7899 | 5.9856 | 4.3664 | -2.193 | 29.4816 | 5.9013 | 4.3049 | -3.4996 | 29.8808 | 7.4691 | 5.4486 | -4.5877 | 29.9799 | 8.9782 | 6.5495 | -5.3582 | 22.296 | 11.9538 | 8.7201 | 10.4778 | 22.3362 | 11.6679 | 8.5116 | 8.903 | 22.4184 | 11.4207 | 8.3312 | 8.2562 | 22.498 | 11.3469 | 8.2774 | 7.89 | 22.5883 | 11.3071 | 8.2484 | 7.5425 | 23.1003 | 11.1256 | 8.116 | 6.7644 | 24.8665 | 10.7446 | 7.838 | 4.672 | 25.1078 | 10.5868 | 7.7229 | 4.09 | 26.0852 | 10.3582 | 7.5562 | 2.6982 | 26.4303 | 10.2895 | 7.5061 | 1.9664 | 27.8951 | 10.2721 | 7.4934 | -0.50607 | 28.7979 | 9.8387 | 7.1772 | -2.106 | 29.3391 | 9.5212 | 6.9456 | -3.2494 | 29.6226 | 9.3767 | 6.8401 | -4.0877 | 29.614 | 9.2243 | 6.729 | -4.382 | 22.296 | 11.9538 | 8.7201 | 10.4778 | 22.3353 | 11.8082 | 8.6139 | 9.6252 | 22.4159 | 11.0332 | 8.0486 | 9.1197 | 22.5006 | 10.3083 | 7.5198 | 8.7606 | 22.6091 | 9.5851 | 6.9922 | 8.4351 | 22.7455 | 8.7493 | 6.3825 | 8.074 | 22.9182 | 7.987 | 5.8264 | 7.6721 | 23.1314 | 7.923 | 5.7797 | 7.2306 | 23.3933 | 7.7967 | 5.6876 | 6.6698 | 23.6914 | 7.6605 | 5.5882 | 6.0724 | 24.7374 | 7.2851 | 5.3144 | 4.2177 | 26.0891 | 6.9877 | 5.0974 | 2.2887 | 28.6197 | 6.6566 | 4.8559 | -0.80336 | 29.0182 | 8.3111 | 6.0629 | -1.9082 | 29.1208 | 9.9122 | 7.2308 | -2.4696 | 22.296 | 11.9538 | 8.7201 | 10.4778 | 22.3382 | 11.5002 | 8.3892 | 7.9919 | 22.4246 | 11.2262 | 8.1894 | 7.1383 | 22.5188 | 11.1374 | 8.1246 | 6.747 | 22.6358 | 11.087 | 8.0878 | 6.3866 | 23.1831 | 10.9145 | 7.9619 | 5.62 | 24.9463 | 10.5344 | 7.6847 | 3.5613 | 25.1709 | 10.3826 | 7.574 | 3.0217 | 26.1077 | 10.1641 | 7.4145 | 1.6715 | 26.414 | 10.0947 | 7.364 | 0.97973 | 27.8733 | 10.0668 | 7.3436 | -1.4873 | 28.9149 | 9.6056 | 7.0071 | -3.2305 | 29.6062 | 9.2576 | 6.7533 | -4.5295 | 29.9748 | 9.0937 | 6.6337 | -5.455 | 29.9867 | 8.9343 | 6.5174 | -5.7704
MOSS LANE | KEARSLEY LOCAL | KEARSLEY | 380858 | 405856 | 32.7601 | 8.19 | 5.8863 | 6.6434 | 32.8742 | 8.0592 | 5.7923 | 5.3371 | 33.078 | 7.9476 | 5.7121 | 4.8952 | 33.3575 | 7.7715 | 5.5855 | 4.606 | 33.7332 | 7.5133 | 5.3999 | 4.143 | 34.2287 | 7.2291 | 5.1957 | 3.5961 | 34.8819 | 6.9653 | 5.0061 | 2.9855 | 35.6957 | 6.7638 | 4.8613 | 2.4683 | 36.4303 | 6.542 | 4.7019 | 1.7904 | 37.1496 | 6.2285 | 4.4765 | 0.74218 | 31.7944 | 5.2347 | 3.7623 | -4.2794 | 25.1037 | 4.1331 | 2.9706 | -9.9557 | 21.618 | 3.5592 | 2.5581 | -14.0833 | 19.0382 | 3.1345 | 2.2528 | -17.6916 | 16.1484 | 2.6587 | 1.9109 | -20.5547 | 32.7064 | 8.19 | 5.8863 | 6.6434 | 32.786 | 8.155 | 5.8612 | 6.1626 | 32.8938 | 8.0385 | 5.7774 | 5.9688 | 33.0287 | 7.8963 | 5.6752 | 5.7915 | 33.2199 | 7.7536 | 5.5727 | 5.5175 | 33.4763 | 7.5979 | 5.4608 | 5.1854 | 33.8004 | 7.1642 | 5.149 | 4.7354 | 34.1889 | 7.0404 | 5.0601 | 4.1929 | 34.5469 | 6.9098 | 4.9662 | 3.683 | 34.9627 | 6.7769 | 4.8707 | 3.1306 | 36.5649 | 6.3415 | 4.5577 | 1.2248 | 35.6729 | 5.8733 | 4.2212 | -1.0002 | 32.1997 | 5.3014 | 3.8103 | -3.9281 | 28.5911 | 4.7073 | 3.3832 | -7.4079 | 26.1525 | 4.3058 | 3.0947 | -9.7227 | 32.7801 | 8.19 | 5.8863 | 6.6434 | 32.9063 | 8.0443 | 5.7816 | 5.2059 | 33.1309 | 7.8948 | 5.6741 | 4.7781 | 33.4341 | 7.6507 | 5.4987 | 4.5805 | 33.8305 | 7.348 | 5.2811 | 4.2184 | 34.3367 | 7.0608 | 5.0747 | 3.799 | 34.9852 | 6.7597 | 4.8583 | 3.3734 | 35.6436 | 6.5221 | 4.6876 | 3.0728 | 36.2814 | 6.3992 | 4.5993 | 2.4327 | 36.8729 | 6.148 | 4.4187 | 1.3835 | 31.0208 | 5.1073 | 3.6707 | -3.4136 | 24.4509 | 4.0256 | 2.8933 | -9.4211 | 19.125 | 3.1488 | 2.2631 | -13.9175 | 15.3167 | 2.5218 | 1.8124 | -17.6281 | 12.6327 | 2.0799 | 1.4949 | -20.2669 | 32.7801 | 8.19 | 5.8863 | 6.6434 | 32.7448 | 8.1914 | 5.8873 | 6.0427 | 32.8554 | 8.1652 | 5.8685 | 5.8282 | 33.036 | 7.9351 | 5.7031 | 5.6833 | 33.3367 | 7.6178 | 5.475 | 5.3133 | 33.8356 | 7.1933 | 5.1699 | 4.8134 | 34.5273 | 6.9823 | 5.0183 | 4.0463 | 35.3758 | 6.8838 | 4.9476 | 2.6282 | 36.1201 | 6.598 | 4.7421 | 1.0251 | 36.9423 | 6.2015 | 4.4572 | -0.77665 | 30.121 | 4.9592 | 3.5643 | -6.9375 | 22.94 | 3.7769 | 2.7145 | -12.3318 | 17.5788 | 2.8942 | 2.0801 | -16.1166 | 15.904 | 2.6185 | 1.8819 | -18.4122 | 14.7622 | 2.4305 | 1.7468 | -17.9103 | 32.7601 | 8.19 | 5.8863 | 6.6434 | 32.8517 | 8.1309 | 5.8439 | 5.7881 | 32.9868 | 8.0524 | 5.7874 | 5.5129 | 33.1548 | 7.9193 | 5.6917 | 5.3832 | 33.4035 | 7.7181 | 5.5471 | 5.1742 | 33.8155 | 7.4666 | 5.3664 | 4.8457 | 34.3958 | 7.2408 | 5.2041 | 4.4102 | 35.1027 | 7.0728 | 5.0834 | 4.0526 | 35.7361 | 6.8814 | 4.9458 | 3.5093 | 36.3906 | 6.6338 | 4.7678 | 2.7882 | 35.3723 | 5.8238 | 4.1857 | -1.0131 | 30.7057 | 5.0555 | 3.6335 | -4.8037 | 29.2742 | 4.8198 | 3.4641 | -7.3672 | 28.9547 | 4.7672 | 3.4263 | -9.1459 | 28.6753 | 4.7212 | 3.3932 | -9.8261 | 32.7601 | 8.19 | 5.8863 | 6.6434 | 32.7747 | 8.0889 | 5.8136 | 5.4297 | 32.9594 | 8.0042 | 5.7528 | 4.9687 | 33.221 | 7.7341 | 5.5587 | 4.6493 | 33.5709 | 7.4035 | 5.321 | 4.142 | 34.0178 | 6.9647 | 5.0056 | 3.5792 | 34.6032 | 6.7346 | 4.8403 | 2.7453 | 35.3903 | 6.6175 | 4.7561 | 1.2319 | 36.0443 | 6.3166 | 4.5399 | -0.41229 | 36.0254 | 5.9313 | 4.2629 | -2.1245 | 29.2465 | 4.8152 | 3.4608 | -7.4688 | 21.5637 | 3.5503 | 2.5517 | -13.2574 | 15.5482 | 2.5599 | 1.8398 | -17.6339 | 13.4244 | 2.2102 | 1.5885 | -20.341 | 12.0282 | 1.9804 | 1.4233 | -20.072
MOSS NOOK PRIMARY | MOSS NOOK | SOUTH MANCHESTER | 384084 | 385010 | 32.008 | 9.6869 | 6.9622 | 23.6034 | 32.0828 | 9.2405 | 6.6414 | 21.1315 | 32.2073 | 9.1371 | 6.567 | 20.4027 | 32.3225 | 9.0675 | 6.517 | 20.1997 | 32.4518 | 8.9953 | 6.4651 | 19.992 | 32.5898 | 8.9441 | 6.4283 | 19.7945 | 32.7345 | 8.8779 | 6.3807 | 19.6368 | 32.8954 | 8.817 | 6.3369 | 19.5066 | 33.0486 | 8.7391 | 6.281 | 19.2626 | 33.1926 | 8.6611 | 6.2249 | 19.0363 | 33.798 | 8.3032 | 5.9676 | 17.6077 | 34.4301 | 7.8258 | 5.6246 | 15.167 | 34.7049 | 7.5932 | 5.4574 | 13.1565 | 34.9215 | 12.8036 | 9.2022 | 11.053 | 35.0362 | 18.2419 | 13.1108 | 9.1456 | 31.9839 | 9.6869 | 6.9622 | 23.6034 | 32.0206 | 9.5256 | 6.8462 | 22.9127 | 32.0897 | 9.4326 | 6.7794 | 22.5776 | 32.1565 | 9.412 | 6.7646 | 22.4018 | 32.2296 | 9.3694 | 6.734 | 22.2333 | 32.2892 | 9.2948 | 6.6804 | 22.0615 | 32.3621 | 9.2271 | 6.6317 | 21.8505 | 32.4544 | 9.143 | 6.5713 | 21.5834 | 32.561 | 9.0538 | 6.5071 | 21.2635 | 32.6698 | 8.9633 | 6.4421 | 20.9435 | 32.9959 | 8.6796 | 6.2382 | 19.9983 | 33.3134 | 8.4229 | 6.0537 | 19.0874 | 33.6231 | 8.4302 | 6.059 | 18.243 | 33.9645 | 12.7397 | 9.1563 | 17.3358 | 34.2158 | 17.1411 | 12.3196 | 16.6903 | 32.0183 | 9.6869 | 6.9622 | 23.6034 | 32.1049 | 9.1753 | 6.5944 | 20.7673 | 32.2265 | 9.0401 | 6.4973 | 19.9842 | 32.3548 | 8.9582 | 6.4385 | 19.8315 | 32.4979 | 8.8777 | 6.3806 | 19.6675 | 32.6516 | 8.8104 | 6.3322 | 19.5183 | 32.8152 | 8.7451 | 6.2853 | 19.4236 | 32.9225 | 8.6828 | 6.2405 | 19.3663 | 33.0272 | 8.6112 | 6.1891 | 19.2563 | 33.1294 | 8.5312 | 6.1315 | 19.1318 | 33.5982 | 8.1665 | 5.8694 | 18.0208 | 34.2904 | 7.6744 | 5.5157 | 15.8828 | 34.7692 | 7.432 | 5.3415 | 14.1616 | 34.9411 | 12.6462 | 9.089 | 12.4275 | 34.9793 | 18.114 | 13.0189 | 10.9664 | 32.0183 | 9.6869 | 6.9622 | 23.6034 | 32.0563 | 9.3324 | 6.7074 | 21.6502 | 32.1563 | 9.2592 | 6.6548 | 21.0804 | 32.252 | 9.193 | 6.6072 | 20.941 | 32.3671 | 9.1051 | 6.544 | 20.773 | 32.5182 | 9.0288 | 6.4892 | 20.5888 | 32.702 | 8.9376 | 6.4236 | 20.3164 | 32.8976 | 8.7709 | 6.3038 | 19.6608 | 33.1425 | 8.5979 | 6.1795 | 18.9281 | 33.3893 | 8.4164 | 6.049 | 18.1748 | 33.8564 | 7.8862 | 5.6679 | 16.0078 | 34.2411 | 7.6076 | 5.4677 | 13.9351 | 34.4839 | 8.4256 | 6.0556 | 12.3265 | 34.6285 | 18.4259 | 13.243 | 11.4011 | 34.5637 | 18.391 | 13.218 | 12.2326 | 32.008 | 9.6869 | 6.9622 | 23.6034 | 32.0694 | 9.4455 | 6.7887 | 22.3655 | 32.1747 | 9.3942 | 6.7518 | 21.9238 | 32.2513 | 9.3384 | 6.7117 | 21.7912 | 32.3288 | 9.288 | 6.6755 | 21.6984 | 32.4334 | 9.2595 | 6.655 | 21.5919 | 32.5573 | 9.2053 | 6.616 | 21.4961 | 32.6903 | 9.1523 | 6.578 | 21.4059 | 32.8274 | 9.0762 | 6.5233 | 21.1723 | 32.9637 | 8.9982 | 6.4672 | 20.9431 | 33.3989 | 8.7559 | 6.2931 | 20.165 | 33.8645 | 8.5515 | 6.1461 | 19.3034 | 34.1941 | 8.5692 | 6.1588 | 18.7427 | 34.4829 | 14.078 | 10.1181 | 18.2588 | 34.6299 | 19.855 | 14.2702 | 18.1358 | 32.008 | 9.6869 | 6.9622 | 23.6034 | 32.0713 | 9.1265 | 6.5594 | 20.4188 | 32.1987 | 8.9957 | 6.4654 | 19.532 | 32.329 | 8.9125 | 6.4056 | 19.3047 | 32.472 | 8.8091 | 6.3313 | 19.0582 | 32.6223 | 8.7235 | 6.2698 | 18.8232 | 32.8122 | 8.6207 | 6.1958 | 18.4947 | 33.1266 | 8.439 | 6.0653 | 17.7523 | 33.4186 | 8.2535 | 5.932 | 16.9569 | 33.5831 | 8.0599 | 5.7928 | 16.1382 | 34.0494 | 7.495 | 5.3868 | 13.7812 | 34.4025 | 7.1854 | 5.1643 | 11.5596 | 34.6244 | 7.9734 | 5.7306 | 9.8181 | 34.7375 | 17.935 | 12.8903 | 8.7487 | 34.6669 | 17.8726 | 12.8454 | 9.4208
MOSS SIDE (Leyland) & SEVEN STARS | LEYLAND | PENWORTHAM WEST / STANAH | 352170 | 422970 | 27.1283 | 14.2896 | 10.2702 | 7.202 | 27.2214 | 13.3703 | 9.6095 | 3.7778 | 27.3549 | 12.7247 | 9.1455 | 2.9811 | 27.5167 | 12.3605 | 8.8838 | 2.8155 | 27.7346 | 11.7936 | 8.4763 | 2.5335 | 28.0124 | 11.1011 | 7.9786 | 2.1959 | 28.365 | 10.4446 | 7.5067 | 1.7914 | 28.8113 | 10.0386 | 7.215 | 1.3554 | 29.2494 | 9.7125 | 6.9806 | 0.66684 | 29.7072 | 9.4085 | 6.7621 | -0.024876 | 31.166 | 8.3292 | 5.9864 | -2.8104 | 32.3148 | 7.275 | 5.2287 | -6.2377 | 33.0486 | 6.5485 | 4.7065 | -8.8067 | 33.636 | 5.7532 | 4.1349 | -11.0274 | 30.3702 | 5.0002 | 3.5938 | -12.7669 | 27.095 | 14.2896 | 10.2702 | 7.202 | 27.1768 | 13.866 | 9.9658 | 5.7197 | 27.259 | 13.6594 | 9.8173 | 5.2622 | 27.3463 | 13.4679 | 9.6796 | 5.0981 | 27.4569 | 13.4178 | 9.6436 | 4.9014 | 27.5983 | 13.2445 | 9.5191 | 4.6447 | 27.7778 | 12.9592 | 9.314 | 4.3174 | 27.9944 | 12.756 | 9.168 | 3.8741 | 28.2162 | 12.5637 | 9.0298 | 3.3528 | 28.4685 | 12.336 | 8.8661 | 2.804 | 29.4211 | 11.6276 | 8.357 | 1.021 | 30.4967 | 11.0336 | 7.93 | -0.94674 | 31.509 | 10.4319 | 7.4976 | -2.7665 | 32.4147 | 9.7483 | 7.0063 | -4.6283 | 32.9535 | 9.0361 | 6.4944 | -5.8375 | 27.1352 | 14.2896 | 10.2702 | 7.202 | 27.2247 | 13.198 | 9.4856 | 3.2217 | 27.3601 | 12.5243 | 9.0015 | 2.3299 | 27.5237 | 12.0526 | 8.6624 | 2.1655 | 27.739 | 11.4767 | 8.2485 | 1.9885 | 28.0068 | 10.7492 | 7.7257 | 1.794 | 28.3397 | 10.097 | 7.2569 | 1.5808 | 28.7545 | 9.6683 | 6.9488 | 1.3159 | 29.1229 | 9.3168 | 6.6962 | 0.83146 | 29.5257 | 9.1252 | 6.5585 | 0.2985 | 30.9805 | 8.2331 | 5.9173 | -2.1675 | 32.1759 | 7.1033 | 5.1053 | -5.4976 | 32.9563 | 6.1505 | 4.4205 | -8.0084 | 31.603 | 5.2032 | 3.7396 | -10.0612 | 26.951 | 4.4373 | 3.1892 | -11.4906 | 27.1353 | 14.2896 | 10.2702 | 7.202 | 27.1394 | 13.5169 | 9.7148 | 4.5483 | 27.2255 | 13.0652 | 9.3902 | 3.9428 | 27.3425 | 12.5304 | 9.0059 | 3.8527 | 27.526 | 12.0091 | 8.6312 | 3.7289 | 27.8037 | 11.5218 | 8.281 | 3.5474 | 28.1894 | 10.8607 | 7.8058 | 3.1319 | 28.7192 | 10.3582 | 7.4446 | 2.2326 | 29.2818 | 9.8712 | 7.0946 | 1.1806 | 29.7798 | 9.263 | 6.6575 | 0.04905 | 31.0692 | 8.0871 | 5.8123 | -3.3093 | 32.1747 | 6.9424 | 4.9896 | -6.3668 | 32.8066 | 6.0655 | 4.3594 | -8.5585 | 32.7978 | 5.3999 | 3.881 | -9.7552 | 31.8311 | 5.2408 | 3.7666 | -9.0032 | 27.1281 | 14.2896 | 10.2702 | 7.202 | 27.2011 | 13.5037 | 9.7054 | 4.3858 | 27.2964 | 12.974 | 9.3246 | 3.7367 | 27.3948 | 12.604 | 9.0588 | 3.6489 | 27.5266 | 12.0908 | 8.6899 | 3.583 | 27.733 | 11.448 | 8.2279 | 3.464 | 28.0198 | 10.8255 | 7.7805 | 3.2368 | 28.3703 | 10.4232 | 7.4914 | 2.9119 | 28.7561 | 10.1259 | 7.2777 | 2.3678 | 29.1621 | 9.8284 | 7.0639 | 1.7536 | 30.5187 | 9.0828 | 6.528 | -0.35113 | 31.6415 | 8.4918 | 6.1032 | -2.4696 | 32.3507 | 8.0335 | 5.7738 | -3.9078 | 32.8131 | 7.514 | 5.4005 | -4.9518 | 32.9573 | 7.1413 | 5.1326 | -5.2497 | 27.1281 | 14.2896 | 10.2702 | 7.202 | 27.149 | 13.1339 | 9.4396 | 2.8337 | 27.2667 | 12.4875 | 8.975 | 1.8643 | 27.4183 | 11.9714 | 8.6041 | 1.6889 | 27.6205 | 11.2991 | 8.1209 | 0.89149 | 27.8689 | 10.617 | 7.6307 | -0.013065 | 28.1981 | 9.8462 | 7.0766 | -1.0667 | 28.6835 | 9.1516 | 6.5774 | -2.6203 | 29.1918 | 8.668 | 6.2299 | -3.7047 | 29.7425 | 8.0916 | 5.8156 | -4.843 | 31.0557 | 6.6427 | 4.7743 | -8.3551 | 32.2699 | 5.493 | 3.9479 | -11.7322 | 27.1045 | 4.4626 | 3.2073 | -14.2385 | 22.8269 | 3.7583 | 2.7011 | -15.6777 | 21.7157 | 3.5753 | 2.5697 | -15.1071
MOSS SIDE (Longsight) | LONGSIGHT | BREDBURY | 384007 | 395893 | 33.8624 | 11.2604 | 8.2143 | 9.4463 | 33.9377 | 10.5068 | 7.6645 | 5.7763 | 34.0604 | 9.9755 | 7.277 | 4.5855 | 34.1552 | 9.5518 | 6.9679 | 4.1038 | 34.2453 | 9.1361 | 6.6647 | 3.5361 | 34.3466 | 8.8675 | 6.4687 | 2.9396 | 34.4632 | 8.5704 | 6.252 | 2.505 | 36.2789 | 8.0602 | 5.8798 | 0.40158 | 36.3731 | 7.8582 | 5.7325 | 0.0057268 | 36.4719 | 7.6761 | 5.5996 | -0.4099 | 38.3967 | 6.8547 | 5.0004 | -4.114 | 38.013 | 6.1661 | 4.4981 | -7.4398 | 35.1335 | 5.699 | 4.1573 | -9.9013 | 32.5934 | 5.287 | 3.8568 | -12.3707 | 30.4203 | 4.9345 | 3.5996 | -14.1257 | 33.8513 | 11.2604 | 8.2143 | 9.4463 | 33.9065 | 11.0217 | 8.0402 | 8.3749 | 34.0041 | 10.6752 | 7.7874 | 7.949 | 34.0791 | 10.3179 | 7.5267 | 7.7232 | 34.1441 | 10.0012 | 7.2958 | 7.4852 | 34.2163 | 9.6447 | 7.0357 | 7.2634 | 34.3035 | 9.1781 | 6.6953 | 6.9635 | 34.4081 | 9.0145 | 6.5759 | 6.5095 | 34.5278 | 8.8668 | 6.4682 | 6.0736 | 34.6507 | 8.712 | 6.3553 | 5.6262 | 35.0203 | 8.4576 | 6.1697 | 4.29 | 35.3924 | 8.2492 | 6.0177 | 2.8631 | 35.7281 | 8.0739 | 5.8898 | 1.5334 | 36.0925 | 7.8749 | 5.7446 | -0.004531 | 36.6854 | 7.5582 | 5.5136 | -1.5138 | 33.8671 | 11.2604 | 8.2143 | 9.4463 | 33.9672 | 10.3758 | 7.569 | 5.1316 | 34.1211 | 9.7536 | 7.1151 | 3.7334 | 34.2544 | 9.2466 | 6.7453 | 3.1558 | 34.3848 | 8.8057 | 6.4236 | 2.4686 | 34.5306 | 8.5629 | 6.2465 | 1.7247 | 34.6981 | 8.2071 | 5.987 | 1.1475 | 36.5518 | 7.6584 | 5.5867 | -1.1146 | 36.6742 | 7.4348 | 5.4236 | -1.6505 | 36.8003 | 7.2158 | 5.2638 | -2.221 | 38.306 | 6.2136 | 4.5327 | -6.6424 | 32.2202 | 5.2264 | 3.8126 | -11.4149 | 29.2469 | 4.7441 | 3.4608 | -13.6563 | 26.7765 | 4.3434 | 3.1685 | -15.6944 | 25.3556 | 4.1129 | 3.0003 | -16.6032 | 33.8671 | 11.2604 | 8.2143 | 9.4463 | 33.8779 | 10.6521 | 7.7706 | 6.5778 | 33.9892 | 10.2204 | 7.4557 | 5.4822 | 34.0865 | 9.8859 | 7.2117 | 4.9114 | 34.1923 | 9.564 | 6.9768 | 4.2327 | 34.3306 | 9.5163 | 6.942 | 3.5035 | 34.4911 | 9.3115 | 6.7926 | 2.7874 | 38.4017 | 8.34 | 6.0839 | -2.2295 | 39.9777 | 7.7896 | 5.6824 | -4.8685 | 39.9903 | 7.4982 | 5.4699 | -5.9098 | 40.3214 | 6.6383 | 4.8425 | -9.0567 | 36.3981 | 5.9041 | 4.307 | -11.9234 | 33.1698 | 5.3805 | 3.925 | -13.6546 | 30.5762 | 4.9598 | 3.6181 | -14.6725 | 29.9373 | 4.8561 | 3.5425 | -14.1598 | 33.8624 | 11.2604 | 8.2143 | 9.4463 | 33.9317 | 10.8381 | 7.9063 | 7.4829 | 34.0418 | 10.3774 | 7.5701 | 6.6484 | 34.1193 | 9.9598 | 7.2655 | 6.2045 | 34.1869 | 9.5701 | 6.9813 | 5.7438 | 34.2757 | 9.3199 | 6.7987 | 5.2753 | 34.3882 | 9.0497 | 6.6016 | 4.9389 | 36.1951 | 8.5452 | 6.2336 | 2.8495 | 36.2838 | 8.3288 | 6.0757 | 2.3819 | 36.3817 | 8.1305 | 5.9311 | 1.8855 | 38.282 | 7.4188 | 5.4119 | -1.2989 | 38.6672 | 7.047 | 5.1407 | -3.0234 | 38.9295 | 6.8417 | 4.9909 | -4.1893 | 39.2353 | 6.6914 | 4.8813 | -5.4459 | 39.2463 | 6.5585 | 4.7843 | -6.183 | 33.8624 | 11.2604 | 8.2143 | 9.4463 | 33.889 | 10.3288 | 7.5347 | 4.8816 | 34.0245 | 9.8026 | 7.1509 | 3.4022 | 34.1508 | 9.4675 | 6.9064 | 2.7777 | 34.2724 | 9.1531 | 6.6771 | 2.0453 | 34.4039 | 9.078 | 6.6223 | 1.2849 | 34.5603 | 8.8585 | 6.4622 | 0.52563 | 38.479 | 7.8737 | 5.7438 | -4.5289 | 40.0573 | 7.3093 | 5.3321 | -7.205 | 40.0708 | 7.0119 | 5.1151 | -8.288 | 37.7228 | 6.119 | 4.4637 | -11.5893 | 33.0048 | 5.3537 | 3.9054 | -14.5884 | 29.5736 | 4.7971 | 3.4994 | -16.4712 | 26.7159 | 4.3336 | 3.1613 | -17.7052 | 25.7357 | 4.1746 | 3.0453 | -17.4823
MOSSLEY | HARTSHEAD-HEYROD | STALYBRIDGE | 397437 | 401979 | 25.3322 | 4.5672 | 3.2825 | 15.4936 | 25.4126 | 4.476 | 3.217 | 15.2562 | 25.5204 | 4.3815 | 3.1491 | 15.1631 | 25.6638 | 4.264 | 3.0647 | 15.0811 | 24.9284 | 4.1043 | 2.9498 | 14.886 | 23.9613 | 3.945 | 2.8354 | 14.6779 | 22.6613 | 3.731 | 2.6816 | 14.4926 | 22.1039 | 3.6392 | 2.6156 | 14.3198 | 21.5135 | 3.542 | 2.5457 | 14.1022 | 20.8182 | 3.4276 | 2.4635 | 13.9117 | 17.276 | 2.8444 | 2.0443 | 11.8179 | 12.7362 | 2.0969 | 1.5071 | 8.1643 | 9.4129 | 1.5498 | 1.1138 | 5.1315 | 9.5043 | 1.5648 | 1.1247 | 1.7858 | 6.0431 | 0.99495 | 0.71509 | -1.0863 | 25.2863 | 4.5672 | 3.2825 | 15.4936 | 25.3628 | 4.517 | 3.2465 | 15.3358 | 25.4172 | 4.4557 | 3.2024 | 15.2435 | 25.49 | 4.3793 | 3.1475 | 15.1261 | 25.5976 | 4.2908 | 3.0839 | 14.9383 | 25.4075 | 4.1832 | 3.0065 | 14.7184 | 24.0371 | 3.9575 | 2.8444 | 14.4207 | 23.2336 | 3.8252 | 2.7493 | 14.0355 | 22.6162 | 3.7236 | 2.6762 | 13.7394 | 21.975 | 3.618 | 2.6003 | 13.44 | 19.9931 | 3.2917 | 2.3658 | 12.5187 | 18.4603 | 3.0393 | 2.1844 | 11.5424 | 16.7611 | 2.7596 | 1.9834 | 10.4926 | 16.778 | 2.7624 | 1.9854 | 9.404 | 17.4085 | 2.8662 | 2.06 | 8.6838 | 25.3438 | 4.5672 | 3.2825 | 15.4936 | 25.4345 | 4.461 | 3.2062 | 15.2593 | 25.5599 | 4.335 | 3.1156 | 15.1919 | 25.4171 | 4.1847 | 3.0076 | 15.1552 | 24.2571 | 3.9937 | 2.8704 | 15.0122 | 23.0511 | 3.7952 | 2.7277 | 14.8658 | 22.2062 | 3.6561 | 2.6277 | 14.7678 | 21.4532 | 3.5321 | 2.5386 | 14.6886 | 20.5226 | 3.3789 | 2.4285 | 14.5606 | 19.7276 | 3.248 | 2.3344 | 14.4144 | 15.9997 | 2.6342 | 1.8933 | 12.4491 | 11.6362 | 1.9158 | 1.3769 | 8.9461 | 8.3819 | 1.38 | 0.99184 | 6.0368 | 7.8657 | 1.295 | 0.93077 | 3.0029 | 4.5705 | 0.75251 | 0.54084 | 0.49139 | 25.3438 | 4.5672 | 3.2825 | 15.4936 | 25.324 | 4.5404 | 3.2633 | 15.647 | 25.3707 | 4.472 | 3.2141 | 15.6873 | 25.4485 | 4.3095 | 3.0973 | 15.6913 | 24.9113 | 4.1015 | 2.9478 | 15.5539 | 24.1402 | 3.9745 | 2.8565 | 15.3849 | 22.5275 | 3.709 | 2.6657 | 15.0172 | 20.654 | 3.4005 | 2.444 | 13.9083 | 18.6309 | 3.0674 | 2.2046 | 12.7458 | 18.2194 | 2.9997 | 2.1559 | 11.5997 | 17.2514 | 2.8403 | 2.0414 | 8.2638 | 12.5009 | 2.0582 | 1.4793 | 5.0022 | 8.4324 | 1.3883 | 0.99782 | 2.3073 | 5.9644 | 0.982 | 0.70578 | 0.49393 | 5.7643 | 0.94905 | 0.6821 | 1.6017 | 25.3322 | 4.5672 | 3.2825 | 15.4936 | 25.3998 | 4.5068 | 3.2391 | 15.3672 | 25.4673 | 4.428 | 3.1825 | 15.3392 | 25.548 | 4.3335 | 3.1146 | 15.3367 | 25.5729 | 4.2104 | 3.0261 | 15.29 | 24.7036 | 4.0673 | 2.9232 | 15.2047 | 23.5626 | 3.8794 | 2.7882 | 15.0813 | 22.9404 | 3.777 | 2.7146 | 14.9462 | 22.4142 | 3.6903 | 2.6523 | 14.7379 | 21.7374 | 3.5789 | 2.5722 | 14.5373 | 19.4139 | 3.1964 | 2.2973 | 13.6042 | 17.2731 | 2.8439 | 2.044 | 12.3003 | 16.3434 | 2.6908 | 1.9339 | 11.377 | 19.2209 | 3.1646 | 2.2744 | 10.5182 | 18.3499 | 3.0212 | 2.1714 | 10.0199 | 25.3322 | 4.5672 | 3.2825 | 15.4936 | 25.3448 | 4.5074 | 3.2395 | 15.5222 | 25.4427 | 4.4145 | 3.1728 | 15.4555 | 25.5834 | 4.2381 | 3.046 | 15.3516 | 24.3863 | 4.015 | 2.8857 | 15.1157 | 23.4886 | 3.8672 | 2.7794 | 14.878 | 21.8476 | 3.597 | 2.5853 | 14.424 | 19.832 | 3.2652 | 2.3468 | 13.1987 | 17.5491 | 2.8893 | 2.0766 | 11.9504 | 17.1194 | 2.8186 | 2.0258 | 10.7177 | 15.8293 | 2.6062 | 1.8731 | 7.1101 | 10.7913 | 1.7767 | 1.277 | 3.6031 | 6.4239 | 1.0576 | 0.76015 | 0.65123 | 3.5773 | 0.58897 | 0.4233 | -1.5076 | 2.9579 | 0.48699 | 0.35001 | -0.79727
MOUNT ST | BARTON | CARRINGTON | 376250 | 397574 | 30.1193 | 6.7793 | 4.9454 | 17.3612 | 30.2468 | 5.8869 | 4.2944 | 12.528 | 30.3802 | 5.5308 | 4.0346 | 11.2919 | 30.5455 | 5.3098 | 3.8735 | 10.9425 | 30.756 | 5.0826 | 3.7077 | 10.4718 | 29.9927 | 4.8651 | 3.549 | 9.9779 | 28.5767 | 4.6354 | 3.3815 | 9.5004 | 27.67 | 4.4883 | 3.2742 | 9.0525 | 26.6845 | 4.3285 | 3.1576 | 8.5918 | 25.7735 | 4.1807 | 3.0498 | 8.1495 | 22.3147 | 3.6197 | 2.6405 | 5.9282 | 18.1994 | 2.9521 | 2.1535 | 2.7287 | 15.4761 | 2.5104 | 1.8313 | 0.38903 | 13.0579 | 2.1181 | 1.5451 | -1.6812 | 11.3524 | 1.8415 | 1.3433 | -3.1894 | 30.103 | 6.7793 | 4.9454 | 17.3612 | 30.1852 | 6.5066 | 4.7465 | 15.9781 | 30.2546 | 6.338 | 4.6235 | 15.5598 | 30.3424 | 6.1801 | 4.5083 | 15.3519 | 30.4612 | 5.9948 | 4.3731 | 15.0774 | 30.6041 | 5.8058 | 4.2352 | 14.7923 | 30.7793 | 5.4947 | 4.0083 | 14.4282 | 30.9879 | 5.3595 | 3.9097 | 13.9546 | 31.1329 | 5.2497 | 3.8296 | 13.5696 | 31.2917 | 5.1354 | 3.7462 | 13.1676 | 29.4357 | 4.7748 | 3.4831 | 11.9239 | 27.7443 | 4.5004 | 3.283 | 10.6338 | 26.3616 | 4.2761 | 3.1194 | 9.4657 | 25.3254 | 4.108 | 2.9967 | 8.2209 | 24.192 | 3.9242 | 2.8626 | 7.4029 | 30.126 | 6.7793 | 4.9454 | 17.3612 | 30.2713 | 5.7387 | 4.1863 | 11.699 | 30.4316 | 5.3085 | 3.8725 | 10.2276 | 30.6296 | 5.042 | 3.6781 | 9.7976 | 29.6022 | 4.8018 | 3.5028 | 9.2468 | 27.9396 | 4.5321 | 3.3061 | 8.6741 | 26.4644 | 4.2928 | 3.1315 | 8.1308 | 24.76 | 4.0163 | 2.9299 | 7.0057 | 23.0587 | 3.7403 | 2.7285 | 5.859 | 21.3828 | 3.4685 | 2.5302 | 4.7061 | 15.5483 | 2.5221 | 1.8398 | 0.9621 | 11.2694 | 1.828 | 1.3335 | -2.2316 | 8.2664 | 1.3409 | 0.97816 | -4.3368 | 6.3483 | 1.0298 | 0.75119 | -5.9488 | 5.0831 | 0.82453 | 0.60148 | -6.6517 | 30.1261 | 6.7793 | 4.9454 | 17.3612 | 30.186 | 6.0455 | 4.4101 | 13.4821 | 30.2948 | 5.7894 | 4.2233 | 12.4073 | 30.4381 | 5.5991 | 4.0845 | 12.0249 | 30.6395 | 5.3872 | 3.9299 | 11.4902 | 30.9095 | 5.1901 | 3.7861 | 10.8996 | 30.7019 | 4.9802 | 3.633 | 10.171 | 28.1482 | 4.5659 | 3.3308 | 8.3666 | 25.6972 | 4.1683 | 3.0407 | 6.5665 | 23.2428 | 3.7702 | 2.7503 | 4.8058 | 17.1451 | 2.7811 | 2.0288 | 0.37171 | 12.9404 | 2.0991 | 1.5312 | -2.3194 | 10.1162 | 1.641 | 1.1971 | -3.9161 | 8.6036 | 1.3956 | 1.0181 | -4.5471 | 8.4563 | 1.3717 | 1.0006 | -3.8738 | 30.1192 | 6.7793 | 4.9454 | 17.3612 | 30.2262 | 6.2725 | 4.5757 | 14.7477 | 30.3248 | 6.0115 | 4.3853 | 14.0073 | 30.4354 | 5.804 | 4.234 | 13.7541 | 30.5777 | 5.6006 | 4.0856 | 13.4585 | 30.7716 | 5.4212 | 3.9547 | 13.1338 | 31.0149 | 5.2056 | 3.7974 | 12.7831 | 31.2806 | 5.074 | 3.7014 | 12.4018 | 30.3509 | 4.9232 | 3.5914 | 11.9464 | 29.3779 | 4.7654 | 3.4763 | 11.4751 | 26.6755 | 4.327 | 3.1565 | 9.9101 | 24.2382 | 3.9317 | 2.8681 | 8.2337 | 22.653 | 3.6745 | 2.6805 | 6.9398 | 21.4383 | 3.4775 | 2.5368 | 5.7671 | 20.5129 | 3.3274 | 2.4273 | 5.0509 | 30.1192 | 6.7793 | 4.9454 | 17.3612 | 30.1945 | 5.6446 | 4.1177 | 11.1645 | 30.3354 | 5.2884 | 3.8578 | 9.5414 | 30.5168 | 5.0845 | 3.7091 | 9.0588 | 29.9231 | 4.8538 | 3.5408 | 8.4365 | 28.629 | 4.6439 | 3.3877 | 7.7945 | 27.2554 | 4.4211 | 3.2251 | 7.0038 | 24.6085 | 3.9917 | 2.9119 | 5.1078 | 22.0755 | 3.5809 | 2.6122 | 3.2419 | 19.5485 | 3.171 | 2.3132 | 1.4119 | 13.1362 | 2.1308 | 1.5544 | -3.2696 | 8.5427 | 1.3857 | 1.0109 | -6.2033 | 5.5443 | 0.89933 | 0.65605 | -8.0359 | 3.6224 | 0.58758 | 0.42863 | -8.9349 | 3.227 | 0.52344 | 0.38184 | -8.5602
MUSGRAVE RD | BOLTON | KEARSLEY | 370045 | 409863 | 29.7516 | 6.057 | 4.4185 | 15.0286 | 29.8283 | 6.031 | 4.3995 | 14.6177 | 29.9413 | 5.9937 | 4.3723 | 14.4484 | 30.0922 | 5.9539 | 4.3433 | 14.346 | 30.2859 | 5.8429 | 4.2623 | 14.1507 | 30.5169 | 5.7286 | 4.1789 | 13.9404 | 30.746 | 5.6053 | 4.089 | 13.7566 | 31.0006 | 5.4822 | 3.9992 | 13.589 | 31.2212 | 5.3633 | 3.9125 | 13.3588 | 31.434 | 5.26 | 3.8371 | 13.1388 | 29.6893 | 4.8159 | 3.5131 | 11.2789 | 26.2956 | 4.2654 | 3.1116 | 7.8788 | 24.9769 | 4.0515 | 2.9555 | 5.0296 | 24.187 | 3.9234 | 2.862 | 2.0677 | 21.5335 | 3.4929 | 2.5481 | -0.40686 | 29.7154 | 6.057 | 4.4185 | 15.0286 | 29.7747 | 6.0705 | 4.4283 | 14.9011 | 29.8332 | 6.0576 | 4.419 | 14.7911 | 29.9119 | 6.0128 | 4.3862 | 14.6846 | 30.0229 | 5.932 | 4.3273 | 14.5387 | 30.1654 | 5.8782 | 4.2881 | 14.3804 | 30.3385 | 5.6748 | 4.1397 | 14.1653 | 30.5391 | 5.5728 | 4.0652 | 13.8824 | 30.6722 | 5.4788 | 3.9967 | 13.6244 | 30.8077 | 5.3944 | 3.9351 | 13.3546 | 31.2175 | 5.101 | 3.7211 | 12.5172 | 30.0213 | 4.8697 | 3.5524 | 11.6356 | 30.0149 | 4.8687 | 3.5517 | 10.7571 | 31.3064 | 5.0782 | 3.7045 | 9.7967 | 31.034 | 5.034 | 3.6722 | 9.1691 | 29.7635 | 6.057 | 4.4185 | 15.0286 | 29.8503 | 6.0234 | 4.394 | 14.5852 | 29.9795 | 5.9582 | 4.3464 | 14.4288 | 30.1534 | 5.8698 | 4.2819 | 14.3679 | 30.3743 | 5.7528 | 4.1966 | 14.2148 | 30.6209 | 5.5995 | 4.0847 | 14.0542 | 30.84 | 5.4406 | 3.9688 | 13.9421 | 31.0956 | 5.241 | 3.8232 | 13.8533 | 31.2969 | 5.2225 | 3.8097 | 13.7273 | 31.5012 | 5.1504 | 3.7572 | 13.5916 | 28.6028 | 4.6397 | 3.3846 | 11.9591 | 24.8129 | 4.0249 | 2.9361 | 8.7209 | 22.9813 | 3.7278 | 2.7194 | 6.0111 | 21.5574 | 3.4968 | 2.5509 | 3.2044 | 19.1871 | 3.1123 | 2.2704 | 0.92276 | 29.7635 | 6.057 | 4.4185 | 15.0286 | 29.7586 | 6.0907 | 4.4431 | 14.9421 | 29.815 | 6.0856 | 4.4394 | 14.886 | 29.9047 | 5.9862 | 4.3668 | 14.8562 | 30.0509 | 5.8957 | 4.3009 | 14.7062 | 30.283 | 5.7205 | 4.173 | 14.5197 | 30.5849 | 5.5864 | 4.0752 | 14.1523 | 30.8656 | 5.3897 | 3.9317 | 13.1045 | 31.1038 | 5.1656 | 3.7682 | 12.0055 | 30.5326 | 4.9527 | 3.6129 | 10.9002 | 31.5812 | 5.1228 | 3.737 | 7.7068 | 25.9461 | 4.2087 | 3.0702 | 4.6536 | 22.7783 | 3.6949 | 2.6954 | 2.1745 | 20.8298 | 3.3788 | 2.4648 | 0.64273 | 20.6456 | 3.3489 | 2.443 | 1.8931 | 29.7516 | 6.057 | 4.4185 | 15.0286 | 29.8156 | 6.0784 | 4.4341 | 14.9003 | 29.8892 | 6.0759 | 4.4323 | 14.8259 | 29.9784 | 6.0522 | 4.415 | 14.7998 | 30.1043 | 5.9583 | 4.3465 | 14.7544 | 30.3033 | 5.8922 | 4.2982 | 14.682 | 30.5701 | 5.7853 | 4.2203 | 14.5849 | 30.797 | 5.6782 | 4.1422 | 14.4627 | 30.9922 | 5.5526 | 4.0505 | 14.2417 | 31.192 | 5.4468 | 3.9734 | 14.0076 | 31.8004 | 5.1753 | 3.7753 | 13.1555 | 31.2959 | 5.0765 | 3.7032 | 12.126 | 32.2792 | 5.236 | 3.8196 | 11.3274 | 33.0058 | 5.5131 | 4.0217 | 10.6625 | 33.1334 | 5.4228 | 3.9558 | 10.4414 | 29.7516 | 6.057 | 4.4185 | 15.0286 | 29.7783 | 6.0509 | 4.414 | 14.7227 | 29.8834 | 6.0188 | 4.3907 | 14.5551 | 30.0308 | 5.9007 | 4.3045 | 14.4382 | 30.2213 | 5.7821 | 4.218 | 14.2118 | 30.4438 | 5.5982 | 4.0838 | 13.9791 | 30.676 | 5.4467 | 3.9733 | 13.5567 | 30.9623 | 5.23 | 3.8152 | 12.4301 | 30.81 | 4.9977 | 3.6457 | 11.2775 | 29.4259 | 4.7732 | 3.482 | 10.1174 | 30.2743 | 4.9108 | 3.5824 | 6.7237 | 24.6183 | 3.9933 | 2.9131 | 3.473 | 20.7988 | 3.3738 | 2.4611 | 0.76941 | 18.5935 | 3.0161 | 2.2002 | -1.0746 | 18.0412 | 2.9265 | 2.1348 | -0.17816
NELSON | NELSON | PADIHAM | 386020 | 438507 | 30.6876 | 12.0769 | 8.8099 | 10.2516 | 30.7864 | 11.7545 | 8.5748 | 8.237 | 30.9385 | 11.432 | 8.3395 | 7.6732 | 31.1282 | 10.9053 | 7.9553 | 7.4867 | 31.3627 | 10.708 | 7.8113 | 7.2762 | 31.6453 | 10.5393 | 7.6883 | 6.9707 | 31.8441 | 10.3322 | 7.5372 | 6.8112 | 32.0383 | 10.1401 | 7.397 | 6.6253 | 32.2221 | 9.9598 | 7.2656 | 6.4085 | 32.4143 | 9.8854 | 7.2113 | 6.2028 | 33.2413 | 9.473 | 6.9105 | 4.9426 | 34.2404 | 8.8811 | 6.4786 | 2.4697 | 34.8143 | 8.2385 | 6.0099 | -0.30475 | 35.1161 | 7.6117 | 5.5526 | -3.1959 | 35.2433 | 7.064 | 5.1531 | -5.4267 | 30.6631 | 12.0769 | 8.8099 | 10.2516 | 30.7797 | 11.9864 | 8.7439 | 9.646 | 30.9216 | 11.8262 | 8.627 | 9.2872 | 31.0913 | 11.6616 | 8.5069 | 9.0205 | 31.3085 | 11.4747 | 8.3707 | 8.7285 | 31.5825 | 11.2459 | 8.2037 | 8.3482 | 31.8726 | 10.9311 | 7.9741 | 7.9348 | 32.0664 | 10.7547 | 7.8454 | 7.4369 | 32.1658 | 10.6268 | 7.7521 | 7.2224 | 32.2754 | 10.4954 | 7.6563 | 7.005 | 32.6681 | 10.1111 | 7.3759 | 6.3415 | 33.1276 | 9.7761 | 7.1316 | 5.6785 | 33.5898 | 9.4287 | 6.8781 | 5.0978 | 34.0537 | 9.2946 | 6.7803 | 4.5323 | 34.3558 | 9.1175 | 6.6511 | 4.1905 | 30.6984 | 12.0769 | 8.8099 | 10.2516 | 30.8087 | 11.6779 | 8.5188 | 7.9137 | 30.9789 | 11.2894 | 8.2354 | 7.295 | 31.1947 | 10.6048 | 7.736 | 7.1083 | 31.4598 | 10.5518 | 7.6974 | 6.9011 | 31.7164 | 10.3273 | 7.5336 | 6.6014 | 31.8762 | 10.0723 | 7.3476 | 6.4481 | 32.0512 | 9.8619 | 7.1941 | 6.2742 | 32.213 | 9.773 | 7.1292 | 6.1159 | 32.3823 | 9.6622 | 7.0484 | 5.9735 | 33.1867 | 9.1432 | 6.6699 | 4.8838 | 34.2649 | 8.4753 | 6.1826 | 2.6063 | 34.8729 | 7.7446 | 5.6496 | -0.0074864 | 35.1695 | 7.1061 | 5.1838 | -2.6534 | 35.2366 | 6.5766 | 4.7976 | -4.5498 | 30.6984 | 12.0769 | 8.8099 | 10.2516 | 30.6912 | 11.8315 | 8.6309 | 8.7957 | 30.763 | 11.6426 | 8.4931 | 8.4037 | 30.8644 | 10.9652 | 7.9989 | 8.3125 | 31.0219 | 10.9682 | 8.0011 | 8.1885 | 31.2789 | 10.9338 | 7.9761 | 7.9465 | 31.6138 | 10.7965 | 7.8759 | 7.7183 | 31.9736 | 10.4288 | 7.6077 | 7.0956 | 32.3016 | 10.1998 | 7.4406 | 6.366 | 32.6395 | 9.86 | 7.1927 | 5.4323 | 33.5481 | 8.9833 | 6.5532 | 2.2912 | 34.1655 | 8.2224 | 5.9981 | -0.64874 | 34.5477 | 7.4892 | 5.4632 | -3.0026 | 34.7433 | 7.075 | 5.1611 | -4.3788 | 34.6255 | 7.0489 | 5.142 | -2.9011 | 30.6876 | 12.0769 | 8.8099 | 10.2516 | 30.7734 | 11.9353 | 8.7067 | 9.3175 | 30.8834 | 11.6635 | 8.5084 | 8.9746 | 31.0055 | 11.153 | 8.136 | 8.8483 | 31.1648 | 10.9652 | 7.999 | 8.7361 | 31.411 | 10.8216 | 7.8942 | 8.5047 | 31.6839 | 10.6244 | 7.7503 | 8.3719 | 31.8509 | 10.4348 | 7.612 | 8.204 | 32.0138 | 10.2578 | 7.4829 | 7.9962 | 32.1878 | 10.174 | 7.4218 | 7.7838 | 32.7985 | 9.8792 | 7.2067 | 7.059 | 33.4118 | 9.6224 | 7.0194 | 6.2998 | 33.8285 | 9.3935 | 6.8524 | 5.8093 | 34.1306 | 9.2538 | 6.7505 | 5.4496 | 34.1946 | 9.162 | 6.6836 | 5.5497 | 30.6876 | 12.0769 | 8.8099 | 10.2516 | 30.7296 | 11.6537 | 8.5012 | 7.7593 | 30.8727 | 11.4088 | 8.3225 | 7.1024 | 31.0581 | 10.7078 | 7.8112 | 6.9005 | 31.2876 | 10.7081 | 7.8114 | 6.6726 | 31.5587 | 10.6484 | 7.7678 | 6.3596 | 31.7864 | 10.4914 | 7.6533 | 6.0662 | 32.1215 | 10.1153 | 7.379 | 5.3432 | 32.4393 | 9.8773 | 7.2053 | 4.6382 | 32.7664 | 9.569 | 6.9805 | 3.9003 | 33.7015 | 8.6618 | 6.3187 | 0.63587 | 34.353 | 7.8661 | 5.7382 | -2.432 | 34.7835 | 7.102 | 5.1808 | -4.9531 | 35.0017 | 6.6304 | 4.8368 | -6.5692 | 34.904 | 6.5494 | 4.7777 | -5.39
NEW MOSTON | CHADDERTON | WHITEGATE | 388333 | 402657 | 29.9652 | 15.6234 | 11.397 | 16.506 | 30.0707 | 15.5244 | 11.3249 | 16.1989 | 30.2075 | 15.4122 | 11.243 | 16.0052 | 30.3825 | 15.2828 | 11.1486 | 15.8194 | 30.5975 | 15.1048 | 11.0187 | 15.5118 | 30.8437 | 14.9547 | 10.9092 | 15.0941 | 31.1264 | 14.7922 | 10.7907 | 14.6944 | 31.4694 | 14.6788 | 10.708 | 14.3258 | 31.7272 | 14.5679 | 10.6271 | 13.9557 | 31.8952 | 14.4661 | 10.5528 | 13.6136 | 32.4774 | 14.0386 | 10.2409 | 11.8575 | 33.198 | 13.5809 | 9.9071 | 9.2899 | 33.6383 | 13.3595 | 9.7456 | 7.3931 | 33.9645 | 13.1881 | 9.6206 | 5.7984 | 34.0841 | 12.9197 | 9.4248 | 4.6702 | 29.9313 | 15.6234 | 11.397 | 16.506 | 30.0129 | 15.5506 | 11.3439 | 16.337 | 30.0915 | 15.4764 | 11.2898 | 16.1984 | 30.1955 | 15.3288 | 11.1822 | 16.053 | 30.3336 | 15.2418 | 11.1187 | 15.8537 | 30.5079 | 15.1365 | 11.0419 | 15.6215 | 30.7175 | 14.9108 | 10.8772 | 15.3245 | 30.9586 | 14.8053 | 10.8003 | 14.9617 | 31.0758 | 14.723 | 10.7402 | 14.7186 | 31.2005 | 14.6315 | 10.6735 | 14.4319 | 31.5912 | 14.357 | 10.4732 | 13.593 | 31.9246 | 14.1296 | 10.3073 | 12.7136 | 32.1843 | 14.0223 | 10.2291 | 11.8868 | 32.4556 | 13.9883 | 10.2043 | 11.0619 | 32.652 | 13.8107 | 10.0747 | 10.5318 | 29.9781 | 15.6234 | 11.397 | 16.506 | 30.1067 | 15.4732 | 11.2875 | 16.097 | 30.2766 | 15.35 | 11.1976 | 15.8294 | 30.4946 | 15.165 | 11.0626 | 15.5757 | 30.761 | 14.9862 | 10.9322 | 15.1448 | 31.0666 | 14.7848 | 10.7853 | 14.6118 | 31.4183 | 14.5959 | 10.6475 | 14.1091 | 31.8433 | 14.4495 | 10.5407 | 13.624 | 32.0726 | 14.3044 | 10.4349 | 13.1434 | 32.2655 | 14.1592 | 10.329 | 12.6685 | 32.9765 | 13.6503 | 9.9577 | 10.6328 | 33.6796 | 13.1456 | 9.5895 | 8.0895 | 33.9915 | 12.9022 | 9.412 | 6.4296 | 34.1994 | 12.7517 | 9.3022 | 5.2632 | 34.2498 | 12.5773 | 9.175 | 4.915 | 29.9781 | 15.6234 | 11.397 | 16.506 | 29.9982 | 15.5564 | 11.3482 | 16.4299 | 30.085 | 15.5242 | 11.3247 | 16.246 | 30.2094 | 15.4082 | 11.24 | 16.0037 | 30.3855 | 15.283 | 11.1488 | 15.5842 | 30.645 | 15.1314 | 11.0382 | 15.1077 | 30.9653 | 14.9454 | 10.9025 | 14.4529 | 31.3312 | 14.7418 | 10.754 | 13.4492 | 31.6183 | 14.5253 | 10.596 | 12.4635 | 31.9017 | 14.324 | 10.4492 | 11.51 | 32.7698 | 14.0859 | 10.2755 | 8.9279 | 33.4719 | 13.5053 | 9.8519 | 6.7838 | 33.7074 | 13.0787 | 9.5407 | 5.5354 | 33.8332 | 12.7774 | 9.3209 | 5.1807 | 33.7674 | 12.7505 | 9.3013 | 6.0064 | 29.9652 | 15.6234 | 11.397 | 16.506 | 30.0571 | 15.5609 | 11.3515 | 16.2727 | 30.1548 | 15.4533 | 11.273 | 16.1267 | 30.2649 | 15.3591 | 11.2042 | 16.0256 | 30.4092 | 15.222 | 11.1042 | 15.8956 | 30.6256 | 15.1038 | 11.018 | 15.7325 | 30.9058 | 14.9621 | 10.9147 | 15.4365 | 31.2153 | 14.8604 | 10.8405 | 15.1293 | 31.4427 | 14.753 | 10.7621 | 14.7737 | 31.6557 | 14.6493 | 10.6864 | 14.4155 | 32.1232 | 14.3307 | 10.454 | 13.2228 | 32.607 | 14.1202 | 10.3005 | 11.9861 | 32.9527 | 14.1152 | 10.2969 | 11.1435 | 33.2667 | 14.139 | 10.3142 | 10.3807 | 33.4477 | 14.0371 | 10.2399 | 9.9923 | 29.9652 | 15.6234 | 11.397 | 16.506 | 30.0238 | 15.4991 | 11.3064 | 16.3113 | 30.1718 | 15.4595 | 11.2775 | 16.0374 | 30.3613 | 15.327 | 11.1808 | 15.7085 | 30.5945 | 15.1783 | 11.0724 | 15.1796 | 30.8577 | 15.0058 | 10.9465 | 14.5724 | 31.163 | 14.8113 | 10.8047 | 13.8627 | 31.5528 | 14.5873 | 10.6412 | 12.7598 | 31.8546 | 14.3557 | 10.4723 | 11.6916 | 32.1477 | 14.1393 | 10.3144 | 10.659 | 33.0078 | 13.8534 | 10.1059 | 7.8604 | 33.6783 | 13.246 | 9.6628 | 5.5768 | 33.9214 | 12.7948 | 9.3336 | 4.1992 | 34.0504 | 12.4692 | 9.0961 | 3.7082 | 34.0093 | 12.4069 | 9.0507 | 4.3457
NEWBIGGIN ON LUNE | PENRITH & SHAP | HARKER / HUTTON | 369770 | 505803 | 3.1874 | 3.1874 | 3.1874 | 2.0557 | 3.2026 | 3.2026 | 3.2026 | 2.0384 | 3.2221 | 3.2221 | 3.2221 | 2.0073 | 3.2454 | 3.2454 | 3.2454 | 1.9755 | 3.2714 | 3.2714 | 3.2714 | 1.9359 | 3.2987 | 3.2987 | 3.2987 | 1.8954 | 3.3271 | 3.3271 | 3.3271 | 1.8596 | 3.3591 | 3.3591 | 3.3591 | 1.8258 | 3.38 | 3.38 | 3.38 | 1.7892 | 3.399 | 3.399 | 3.399 | 1.7576 | 3.4426 | 3.4426 | 3.4426 | 1.6196 | 3.4887 | 3.4887 | 3.4887 | 1.417 | 3.5207 | 3.5207 | 3.5207 | 1.2514 | 3.5443 | 3.5443 | 3.5443 | 1.1338 | 3.5579 | 3.5579 | 3.5579 | 1.0496 | 3.1878 | 3.1878 | 3.1878 | 2.0557 | 3.2127 | 3.2127 | 3.2127 | 2.0342 | 3.2366 | 3.2366 | 3.2366 | 2.0012 | 3.262 | 3.262 | 3.262 | 1.9638 | 3.2961 | 3.2961 | 3.2961 | 1.9199 | 3.3246 | 3.3246 | 3.3246 | 1.8756 | 3.3457 | 3.3457 | 3.3457 | 1.8241 | 3.3696 | 3.3696 | 3.3696 | 1.7653 | 3.3833 | 3.3833 | 3.3833 | 1.7242 | 3.3974 | 3.3974 | 3.3974 | 1.6831 | 3.4397 | 3.4397 | 3.4397 | 1.5656 | 3.4699 | 3.4699 | 3.4699 | 1.4673 | 3.4902 | 3.4902 | 3.4902 | 1.3774 | 3.5092 | 3.5092 | 3.5092 | 1.2713 | 3.5217 | 3.5217 | 3.5217 | 1.1835 | 3.1873 | 3.1873 | 3.1873 | 2.0557 | 3.2025 | 3.2025 | 3.2025 | 2.0409 | 3.2218 | 3.2218 | 3.2218 | 2.0125 | 3.2449 | 3.2449 | 3.2449 | 1.9858 | 3.2705 | 3.2705 | 3.2705 | 1.9517 | 3.2973 | 3.2973 | 3.2973 | 1.9177 | 3.3252 | 3.3252 | 3.3252 | 1.8902 | 3.3563 | 3.3563 | 3.3563 | 1.8667 | 3.3767 | 3.3767 | 3.3767 | 1.8209 | 3.3957 | 3.3957 | 3.3957 | 1.752 | 3.4314 | 3.4314 | 3.4314 | 1.5361 | 3.4581 | 3.4581 | 3.4581 | 1.3108 | 3.473 | 3.473 | 3.473 | 1.1339 | 3.4776 | 3.4776 | 3.4776 | 1.0108 | 3.4723 | 3.4723 | 3.4723 | 0.92813 | 3.1873 | 3.1873 | 3.1873 | 2.0557 | 3.1923 | 3.1923 | 3.1923 | 2.0519 | 3.2002 | 3.2002 | 3.2002 | 2.0317 | 3.211 | 3.211 | 3.211 | 2.0033 | 3.2244 | 3.2244 | 3.2244 | 1.9733 | 3.2425 | 3.2425 | 3.2425 | 1.9392 | 3.2628 | 3.2628 | 3.2628 | 1.9023 | 3.2851 | 3.2851 | 3.2851 | 1.848 | 3.3054 | 3.3054 | 3.3054 | 1.7869 | 3.3247 | 3.3247 | 3.3247 | 1.7255 | 3.3822 | 3.3822 | 3.3822 | 1.5507 | 3.4309 | 3.4309 | 3.4309 | 1.3461 | 3.4451 | 3.4451 | 3.4451 | 1.1826 | 3.4448 | 3.4448 | 3.4448 | 1.085 | 3.4222 | 3.4222 | 3.4222 | 1.0952 | 3.1874 | 3.1874 | 3.1874 | 2.0557 | 3.2012 | 3.2012 | 3.2012 | 2.0408 | 3.2167 | 3.2167 | 3.2167 | 2.0139 | 3.2342 | 3.2342 | 3.2342 | 1.9879 | 3.2542 | 3.2542 | 3.2542 | 1.9611 | 3.2796 | 3.2796 | 3.2796 | 1.9344 | 3.3087 | 3.3087 | 3.3087 | 1.9084 | 3.3387 | 3.3387 | 3.3387 | 1.884 | 3.3572 | 3.3572 | 3.3572 | 1.8529 | 3.3755 | 3.3755 | 3.3755 | 1.8229 | 3.4226 | 3.4226 | 3.4226 | 1.7141 | 3.4639 | 3.4639 | 3.4639 | 1.5477 | 3.4917 | 3.4917 | 3.4917 | 1.4032 | 3.5134 | 3.5134 | 3.5134 | 1.2801 | 3.5196 | 3.5196 | 3.5196 | 1.2148 | 3.1874 | 3.1874 | 3.1874 | 2.0557 | 3.2017 | 3.2017 | 3.2017 | 2.0419 | 3.2213 | 3.2213 | 3.2213 | 2.0078 | 3.2456 | 3.2456 | 3.2456 | 1.9632 | 3.272 | 3.272 | 3.272 | 1.9179 | 3.2995 | 3.2995 | 3.2995 | 1.8737 | 3.3292 | 3.3292 | 3.3292 | 1.8263 | 3.3651 | 3.3651 | 3.3651 | 1.7551 | 3.3903 | 3.3903 | 3.3903 | 1.6819 | 3.4125 | 3.4125 | 3.4125 | 1.6092 | 3.4602 | 3.4602 | 3.4602 | 1.4051 | 3.5026 | 3.5026 | 3.5026 | 1.2221 | 3.5299 | 3.5299 | 3.5299 | 1.1019 | 3.5433 | 3.5433 | 3.5433 | 1.0587 | 3.5366 | 3.5366 | 3.5366 | 1.0845
NEWBY | PENRITH & SHAP | HARKER / HUTTON | 360520 | 521151 | 15.0419 | 15.0419 | 15.0419 | 8.7131 | 15.0952 | 15.0952 | 15.0952 | 8.4174 | 15.1651 | 15.1651 | 15.1651 | 8.3149 | 15.2537 | 15.2537 | 15.2537 | 8.2612 | 15.3233 | 15.3233 | 15.3233 | 8.1038 | 15.3925 | 15.3925 | 15.3925 | 7.9355 | 15.4731 | 15.4731 | 15.4731 | 7.788 | 15.5715 | 15.5715 | 15.5715 | 7.6559 | 15.645 | 15.645 | 15.645 | 7.5349 | 15.7082 | 15.7082 | 15.7082 | 7.4342 | 15.9061 | 15.9061 | 15.9061 | 6.8442 | 16.1002 | 16.1002 | 16.1002 | 5.8881 | 16.2309 | 16.2309 | 16.2309 | 5.1073 | 16.3092 | 16.3092 | 16.3092 | 4.4282 | 16.3541 | 16.3541 | 16.3541 | 3.704 | 15.0421 | 15.0421 | 15.0421 | 8.7131 | 15.1028 | 15.1028 | 15.1028 | 8.594 | 15.1659 | 15.1659 | 15.1659 | 8.4769 | 15.2519 | 15.2519 | 15.2519 | 8.3578 | 15.3586 | 15.3586 | 15.3586 | 8.22 | 15.4405 | 15.4405 | 15.4405 | 8.1068 | 15.5221 | 15.5221 | 15.5221 | 7.9659 | 15.6014 | 15.6014 | 15.6014 | 7.7864 | 15.6381 | 15.6381 | 15.6381 | 7.6946 | 15.6768 | 15.6768 | 15.6768 | 7.6039 | 15.8031 | 15.8031 | 15.8031 | 7.3368 | 15.9333 | 15.9333 | 15.9333 | 7.0791 | 16.0564 | 16.0564 | 16.0564 | 6.773 | 16.187 | 16.187 | 16.187 | 6.2939 | 16.2799 | 16.2799 | 16.2799 | 5.8053 | 15.042 | 15.042 | 15.042 | 8.7131 | 15.0958 | 15.0958 | 15.0958 | 8.3858 | 15.1659 | 15.1659 | 15.1659 | 8.2841 | 15.2548 | 15.2548 | 15.2548 | 8.2447 | 15.3447 | 15.3447 | 15.3447 | 8.1012 | 15.4221 | 15.4221 | 15.4221 | 7.9491 | 15.5127 | 15.5127 | 15.5127 | 7.8259 | 15.6211 | 15.6211 | 15.6211 | 7.7195 | 15.6866 | 15.6866 | 15.6866 | 7.6367 | 15.7504 | 15.7504 | 15.7504 | 7.566 | 15.9609 | 15.9609 | 15.9609 | 7.0669 | 16.1642 | 16.1642 | 16.1642 | 6.1878 | 16.2828 | 16.2828 | 16.2828 | 5.4766 | 16.3574 | 16.3574 | 16.3574 | 4.8852 | 16.3908 | 16.3908 | 16.3908 | 4.2659 | 15.042 | 15.042 | 15.042 | 8.7131 | 15.0437 | 15.0437 | 15.0437 | 8.5573 | 15.0705 | 15.0705 | 15.0705 | 8.4853 | 15.1136 | 15.1136 | 15.1136 | 8.3978 | 15.1779 | 15.1779 | 15.1779 | 8.244 | 15.274 | 15.274 | 15.274 | 8.0881 | 15.372 | 15.372 | 15.372 | 7.9064 | 15.4639 | 15.4639 | 15.4639 | 7.5764 | 15.5419 | 15.5419 | 15.5419 | 7.2311 | 15.6205 | 15.6205 | 15.6205 | 6.885 | 15.8321 | 15.8321 | 15.8321 | 5.926 | 16.031 | 16.031 | 16.031 | 5.0924 | 16.1445 | 16.1445 | 16.1445 | 4.51 | 16.1972 | 16.1972 | 16.1972 | 4.2984 | 16.1796 | 16.1796 | 16.1796 | 4.6726 | 15.0419 | 15.0419 | 15.0419 | 8.7131 | 15.0876 | 15.0876 | 15.0876 | 8.6013 | 15.1353 | 15.1353 | 15.1353 | 8.5252 | 15.1917 | 15.1917 | 15.1917 | 8.4663 | 15.2646 | 15.2646 | 15.2646 | 8.3551 | 15.342 | 15.342 | 15.342 | 8.2696 | 15.4179 | 15.4179 | 15.4179 | 8.1904 | 15.5047 | 15.5047 | 15.5047 | 8.0971 | 15.5677 | 15.5677 | 15.5677 | 7.9828 | 15.6322 | 15.6322 | 15.6322 | 7.8704 | 15.8195 | 15.8195 | 15.8195 | 7.4487 | 16.0112 | 16.0112 | 16.0112 | 6.9524 | 16.143 | 16.143 | 16.143 | 6.6269 | 16.2349 | 16.2349 | 16.2349 | 6.2674 | 16.2666 | 16.2666 | 16.2666 | 6.0226 | 15.0419 | 15.0419 | 15.0419 | 8.7131 | 15.0723 | 15.0723 | 15.0723 | 8.4138 | 15.1397 | 15.1397 | 15.1397 | 8.2894 | 15.2305 | 15.2305 | 15.2305 | 8.1662 | 15.3092 | 15.3092 | 15.3092 | 7.9773 | 15.3772 | 15.3772 | 15.3772 | 7.7916 | 15.458 | 15.458 | 15.458 | 7.5744 | 15.563 | 15.563 | 15.563 | 7.2019 | 15.6422 | 15.6422 | 15.6422 | 6.837 | 15.7113 | 15.7113 | 15.7113 | 6.4709 | 15.9188 | 15.9188 | 15.9188 | 5.4459 | 16.1108 | 16.1108 | 16.1108 | 4.5531 | 16.2301 | 16.2301 | 16.2301 | 3.9135 | 16.2791 | 16.2791 | 16.2791 | 3.6345 | 16.2639 | 16.2639 | 16.2639 | 3.9342
NEWTON | HYDE | STALYBRIDGE | 396385 | 396464 | 7.5907 | 7.5907 | 7.5907 | 7.5907 | 7.6257 | 7.6257 | 7.6257 | 7.6257 | 7.6745 | 7.6745 | 7.6745 | 7.6745 | 7.74 | 7.74 | 7.74 | 7.74 | 7.8339 | 7.8339 | 7.8339 | 7.8339 | 7.9364 | 7.9364 | 7.9364 | 7.9364 | 8.0426 | 8.0426 | 8.0426 | 8.0426 | 8.1553 | 8.1553 | 8.1553 | 8.1553 | 8.2535 | 8.2535 | 8.2535 | 8.2535 | 8.3423 | 8.3423 | 8.3423 | 8.3423 | 8.5342 | 8.5342 | 8.5342 | 8.5342 | 8.736 | 8.736 | 8.5983 | 8.736 | 8.8803 | 8.8803 | 8.6547 | 8.8803 | 9.0054 | 9.0054 | 8.8246 | 9.0054 | 9.0957 | 9.0957 | 8.7792 | 9.0957 | 7.5862 | 7.5862 | 7.5862 | 7.5862 | 7.6057 | 7.6057 | 7.6057 | 7.6057 | 7.6221 | 7.6221 | 7.6221 | 7.6221 | 7.6442 | 7.6442 | 7.6442 | 7.6442 | 7.6754 | 7.6754 | 7.6754 | 7.6754 | 7.7064 | 7.7064 | 7.7064 | 7.7064 | 7.7491 | 7.7491 | 7.7491 | 7.7491 | 7.8145 | 7.8145 | 7.8145 | 7.8145 | 7.8748 | 7.8748 | 7.8748 | 7.8748 | 7.9379 | 7.9379 | 7.9379 | 7.9379 | 8.1434 | 8.1434 | 8.1434 | 8.1434 | 8.3767 | 8.3767 | 8.3767 | 8.3767 | 8.5843 | 8.5843 | 8.5843 | 8.5843 | 8.7068 | 8.7068 | 8.7068 | 8.7068 | 8.7921 | 8.7921 | 8.7921 | 8.7921 | 7.5926 | 7.5926 | 7.5926 | 7.5926 | 7.6301 | 7.6301 | 7.6301 | 7.6301 | 7.6822 | 7.6822 | 7.6822 | 7.6822 | 7.7527 | 7.7527 | 7.7527 | 7.7527 | 7.8521 | 7.8521 | 7.8521 | 7.8521 | 7.9607 | 7.9607 | 7.9607 | 7.9607 | 8.074 | 8.074 | 8.074 | 8.074 | 8.1946 | 8.1946 | 8.1946 | 8.1946 | 8.2973 | 8.2973 | 8.2973 | 8.2973 | 8.3572 | 8.3572 | 8.3572 | 8.3572 | 8.5502 | 8.5502 | 8.5502 | 8.5502 | 8.7608 | 8.7608 | 8.5542 | 8.7608 | 8.9119 | 8.9119 | 8.6064 | 8.9119 | 9.0357 | 9.0357 | 8.7769 | 9.0357 | 9.1151 | 9.1151 | 8.7488 | 9.1151 | 7.5926 | 7.5926 | 7.5926 | 7.5926 | 7.6045 | 7.6045 | 7.6045 | 7.6045 | 7.6421 | 7.6421 | 7.6421 | 7.6421 | 7.7039 | 7.7039 | 7.7039 | 7.7039 | 7.7972 | 7.7972 | 7.7972 | 7.7972 | 7.9105 | 7.9105 | 7.9105 | 7.9105 | 8.0665 | 8.0665 | 8.0665 | 8.0665 | 8.1842 | 8.1842 | 8.1842 | 8.1842 | 8.2509 | 8.2509 | 8.2509 | 8.2509 | 8.3177 | 8.3177 | 8.3177 | 8.3177 | 8.5211 | 8.5211 | 8.5211 | 8.5211 | 8.7181 | 8.7181 | 8.7181 | 8.7181 | 8.8549 | 8.8549 | 8.8549 | 8.8549 | 8.9525 | 8.9525 | 8.8068 | 8.9525 | 8.9657 | 8.9657 | 8.7822 | 8.9657 | 7.5907 | 7.5907 | 7.5907 | 7.5907 | 7.6191 | 7.6191 | 7.6191 | 7.6191 | 7.6576 | 7.6576 | 7.6576 | 7.6576 | 7.7026 | 7.7026 | 7.7026 | 7.7026 | 7.7596 | 7.7596 | 7.7596 | 7.7596 | 7.8312 | 7.8312 | 7.8312 | 7.8312 | 7.9157 | 7.9157 | 7.9157 | 7.9157 | 8.0093 | 8.0093 | 8.0093 | 8.0093 | 8.0969 | 8.0969 | 8.0969 | 8.0969 | 8.1867 | 8.1867 | 8.1867 | 8.1867 | 8.4517 | 8.4517 | 8.4517 | 8.4517 | 8.6277 | 8.6277 | 8.6277 | 8.6277 | 8.7527 | 8.7527 | 8.7527 | 8.7527 | 8.8552 | 8.8552 | 8.8552 | 8.8552 | 8.9065 | 8.9065 | 8.9065 | 8.9065 | 7.5907 | 7.5907 | 7.5907 | 7.5907 | 7.6093 | 7.6093 | 7.6093 | 7.6093 | 7.6583 | 7.6583 | 7.6583 | 7.6583 | 7.7339 | 7.7339 | 7.7339 | 7.7339 | 7.8379 | 7.8379 | 7.8379 | 7.8379 | 7.9491 | 7.9491 | 7.9491 | 7.9491 | 8.0981 | 8.0981 | 8.0981 | 8.0981 | 8.2266 | 8.2266 | 8.2266 | 8.2266 | 8.2962 | 8.2962 | 8.2962 | 8.2962 | 8.365 | 8.365 | 8.365 | 8.365 | 8.5735 | 8.5735 | 8.5735 | 8.5735 | 8.7713 | 8.7713 | 8.7713 | 8.7713 | 8.9114 | 8.9114 | 8.8602 | 8.9114 | 9.0064 | 9.0064 | 8.6992 | 9.0064 | 9.022 | 9.022 | 8.6605 | 9.022
NEWTON HEATH | CHADDERTON | WHITEGATE | 388030 | 400511 | 12.1396 | 12.1396 | 12.1396 | 2.2034 | 12.1839 | 12.1839 | 12.1839 | 1.2514 | 12.2384 | 12.2384 | 12.2384 | 1.0917 | 12.3046 | 12.3046 | 12.3046 | 0.85408 | 12.3801 | 12.3801 | 12.3801 | 0.5201 | 12.4619 | 12.4619 | 12.4619 | 0.29059 | 12.5596 | 12.5596 | 12.5596 | 0.072704 | 12.6777 | 12.6777 | 12.6777 | -0.11295 | 12.7699 | 12.7699 | 12.7699 | -0.28732 | 12.8596 | 12.8596 | 12.8596 | -0.44807 | 13.1552 | 13.1552 | 13.1552 | -1.6399 | 13.4636 | 13.4636 | 13.4636 | -3.6306 | 13.6822 | 13.6822 | 13.6822 | -5.1754 | 13.8615 | 13.8615 | 13.8615 | -6.5819 | 13.9594 | 13.9594 | 13.9594 | -7.6276 | 12.1307 | 12.1307 | 12.1307 | 2.2034 | 12.1737 | 12.1737 | 12.1737 | 1.7483 | 12.2197 | 12.2197 | 12.2197 | 1.7825 | 12.2686 | 12.2686 | 12.2686 | 1.6735 | 12.3189 | 12.3189 | 12.3189 | 1.5275 | 12.3855 | 12.3855 | 12.3855 | 1.4095 | 12.461 | 12.461 | 12.461 | 1.25 | 12.5429 | 12.5429 | 12.5429 | 1.0477 | 12.5855 | 12.5855 | 12.5855 | 0.91164 | 12.631 | 12.631 | 12.631 | 0.76611 | 12.7777 | 12.7777 | 12.7777 | 0.32142 | 12.9324 | 12.9324 | 12.9324 | -0.15409 | 13.0849 | 13.0849 | 13.0849 | -0.65484 | 13.2472 | 13.2472 | 13.2472 | -1.1852 | 13.3686 | 13.3686 | 13.3686 | -1.5738 | 12.1434 | 12.1434 | 12.1434 | 2.2034 | 12.2022 | 12.2022 | 12.2022 | 1.0983 | 12.2744 | 12.2744 | 12.2744 | 0.85342 | 12.3602 | 12.3602 | 12.3602 | 0.54603 | 12.4495 | 12.4495 | 12.4495 | 0.14016 | 12.5549 | 12.5549 | 12.5549 | -0.16365 | 12.68 | 12.68 | 12.68 | -0.44963 | 12.829 | 12.829 | 12.829 | -0.71602 | 12.9435 | 12.9435 | 12.9435 | -0.97403 | 13.0556 | 13.0556 | 13.0556 | -1.231 | 13.4281 | 13.4281 | 13.4281 | -2.7329 | 13.7909 | 13.7909 | 13.7909 | -4.668 | 13.9972 | 13.9972 | 13.9972 | -5.9875 | 14.1544 | 14.1544 | 14.1544 | -7.009 | 14.2123 | 14.2123 | 14.2123 | -7.4419 | 12.1434 | 12.1434 | 12.1434 | 2.2034 | 12.1352 | 12.1352 | 12.1352 | 1.4936 | 12.1682 | 12.1682 | 12.1682 | 1.3353 | 12.2138 | 12.2138 | 12.2138 | 1.0322 | 12.2825 | 12.2825 | 12.2825 | 0.6152 | 12.3681 | 12.3681 | 12.3681 | 0.29184 | 12.4798 | 12.4798 | 12.4798 | -0.13013 | 12.6166 | 12.6166 | 12.6166 | -0.90035 | 12.7333 | 12.7333 | 12.7333 | -1.6485 | 12.8496 | 12.8496 | 12.8496 | -2.3656 | 13.2072 | 13.2072 | 13.2072 | -4.3468 | 13.5478 | 13.5478 | 13.5478 | -5.9495 | 13.777 | 13.777 | 13.777 | -6.9029 | 13.9164 | 13.9164 | 13.9164 | -7.1438 | 13.8994 | 13.8994 | 13.8994 | -6.5231 | 12.1396 | 12.1396 | 12.1396 | 2.2034 | 12.1794 | 12.1794 | 12.1794 | 1.4792 | 12.2187 | 12.2187 | 12.2187 | 1.3853 | 12.2598 | 12.2598 | 12.2598 | 1.2025 | 12.3159 | 12.3159 | 12.3159 | 0.99016 | 12.3869 | 12.3869 | 12.3869 | 0.88159 | 12.4812 | 12.4812 | 12.4812 | 0.74747 | 12.5853 | 12.5853 | 12.5853 | 0.59083 | 12.6646 | 12.6646 | 12.6646 | 0.40636 | 12.7464 | 12.7464 | 12.7464 | 0.21621 | 13.0208 | 13.0208 | 13.0208 | -0.50896 | 13.2986 | 13.2986 | 13.2986 | -1.3405 | 13.4984 | 13.4984 | 13.4984 | -1.9302 | 13.6749 | 13.6749 | 13.6749 | -2.4985 | 13.7427 | 13.7427 | 13.7427 | -2.8387 | 12.1396 | 12.1396 | 12.1396 | 2.2034 | 12.1494 | 12.1494 | 12.1494 | 1.1988 | 12.2087 | 12.2087 | 12.2087 | 0.94084 | 12.286 | 12.286 | 12.286 | 0.58506 | 12.3698 | 12.3698 | 12.3698 | 0.11918 | 12.463 | 12.463 | 12.463 | -0.23887 | 12.5763 | 12.5763 | 12.5763 | -0.7062 | 12.7279 | 12.7279 | 12.7279 | -1.5335 | 12.8496 | 12.8496 | 12.8496 | -2.3217 | 12.9693 | 12.9693 | 12.9693 | -3.08 | 13.3277 | 13.3277 | 13.3277 | -5.193 | 13.6524 | 13.6524 | 13.6524 | -6.904 | 13.873 | 13.873 | 13.873 | -7.9642 | 14.0191 | 14.0191 | 14.0191 | -8.3345 | 14.0188 | 14.0188 | 14.0188 | -7.7946
NEWTON LE WILLOWS | GOLBORNE | BOLD | 357891 | 395944 | 26.2883 | 12.769 | 9.1773 | 13.6982 | 26.3742 | 12.4114 | 8.9203 | 12.9087 | 26.4776 | 11.8716 | 8.5324 | 12.5161 | 26.6176 | 11.378 | 8.1776 | 12.2164 | 26.8201 | 10.8679 | 7.811 | 11.7769 | 27.0615 | 10.3521 | 7.4403 | 11.3116 | 27.3279 | 9.9547 | 7.1547 | 10.8609 | 27.6492 | 9.8246 | 7.0611 | 10.4222 | 27.9708 | 9.6806 | 6.9576 | 9.8608 | 28.3111 | 9.542 | 6.858 | 9.2654 | 29.6046 | 8.9554 | 6.4364 | 6.4287 | 30.9889 | 8.3022 | 5.9669 | 2.2616 | 31.6739 | 8.0584 | 5.7917 | -1.0118 | 32.223 | 8.2824 | 5.9527 | -4.295 | 32.6151 | 7.9903 | 5.7428 | -7.4641 | 26.2624 | 12.769 | 9.1773 | 13.6982 | 26.3435 | 12.5493 | 9.0194 | 13.4278 | 26.4117 | 12.2983 | 8.8391 | 13.22 | 26.4956 | 12.0504 | 8.6608 | 13.0144 | 26.6141 | 11.7894 | 8.4732 | 12.7481 | 26.7588 | 11.5328 | 8.2889 | 12.4579 | 26.9447 | 11.3164 | 8.1334 | 12.0615 | 27.1824 | 11.1613 | 8.0218 | 11.4829 | 27.3521 | 11.0293 | 7.927 | 10.9641 | 27.5388 | 10.8862 | 7.8241 | 10.4299 | 28.2004 | 10.4569 | 7.5156 | 8.5988 | 28.9968 | 10.0282 | 7.2074 | 6.6363 | 29.8039 | 9.8513 | 7.0803 | 4.7553 | 30.6884 | 10.0393 | 7.2154 | 2.7234 | 31.2953 | 10.0453 | 7.2198 | 1.426 | 26.2938 | 12.769 | 9.1773 | 13.6982 | 26.3842 | 12.3739 | 8.8934 | 12.8396 | 26.4945 | 11.8077 | 8.4864 | 12.4586 | 26.6429 | 11.2922 | 8.1159 | 12.2095 | 26.853 | 10.7574 | 7.7316 | 11.8269 | 27.0807 | 10.2407 | 7.3602 | 11.4315 | 27.3432 | 9.842 | 7.0736 | 11.0819 | 27.6544 | 9.7109 | 6.9794 | 10.7575 | 27.9539 | 9.565 | 6.8746 | 10.3376 | 28.2728 | 9.423 | 6.7725 | 9.8585 | 29.5834 | 8.7937 | 6.3202 | 7.2998 | 31.0442 | 8.071 | 5.8008 | 3.2716 | 31.8103 | 7.7504 | 5.5704 | 0.098689 | 32.4138 | 7.9031 | 5.6801 | -2.9693 | 32.8079 | 7.5974 | 5.4604 | -5.8622 | 26.2938 | 12.769 | 9.1773 | 13.6982 | 26.2812 | 12.6064 | 9.0605 | 13.3447 | 26.3368 | 12.2798 | 8.8258 | 13.1048 | 26.4324 | 11.925 | 8.5708 | 12.9075 | 26.6006 | 11.5445 | 8.2972 | 12.5403 | 26.8415 | 11.1562 | 8.0182 | 12.1224 | 27.1592 | 10.7373 | 7.7171 | 11.5297 | 27.6487 | 10.4927 | 7.5413 | 10.2881 | 28.1431 | 10.2214 | 7.3463 | 8.9668 | 28.6474 | 9.9789 | 7.172 | 7.6337 | 29.8253 | 9.9765 | 7.1703 | 3.7328 | 30.8832 | 9.0492 | 6.5038 | -0.074243 | 31.5501 | 8.2986 | 5.9644 | -3.025 | 32.0037 | 8.0512 | 5.7865 | -4.9957 | 32.1305 | 7.8654 | 5.653 | -4.4691 | 26.2883 | 12.769 | 9.1773 | 13.6982 | 26.361 | 12.5114 | 8.9922 | 13.3767 | 26.438 | 11.9881 | 8.6161 | 13.1215 | 26.5306 | 11.5125 | 8.2743 | 12.9226 | 26.6637 | 11.0418 | 7.936 | 12.6833 | 26.8541 | 10.5579 | 7.5882 | 12.399 | 27.0748 | 10.1821 | 7.3181 | 12.0824 | 27.3375 | 10.0674 | 7.2357 | 11.7316 | 27.6149 | 9.9344 | 7.1401 | 11.2415 | 27.9179 | 9.7996 | 7.0431 | 10.6618 | 28.9652 | 9.3713 | 6.7354 | 8.728 | 30.0379 | 9.0815 | 6.5271 | 6.6335 | 30.7887 | 9.1741 | 6.5936 | 5.2138 | 31.4006 | 9.81 | 7.0507 | 3.9957 | 31.7546 | 9.9808 | 7.1734 | 3.2788 | 26.2883 | 12.769 | 9.1773 | 13.6982 | 26.3001 | 12.5334 | 9.008 | 12.9992 | 26.3919 | 12.1798 | 8.7538 | 12.6039 | 26.5288 | 11.8028 | 8.4829 | 12.2953 | 26.7278 | 11.4025 | 8.1952 | 11.8295 | 26.9538 | 11.006 | 7.9102 | 11.3518 | 27.2449 | 10.5736 | 7.5995 | 10.6899 | 27.7259 | 10.3119 | 7.4114 | 9.3518 | 28.2044 | 10.0281 | 7.2074 | 7.969 | 28.6884 | 9.776 | 7.0262 | 6.5734 | 29.9015 | 9.7121 | 6.9803 | 2.4235 | 31.0184 | 8.7251 | 6.2709 | -1.6688 | 31.7717 | 7.9187 | 5.6913 | -4.9075 | 32.2633 | 7.6151 | 5.4731 | -7.1883 | 32.4101 | 7.376 | 5.3012 | -6.9806
NEWTONGATE T11 & T12 | PENRITH & SHAP | HARKER / HUTTON | 349973 | 530340 | 31.6926 | 7.8401 | 5.6348 | 8.9378 | 31.8821 | 7.2911 | 5.2403 | 6.6564 | 32.1649 | 6.8672 | 4.9356 | 6.0724 | 32.3672 | 6.5182 | 4.6848 | 5.7891 | 32.6715 | 6.1571 | 4.4252 | 5.4108 | 33.115 | 5.7227 | 4.113 | 4.9428 | 32.2253 | 5.3056 | 3.8133 | 4.3945 | 31.0023 | 5.1043 | 3.6686 | 3.7152 | 29.3726 | 4.836 | 3.4757 | 2.8447 | 27.1053 | 4.4627 | 3.2074 | 1.3758 | 14.623 | 2.4076 | 1.7304 | -8.4459 | 7.0081 | 1.1538 | 0.82928 | -13.6984 | 2.6844 | 0.44197 | 0.31765 | -20.5953 | 2.6844 | 0.44197 | 0.31765 | -23.3599 | 2.6844 | 0.44197 | 0.31765 | -24.8294 | 31.6702 | 7.8401 | 5.6348 | 8.9378 | 31.8104 | 7.6147 | 5.4729 | 8.1807 | 31.999 | 7.5212 | 5.4057 | 7.8862 | 32.2376 | 7.3947 | 5.3147 | 7.6439 | 32.4764 | 7.196 | 5.1719 | 7.3883 | 32.7112 | 6.9864 | 5.0212 | 7.1141 | 33.0163 | 6.6842 | 4.8041 | 6.7675 | 33.4067 | 6.443 | 4.6307 | 6.3249 | 33.7768 | 6.2076 | 4.4615 | 5.8194 | 34.2196 | 5.9418 | 4.2705 | 5.2712 | 32.1668 | 5.296 | 3.8064 | 2.9473 | 28.226 | 4.6472 | 3.34 | -0.48777 | 22.2837 | 3.6688 | 2.6369 | -4.1042 | 13.6437 | 2.2463 | 1.6145 | -11.6495 | 4.816 | 0.79291 | 0.56988 | -17.5465 | 31.7038 | 7.8401 | 5.6348 | 8.9378 | 31.8904 | 7.1312 | 5.1254 | 6.3182 | 32.161 | 6.6149 | 4.7542 | 5.6811 | 32.3479 | 6.1922 | 4.4505 | 5.4102 | 32.6187 | 5.6998 | 4.0965 | 5.059 | 31.8369 | 5.2417 | 3.7673 | 4.6372 | 29.1759 | 4.8036 | 3.4524 | 4.1605 | 27.2592 | 4.488 | 3.2256 | 3.5848 | 25.2898 | 4.1638 | 2.9926 | 2.8924 | 23.17 | 3.8148 | 2.7417 | 2.0664 | 5.6394 | 0.92849 | 0.66733 | -10.8905 | 2.6844 | 0.44197 | 0.31765 | -20.118 | 2.6844 | 0.44197 | 0.31765 | -23.887 | 2.6844 | 0.44197 | 0.31765 | -26.7443 | 2.6844 | 0.44197 | 0.31765 | -27.6799 | 31.7039 | 7.8401 | 5.6348 | 8.9378 | 31.7898 | 7.2718 | 5.2264 | 7.1903 | 32.0055 | 6.9496 | 4.9948 | 6.7466 | 32.2275 | 6.4292 | 4.6208 | 6.4792 | 32.5019 | 6.0053 | 4.3161 | 6.1347 | 32.8469 | 5.408 | 3.8868 | 5.6701 | 28.8351 | 4.7475 | 3.4121 | 4.9879 | 24.1964 | 3.9837 | 2.8632 | 2.9131 | 8.6843 | 1.4298 | 1.0276 | -10.3265 | 5.0963 | 0.83907 | 0.60306 | -11.8098 | 2.6844 | 0.44197 | 0.31765 | -17.1257 | 2.6844 | 0.44197 | 0.31765 | -21.9273 | 2.6844 | 0.44197 | 0.31765 | -24.8935 | 2.6844 | 0.44197 | 0.31765 | -26.5984 | 2.6844 | 0.44197 | 0.31765 | -25.4161 | 31.6925 | 7.8401 | 5.6348 | 8.9378 | 31.8463 | 7.4911 | 5.384 | 7.696 | 32.0753 | 7.1096 | 5.1098 | 7.3303 | 32.2743 | 6.7738 | 4.8685 | 7.123 | 32.4954 | 6.4472 | 4.6337 | 6.8948 | 32.8339 | 6.0437 | 4.3437 | 6.5908 | 33.3164 | 5.6536 | 4.0634 | 6.1866 | 33.3224 | 5.4863 | 3.9431 | 5.6673 | 31.8721 | 5.2475 | 3.7715 | 4.9476 | 30.0679 | 4.9505 | 3.558 | 3.935 | 18.6587 | 3.072 | 2.2079 | -4.9732 | 12.2223 | 2.0123 | 1.4463 | -9.2179 | 3.5076 | 0.5775 | 0.41506 | -15.3577 | 2.6844 | 0.44197 | 0.31765 | -17.2328 | 2.6844 | 0.44197 | 0.31765 | -17.3528 | 31.6925 | 7.8401 | 5.6348 | 8.9378 | 31.8198 | 7.075 | 5.0849 | 6.1231 | 32.0946 | 6.6979 | 4.8139 | 5.426 | 32.2873 | 6.1575 | 4.4255 | 5.0765 | 32.5565 | 5.7244 | 4.1143 | 4.6733 | 31.1642 | 5.1309 | 3.6877 | 4.2149 | 27.1593 | 4.4716 | 3.2138 | 3.5736 | 22.5767 | 3.7171 | 2.6715 | 1.5261 | 7.0902 | 1.1674 | 0.839 | -11.6337 | 4.1488 | 0.68307 | 0.49093 | -12.4959 | 2.6844 | 0.44197 | 0.31765 | -17.7413 | 2.6844 | 0.44197 | 0.31765 | -23.1476 | 2.6844 | 0.44197 | 0.31765 | -26.7826 | 2.6844 | 0.44197 | 0.31765 | -28.9222 | 2.6844 | 0.44197 | 0.31765 | -27.9152
NEWTONGATE T13 | PENRITH & SHAP | HARKER / HUTTON | 349973 | 530340 | 16.8444 | 16.8444 | 16.8444 | 10.803 | 16.9252 | 16.9252 | 16.9252 | 8.5385 | 17.0058 | 17.0058 | 17.0058 | 7.8125 | 17.1051 | 17.1051 | 17.1051 | 7.4658 | 17.2374 | 17.2374 | 16.2358 | 7.0601 | 17.4017 | 17.4017 | 15.2542 | 6.8551 | 17.6065 | 17.6065 | 14.2549 | 6.6424 | 17.8686 | 17.8686 | 14.1744 | 6.4063 | 18.156 | 18.156 | 14.0943 | 6.142 | 18.4736 | 18.4736 | 14.0538 | 5.873 | 19.2535 | 19.2535 | 13.8763 | 4.5761 | 19.8619 | 19.5193 | 14.0289 | 2.7502 | 20.2404 | 20.2404 | 14.9454 | 1.3722 | 20.5032 | 20.5032 | 16.0056 | 0.037384 | 20.6434 | 20.6434 | 16.0559 | -1.1182 | 16.841 | 16.841 | 16.841 | 10.803 | 16.9294 | 16.9294 | 16.9294 | 10.3839 | 17.0239 | 17.0239 | 17.0239 | 10.1007 | 17.1338 | 17.1338 | 17.1338 | 9.8722 | 17.229 | 17.229 | 17.0448 | 9.6222 | 17.3428 | 17.3428 | 16.2065 | 9.4206 | 17.4845 | 17.4845 | 15.3069 | 9.171 | 17.6525 | 17.6525 | 15.2343 | 8.8519 | 17.774 | 17.774 | 15.1904 | 8.7109 | 17.917 | 17.917 | 15.1223 | 8.5666 | 18.4976 | 18.4976 | 14.965 | 7.9623 | 19.2095 | 19.2095 | 14.7749 | 7.1538 | 19.7557 | 19.7557 | 15.3098 | 6.3736 | 20.2985 | 20.2985 | 16.1793 | 5.5479 | 20.5609 | 20.5609 | 16.2372 | 5.047 | 16.8456 | 16.8456 | 16.8456 | 10.803 | 16.9167 | 16.9167 | 16.9167 | 8.1809 | 16.9912 | 16.9912 | 16.9912 | 7.41 | 17.0812 | 17.0812 | 17.0812 | 7.0864 | 17.1987 | 17.1987 | 16.0452 | 6.7004 | 17.348 | 17.348 | 15.0204 | 6.5209 | 17.5218 | 17.5218 | 13.989 | 6.3493 | 17.7424 | 17.7424 | 13.881 | 6.159 | 17.9764 | 17.9764 | 13.7678 | 5.964 | 18.2467 | 18.2467 | 13.7007 | 5.7509 | 19.057 | 18.6491 | 13.4035 | 4.5566 | 19.7488 | 18.6879 | 13.4314 | 2.7307 | 20.1932 | 19.7201 | 14.1732 | 1.344 | 20.4817 | 20.4817 | 15.0743 | 0.05157 | 20.5942 | 20.5942 | 15.0289 | -0.99682 | 16.8457 | 16.8457 | 16.8457 | 10.803 | 16.8791 | 16.8791 | 16.8791 | 9.0367 | 16.9313 | 16.9313 | 16.9313 | 8.4328 | 17.0016 | 17.0016 | 17.0016 | 8.1173 | 17.1066 | 17.1066 | 17.1066 | 7.7335 | 17.2521 | 17.2521 | 17.2521 | 7.5473 | 17.4451 | 17.4451 | 17.4451 | 7.2754 | 17.7028 | 17.7028 | 17.7028 | 6.7051 | 17.9959 | 17.9959 | 17.5452 | 6.1005 | 18.3204 | 18.3204 | 17.3683 | 5.4788 | 19.1961 | 19.1961 | 16.8667 | 3.6548 | 19.7638 | 19.7638 | 16.398 | 1.9752 | 20.1074 | 20.1074 | 15.9415 | 0.76581 | 20.2884 | 20.2884 | 15.4531 | 0.048062 | 20.2635 | 20.2635 | 15.1304 | 0.41407 | 16.8443 | 16.8443 | 16.8443 | 10.803 | 16.9105 | 16.9105 | 16.9105 | 10.1205 | 16.9743 | 16.9743 | 16.9743 | 9.6798 | 17.0471 | 17.0471 | 17.0471 | 9.3634 | 17.144 | 17.144 | 16.4711 | 9.0287 | 17.2798 | 17.2798 | 15.5049 | 8.9034 | 17.4467 | 17.4467 | 14.5152 | 8.7615 | 17.6481 | 17.6481 | 14.4417 | 8.5781 | 17.8674 | 17.8674 | 14.3658 | 8.341 | 18.1197 | 18.1197 | 14.3285 | 8.0881 | 18.924 | 18.924 | 14.203 | 7.2049 | 19.537 | 19.537 | 14.4784 | 6.2921 | 19.9089 | 19.9089 | 15.4837 | 5.7161 | 20.1436 | 20.1436 | 16.6582 | 5.2844 | 20.2091 | 20.2091 | 16.8324 | 5.1361 | 16.8443 | 16.8443 | 16.8443 | 10.803 | 16.8851 | 16.8851 | 16.8851 | 7.9275 | 16.9524 | 16.9524 | 16.9524 | 7.1025 | 17.0368 | 17.0368 | 17.0368 | 6.761 | 17.149 | 17.149 | 17.149 | 6.3484 | 17.293 | 17.293 | 17.293 | 6.1458 | 17.4657 | 17.4657 | 17.4657 | 5.8578 | 17.694 | 17.694 | 17.5372 | 5.2714 | 17.938 | 17.938 | 17.3675 | 4.6788 | 18.2195 | 18.2195 | 17.192 | 4.0647 | 19.1263 | 19.1263 | 16.6809 | 2.1883 | 19.817 | 19.817 | 16.1924 | 0.38376 | 20.2493 | 20.2493 | 15.715 | -0.96261 | 20.4887 | 20.4887 | 15.2111 | -1.8107 | 20.4873 | 20.4873 | 14.8764 | -1.5543
NORBRECK | BISPHAM | PENWORTHAM WEST / STANAH | 331831 | 441463 | 27.8705 | 12.1036 | 8.8294 | 23.2687 | 27.9434 | 12.0404 | 8.7833 | 23.237 | 28.0278 | 11.988 | 8.745 | 23.1631 | 28.0788 | 11.9294 | 8.7023 | 23.1025 | 28.1375 | 11.8739 | 8.6619 | 23.0433 | 28.2022 | 11.7954 | 8.6046 | 22.9919 | 28.2744 | 11.7221 | 8.5511 | 22.9546 | 28.3465 | 11.6575 | 8.504 | 22.9203 | 28.3952 | 11.6077 | 8.4676 | 22.8414 | 28.4408 | 11.5628 | 8.4349 | 22.7715 | 28.6325 | 11.3882 | 8.3075 | 22.1635 | 28.8141 | 11.1272 | 8.1171 | 21.0185 | 28.95 | 11.2293 | 8.1916 | 20.0372 | 29.0741 | 11.6691 | 8.5124 | 18.9321 | 29.162 | 11.5298 | 8.4108 | 17.985 | 27.8708 | 12.1036 | 8.8294 | 23.2687 | 27.9193 | 12.0753 | 8.8088 | 23.2429 | 27.9675 | 12.0498 | 8.7901 | 23.1896 | 28.0067 | 12.0233 | 8.7708 | 23.1435 | 28.033 | 11.9902 | 8.7467 | 23.0915 | 28.0657 | 11.9544 | 8.7206 | 23.0355 | 28.1036 | 11.8386 | 8.6361 | 22.9666 | 28.1455 | 11.7946 | 8.604 | 22.885 | 28.183 | 11.7551 | 8.5752 | 22.7736 | 28.2219 | 11.7168 | 8.5472 | 22.661 | 28.3384 | 11.607 | 8.4672 | 22.3346 | 28.4455 | 11.5307 | 8.4115 | 22.0404 | 28.5444 | 11.5874 | 8.4529 | 21.7417 | 28.6244 | 11.9325 | 8.7046 | 21.4181 | 28.6791 | 12.1689 | 8.8771 | 21.1787 | 27.8707 | 12.1036 | 8.8294 | 23.2687 | 27.9442 | 12.0307 | 8.7762 | 23.2478 | 28.0393 | 11.9676 | 8.7302 | 23.1857 | 28.0982 | 11.9206 | 8.6959 | 23.1461 | 28.1665 | 11.8477 | 8.6427 | 23.1079 | 28.2427 | 11.7716 | 8.5872 | 23.0804 | 28.3119 | 11.693 | 8.5299 | 23.0736 | 28.3726 | 11.6237 | 8.4793 | 23.0755 | 28.4247 | 11.5857 | 8.4516 | 23.0454 | 28.4726 | 11.5513 | 8.4265 | 23.013 | 28.6948 | 11.2846 | 8.232 | 22.3983 | 28.911 | 11.1762 | 8.1529 | 21.2535 | 29.057 | 11.1907 | 8.1635 | 20.3415 | 29.1877 | 11.6365 | 8.4887 | 19.419 | 29.277 | 11.4928 | 8.3839 | 18.6899 | 27.8707 | 12.1036 | 8.8294 | 23.2687 | 27.9028 | 12.0574 | 8.7957 | 23.2889 | 27.9603 | 11.9967 | 8.7515 | 23.2466 | 28.0349 | 11.9534 | 8.7198 | 23.1999 | 28.08 | 11.8984 | 8.6797 | 23.1454 | 28.1475 | 11.8471 | 8.6423 | 23.0852 | 28.2309 | 11.7733 | 8.5884 | 22.9682 | 28.3277 | 11.7069 | 8.54 | 22.6402 | 28.3918 | 11.642 | 8.4927 | 22.2826 | 28.453 | 11.5814 | 8.4484 | 21.9216 | 28.637 | 12.3921 | 9.0399 | 20.8796 | 28.8295 | 12.1141 | 8.837 | 19.8861 | 28.9713 | 11.8458 | 8.6413 | 19.0779 | 29.0856 | 11.7025 | 8.5368 | 18.5465 | 29.1127 | 11.6877 | 8.526 | 18.9489 | 27.8705 | 12.1036 | 8.8294 | 23.2687 | 27.9302 | 12.0632 | 8.8 | 23.248 | 28.0025 | 12.0189 | 8.7676 | 23.1954 | 28.0423 | 11.9668 | 8.7296 | 23.1648 | 28.0809 | 11.921 | 8.6962 | 23.1437 | 28.1393 | 11.847 | 8.6422 | 23.1123 | 28.2132 | 11.7784 | 8.5922 | 23.0835 | 28.2874 | 11.7157 | 8.5464 | 23.0615 | 28.3316 | 11.6669 | 8.5109 | 22.9909 | 28.3753 | 11.6195 | 8.4763 | 22.9225 | 28.5186 | 11.5182 | 8.4024 | 22.6743 | 28.6781 | 11.4177 | 8.329 | 22.2837 | 28.7958 | 11.6775 | 8.5186 | 21.9912 | 28.9086 | 12.3338 | 8.9974 | 21.6381 | 28.9723 | 12.3659 | 9.0207 | 21.3886 | 27.8705 | 12.1036 | 8.8294 | 23.2687 | 27.9371 | 12.0352 | 8.7795 | 23.2647 | 28.0232 | 11.9664 | 8.7293 | 23.1871 | 28.0761 | 11.9121 | 8.6897 | 23.1004 | 28.1366 | 11.8505 | 8.6448 | 23.0106 | 28.2029 | 11.7944 | 8.6039 | 22.9293 | 28.2799 | 11.7166 | 8.5471 | 22.7889 | 28.3791 | 11.6436 | 8.4938 | 22.4218 | 28.4495 | 11.5734 | 8.4426 | 22.0304 | 28.5157 | 11.5114 | 8.3974 | 21.6371 | 28.7034 | 12.284 | 8.961 | 20.5066 | 28.8783 | 11.9914 | 8.7476 | 19.4396 | 29.0061 | 11.7237 | 8.5523 | 18.566 | 29.1029 | 11.5459 | 8.4226 | 17.9607 | 29.1268 | 11.5176 | 8.4019 | 18.2823
NORBURY | HAZEL GROVE | BREDBURY | 392447 | 385492 | 25.0369 | 4.1221 | 2.9627 | 17.3854 | 24.1838 | 3.9817 | 2.8617 | 17.0455 | 3.4612 | 0.56986 | 0.40957 | 3.4612 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 25.0369 | 4.1221 | 2.9627 | 17.3854 | 24.5727 | 4.0457 | 2.9077 | 17.2187 | 4.4513 | 0.73288 | 0.52673 | 4.4513 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 25.0369 | 4.1221 | 2.9627 | 17.3854 | 24.0447 | 3.9588 | 2.8453 | 17.0322 | 3.1739 | 0.52256 | 0.37558 | 3.1739 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.5207 | 25.0369 | 4.1221 | 2.9627 | 17.3854 | 24.5259 | 4.038 | 2.9022 | 17.2834 | 23.3797 | 3.8493 | 2.7666 | 17.1778 | 20.5405 | 3.3818 | 2.4306 | 16.9919 | 13.8833 | 2.2858 | 1.6428 | 12.6546 | 13.1938 | 2.1723 | 1.5612 | 12.7443 | 12.5645 | 2.0686 | 1.4868 | 12.5645 | 10.9363 | 1.8006 | 1.2941 | 10.9363 | 9.1957 | 1.514 | 1.0881 | 9.1957 | 7.1962 | 1.1848 | 0.85154 | 7.1962 | 2.6346 | 0.43376 | 0.31175 | 2.6346 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 25.0369 | 4.1221 | 2.9627 | 17.3854 | 24.4878 | 4.0317 | 2.8977 | 17.1706 | 3.9416 | 0.64895 | 0.46641 | 3.9416 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0.59546 | 0.098038 | 0.070461 | 0.59546 | 25.0369 | 4.1221 | 2.9627 | 17.3854 | 24.1385 | 3.9742 | 2.8563 | 17.0991 | 22.7986 | 3.7536 | 2.6978 | 16.8765 | 19.9009 | 3.2765 | 2.3549 | 16.587 | 12.9778 | 2.1367 | 1.5357 | 12.1591 | 12.2029 | 2.0091 | 1.444 | 12.1942 | 11.427 | 1.8814 | 1.3522 | 11.427 | 9.6578 | 1.5901 | 1.1428 | 9.6578 | 7.8072 | 1.2854 | 0.92384 | 7.8072 | 5.7015 | 0.93871 | 0.67467 | 5.7015 | 0.82514 | 0.13585 | 0.09764 | 0.82514 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844
NORTHENDEN | WEST DIDSBURY | SOUTH MANCHESTER | 382555 | 390327 | 20.8794 | 12.4514 | 9.0831 | 12.0201 | 21.1261 | 12.2751 | 8.9545 | 11.2785 | 21.336 | 12.1834 | 8.8876 | 10.9272 | 21.6038 | 12.0658 | 8.8018 | 10.5868 | 21.8953 | 11.9242 | 8.6985 | 10.1628 | 22.1621 | 11.8275 | 8.628 | 9.694 | 22.3763 | 11.6639 | 8.5087 | 9.1944 | 22.5871 | 11.4572 | 8.3579 | 8.6615 | 22.8022 | 11.2987 | 8.2422 | 8.069 | 23.0239 | 11.0363 | 8.0508 | 7.056 | 23.6158 | 10.2963 | 7.511 | 3.6855 | 24.0887 | 9.6143 | 7.0135 | 0.43478 | 24.4086 | 9.111 | 6.6463 | -1.8038 | 24.6562 | 8.6762 | 6.3291 | -3.4753 | 24.7626 | 8.556 | 6.2415 | -4.3375 | 20.867 | 12.4514 | 9.0831 | 12.0201 | 20.9893 | 12.375 | 9.0274 | 11.7355 | 21.0714 | 12.2495 | 8.9359 | 11.5534 | 21.1787 | 12.1238 | 8.8441 | 11.3752 | 21.3192 | 11.9227 | 8.6975 | 11.1427 | 21.4689 | 11.8888 | 8.6727 | 10.847 | 21.6539 | 11.6875 | 8.5258 | 10.4897 | 21.8811 | 11.615 | 8.473 | 10.0718 | 22.0921 | 11.5271 | 8.4088 | 9.6793 | 22.3274 | 11.4534 | 8.3551 | 9.2521 | 23.0751 | 11.1333 | 8.1216 | 7.6619 | 23.5227 | 10.6582 | 7.775 | 4.9993 | 23.9089 | 10.0858 | 7.3574 | 2.6185 | 24.2059 | 9.8511 | 7.1863 | 0.45708 | 24.3789 | 9.5662 | 6.9784 | -0.77614 | 20.8841 | 12.4514 | 9.0831 | 12.0201 | 21.1576 | 12.2417 | 8.9302 | 11.1837 | 21.4109 | 12.1127 | 8.836 | 10.7882 | 21.6913 | 11.9627 | 8.7266 | 10.43 | 21.9245 | 11.7605 | 8.5791 | 9.9926 | 22.1923 | 11.7319 | 8.5582 | 9.5212 | 22.3703 | 11.5272 | 8.4089 | 9.0406 | 22.5714 | 11.3386 | 8.2713 | 8.5292 | 22.77 | 11.1529 | 8.1359 | 7.9696 | 22.9826 | 10.9308 | 7.9739 | 7.3662 | 23.7043 | 10.1543 | 7.4074 | 4.0504 | 24.2167 | 9.3723 | 6.837 | 0.42993 | 24.557 | 8.782 | 6.4064 | -2.1519 | 24.7421 | 8.3075 | 6.0602 | -4.3947 | 24.7693 | 8.0304 | 5.8581 | -5.4964 | 20.8843 | 12.4514 | 9.0831 | 12.0201 | 21.1161 | 12.3133 | 8.9824 | 11.516 | 21.3586 | 12.1711 | 8.8786 | 11.1868 | 21.6419 | 12.1266 | 8.8462 | 10.8533 | 21.8847 | 11.8884 | 8.6724 | 10.4087 | 22.0921 | 11.8884 | 8.6724 | 9.8774 | 22.2779 | 11.6887 | 8.5268 | 9.2409 | 22.5115 | 11.4705 | 8.3676 | 8.3439 | 22.7531 | 11.2324 | 8.1938 | 7.4042 | 23.0025 | 10.9579 | 7.9936 | 6.4212 | 23.6257 | 10.0151 | 7.3058 | 2.7166 | 24.0714 | 9.3511 | 6.8215 | -0.34161 | 24.3065 | 8.8302 | 6.4415 | -2.2904 | 24.4416 | 8.5826 | 6.2609 | -3.5896 | 24.3853 | 8.3876 | 6.1186 | -3.9069 | 20.8791 | 12.4514 | 9.0831 | 12.0201 | 21.0799 | 12.3365 | 8.9993 | 11.5808 | 21.2438 | 12.2682 | 8.9495 | 11.3515 | 21.4331 | 12.1766 | 8.8827 | 11.1461 | 21.6641 | 12.0603 | 8.7979 | 10.898 | 21.864 | 11.9986 | 8.7528 | 10.5885 | 22.0863 | 11.8762 | 8.6636 | 10.2286 | 22.3477 | 11.6951 | 8.5314 | 9.8321 | 22.5202 | 11.5464 | 8.4229 | 9.3518 | 22.7039 | 11.3644 | 8.2901 | 8.8375 | 23.3372 | 10.7517 | 7.8432 | 6.144 | 23.8111 | 10.163 | 7.4138 | 3.3123 | 24.1031 | 9.7104 | 7.0836 | 1.2677 | 24.3343 | 9.2901 | 6.777 | -0.373 | 24.4232 | 9.2376 | 6.7387 | -1.1271 | 20.8791 | 12.4514 | 9.0831 | 12.0201 | 21.0917 | 12.2651 | 8.9472 | 11.2441 | 21.3356 | 12.0896 | 8.8192 | 10.8171 | 21.6282 | 12.0402 | 8.7832 | 10.4184 | 21.8673 | 11.8054 | 8.6118 | 9.9309 | 22.1298 | 11.7854 | 8.5973 | 9.4116 | 22.2944 | 11.5868 | 8.4524 | 8.7996 | 22.5158 | 11.3632 | 8.2893 | 7.9017 | 22.7362 | 11.1256 | 8.116 | 6.9739 | 22.9704 | 10.8542 | 7.918 | 6.0185 | 23.7365 | 10.0281 | 7.3154 | 2.8411 | 24.2178 | 9.225 | 6.7295 | -0.63981 | 24.5258 | 8.6766 | 6.3295 | -3.0334 | 24.6739 | 8.362 | 6.0999 | -4.5982 | 24.6342 | 8.1706 | 5.9603 | -4.8742
NWGB PARTINGTON | CARRINGTON BSP | CARRINGTON | 372569 | 392079 | 22.1333 | 11.2763 | 8.2259 | 16.4373 | 22.164 | 11.2383 | 8.1982 | 16.3948 | 22.194 | 11.2114 | 8.1786 | 16.351 | 22.2389 | 11.1542 | 8.1368 | 16.3056 | 22.3145 | 11.0925 | 8.0918 | 16.1752 | 22.396 | 10.9966 | 8.0218 | 15.9786 | 23.6364 | 10.6818 | 7.7922 | 14.54 | 23.7469 | 10.6293 | 7.754 | 14.3161 | 23.8809 | 10.5963 | 7.7299 | 14.0493 | 24.0304 | 10.5287 | 7.6805 | 13.6754 | 27.5332 | 9.7221 | 7.0921 | 8.9525 | 29.4056 | 9.2566 | 6.7526 | 5.6266 | 30.3987 | 9.2649 | 6.7586 | 3.5232 | 30.2424 | 9.6643 | 7.05 | 2.7278 | 30.177 | 9.6313 | 7.0259 | 1.8741 | 22.1294 | 11.2763 | 8.2259 | 16.4373 | 22.1563 | 11.2739 | 8.2241 | 16.3869 | 22.1786 | 11.2626 | 8.2159 | 16.3316 | 22.2061 | 11.2302 | 8.1922 | 16.2813 | 22.2438 | 11.1928 | 8.165 | 16.222 | 22.292 | 11.1625 | 8.1429 | 16.1498 | 22.3558 | 11.043 | 8.0557 | 16.0511 | 22.4321 | 11.0043 | 8.0275 | 15.924 | 22.5035 | 10.958 | 7.9937 | 15.7608 | 22.5877 | 10.9051 | 7.9551 | 15.5724 | 22.8898 | 10.7298 | 7.8273 | 14.8929 | 23.258 | 10.5304 | 7.6818 | 13.881 | 23.6406 | 10.5755 | 7.7147 | 12.8253 | 28.6713 | 9.9387 | 7.2501 | 6.7818 | 42.8637 | 7.2509 | 5.2894 | -8.852 | 22.1344 | 11.2763 | 8.2259 | 16.4373 | 22.1621 | 11.246 | 8.2038 | 16.3944 | 22.1901 | 11.1812 | 8.1565 | 16.3515 | 22.2309 | 11.1062 | 8.1018 | 16.3079 | 22.299 | 10.9879 | 8.0155 | 15.8422 | 22.3727 | 10.8078 | 7.8841 | 15.3341 | 23.581 | 10.4942 | 7.6553 | 13.6007 | 23.685 | 10.4098 | 7.5938 | 13.0652 | 23.7927 | 10.3046 | 7.517 | 12.5026 | 23.9178 | 10.1922 | 7.4351 | 11.9174 | 27.2799 | 9.2431 | 6.7427 | 6.5629 | 34.7988 | 7.5646 | 5.5182 | -3.7531 | 34.7705 | 7.5489 | 5.5068 | -5.877 | 34.6246 | 7.6474 | 5.5787 | -8.2854 | 34.5452 | 7.5788 | 5.5287 | -9.2843 | 22.1344 | 11.2763 | 8.2259 | 16.4373 | 22.1342 | 11.2733 | 8.2237 | 16.4836 | 25.2401 | 10.6811 | 7.7917 | 13.1615 | 25.083 | 10.6262 | 7.7516 | 13.3388 | 24.9551 | 10.4998 | 7.6595 | 13.0737 | 24.857 | 10.439 | 7.6151 | 12.6851 | 25.9292 | 10.1309 | 7.3903 | 11.0025 | 25.9052 | 10.0436 | 7.3267 | 10.2813 | 26.0032 | 9.9166 | 7.234 | 9.4039 | 33.2056 | 8.5644 | 6.2476 | 0.91477 | 34.3901 | 9.1226 | 6.6548 | -2.6519 | 34.0403 | 8.6551 | 6.3138 | -4.5271 | 33.9289 | 8.1894 | 5.974 | -6.5248 | 33.7863 | 7.7315 | 5.64 | -8.4586 | 33.6334 | 7.7032 | 5.6194 | -8.1271 | 22.1333 | 11.2763 | 8.2259 | 16.4373 | 22.1577 | 11.2533 | 8.2091 | 16.4015 | 22.1793 | 11.235 | 8.1958 | 16.3681 | 22.2069 | 11.1799 | 8.1556 | 16.3482 | 22.2513 | 11.1368 | 8.1241 | 16.3186 | 22.3196 | 11.0653 | 8.072 | 16.2693 | 23.5407 | 10.768 | 7.8551 | 14.9431 | 23.64 | 10.7349 | 7.831 | 14.7935 | 23.744 | 10.7045 | 7.8088 | 14.5825 | 23.8646 | 10.66 | 7.7763 | 14.3478 | 27.2927 | 9.9367 | 7.2487 | 10.0469 | 29.1139 | 9.6132 | 7.0127 | 7.4161 | 30.0803 | 9.7273 | 7.0959 | 5.8199 | 29.9228 | 10.2429 | 7.4721 | 5.5453 | 29.7962 | 10.3594 | 7.5571 | 5.4497 | 22.1333 | 11.2763 | 8.2259 | 16.4373 | 22.135 | 11.259 | 8.2133 | 16.4694 | 25.2453 | 10.6628 | 7.7784 | 13.1287 | 25.0911 | 10.6074 | 7.738 | 13.2862 | 24.9693 | 10.4638 | 7.6332 | 12.9996 | 24.8619 | 10.4076 | 7.5922 | 12.6096 | 25.9167 | 10.1013 | 7.3688 | 10.928 | 25.8856 | 10.0121 | 7.3037 | 10.2095 | 25.9621 | 9.8864 | 7.212 | 9.3469 | 33.1445 | 8.5356 | 6.2266 | 0.86822 | 34.3219 | 9.0802 | 6.6239 | -2.7525 | 34.0337 | 8.5863 | 6.2636 | -4.7727 | 34.0162 | 8.0921 | 5.9031 | -6.9238 | 33.8987 | 7.607 | 5.5492 | -8.9925 | 33.7537 | 7.5643 | 5.5181 | -8.7604
OFFERTON | VERNON PARK | BREDBURY | 391010 | 389489 | 28.594 | 12.8376 | 9.3648 | 19.854 | 28.6572 | 12.3439 | 9.0047 | 18.1656 | 28.707 | 12.2995 | 8.9723 | 17.4357 | 28.7712 | 12.1011 | 8.8276 | 16.8427 | 28.852 | 11.8667 | 8.6566 | 16.223 | 28.9458 | 11.4812 | 8.3754 | 15.602 | 29.0561 | 11.0809 | 8.0834 | 14.9897 | 29.1915 | 10.7979 | 7.8769 | 14.3879 | 29.3031 | 10.7722 | 7.8582 | 13.7449 | 29.414 | 10.5947 | 7.7287 | 13.1139 | 29.7814 | 10.1662 | 7.4161 | 11.9007 | 30.1481 | 9.6183 | 7.0164 | 9.625 | 30.4104 | 9.1475 | 6.673 | 7.7199 | 30.647 | 8.6673 | 6.3227 | 5.6722 | 30.8214 | 8.2437 | 6.0136 | 3.8933 | 28.5757 | 12.8376 | 9.3648 | 19.854 | 28.6186 | 12.593 | 9.1864 | 18.6174 | 28.6565 | 12.483 | 9.1062 | 17.988 | 28.7082 | 12.2817 | 8.9593 | 17.3974 | 28.7816 | 12.0271 | 8.7736 | 16.7913 | 28.8667 | 11.84 | 8.6371 | 16.1803 | 28.9657 | 11.5068 | 8.3941 | 15.5374 | 29.0671 | 11.3299 | 8.265 | 14.8556 | 29.1311 | 11.1717 | 8.1496 | 14.1734 | 29.1992 | 11.0114 | 8.0327 | 13.4886 | 29.4204 | 10.8096 | 7.8854 | 12.9593 | 29.6357 | 10.6312 | 7.7553 | 12.2856 | 29.8391 | 10.4354 | 7.6125 | 11.6165 | 30.0498 | 10.1436 | 7.3996 | 10.8748 | 30.1986 | 9.8852 | 7.2111 | 10.3452 | 28.6013 | 12.8376 | 9.3648 | 19.854 | 28.664 | 12.4008 | 9.0462 | 18.0681 | 28.7189 | 12.2439 | 8.9318 | 17.3297 | 28.7907 | 11.9855 | 8.7432 | 16.7538 | 28.8802 | 11.7445 | 8.5674 | 16.1574 | 28.9837 | 11.2364 | 8.1968 | 15.5652 | 29.1054 | 10.9525 | 7.9897 | 14.9101 | 29.2539 | 10.7815 | 7.865 | 14.3527 | 29.3719 | 10.629 | 7.7537 | 13.7601 | 29.4879 | 10.4121 | 7.5955 | 13.181 | 29.8494 | 9.981 | 7.281 | 12.2702 | 30.2348 | 9.4089 | 6.8636 | 10.1408 | 30.5204 | 8.9152 | 6.5035 | 8.362 | 30.7701 | 8.4178 | 6.1406 | 6.4669 | 30.9442 | 7.9684 | 5.8129 | 4.863 | 28.6013 | 12.8376 | 9.3648 | 19.854 | 28.6192 | 12.4888 | 9.1104 | 18.3946 | 28.6417 | 12.3634 | 9.0189 | 17.738 | 28.6775 | 12.1221 | 8.8429 | 17.1727 | 28.7348 | 11.8553 | 8.6483 | 16.5719 | 28.8232 | 11.5149 | 8.4 | 15.9589 | 28.9402 | 11.2605 | 8.2144 | 15.1759 | 29.0896 | 10.9461 | 7.985 | 14.1621 | 29.2217 | 10.6471 | 7.7669 | 12.9566 | 29.3546 | 10.2711 | 7.4926 | 11.7406 | 29.7627 | 9.7671 | 7.125 | 9.6319 | 30.1536 | 9.1931 | 6.7063 | 7.6068 | 30.4125 | 8.703 | 6.3487 | 5.9781 | 30.6073 | 8.3525 | 6.093 | 4.9016 | 30.6421 | 8.2647 | 6.029 | 5.5524 | 28.594 | 12.8376 | 9.3648 | 19.854 | 28.6489 | 12.4726 | 9.0986 | 18.4735 | 28.6862 | 12.3986 | 9.0446 | 17.8273 | 28.7258 | 12.2067 | 8.9046 | 17.2735 | 28.7799 | 11.9908 | 8.7471 | 16.7186 | 28.8616 | 11.6222 | 8.4782 | 16.1538 | 28.9688 | 11.1888 | 8.1621 | 15.5835 | 29.0888 | 10.9491 | 7.9872 | 15.0085 | 29.1847 | 10.9214 | 7.967 | 14.3687 | 29.2835 | 10.7502 | 7.8421 | 13.7274 | 29.6087 | 10.4682 | 7.6364 | 13.265 | 29.9261 | 10.2187 | 7.4544 | 12.557 | 30.1371 | 10.0074 | 7.3002 | 12.0646 | 30.316 | 9.834 | 7.1738 | 11.5808 | 30.4139 | 9.7041 | 7.079 | 11.2989 | 28.594 | 12.8376 | 9.3648 | 19.854 | 28.6303 | 12.4274 | 9.0656 | 18.0574 | 28.6786 | 12.2695 | 8.9504 | 17.2932 | 28.7428 | 12.0094 | 8.7607 | 16.6759 | 28.8241 | 11.7302 | 8.557 | 16.0281 | 28.9165 | 11.3912 | 8.3097 | 15.3833 | 29.0304 | 11.1278 | 8.1176 | 14.5674 | 29.1906 | 10.7876 | 7.8694 | 13.4406 | 29.3265 | 10.4736 | 7.6403 | 12.1722 | 29.4616 | 10.1118 | 7.3765 | 10.9047 | 29.8723 | 9.5554 | 6.9705 | 8.637 | 30.2567 | 8.9525 | 6.5308 | 6.4632 | 30.5196 | 8.4345 | 6.1528 | 4.686 | 30.7101 | 8.0458 | 5.8693 | 3.4279 | 30.7515 | 7.9179 | 5.776 | 3.8748
OPENSHAW | DROYLSDEN | STALYBRIDGE | 388606 | 397346 | 25.3567 | 11.8222 | 8.6241 | 6.8635 | 25.4525 | 11.5033 | 8.3915 | 6.2644 | 25.5872 | 11.2482 | 8.2054 | 5.8867 | 25.746 | 11.0074 | 8.0298 | 5.5686 | 25.9434 | 10.722 | 7.8215 | 5.155 | 26.1876 | 10.4758 | 7.642 | 4.707 | 26.4912 | 10.3075 | 7.5192 | 4.2647 | 26.8733 | 10.1526 | 7.4061 | 3.8297 | 27.1892 | 9.9821 | 7.2818 | 3.349 | 27.4947 | 9.8232 | 7.1659 | 2.8287 | 28.4712 | 9.1814 | 6.6977 | 0.23739 | 29.344 | 8.4504 | 6.1644 | -3.2122 | 29.902 | 7.8602 | 5.7339 | -5.717 | 30.3015 | 7.7605 | 5.6612 | -8.0442 | 30.5181 | 7.2828 | 5.3127 | -9.7256 | 25.3365 | 11.8222 | 8.6241 | 6.8635 | 25.4138 | 11.6145 | 8.4726 | 6.6166 | 25.509 | 11.3932 | 8.3112 | 6.3477 | 25.615 | 11.1301 | 8.1193 | 5.8991 | 25.7494 | 10.9267 | 7.9709 | 5.6343 | 25.9207 | 10.6977 | 7.8038 | 5.3045 | 26.1263 | 10.4551 | 7.6269 | 4.9018 | 26.3514 | 10.3153 | 7.5249 | 4.4196 | 26.5209 | 10.2116 | 7.4492 | 4.1484 | 26.7105 | 10.108 | 7.3736 | 3.8725 | 27.3875 | 9.7947 | 7.1451 | 2.9955 | 28.1772 | 9.4427 | 6.8883 | 1.4808 | 28.9476 | 9.0669 | 6.6142 | 0.063321 | 29.6241 | 9.0289 | 6.5864 | -1.4144 | 30.0526 | 9.0337 | 6.59 | -2.3751 | 25.3631 | 11.8222 | 8.6241 | 6.8635 | 25.4793 | 11.4534 | 8.3551 | 6.1268 | 25.6404 | 11.1599 | 8.141 | 5.6062 | 25.831 | 10.8643 | 7.9253 | 5.1907 | 26.0622 | 10.5693 | 7.7102 | 4.6739 | 26.3408 | 10.2729 | 7.4939 | 4.1205 | 26.6789 | 10.0679 | 7.3444 | 3.5863 | 27.0513 | 9.869 | 7.1993 | 3.0465 | 27.3366 | 9.6797 | 7.0612 | 2.4791 | 27.6415 | 9.4852 | 6.9193 | 1.8441 | 28.6475 | 8.6931 | 6.3415 | -1.1402 | 29.6269 | 7.8017 | 5.6913 | -4.7327 | 30.2688 | 7.2992 | 5.3247 | -7.1578 | 30.6959 | 7.0859 | 5.1691 | -9.0511 | 30.8394 | 6.9103 | 5.041 | -10.0114 | 25.3631 | 11.8222 | 8.6241 | 6.8635 | 25.3766 | 11.551 | 8.4263 | 6.5476 | 25.4723 | 11.3236 | 8.2604 | 6.2087 | 25.5917 | 11.0472 | 8.0588 | 5.8257 | 25.7602 | 10.7633 | 7.8517 | 5.317 | 26.0093 | 10.4456 | 7.6199 | 4.7534 | 26.3368 | 10.2055 | 7.4448 | 4.026 | 26.7412 | 9.8058 | 7.1532 | 2.7501 | 27.0971 | 9.5587 | 6.9729 | 1.4679 | 27.4344 | 9.2871 | 6.7748 | 0.2075 | 28.4854 | 8.7002 | 6.3467 | -3.327 | 29.3925 | 8.0679 | 5.8854 | -6.3652 | 29.9536 | 7.5662 | 5.5195 | -8.1568 | 30.2453 | 7.3196 | 5.3396 | -8.9079 | 30.2355 | 7.1667 | 5.228 | -8.6085 | 25.3566 | 11.8222 | 8.6241 | 6.8635 | 25.4406 | 11.5881 | 8.4534 | 6.6074 | 25.5454 | 11.356 | 8.2841 | 6.3446 | 25.6551 | 11.1273 | 8.1172 | 6.0847 | 25.7946 | 10.8749 | 7.9331 | 5.8512 | 26.0017 | 10.665 | 7.7799 | 5.5639 | 26.2786 | 10.5134 | 7.6694 | 5.2345 | 26.6051 | 10.3773 | 7.5701 | 4.8446 | 26.9098 | 10.2011 | 7.4416 | 4.351 | 27.2014 | 10.0438 | 7.3268 | 3.836 | 28.0912 | 9.5333 | 6.9544 | 1.9203 | 28.9301 | 9.0893 | 6.6305 | -0.046257 | 29.4684 | 8.7576 | 6.3885 | -1.4171 | 29.8614 | 8.8206 | 6.4345 | -2.614 | 30.025 | 8.6913 | 6.3402 | -3.3079 | 25.3566 | 11.8222 | 8.6241 | 6.8635 | 25.3995 | 11.4747 | 8.3706 | 6.2482 | 25.5394 | 11.2309 | 8.1928 | 5.7925 | 25.71 | 10.9275 | 7.9715 | 5.3226 | 25.9199 | 10.6323 | 7.7561 | 4.7345 | 26.1699 | 10.3048 | 7.5172 | 4.1175 | 26.4783 | 10.0511 | 7.3321 | 3.325 | 26.8826 | 9.6755 | 7.0581 | 1.9674 | 27.2032 | 9.3712 | 6.8361 | 0.63993 | 27.5191 | 9.09 | 6.631 | -0.66878 | 28.5619 | 8.5192 | 6.2146 | -4.4016 | 29.5283 | 7.7636 | 5.6635 | -7.6724 | 30.1652 | 7.2229 | 5.269 | -9.7211 | 30.499 | 6.9288 | 5.0545 | -10.7363 | 30.5201 | 6.7479 | 4.9225 | -10.571
ORMSKIRK | SKELMERSDALE | WASHWAY FARM / KIRKBY | 341294 | 408158 | 29.5528 | 14.5436 | 10.4528 | 13.8695 | 29.6522 | 14.2349 | 10.2309 | 12.94 | 29.8088 | 13.8962 | 9.9874 | 12.2707 | 29.9996 | 13.8754 | 9.9725 | 11.9022 | 30.1617 | 13.916 | 10.0017 | 11.6328 | 30.3462 | 13.7413 | 9.8761 | 11.3585 | 30.5442 | 13.5352 | 9.728 | 11.1071 | 30.7841 | 13.3413 | 9.5887 | 10.8559 | 30.9664 | 13.139 | 9.4433 | 10.5601 | 31.1458 | 13.0046 | 9.3467 | 10.2849 | 31.6943 | 12.4335 | 8.9362 | 8.8268 | 32.2161 | 11.8703 | 8.5314 | 6.6289 | 32.5748 | 11.5237 | 8.2823 | 4.9986 | 32.865 | 11.3451 | 8.154 | 3.462 | 33.0427 | 10.8965 | 7.8316 | 2.4034 | 29.5145 | 14.5436 | 10.4528 | 13.8695 | 29.5917 | 14.4263 | 10.3684 | 13.3953 | 29.6861 | 14.3933 | 10.3448 | 13.1434 | 29.8074 | 14.3301 | 10.2993 | 12.9444 | 29.9704 | 14.1419 | 10.1641 | 12.7035 | 30.1745 | 13.9468 | 10.0238 | 12.4437 | 30.4154 | 13.8887 | 9.9821 | 12.1129 | 30.6362 | 13.6743 | 9.828 | 11.6735 | 30.7409 | 13.4626 | 9.6758 | 11.3849 | 30.8514 | 13.1734 | 9.468 | 11.0948 | 31.2008 | 12.9822 | 9.3306 | 10.2528 | 31.5581 | 12.6844 | 9.1165 | 9.4082 | 31.889 | 12.5028 | 8.986 | 8.6197 | 32.2263 | 12.4392 | 8.9403 | 7.7639 | 32.4622 | 12.1895 | 8.7609 | 7.177 | 29.5688 | 14.5436 | 10.4528 | 13.8695 | 29.6902 | 14.0976 | 10.1322 | 12.7678 | 29.8779 | 13.838 | 9.9457 | 12.0187 | 30.0901 | 13.6512 | 9.8114 | 11.5987 | 30.2854 | 13.492 | 9.6969 | 11.2698 | 30.4935 | 13.237 | 9.5137 | 10.9337 | 30.7326 | 12.9385 | 9.2991 | 10.6314 | 31.0202 | 12.6671 | 9.1041 | 10.3215 | 31.2327 | 12.436 | 8.938 | 9.9961 | 31.4415 | 12.2025 | 8.7702 | 9.6616 | 32.1023 | 11.3147 | 8.1321 | 8.0627 | 32.7394 | 10.4474 | 7.5087 | 5.9819 | 33.1831 | 9.8345 | 7.0682 | 4.638 | 33.5424 | 9.4211 | 6.7711 | 3.6102 | 33.7456 | 8.8537 | 6.3633 | 3.3224 | 29.5688 | 14.5436 | 10.4528 | 13.8695 | 29.585 | 14.0856 | 10.1236 | 13.2606 | 29.6795 | 14.1147 | 10.1445 | 12.6386 | 29.8073 | 14.6146 | 10.5038 | 12.2582 | 29.9751 | 14.3654 | 10.3247 | 11.9574 | 30.1365 | 14.1371 | 10.1606 | 11.6324 | 30.3366 | 13.8105 | 9.9259 | 11.2206 | 30.5678 | 13.5271 | 9.7222 | 10.4602 | 30.7655 | 13.1754 | 9.4694 | 9.6813 | 30.9634 | 12.8136 | 9.2094 | 8.9189 | 31.5767 | 11.7747 | 8.4627 | 6.8232 | 32.1712 | 10.8834 | 7.8221 | 5.0836 | 32.5749 | 10.1615 | 7.3033 | 4.0962 | 32.9001 | 9.5653 | 6.8748 | 3.7877 | 33.0606 | 8.86 | 6.3679 | 4.5043 | 29.5528 | 14.5436 | 10.4528 | 13.8695 | 29.6368 | 14.2573 | 10.247 | 13.096 | 29.7475 | 13.9305 | 10.0121 | 12.4804 | 29.8727 | 13.9452 | 10.0227 | 12.1641 | 30.0316 | 14.008 | 10.0678 | 11.9875 | 30.1979 | 13.8503 | 9.9545 | 11.7944 | 30.4089 | 13.657 | 9.8156 | 11.5919 | 30.63 | 13.4658 | 9.6781 | 11.3659 | 30.7891 | 13.2579 | 9.5287 | 11.0651 | 30.9506 | 13.1194 | 9.4291 | 10.7683 | 31.4685 | 12.6386 | 9.0836 | 9.8035 | 31.9936 | 12.2897 | 8.8329 | 8.7807 | 32.3716 | 12.1182 | 8.7096 | 8.11 | 32.6943 | 12.1199 | 8.7108 | 7.4705 | 32.8761 | 11.8145 | 8.4913 | 7.1274 | 29.5528 | 14.5436 | 10.4528 | 13.8695 | 29.6141 | 14.0424 | 10.0926 | 12.8376 | 29.7737 | 13.9935 | 10.0574 | 12.0693 | 29.9785 | 14.4782 | 10.4057 | 11.595 | 30.1756 | 14.2135 | 10.2155 | 11.2065 | 30.3619 | 13.9745 | 10.0438 | 10.8176 | 30.575 | 13.6413 | 9.8043 | 10.3301 | 30.8437 | 13.3358 | 9.5847 | 9.4715 | 31.0473 | 12.9684 | 9.3207 | 8.64 | 31.2483 | 12.6019 | 9.0572 | 7.8252 | 31.859 | 11.5482 | 8.2999 | 5.569 | 32.4234 | 10.6118 | 7.6269 | 3.7046 | 32.8103 | 9.8454 | 7.0761 | 2.6035 | 33.1046 | 9.2327 | 6.6357 | 2.1741 | 33.2655 | 8.5032 | 6.1114 | 2.7527
PADIHAM | PADIHAM | PADIHAM | 378428 | 433238 | 16.0311 | 2.6394 | 1.897 | 16.0311 | 12.6943 | 2.09 | 1.5021 | 12.6943 | 9.073 | 1.4938 | 1.0736 | 9.073 | 6.3918 | 1.0524 | 0.75636 | 6.3918 | 5.2194 | 0.85933 | 0.61762 | 5.2194 | 2.7877 | 0.45897 | 0.32987 | 2.7877 | 0.76133 | 0.12535 | 0.090089 | 0.76133 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 16.0311 | 2.6394 | 1.897 | 16.0311 | 14.7377 | 2.4264 | 1.7439 | 14.7377 | 13.7857 | 2.2697 | 1.6313 | 13.7857 | 12.8944 | 2.123 | 1.5258 | 12.8944 | 11.5995 | 1.9098 | 1.3726 | 11.5995 | 10.5382 | 1.735 | 1.247 | 10.5382 | 7.7043 | 1.2684 | 0.91166 | 7.7043 | 6.7715 | 1.1149 | 0.80129 | 6.7715 | 5.7642 | 0.94903 | 0.68209 | 5.7642 | 4.8964 | 0.80615 | 0.5794 | 4.8964 | 1.8607 | 0.30636 | 0.22019 | 1.8607 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0.76851 | 0.12653 | 0.09094 | 0.76851 | 1.3989 | 0.23032 | 0.16554 | 1.3989 | 16.0311 | 2.6394 | 1.897 | 16.0311 | 11.9563 | 1.9685 | 1.4148 | 11.9563 | 7.6715 | 1.2631 | 0.90778 | 7.6715 | 5.1911 | 0.85468 | 0.61427 | 5.1911 | 3.7327 | 0.61455 | 0.44169 | 3.7327 | 0.636 | 0.10471 | 0.075259 | 0.636 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 16.0311 | 2.6394 | 1.897 | 16.0311 | 13.1767 | 2.1694 | 1.5592 | 13.1767 | 10.6933 | 1.7606 | 1.2654 | 10.6933 | 7.1287 | 1.1737 | 0.84355 | 7.1287 | 5.8876 | 0.96935 | 0.69669 | 5.8876 | 4.7445 | 0.78115 | 0.56143 | 4.7445 | 1.9615 | 0.32294 | 0.23211 | 1.9615 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 16.0311 | 2.6394 | 1.897 | 16.0311 | 13.6682 | 2.2504 | 1.6174 | 13.6682 | 10.3473 | 1.7036 | 1.2244 | 10.3473 | 7.5285 | 1.2395 | 0.89086 | 7.5285 | 6.622 | 1.0903 | 0.78359 | 6.622 | 4.3272 | 0.71244 | 0.51205 | 4.3272 | 2.3774 | 0.39142 | 0.28132 | 2.3774 | 0.86681 | 0.14271 | 0.10257 | 0.86681 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 16.0311 | 2.6394 | 1.897 | 16.0311 | 11.6641 | 1.9204 | 1.3802 | 11.6641 | 8.7899 | 1.4472 | 1.0401 | 8.7899 | 5.2091 | 0.85764 | 0.6164 | 5.2091 | 3.9158 | 0.64471 | 0.46336 | 3.9158 | 2.7137 | 0.44679 | 0.32112 | 2.7137 | 0.0015473 | 0.00025476 | 0.0001831 | 0.0015473 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844
PEEL ST | PADIHAM | PADIHAM | 374463 | 441514 | 19.7449 | 19.7449 | 19.7449 | 11.432 | 19.8326 | 19.8326 | 19.8326 | 11.0554 | 19.9692 | 19.9692 | 19.9692 | 10.8379 | 20.1469 | 20.1469 | 20.1469 | 10.593 | 20.3657 | 20.3657 | 20.3657 | 10.2987 | 20.6273 | 20.6273 | 20.6273 | 9.9979 | 23.7965 | 23.7965 | 20.6654 | 6.8093 | 24.0237 | 24.0237 | 20.4132 | 6.527 | 24.2624 | 24.2624 | 20.3514 | 6.0706 | 24.5131 | 24.5131 | 20.2339 | 5.5834 | 26.8755 | 26.8755 | 19.8042 | 2.1808 | 27.6717 | 27.1297 | 19.4987 | -0.12447 | 36.02 | 25.2521 | 18.1492 | -9.6655 | 36.402 | 24.8056 | 17.8283 | -11.2392 | 36.6491 | 24.3444 | 17.4968 | -12.4524 | 19.7185 | 19.7185 | 19.7185 | 11.432 | 19.7844 | 19.7844 | 19.7844 | 11.1533 | 19.8617 | 19.8617 | 19.8617 | 11.0034 | 19.9617 | 19.9617 | 19.9617 | 10.7947 | 20.095 | 20.095 | 20.095 | 10.5303 | 20.262 | 20.262 | 20.262 | 10.2331 | 20.4653 | 20.4653 | 20.4653 | 9.8329 | 20.6566 | 20.6566 | 20.6566 | 9.3594 | 20.8143 | 20.8143 | 20.8143 | 8.9968 | 20.9876 | 20.9876 | 20.9876 | 8.6259 | 23.1065 | 23.1065 | 20.8829 | 5.8309 | 23.7367 | 23.7367 | 20.6635 | 4.4721 | 24.3421 | 24.3421 | 20.4267 | 3.2043 | 24.9249 | 24.9249 | 20.0995 | 1.9455 | 25.3155 | 25.3155 | 19.7533 | 1.2241 | 19.756 | 19.756 | 19.756 | 11.432 | 19.8525 | 19.8525 | 19.8525 | 11.0475 | 20.0028 | 20.0028 | 20.0028 | 10.8504 | 20.1994 | 20.1994 | 20.1994 | 10.6453 | 20.4403 | 20.4403 | 20.4403 | 10.3981 | 20.7013 | 20.7013 | 20.7013 | 10.1553 | 20.9627 | 20.9627 | 20.8151 | 9.9081 | 21.2133 | 21.2133 | 20.6598 | 9.6809 | 21.4502 | 21.4502 | 20.5727 | 9.2547 | 21.6998 | 21.6998 | 20.5338 | 8.826 | 30.4526 | 26.6801 | 19.1755 | -1.4035 | 32.696 | 25.6457 | 18.4321 | -5.5485 | 33.2583 | 25.1474 | 18.0739 | -7.5287 | 33.6654 | 24.4961 | 17.6058 | -9.2196 | 33.892 | 23.9732 | 17.23 | -10.4041 | 19.756 | 19.756 | 19.756 | 11.432 | 19.7831 | 19.7831 | 19.7831 | 11.2632 | 19.8653 | 19.8653 | 19.8653 | 11.1556 | 20.0147 | 20.0147 | 20.0147 | 10.9741 | 20.1815 | 20.1815 | 20.1815 | 10.7609 | 20.4387 | 20.4387 | 20.4387 | 10.5147 | 22.294 | 22.294 | 20.9352 | 8.6378 | 22.5773 | 22.5773 | 20.5097 | 8.0119 | 22.8491 | 22.8491 | 20.4571 | 7.3201 | 32.2802 | 26.7633 | 19.2353 | -2.532 | 34.5447 | 25.8454 | 18.5756 | -5.9558 | 35.1716 | 25.2635 | 18.1574 | -7.9832 | 35.6199 | 24.6845 | 17.7413 | -9.7295 | 35.9745 | 24.1141 | 17.3313 | -11.1521 | 36.0451 | 23.7826 | 17.093 | -11.497 | 19.7449 | 19.7449 | 19.7449 | 11.432 | 19.8191 | 19.8191 | 19.8191 | 11.1143 | 19.9167 | 19.9167 | 19.9167 | 10.9481 | 20.0336 | 20.0336 | 20.0336 | 10.7728 | 20.1866 | 20.1866 | 20.1866 | 10.5758 | 20.4163 | 20.4163 | 20.4163 | 10.3419 | 23.5879 | 23.5879 | 20.7269 | 7.1925 | 23.8349 | 23.8349 | 20.4806 | 6.9531 | 24.0327 | 24.0327 | 20.4296 | 6.6385 | 24.2466 | 24.2466 | 20.3243 | 6.2198 | 26.515 | 26.515 | 19.9359 | 3.2246 | 27.2473 | 27.2473 | 19.7498 | 1.7144 | 35.591 | 25.6553 | 18.4389 | -7.4438 | 35.9558 | 25.3225 | 18.1998 | -8.6394 | 36.1152 | 24.9646 | 17.9425 | -9.2975 | 19.7449 | 19.7449 | 19.7449 | 11.432 | 19.8046 | 19.8046 | 19.8046 | 11.1249 | 19.9354 | 19.9354 | 19.9354 | 10.9143 | 20.1415 | 20.1415 | 20.1415 | 10.6315 | 20.3512 | 20.3512 | 20.3512 | 10.3282 | 20.5979 | 20.5979 | 20.5979 | 10.0254 | 22.4161 | 22.4161 | 20.8628 | 8.0867 | 22.6875 | 22.6875 | 20.428 | 7.3683 | 22.9486 | 22.9486 | 20.3621 | 6.6176 | 32.3676 | 26.6113 | 19.1261 | -3.2917 | 34.6327 | 25.642 | 18.4294 | -7.0218 | 35.3554 | 25.0172 | 17.9803 | -9.2408 | 35.852 | 24.4457 | 17.5696 | -10.9089 | 36.2222 | 23.9113 | 17.1855 | -12.1311 | 36.3037 | 23.6417 | 16.9917 | -12.1268
PENDLETON | FREDERICK RD | KEARSLEY | 381161 | 398842 | 31.4189 | 9.4377 | 6.8847 | 13.2444 | 31.5047 | 8.9347 | 6.5178 | 10.8976 | 31.6249 | 8.6841 | 6.3349 | 10.1782 | 31.7471 | 8.4212 | 6.1431 | 9.6819 | 31.8824 | 8.2913 | 6.0484 | 8.9951 | 32.0431 | 8.037 | 5.8629 | 8.1437 | 32.2377 | 7.7986 | 5.689 | 7.1704 | 32.4751 | 7.5704 | 5.5225 | 6.2007 | 32.715 | 7.3296 | 5.3469 | 5.1611 | 32.9694 | 7.1995 | 5.2519 | 4.7603 | 33.7606 | 6.7623 | 4.933 | 3.267 | 34.4505 | 6.321 | 4.6111 | 1.4784 | 34.9029 | 5.9675 | 4.3532 | 0.16478 | 34.1032 | 5.5319 | 4.0354 | -1.0924 | 32.0499 | 5.1988 | 3.7925 | -2.1269 | 31.4107 | 9.4377 | 6.8847 | 13.2444 | 31.5101 | 9.2375 | 6.7386 | 12.3114 | 31.6377 | 9.1095 | 6.6453 | 12.1117 | 31.7664 | 9.0083 | 6.5714 | 11.8609 | 31.9082 | 8.8991 | 6.4918 | 11.6301 | 32.0744 | 8.7748 | 6.4011 | 11.3964 | 32.2527 | 8.5295 | 6.2222 | 11.126 | 32.4431 | 8.3972 | 6.1257 | 10.7976 | 32.577 | 8.2696 | 6.0326 | 10.4364 | 32.7224 | 8.148 | 5.9438 | 10.0695 | 33.2227 | 7.8161 | 5.7018 | 8.9723 | 33.7961 | 7.4724 | 5.451 | 7.8602 | 34.3613 | 7.3235 | 5.3424 | 6.8587 | 35.0194 | 7.1182 | 5.1926 | 5.7127 | 35.4852 | 6.8241 | 4.9781 | 4.7562 | 31.4221 | 9.4377 | 6.8847 | 13.2444 | 31.5194 | 8.8384 | 6.4475 | 10.5301 | 31.6527 | 8.4421 | 6.1584 | 9.6905 | 31.7904 | 8.3418 | 6.0852 | 9.1288 | 31.9413 | 8.0927 | 5.9035 | 8.374 | 32.1167 | 7.8416 | 5.7204 | 7.4504 | 32.3251 | 7.5514 | 5.5087 | 6.3977 | 32.6188 | 7.2725 | 5.3052 | 5.2989 | 32.8484 | 6.9988 | 5.1055 | 4.2171 | 33.0934 | 6.8444 | 4.9929 | 3.7703 | 33.9284 | 6.3162 | 4.6076 | 2.0979 | 34.7294 | 5.8127 | 4.2403 | 0.25346 | 33.294 | 5.4006 | 3.9397 | -0.99988 | 30.6443 | 4.9708 | 3.6261 | -2.0488 | 29.0143 | 4.7064 | 3.4333 | -2.7391 | 31.4221 | 9.4377 | 6.8847 | 13.2444 | 31.461 | 9.0095 | 6.5723 | 11.2916 | 31.5553 | 8.6497 | 6.3098 | 10.6321 | 31.7061 | 8.5884 | 6.2651 | 10.0544 | 31.8168 | 8.4193 | 6.1417 | 9.3323 | 31.9682 | 8.1743 | 5.963 | 8.4262 | 32.1612 | 7.8461 | 5.7236 | 7.332 | 32.3937 | 7.497 | 5.4689 | 6.0696 | 32.6382 | 7.1656 | 5.2272 | 4.7653 | 32.8992 | 6.9515 | 5.071 | 4.1074 | 33.7203 | 6.2949 | 4.592 | 2.2096 | 34.4371 | 5.8547 | 4.2709 | 0.56639 | 33.8595 | 5.4923 | 4.0066 | -0.48117 | 31.93 | 5.1794 | 3.7783 | -1.1864 | 30.6075 | 4.9648 | 3.6218 | -1.3898 | 31.4189 | 9.4377 | 6.8847 | 13.2444 | 31.5003 | 9.131 | 6.6609 | 11.7833 | 31.6069 | 8.9205 | 6.5074 | 11.2601 | 31.7062 | 8.5703 | 6.2519 | 10.8031 | 31.8145 | 8.5423 | 6.2315 | 10.1909 | 31.956 | 8.3146 | 6.0654 | 9.415 | 32.134 | 8.0744 | 5.8901 | 8.5008 | 32.3393 | 7.8607 | 5.7343 | 7.5673 | 32.5431 | 7.6227 | 5.5606 | 6.534 | 32.7631 | 7.4939 | 5.4667 | 6.1255 | 33.4986 | 7.1046 | 5.1827 | 4.8566 | 34.2082 | 6.7762 | 4.9432 | 3.6163 | 34.7061 | 6.5144 | 4.7522 | 2.739 | 35.1387 | 6.0984 | 4.4487 | 1.8444 | 35.3789 | 5.9592 | 4.3472 | 1.1938 | 31.4189 | 9.4377 | 6.8847 | 13.2444 | 31.4795 | 8.8023 | 6.4212 | 10.3305 | 31.6022 | 8.4715 | 6.1798 | 9.4421 | 31.7845 | 8.3184 | 6.0682 | 8.8199 | 31.9217 | 8.1517 | 5.9465 | 8.059 | 32.0806 | 7.8912 | 5.7566 | 7.1344 | 32.2705 | 7.5636 | 5.5175 | 6.0285 | 32.5079 | 7.2076 | 5.2579 | 4.7365 | 32.7334 | 6.8287 | 4.9815 | 3.1193 | 32.975 | 6.5612 | 4.7863 | 2.1502 | 33.7816 | 5.744 | 4.1902 | -0.6897 | 31.6016 | 5.1261 | 3.7394 | -3.2903 | 28.3658 | 4.6012 | 3.3565 | -5.3035 | 25.1221 | 4.075 | 2.9727 | -7.2478 | 22.1242 | 3.5888 | 2.618 | -9.0092
PETTERIL BANK | CARLISLE | HARKER / HUTTON | 341768 | 553686 | 30.2584 | 10.8242 | 7.7795 | 13.4253 | 30.3779 | 10.812 | 7.7708 | 12.7363 | 30.5358 | 10.5849 | 7.6076 | 12.5543 | 30.7639 | 10.3637 | 7.4486 | 12.4551 | 31.0915 | 10.1024 | 7.2608 | 12.2085 | 31.499 | 9.8334 | 7.0674 | 11.9134 | 31.9939 | 9.5944 | 6.8957 | 11.6118 | 32.6055 | 9.4267 | 6.7752 | 11.2277 | 33.181 | 9.2583 | 6.6541 | 10.7448 | 33.7148 | 9.1038 | 6.5431 | 10.2638 | 34.8104 | 8.5015 | 6.1102 | 8.1182 | 35.828 | 7.7612 | 5.5781 | 4.6083 | 36.4856 | 7.2504 | 5.211 | 1.9861 | 36.9487 | 6.7242 | 4.8328 | -0.46329 | 37.1975 | 6.2134 | 4.4657 | -2.9717 | 30.2161 | 10.8242 | 7.7795 | 13.4253 | 30.3023 | 10.9514 | 7.871 | 13.1694 | 30.3659 | 10.7044 | 7.6935 | 13.0607 | 30.4586 | 10.4378 | 7.5019 | 12.9667 | 30.599 | 10.2852 | 7.3922 | 12.8141 | 30.7801 | 10.0911 | 7.2527 | 12.5871 | 31.0119 | 9.7763 | 7.0264 | 12.1929 | 31.2981 | 9.5131 | 6.8373 | 11.6927 | 31.5419 | 9.5023 | 6.8295 | 11.2955 | 31.8157 | 9.3993 | 6.7554 | 10.8787 | 32.8167 | 8.9985 | 6.4674 | 9.5471 | 34.0029 | 8.6122 | 6.1897 | 8.1678 | 35.1489 | 8.2616 | 5.9377 | 6.8572 | 35.9145 | 7.9788 | 5.7345 | 5.5588 | 36.386 | 7.6828 | 5.5218 | 4.8243 | 30.2708 | 10.8242 | 7.7795 | 13.4253 | 30.3986 | 10.7807 | 7.7483 | 12.6607 | 30.5731 | 10.5149 | 7.5572 | 12.4889 | 30.8246 | 10.2585 | 7.373 | 12.4348 | 31.1775 | 9.9572 | 7.1564 | 12.2409 | 31.6097 | 9.6652 | 6.9466 | 12.012 | 32.1275 | 9.3829 | 6.7437 | 11.8091 | 32.7621 | 9.2011 | 6.613 | 11.5015 | 33.3214 | 9.0085 | 6.4746 | 11.1473 | 33.6081 | 8.8489 | 6.3599 | 10.7742 | 34.6748 | 8.1248 | 5.8394 | 8.5363 | 35.7874 | 7.263 | 5.2201 | 4.8772 | 36.5401 | 6.5193 | 4.6855 | 2.0869 | 36.4796 | 6.0061 | 4.3167 | -0.29187 | 32.8297 | 5.4052 | 3.8848 | -2.1424 | 30.2709 | 10.8242 | 7.7795 | 13.4253 | 30.2715 | 10.9235 | 7.851 | 13.2053 | 30.3664 | 10.8309 | 7.7844 | 13.1478 | 30.5403 | 10.6656 | 7.6656 | 13.0827 | 30.8281 | 10.4148 | 7.4854 | 12.8485 | 31.2549 | 10.0361 | 7.2132 | 12.553 | 31.8315 | 9.8208 | 7.0584 | 12.0944 | 32.6208 | 9.3674 | 6.7325 | 11.061 | 33.2494 | 9.1173 | 6.5528 | 9.9531 | 33.6441 | 8.7904 | 6.3178 | 8.8275 | 34.7851 | 7.8883 | 5.6695 | 5.5096 | 35.7654 | 6.9492 | 4.9945 | 2.3786 | 36.3742 | 6.3041 | 4.5309 | -0.025991 | 34.9084 | 5.7474 | 4.1308 | -1.3336 | 33.7847 | 5.5624 | 3.9978 | -0.65413 | 30.2584 | 10.8242 | 7.7795 | 13.4253 | 30.355 | 10.9141 | 7.8442 | 13.0606 | 30.4619 | 10.7026 | 7.6921 | 12.9697 | 30.5993 | 10.4968 | 7.5442 | 12.9613 | 30.8011 | 10.269 | 7.3805 | 12.9095 | 31.1141 | 10.0348 | 7.2122 | 12.807 | 31.5389 | 9.808 | 7.0492 | 12.5856 | 32.0441 | 9.6497 | 6.9354 | 12.2661 | 32.5175 | 9.4944 | 6.8238 | 11.8572 | 33.0297 | 9.3484 | 6.7189 | 11.4297 | 34.3219 | 8.8594 | 6.3675 | 9.9187 | 35.2567 | 8.4398 | 6.0658 | 8.1435 | 35.877 | 8.1531 | 5.8598 | 6.79 | 36.2787 | 7.933 | 5.7016 | 5.8296 | 36.3789 | 7.8078 | 5.6116 | 5.4741 | 30.2584 | 10.8242 | 7.7795 | 13.4253 | 30.2861 | 10.8215 | 7.7777 | 12.8543 | 30.4315 | 10.7058 | 7.6945 | 12.6648 | 30.6662 | 10.5262 | 7.5654 | 12.5093 | 30.9961 | 10.2655 | 7.378 | 12.1949 | 31.3923 | 9.8091 | 7.05 | 11.85 | 31.9018 | 9.6565 | 6.9403 | 11.3324 | 32.6546 | 9.1769 | 6.5956 | 10.2249 | 33.2951 | 8.9317 | 6.4194 | 9.0776 | 33.633 | 8.5976 | 6.1792 | 7.9096 | 34.7638 | 7.6615 | 5.5065 | 4.3801 | 35.8304 | 6.6956 | 4.8123 | 0.97727 | 36.2331 | 5.9655 | 4.2875 | -1.7005 | 32.5672 | 5.3619 | 3.8537 | -3.2802 | 31.4947 | 5.1854 | 3.7268 | -2.5496
PHILLIPS LANE | NELSON | PADIHAM | 387571 | 439522 | 19.2259 | 19.2259 | 19.2259 | 12.3102 | 19.2627 | 19.2627 | 19.2233 | 11.9855 | 19.3134 | 19.3134 | 18.1717 | 11.8585 | 19.3665 | 19.3665 | 17.0187 | 11.7778 | 19.4306 | 19.4306 | 15.7916 | 11.6645 | 19.5053 | 19.5053 | 14.5991 | 11.5418 | 19.5896 | 18.3657 | 13.3975 | 11.4247 | 19.6883 | 18.2525 | 13.315 | 11.3053 | 19.7614 | 18.1705 | 13.2551 | 11.1802 | 19.8302 | 18.1907 | 13.2699 | 11.0641 | 20.0878 | 18.1734 | 13.2573 | 10.2744 | 20.3849 | 18.9071 | 13.7925 | 8.706 | 20.5724 | 20.5724 | 15.3551 | 7.2629 | 20.7296 | 20.7296 | 17.5642 | 5.7424 | 20.8323 | 20.8323 | 17.9758 | 4.4857 | 19.216 | 19.216 | 19.216 | 12.3102 | 19.259 | 19.259 | 19.259 | 12.2213 | 19.3037 | 19.3037 | 18.1676 | 12.1339 | 19.3583 | 19.3583 | 17.0314 | 12.0508 | 19.4287 | 19.4287 | 15.9093 | 11.9512 | 19.5164 | 19.5164 | 14.7718 | 11.8373 | 19.6161 | 18.5368 | 13.5224 | 11.6903 | 19.727 | 18.5024 | 13.4973 | 11.4967 | 19.7767 | 18.4582 | 13.465 | 11.3748 | 19.8293 | 18.4078 | 13.4282 | 11.2527 | 20.0033 | 18.2538 | 13.3159 | 10.8817 | 20.1582 | 18.1006 | 13.2041 | 10.4998 | 20.3006 | 19.3859 | 14.1417 | 10.1438 | 20.4467 | 20.4467 | 15.8448 | 9.7599 | 20.5447 | 20.5447 | 16.4032 | 9.5024 | 19.2292 | 19.2292 | 19.2292 | 12.3102 | 19.2695 | 19.2695 | 19.2356 | 11.9404 | 19.3251 | 19.3251 | 18.1271 | 11.8056 | 19.3759 | 19.3759 | 16.937 | 11.7245 | 19.4442 | 19.4442 | 15.7224 | 11.6115 | 19.5234 | 19.5234 | 14.5036 | 11.4896 | 19.6128 | 18.2596 | 13.3201 | 11.3728 | 19.7106 | 18.118 | 13.2168 | 11.2553 | 19.7768 | 18.0261 | 13.1498 | 11.1466 | 19.8428 | 18.0071 | 13.136 | 11.048 | 20.1025 | 18.0482 | 13.1659 | 10.3071 | 20.4165 | 18.742 | 13.672 | 8.8996 | 20.6489 | 20.6489 | 15.1983 | 7.5225 | 20.8163 | 20.8163 | 17.3876 | 6.0908 | 20.9147 | 20.9147 | 17.7848 | 4.9453 | 19.2292 | 19.2292 | 19.2292 | 12.3102 | 19.2279 | 19.2279 | 19.2279 | 12.1277 | 19.2521 | 19.2521 | 19.2521 | 12.0499 | 19.2869 | 19.2869 | 19.1914 | 11.9959 | 19.3333 | 19.3333 | 19.1147 | 11.9035 | 19.3997 | 19.3997 | 19.0255 | 11.7891 | 19.4961 | 19.4961 | 18.9607 | 11.5917 | 19.5941 | 19.5941 | 18.8117 | 11.1342 | 19.6823 | 19.6823 | 18.6717 | 10.6679 | 19.7724 | 19.7724 | 18.6065 | 10.1441 | 20.0491 | 20.0491 | 18.686 | 8.4865 | 20.3116 | 20.3116 | 18.4045 | 6.9144 | 20.4918 | 20.4918 | 18.1504 | 5.6611 | 20.6165 | 20.6165 | 17.9312 | 4.8727 | 20.624 | 20.624 | 17.9018 | 5.4551 | 19.2259 | 19.2259 | 19.2259 | 12.3102 | 19.2582 | 19.2582 | 19.2582 | 12.2202 | 19.295 | 19.295 | 18.2058 | 12.1489 | 19.3368 | 19.3368 | 17.0681 | 12.0992 | 19.3806 | 19.3806 | 15.8537 | 12.045 | 19.4389 | 19.4389 | 14.6643 | 11.9743 | 19.5123 | 18.4592 | 13.4657 | 11.8862 | 19.5959 | 18.3489 | 13.3853 | 11.7831 | 19.6656 | 18.2672 | 13.3257 | 11.6578 | 19.7378 | 18.282 | 13.3365 | 11.532 | 19.9706 | 18.3161 | 13.3614 | 11.1078 | 20.1889 | 19.2631 | 14.0521 | 10.6381 | 20.341 | 20.341 | 15.7552 | 10.3225 | 20.4638 | 20.4638 | 18.1281 | 10.0432 | 20.512 | 20.512 | 18.6877 | 9.9498 | 19.2259 | 19.2259 | 19.2259 | 12.3102 | 19.2402 | 19.2402 | 19.2402 | 11.9693 | 19.2875 | 19.2875 | 19.2495 | 11.8334 | 19.3402 | 19.3402 | 19.1523 | 11.739 | 19.4064 | 19.4064 | 19.0665 | 11.6099 | 19.4816 | 19.4816 | 18.9717 | 11.4752 | 19.5828 | 19.5828 | 18.9101 | 11.2606 | 19.7064 | 19.7064 | 18.7551 | 10.7696 | 19.7971 | 19.7971 | 18.6165 | 10.2869 | 19.8885 | 19.8885 | 18.5417 | 9.7123 | 20.1704 | 20.1704 | 18.6114 | 7.9901 | 20.4367 | 20.4367 | 18.3136 | 6.344 | 20.6249 | 20.6249 | 18.0489 | 5.0004 | 20.7492 | 20.7492 | 17.8127 | 4.0799 | 20.7582 | 20.7582 | 17.7634 | 4.5002
PICCADILLY | BLOOM ST | SOUTH MANCHESTER | 384427 | 398261 | 30.0678 | 8.5671 | 6.2496 | 17.5555 | 30.0864 | 8.2546 | 6.0216 | 16.6347 | 30.1327 | 8.0919 | 5.9029 | 16.2896 | 30.165 | 7.9698 | 5.8138 | 16.17 | 30.1861 | 7.8455 | 5.7232 | 16.088 | 30.2065 | 7.6932 | 5.6121 | 16.012 | 30.2265 | 7.5759 | 5.5265 | 15.9482 | 30.2478 | 7.4979 | 5.4696 | 15.8848 | 30.2803 | 7.411 | 5.4062 | 15.7545 | 30.3098 | 7.3317 | 5.3484 | 15.6344 | 30.3859 | 7.096 | 5.1764 | 15.1826 | 30.4473 | 6.9494 | 5.0695 | 14.5944 | 30.4816 | 6.8766 | 5.0164 | 14.14 | 30.501 | 7.9642 | 5.8097 | 13.6823 | 30.4905 | 7.9932 | 5.8309 | 13.3151 | 30.067 | 8.5671 | 6.2496 | 17.5555 | 30.0922 | 8.4455 | 6.1609 | 17.2014 | 30.1464 | 8.303 | 6.0569 | 16.9451 | 30.1903 | 8.193 | 5.9767 | 16.7854 | 30.2272 | 8.094 | 5.9045 | 16.6581 | 30.2685 | 7.9863 | 5.8259 | 16.5203 | 30.3145 | 7.78 | 5.6754 | 16.3689 | 30.3677 | 7.7039 | 5.6199 | 16.1954 | 30.4114 | 7.6299 | 5.5659 | 16.0288 | 30.4548 | 7.5541 | 5.5106 | 15.864 | 30.5727 | 7.3458 | 5.3587 | 15.416 | 30.6757 | 7.1558 | 5.2201 | 15.0157 | 30.7579 | 7.0758 | 5.1617 | 14.7024 | 30.8394 | 7.7095 | 5.624 | 14.3784 | 30.9096 | 8.2775 | 6.0383 | 14.0799 | 30.0681 | 8.5671 | 6.2496 | 17.5555 | 30.0893 | 8.2163 | 5.9937 | 16.4899 | 30.1369 | 7.999 | 5.8351 | 16.1139 | 30.1719 | 7.8749 | 5.7446 | 15.9896 | 30.1951 | 7.7276 | 5.6372 | 15.9039 | 30.2177 | 7.5676 | 5.5204 | 15.8242 | 30.2389 | 7.4254 | 5.4167 | 15.7606 | 30.2611 | 7.3141 | 5.3356 | 15.698 | 30.2859 | 7.1443 | 5.2117 | 15.6064 | 30.3064 | 7.1397 | 5.2083 | 15.5271 | 30.3547 | 6.9002 | 5.0336 | 15.2034 | 30.385 | 6.6844 | 4.8762 | 14.7611 | 30.3856 | 6.5653 | 4.7893 | 14.4646 | 30.3535 | 7.7233 | 5.634 | 14.2304 | 30.2786 | 7.7601 | 5.6609 | 14.1535 | 30.0681 | 8.5671 | 6.2496 | 17.5555 | 30.0787 | 8.297 | 6.0525 | 16.7994 | 30.1174 | 8.1623 | 5.9543 | 16.5041 | 30.1429 | 8.0807 | 5.8948 | 16.4007 | 30.1566 | 7.9457 | 5.7963 | 16.3364 | 30.1708 | 7.8162 | 5.7018 | 16.2754 | 30.1831 | 7.7116 | 5.6255 | 16.2025 | 30.1951 | 7.6086 | 5.5504 | 16.0522 | 30.2184 | 7.5085 | 5.4774 | 15.8478 | 30.2377 | 7.4984 | 5.47 | 15.6543 | 30.2774 | 8.3171 | 6.0672 | 15.1424 | 30.2973 | 8.0512 | 5.8733 | 14.7079 | 30.2909 | 7.856 | 5.7308 | 14.4247 | 30.2552 | 7.9909 | 5.8292 | 14.3388 | 30.1767 | 7.8812 | 5.7492 | 14.6669 | 30.0678 | 8.5671 | 6.2496 | 17.5555 | 30.0856 | 8.3584 | 6.0973 | 16.982 | 30.1304 | 8.2152 | 5.9928 | 16.7123 | 30.1608 | 8.0896 | 5.9013 | 16.6029 | 30.1796 | 7.985 | 5.8249 | 16.5401 | 30.1991 | 7.8418 | 5.7205 | 16.4799 | 30.2188 | 7.7217 | 5.6329 | 16.4204 | 30.2389 | 7.6382 | 5.572 | 16.355 | 30.2705 | 7.5517 | 5.5089 | 16.22 | 30.2995 | 7.4718 | 5.4506 | 16.0917 | 30.3747 | 7.2594 | 5.2956 | 15.7388 | 30.4358 | 7.1781 | 5.2363 | 15.4269 | 30.4706 | 7.1455 | 5.2125 | 15.2362 | 30.4919 | 8.3387 | 6.083 | 15.0826 | 30.4876 | 8.4424 | 6.1586 | 15.0957 | 30.0678 | 8.5671 | 6.2496 | 17.5555 | 30.0845 | 8.1854 | 5.9712 | 16.3626 | 30.1315 | 8.0006 | 5.8363 | 15.9589 | 30.1656 | 7.9226 | 5.7794 | 15.8293 | 30.188 | 7.7792 | 5.6748 | 15.7393 | 30.2094 | 7.6514 | 5.5816 | 15.6568 | 30.229 | 7.5436 | 5.5029 | 15.5623 | 30.2503 | 7.4367 | 5.425 | 15.3839 | 30.2747 | 7.3399 | 5.3544 | 15.1744 | 30.2948 | 7.329 | 5.3464 | 14.9766 | 30.3403 | 8.133 | 5.9329 | 14.4567 | 30.3673 | 7.8669 | 5.7388 | 14.0201 | 30.3643 | 7.6663 | 5.5924 | 13.7344 | 30.3279 | 7.7989 | 5.6892 | 13.646 | 30.2515 | 7.683 | 5.6046 | 13.964
PIMBO | SKELMERSDALE | WASHWAY FARM / KIRKBY | 349148 | 404549 | 40.7057 | 6.7019 | 4.8168 | 26.4316 | 39.6176 | 6.5227 | 4.688 | 25.7998 | 35.761 | 5.8878 | 4.2317 | 25.231 | 31.9045 | 5.2528 | 3.7753 | 24.6555 | 28.058 | 4.6195 | 3.3202 | 24.3496 | 24.3486 | 4.0088 | 2.8812 | 24.2064 | 20.584 | 3.389 | 2.4357 | 20.584 | 19.8625 | 3.2702 | 2.3504 | 19.8625 | 18.8978 | 3.1114 | 2.2362 | 18.8978 | 18.136 | 2.9859 | 2.1461 | 18.136 | 14.8783 | 2.4496 | 1.7606 | 14.8783 | 11.4575 | 1.8864 | 1.3558 | 11.4575 | 11.6225 | 1.9136 | 1.3753 | 11.6225 | 19.9881 | 3.2909 | 2.3652 | 15.1916 | 25.571 | 4.2101 | 3.0259 | 14.0598 | 40.7057 | 6.7019 | 4.8168 | 26.4316 | 40.3949 | 6.6507 | 4.78 | 26.3042 | 37.0518 | 6.1003 | 4.3844 | 26.0546 | 33.8235 | 5.5688 | 4.0024 | 25.9447 | 30.5797 | 5.0347 | 3.6185 | 25.8873 | 27.3708 | 4.5064 | 3.2388 | 25.8921 | 23.808 | 3.9198 | 2.8172 | 23.808 | 23.2734 | 3.8318 | 2.754 | 23.2734 | 22.7156 | 3.7399 | 2.688 | 22.7156 | 22.1026 | 3.639 | 2.6154 | 22.1026 | 20.368 | 3.3534 | 2.4102 | 20.368 | 18.5771 | 3.0586 | 2.1983 | 18.5771 | 18.2378 | 3.0027 | 2.1581 | 18.2378 | 24.3148 | 4.0033 | 2.8772 | 20.6709 | 28.8373 | 4.7478 | 3.4124 | 19.7875 | 40.7057 | 6.7019 | 4.8168 | 26.4316 | 39.2782 | 6.4669 | 4.6479 | 25.6488 | 35.0265 | 5.7668 | 4.1447 | 25.0031 | 30.7752 | 5.0669 | 3.6417 | 24.3745 | 26.6169 | 4.3823 | 3.1496 | 24.0089 | 22.5658 | 3.7153 | 2.6702 | 22.5658 | 18.6977 | 3.0784 | 2.2125 | 18.6977 | 17.5868 | 2.8955 | 2.0811 | 17.5868 | 16.328 | 2.6883 | 1.9321 | 16.328 | 15.3074 | 2.5203 | 1.8114 | 15.3074 | 11.1281 | 1.8322 | 1.3168 | 11.1281 | 7.5169 | 1.2376 | 0.88949 | 7.5169 | 6.8063 | 1.1206 | 0.80541 | 6.8063 | 14.8693 | 2.4481 | 1.7595 | 14.8693 | 20.8369 | 3.4306 | 2.4657 | 15.0971 | 40.7057 | 6.7019 | 4.8168 | 26.4316 | 39.6802 | 6.533 | 4.6954 | 25.9521 | 38.507 | 6.3399 | 4.5566 | 25.379 | 44.7431 | 7.3666 | 5.2945 | 24.7646 | 42.6144 | 7.0161 | 5.0426 | 24.4004 | 42.2393 | 6.9544 | 4.9983 | 24.1827 | 40.9632 | 6.7443 | 4.8472 | 23.8799 | 40.0659 | 6.5965 | 4.7411 | 23.3599 | 38.5748 | 6.3511 | 4.5646 | 22.7423 | 36.6163 | 6.0286 | 4.3329 | 21.9058 | 31.5932 | 5.2016 | 3.7385 | 19.1714 | 27.1752 | 4.4742 | 3.2157 | 16.9183 | 23.7467 | 3.9097 | 2.81 | 15.6735 | 21.3354 | 3.5127 | 2.5247 | 15.3766 | 20.0537 | 3.3017 | 2.373 | 16.2302 | 40.7057 | 6.7019 | 4.8168 | 26.4316 | 40.0827 | 6.5993 | 4.7431 | 26.1417 | 36.3446 | 5.9839 | 4.3007 | 25.6592 | 32.5647 | 5.3615 | 3.8534 | 25.1291 | 28.8451 | 4.7491 | 3.4133 | 24.9154 | 25.2518 | 4.1575 | 2.9881 | 24.861 | 21.5765 | 3.5524 | 2.5532 | 21.5765 | 20.9208 | 3.4444 | 2.4756 | 20.9208 | 19.99 | 3.2912 | 2.3654 | 19.99 | 19.255 | 3.1702 | 2.2785 | 19.255 | 16.55 | 2.7248 | 1.9584 | 16.55 | 15.0809 | 2.4829 | 1.7845 | 15.0809 | 16.4421 | 2.7071 | 1.9456 | 16.4421 | 25.6707 | 4.2265 | 3.0377 | 19.914 | 32.5832 | 5.3646 | 3.8556 | 19.4837 | 40.7057 | 6.7019 | 4.8168 | 26.4316 | 39.2747 | 6.4663 | 4.6474 | 25.6507 | 37.9792 | 6.253 | 4.4941 | 24.9948 | 44.1708 | 7.2724 | 5.2268 | 24.3536 | 42.0601 | 6.9249 | 4.977 | 23.9709 | 41.6075 | 6.8504 | 4.9235 | 23.7589 | 40.3339 | 6.6407 | 4.7728 | 23.4742 | 39.4064 | 6.488 | 4.663 | 22.9652 | 37.7754 | 6.2194 | 4.47 | 22.2067 | 35.6802 | 5.8745 | 4.2221 | 21.2455 | 30.4874 | 5.0195 | 3.6076 | 18.3796 | 25.7775 | 4.2441 | 3.0503 | 15.8876 | 22.0204 | 3.6255 | 2.6057 | 14.3642 | 19.3593 | 3.1874 | 2.2908 | 13.8625 | 17.947 | 2.9548 | 2.1237 | 14.6084
MORTON PARK & PIRELLI | CARLISLE | HARKER / HUTTON | 339059 | 553548 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 1.6391 | 0.44197 | 0.31765 | 1.6391 | -1.5484 | -0.5877 | -0.48021 | -1.5484 | -4.0058 | -1.5204 | -1.2423 | -4.0058 | -6.6414 | -2.5208 | -2.0598 | -6.6414 | -9.2958 | -3.5283 | -2.883 | -9.2958 | -12.1731 | -4.6205 | -3.7754 | -12.1731 | -14.2736 | -5.4177 | -4.4268 | -14.2736 | -16.4429 | -6.2411 | -5.0996 | -16.4429 | -18.5669 | -7.0473 | -5.7583 | -18.5669 | -27.0162 | -10.2543 | -8.3788 | -27.0162 | -36.7955 | -13.9662 | -11.4117 | -36.7955 | -46.8209 | -17.1075 | -13.9785 | -46.8209 | -53.3062 | -18.4538 | -15.0785 | -53.3062 | -60.7361 | -19.8422 | -16.213 | -60.7361 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0.51038 | 0.19372 | 0.15829 | 0.51038 | -1.7831 | -0.67679 | -0.553 | -1.7831 | -4.1149 | -1.5618 | -1.2762 | -4.1149 | -6.6053 | -2.5071 | -2.0485 | -6.6053 | -8.628 | -3.2748 | -2.6759 | -8.628 | -10.6697 | -4.0498 | -3.3091 | -10.6697 | -12.7628 | -4.8443 | -3.9582 | -12.7628 | -19.0987 | -7.2491 | -5.9232 | -19.0987 | -25.4259 | -9.6507 | -7.8856 | -25.4259 | -32.7824 | -12.4429 | -10.1671 | -32.7824 | -37.0662 | -14.0689 | -11.4957 | -37.0662 | -38.5216 | -14.6213 | -11.947 | -38.5216 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0.80805 | 0.3067 | 0.25061 | 0.80805 | -2.7584 | -1.047 | -0.85548 | -2.7584 | -5.4555 | -2.0707 | -1.692 | -5.4555 | -8.3401 | -3.1656 | -2.5866 | -8.3401 | -11.1969 | -4.2499 | -3.4726 | -11.1969 | -14.2649 | -5.4144 | -4.4241 | -14.2649 | -18.0041 | -6.8337 | -5.5838 | -18.0041 | -20.3089 | -7.7085 | -6.2986 | -20.3089 | -22.5202 | -8.5478 | -6.9844 | -22.5202 | -33.7746 | -12.8196 | -10.4748 | -33.7746 | -43.7822 | -16.6181 | -13.5786 | -43.7822 | -61.5922 | -19.8731 | -16.2383 | -61.5922 | -68.4743 | -21.3064 | -17.4094 | -68.4743 | -75.2996 | -22.7136 | -18.5592 | -75.2996 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.4734 | 0.44197 | 0.31765 | 2.4734 | -0.19466 | -0.073884 | -0.06037 | -0.19466 | -2.7952 | -1.0609 | -0.86689 | -2.7952 | -8.2197 | -3.1199 | -2.5493 | -8.2197 | -13.37 | -5.0747 | -4.1465 | -13.37 | -17.3089 | -6.5698 | -5.3682 | -17.3089 | -20.5055 | -7.7831 | -6.3595 | -20.5055 | -23.7099 | -8.9994 | -7.3534 | -23.7099 | -26.8346 | -10.1854 | -8.3224 | -26.8346 | -35.6372 | -13.5265 | -11.0525 | -35.6372 | -45.1507 | -17.1375 | -14.003 | -45.1507 | -64.1224 | -20.6993 | -16.9134 | -64.1224 | -69.935 | -21.9227 | -17.913 | -69.935 | -70.2571 | -22.0766 | -18.0387 | -70.2571 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 1.3398 | 0.44197 | 0.31765 | 1.3398 | -0.99112 | -0.37619 | -0.30738 | -0.99112 | -3.4363 | -1.3043 | -1.0657 | -3.4363 | -5.914 | -2.2447 | -1.8341 | -5.914 | -8.6479 | -3.2824 | -2.682 | -8.6479 | -10.6402 | -4.0386 | -3.2999 | -10.6402 | -12.7404 | -4.8358 | -3.9513 | -12.7404 | -14.818 | -5.6244 | -4.5956 | -14.818 | -22.4194 | -8.5095 | -6.9531 | -22.4194 | -29.9789 | -11.3788 | -9.2976 | -29.9789 | -36.0761 | -13.6931 | -11.1886 | -36.0761 | -37.2853 | -14.1521 | -11.5636 | -37.2853 | -38.4798 | -14.6055 | -11.9341 | -38.4798 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0.26106 | 0.099087 | 0.080964 | 0.26106 | -2.9201 | -1.1083 | -0.90563 | -2.9201 | -5.6485 | -2.144 | -1.7518 | -5.6485 | -11.2651 | -4.2758 | -3.4938 | -11.2651 | -16.5393 | -6.2777 | -5.1295 | -16.5393 | -20.5506 | -7.8002 | -6.3735 | -20.5506 | -23.8304 | -9.0451 | -7.3907 | -23.8304 | -27.1043 | -10.2878 | -8.4061 | -27.1043 | -30.3368 | -11.5147 | -9.4086 | -30.3368 | -39.7052 | -15.0706 | -12.3141 | -39.7052 | -54.3779 | -18.81 | -15.3696 | -54.3779 | -74.7176 | -22.4848 | -18.3723 | -74.7176 | -80.9623 | -23.7851 | -19.4347 | -80.9623 | -81.6439 | -23.9992 | -19.6097 | -81.6439
PORTWOOD | VERNON PARK | BREDBURY | 389826 | 390619 | 28.353 | 9.5086 | 6.9364 | 13.8818 | 28.4679 | 8.8704 | 6.4709 | 11.3924 | 28.5828 | 8.3164 | 6.0667 | 10.174 | 28.6932 | 8.1885 | 5.9734 | 9.0478 | 28.8077 | 7.8975 | 5.7611 | 7.9638 | 28.9303 | 7.4727 | 5.4513 | 7.0452 | 29.0659 | 7.1374 | 5.2067 | 6.1383 | 29.219 | 6.8319 | 4.9838 | 5.2302 | 29.3339 | 6.5264 | 4.7609 | 4.2653 | 29.4467 | 6.2505 | 4.5596 | 3.3836 | 29.7849 | 5.6056 | 4.0892 | 1.6395 | 30.1035 | 5.0208 | 3.6626 | -0.18408 | 27.9468 | 4.5332 | 3.3069 | -1.4532 | 28.475 | 4.6189 | 3.3694 | -2.6678 | 29.0597 | 4.7138 | 3.4386 | -3.616 | 28.3452 | 9.5086 | 6.9364 | 13.8818 | 28.4451 | 9.0503 | 6.6021 | 12.5167 | 28.5564 | 8.7369 | 6.3735 | 11.6945 | 28.6697 | 8.48 | 6.1861 | 10.9504 | 28.7958 | 8.3107 | 6.0625 | 10.2125 | 28.9354 | 8.0458 | 5.8693 | 9.4547 | 29.0984 | 7.6152 | 5.5552 | 8.6448 | 29.2902 | 7.3575 | 5.3672 | 7.7705 | 29.4031 | 7.1304 | 5.2015 | 7.0303 | 29.5285 | 6.9112 | 5.0416 | 6.2929 | 29.9164 | 6.4699 | 4.7197 | 5.3161 | 30.3098 | 6.0913 | 4.4435 | 4.3706 | 30.6134 | 5.7426 | 4.1892 | 3.5258 | 30.8442 | 5.9548 | 4.3439 | 2.6282 | 31.0267 | 6.116 | 4.4616 | 1.8779 | 28.3564 | 9.5086 | 6.9364 | 13.8818 | 28.4814 | 8.777 | 6.4027 | 11.0714 | 28.611 | 8.1372 | 5.936 | 9.7561 | 28.7362 | 7.9289 | 5.784 | 8.5667 | 28.8671 | 7.5511 | 5.5084 | 7.4131 | 29.008 | 7.086 | 5.1692 | 6.4179 | 29.1643 | 6.6684 | 4.8645 | 5.3508 | 29.341 | 6.2934 | 4.591 | 4.2014 | 29.4709 | 5.9287 | 4.3249 | 3.1283 | 29.5985 | 5.5849 | 4.0741 | 2.1976 | 29.0651 | 4.7147 | 3.4393 | 0.23077 | 24.1902 | 3.9239 | 2.8624 | -1.6354 | 20.0832 | 3.2577 | 2.3764 | -2.7748 | 19.4374 | 3.1529 | 2.3 | -3.7268 | 19.4775 | 3.1594 | 2.3048 | -4.2335 | 28.3564 | 9.5086 | 6.9364 | 13.8818 | 28.4281 | 8.8881 | 6.4838 | 11.6488 | 28.5132 | 8.4173 | 6.1403 | 10.5031 | 28.5939 | 8.18 | 5.9672 | 9.3824 | 28.6775 | 7.8253 | 5.7084 | 8.2919 | 28.7818 | 7.446 | 5.4318 | 7.3375 | 28.9042 | 7.1187 | 5.193 | 6.2433 | 29.0394 | 6.7145 | 4.8981 | 4.8981 | 29.1654 | 6.3271 | 4.6155 | 3.5893 | 29.2894 | 5.958 | 4.3463 | 2.4164 | 29.6694 | 5.0759 | 3.7028 | 0.17369 | 26.4961 | 4.2979 | 3.1353 | -1.5143 | 23.1512 | 3.7554 | 2.7395 | -2.4746 | 26.4059 | 4.2833 | 3.1246 | -3.0523 | 22.7997 | 3.6983 | 2.6979 | -3.0047 | 28.353 | 9.5086 | 6.9364 | 13.8818 | 28.4581 | 9.0151 | 6.5764 | 12.1751 | 28.563 | 8.5184 | 6.2141 | 11.1414 | 28.6535 | 8.3814 | 6.1141 | 10.0629 | 28.7465 | 8.1188 | 5.9225 | 9.0505 | 28.8575 | 7.7099 | 5.6243 | 8.1849 | 28.9876 | 7.3843 | 5.3868 | 7.3023 | 29.1264 | 7.0789 | 5.164 | 6.4108 | 29.2277 | 6.7755 | 4.9427 | 5.4454 | 29.331 | 6.496 | 4.7388 | 4.5499 | 29.6551 | 5.9209 | 4.3192 | 3.0528 | 29.9736 | 5.4981 | 4.0108 | 1.8676 | 30.2119 | 5.1422 | 3.7512 | 1.1021 | 30.4371 | 5.36 | 3.9101 | 0.34484 | 30.5956 | 5.5818 | 4.0719 | -0.16035 | 28.353 | 9.5086 | 6.9364 | 13.8818 | 28.4534 | 8.7452 | 6.3795 | 10.9196 | 28.5779 | 8.2456 | 6.015 | 9.5656 | 28.6988 | 7.9722 | 5.8156 | 8.3642 | 28.8226 | 7.5931 | 5.5391 | 7.1987 | 28.9542 | 7.2054 | 5.2562 | 6.1967 | 29.1004 | 6.8667 | 5.0092 | 5.0587 | 29.2722 | 6.4448 | 4.7014 | 3.6406 | 29.4006 | 6.0502 | 4.4136 | 2.3113 | 29.5271 | 5.6802 | 4.1436 | 1.1408 | 29.4662 | 4.7797 | 3.4867 | -1.1431 | 24.5573 | 3.9834 | 2.9059 | -2.8526 | 21.1205 | 3.426 | 2.4992 | -3.8364 | 24.2959 | 3.941 | 2.8749 | -4.4405 | 20.5568 | 3.3345 | 2.4325 | -4.466
POULTON | BISPHAM | PENWORTHAM WEST / STANAH | 335679 | 439130 | 16.0561 | 9.1726 | 6.6913 | 11.0114 | 16.1296 | 9.107 | 6.6435 | 10.5359 | 16.2258 | 8.729 | 6.3677 | 10.2368 | 16.341 | 8.4417 | 6.1581 | 10.0258 | 16.4851 | 8.1559 | 5.9496 | 9.7957 | 16.652 | 7.6112 | 5.5523 | 9.5561 | 16.8448 | 7.0709 | 5.1581 | 9.32 | 17.0786 | 6.8915 | 5.0273 | 9.0642 | 17.301 | 6.7432 | 4.919 | 8.7522 | 17.5306 | 6.668 | 4.8642 | 8.4548 | 18.3722 | 6.3809 | 4.6548 | 6.7907 | 19.3189 | 6.6179 | 4.8277 | 3.9429 | 20.0098 | 8.2472 | 6.0162 | 1.8466 | 20.6435 | 10.5096 | 7.6666 | -0.078867 | 21.1385 | 10.8291 | 7.8997 | -1.5136 | 16.0487 | 9.1726 | 6.6913 | 11.0114 | 16.1193 | 9.1303 | 6.6604 | 10.7409 | 16.1964 | 9.0803 | 6.624 | 10.5115 | 16.2878 | 8.9692 | 6.5429 | 10.3327 | 16.4036 | 8.9463 | 6.5262 | 10.145 | 16.5413 | 8.8561 | 6.4604 | 9.938 | 16.7087 | 8.6457 | 6.3069 | 9.679 | 16.9134 | 8.549 | 6.2364 | 9.338 | 17.0362 | 8.4242 | 6.1453 | 9.0372 | 17.1691 | 8.298 | 6.0533 | 8.7354 | 17.6281 | 7.9397 | 5.7919 | 7.8247 | 18.1468 | 7.7259 | 5.6359 | 6.9172 | 18.658 | 8.7361 | 6.3728 | 6.0601 | 19.2009 | 10.5034 | 7.6621 | 5.1341 | 19.5675 | 10.7823 | 7.8655 | 4.2963 | 16.0592 | 9.1726 | 6.6913 | 11.0114 | 16.1343 | 9.076 | 6.6208 | 10.4773 | 16.2337 | 8.7192 | 6.3606 | 10.1687 | 16.3538 | 8.315 | 6.0657 | 9.9575 | 16.5014 | 7.9516 | 5.8006 | 9.73 | 16.6702 | 7.3353 | 5.351 | 9.4951 | 16.8631 | 6.8226 | 4.977 | 9.2642 | 17.0948 | 6.6126 | 4.8238 | 9.0181 | 17.3044 | 6.4455 | 4.7019 | 8.7569 | 17.5203 | 6.3514 | 4.6333 | 8.5142 | 18.3695 | 5.8851 | 4.2931 | 6.4435 | 19.3821 | 5.987 | 4.3674 | 3.428 | 20.1349 | 7.4871 | 5.4617 | 1.1992 | 20.8003 | 9.6602 | 7.047 | -0.78294 | 21.2853 | 9.8974 | 7.22 | -2.1594 | 16.0592 | 9.1726 | 6.6913 | 11.0114 | 16.0784 | 9.1259 | 6.6572 | 10.7351 | 16.1378 | 8.794 | 6.4151 | 10.5185 | 16.2214 | 8.5011 | 6.2015 | 10.349 | 16.3389 | 8.0899 | 5.9015 | 10.1498 | 16.5008 | 7.5527 | 5.5096 | 9.9104 | 16.7208 | 6.9845 | 5.0951 | 9.5553 | 17.0452 | 7.1676 | 5.2287 | 8.8591 | 17.3693 | 7.224 | 5.2698 | 8.1162 | 17.7012 | 7.5385 | 5.4992 | 7.3865 | 18.71 | 12.6174 | 9.2043 | 5.2613 | 19.6456 | 11.9039 | 8.6837 | 2.8234 | 20.3095 | 11.2137 | 8.1803 | 0.79833 | 20.7793 | 10.6318 | 7.7557 | -0.63552 | 20.8136 | 10.3181 | 7.5269 | -0.59862 | 16.056 | 9.1726 | 6.6913 | 11.0114 | 16.118 | 9.1232 | 6.6552 | 10.6211 | 16.1921 | 8.7723 | 6.3993 | 10.3702 | 16.2725 | 8.5048 | 6.2041 | 10.2193 | 16.3727 | 8.2189 | 5.9956 | 10.0778 | 16.5097 | 7.6904 | 5.61 | 9.902 | 16.6796 | 7.1921 | 5.2465 | 9.7059 | 16.8743 | 7.0151 | 5.1174 | 9.4953 | 17.0612 | 6.8713 | 5.0125 | 9.2071 | 17.2606 | 6.7948 | 4.9567 | 8.9199 | 17.9421 | 6.6394 | 4.8433 | 7.9753 | 18.6378 | 7.0782 | 5.1635 | 6.1293 | 19.1204 | 8.8449 | 6.4522 | 4.6887 | 19.5044 | 11.3022 | 8.2448 | 3.5136 | 19.7084 | 11.8086 | 8.6142 | 2.9079 | 16.056 | 9.1726 | 6.6913 | 11.0114 | 16.0977 | 9.0823 | 6.6254 | 10.5135 | 16.19 | 8.7349 | 6.372 | 10.1979 | 16.3107 | 8.4238 | 6.145 | 9.9494 | 16.4583 | 7.9757 | 5.8182 | 9.6811 | 16.6236 | 7.4278 | 5.4185 | 9.4098 | 16.8364 | 6.8532 | 4.9993 | 9.0309 | 17.1677 | 7.0319 | 5.1297 | 8.2792 | 17.4838 | 7.0879 | 5.1706 | 7.5075 | 17.8076 | 7.3968 | 5.3958 | 6.7526 | 18.8226 | 12.4517 | 9.0833 | 4.5576 | 19.7933 | 11.7806 | 8.5938 | 2.4245 | 20.5048 | 11.0901 | 8.0901 | 0.36605 | 21.0014 | 10.4862 | 7.6495 | -1.078 | 21.0621 | 10.1696 | 7.4186 | -1.0219
POYNTON | HAZEL GROVE | BREDBURY | 392096 | 383493 | 22.6157 | 13.6497 | 9.8103 | 12.7201 | 22.6743 | 13.4803 | 9.6886 | 11.934 | 22.7628 | 13.2284 | 9.5075 | 11.7143 | 22.8836 | 13.0088 | 9.3496 | 11.6513 | 23.0371 | 12.761 | 9.1716 | 11.3366 | 23.2236 | 12.4381 | 8.9395 | 11.2249 | 23.4534 | 12.1104 | 8.704 | 11.1048 | 23.6875 | 11.9199 | 8.567 | 10.9694 | 23.8843 | 11.7835 | 8.469 | 10.7825 | 24.0675 | 11.7641 | 8.4551 | 10.6007 | 24.6614 | 11.396 | 8.1906 | 9.4018 | 25.2022 | 10.899 | 7.8333 | 7.4016 | 25.5593 | 10.4744 | 7.5282 | 5.7299 | 25.8306 | 10.1569 | 7.3 | 3.9023 | 25.9917 | 9.9132 | 7.1248 | 2.34 | 22.5746 | 13.6497 | 9.8103 | 12.7201 | 22.6279 | 13.5923 | 9.769 | 12.4786 | 22.6863 | 13.4083 | 9.6368 | 12.3589 | 22.7766 | 13.1957 | 9.484 | 12.2665 | 22.8986 | 12.9846 | 9.3323 | 12.1413 | 23.0432 | 12.7601 | 9.1709 | 11.9942 | 23.2188 | 12.4257 | 8.9306 | 11.8036 | 23.3492 | 12.3401 | 8.8691 | 11.5675 | 23.4403 | 12.2588 | 8.8106 | 11.3794 | 23.5424 | 12.1917 | 8.7624 | 11.1848 | 23.9162 | 11.9722 | 8.6047 | 10.5648 | 24.3679 | 11.8069 | 8.4859 | 9.9027 | 24.8517 | 11.6067 | 8.342 | 9.217 | 25.3688 | 11.5023 | 8.2669 | 8.4514 | 25.6561 | 11.3918 | 8.1875 | 7.8961 | 22.6264 | 13.6497 | 9.8103 | 12.7201 | 22.6918 | 13.4528 | 9.6688 | 11.8288 | 22.7915 | 13.1781 | 9.4714 | 11.6024 | 22.9276 | 12.9187 | 9.2849 | 11.5695 | 23.0982 | 12.6625 | 9.1008 | 11.2876 | 23.302 | 12.3036 | 8.8429 | 11.2153 | 23.5186 | 11.9379 | 8.58 | 11.1518 | 23.7344 | 11.753 | 8.4471 | 11.0796 | 23.8917 | 11.7329 | 8.4326 | 10.9682 | 24.061 | 11.6369 | 8.3637 | 10.8502 | 24.6618 | 11.2211 | 8.0648 | 9.8134 | 25.2729 | 10.7009 | 7.6909 | 7.909 | 25.6987 | 10.2191 | 7.3446 | 6.3157 | 26.0086 | 9.832 | 7.0665 | 4.6077 | 26.1694 | 9.5184 | 6.8411 | 3.2064 | 22.6264 | 13.6497 | 9.8103 | 12.7201 | 22.6192 | 13.5377 | 9.7298 | 12.2591 | 22.6599 | 13.438 | 9.6582 | 12.1364 | 22.7303 | 13.311 | 9.5669 | 12.1098 | 22.8436 | 13.0741 | 9.3966 | 11.8139 | 23.0254 | 12.7695 | 9.1777 | 11.7072 | 23.2653 | 12.5237 | 9.001 | 11.4914 | 23.5353 | 12.2715 | 8.8198 | 10.9186 | 23.7374 | 12.1244 | 8.714 | 10.2953 | 23.9322 | 11.8946 | 8.5489 | 9.6608 | 24.5449 | 11.2872 | 8.1124 | 7.7866 | 25.0899 | 10.7318 | 7.7132 | 5.9967 | 25.4437 | 10.24 | 7.3597 | 4.5693 | 25.6829 | 9.8444 | 7.0753 | 3.6019 | 25.7392 | 9.717 | 6.9838 | 4.095 | 22.6157 | 13.6497 | 9.8103 | 12.7201 | 22.6639 | 13.564 | 9.7487 | 12.3447 | 22.7221 | 13.3285 | 9.5794 | 12.2361 | 22.7969 | 13.1276 | 9.4351 | 12.2185 | 22.9022 | 12.8975 | 9.2697 | 11.9686 | 23.0663 | 12.5873 | 9.0467 | 11.9038 | 23.2855 | 12.262 | 8.813 | 11.8131 | 23.5036 | 12.0711 | 8.6757 | 11.7101 | 23.6709 | 11.9421 | 8.583 | 11.549 | 23.8527 | 11.9322 | 8.5759 | 11.3841 | 24.4032 | 11.6834 | 8.3971 | 10.761 | 24.9283 | 11.4417 | 8.2234 | 10.0409 | 25.2916 | 11.2479 | 8.0841 | 9.5397 | 25.5553 | 11.221 | 8.0647 | 9.0449 | 25.6736 | 11.2758 | 8.1041 | 8.7915 | 22.6157 | 13.6497 | 9.8103 | 12.7201 | 22.6394 | 13.4516 | 9.6679 | 11.8516 | 22.7222 | 13.3271 | 9.5785 | 11.5963 | 22.8399 | 13.1803 | 9.473 | 11.506 | 22.9893 | 12.9298 | 9.2929 | 11.155 | 23.1665 | 12.6131 | 9.0653 | 11.0152 | 23.3854 | 12.3716 | 8.8917 | 10.7601 | 23.6274 | 12.0944 | 8.6925 | 10.1342 | 23.8151 | 11.9432 | 8.5838 | 9.4815 | 23.9954 | 11.7064 | 8.4136 | 8.8171 | 24.5987 | 11.0733 | 7.9586 | 6.8196 | 25.1761 | 10.4835 | 7.5347 | 4.886 | 25.5736 | 9.962 | 7.1599 | 3.3156 | 25.8291 | 9.5392 | 6.856 | 2.1999 | 25.892 | 9.3873 | 6.7468 | 2.5499
PREESALL | THORNTON | PENWORTHAM WEST / STANAH | 336965 | 446547 | 29.8751 | 15.1547 | 10.8919 | 17.9607 | 29.957 | 14.9247 | 10.7267 | 17.226 | 30.0599 | 14.7262 | 10.584 | 17.0028 | 30.1895 | 14.5148 | 10.4321 | 16.8367 | 30.3512 | 14.5956 | 10.4901 | 16.5828 | 30.5377 | 14.7296 | 10.5865 | 16.3203 | 30.6829 | 14.6891 | 10.5574 | 16.0833 | 30.8537 | 14.5802 | 10.4791 | 15.8517 | 30.9889 | 14.3495 | 10.3132 | 15.5931 | 31.1172 | 14.204 | 10.2087 | 15.3612 | 31.5162 | 13.6844 | 9.8352 | 14.1507 | 31.9236 | 13.1265 | 9.4343 | 12.2219 | 32.2153 | 12.6911 | 9.1213 | 10.7123 | 32.4641 | 12.3859 | 8.902 | 9.2046 | 32.643 | 11.953 | 8.5908 | 7.7343 | 29.8519 | 15.1547 | 10.8919 | 17.9607 | 29.9245 | 15.0227 | 10.7971 | 17.6377 | 29.9926 | 14.9152 | 10.7199 | 17.4974 | 30.077 | 14.8079 | 10.6427 | 17.323 | 30.1903 | 14.5674 | 10.4699 | 17.0937 | 30.3302 | 14.3178 | 10.2905 | 16.8561 | 30.4976 | 14.1569 | 10.1748 | 16.5456 | 30.6911 | 14.1111 | 10.1419 | 16.1156 | 30.8018 | 14.0961 | 10.1311 | 15.7948 | 30.9169 | 14.0749 | 10.1159 | 15.4667 | 31.2756 | 13.9168 | 10.0023 | 14.4742 | 31.5422 | 13.7378 | 9.8736 | 13.4675 | 31.7692 | 13.5393 | 9.731 | 12.4995 | 31.9921 | 13.4861 | 9.6927 | 11.4466 | 32.1537 | 13.3028 | 9.561 | 10.7405 | 29.8832 | 15.1547 | 10.8919 | 17.9607 | 29.9698 | 14.8881 | 10.7004 | 17.1566 | 30.0838 | 14.6176 | 10.506 | 16.9413 | 30.2305 | 14.3402 | 10.3066 | 16.8127 | 30.4144 | 14.6048 | 10.4968 | 16.6011 | 30.5906 | 14.6755 | 10.5475 | 16.3889 | 30.7506 | 14.555 | 10.461 | 16.2223 | 30.9437 | 14.2737 | 10.2588 | 16.0675 | 31.0897 | 14.0749 | 10.1159 | 15.8882 | 31.2284 | 13.8729 | 9.9707 | 15.7249 | 31.6639 | 13.2621 | 9.5317 | 14.7264 | 32.1073 | 12.568 | 9.0329 | 12.8874 | 32.4227 | 12.101 | 8.6972 | 11.2367 | 32.6848 | 11.7789 | 8.4658 | 9.7738 | 32.861 | 11.3198 | 8.1358 | 8.5811 | 29.8832 | 15.1547 | 10.8919 | 17.9607 | 29.8921 | 14.9604 | 10.7523 | 17.565 | 29.9473 | 14.7244 | 10.5827 | 17.4531 | 30.025 | 14.4784 | 10.4059 | 17.3456 | 30.1431 | 14.8098 | 10.6441 | 17.1585 | 30.3224 | 14.822 | 10.6529 | 16.9544 | 30.4874 | 14.6015 | 10.4944 | 16.6934 | 30.6532 | 14.2537 | 10.2444 | 16.1517 | 30.7907 | 13.9304 | 10.0121 | 15.578 | 30.9248 | 13.6672 | 9.8229 | 15.0146 | 31.3332 | 13.3097 | 9.566 | 13.3761 | 31.7513 | 12.7223 | 9.1438 | 11.7183 | 32.0436 | 12.2362 | 8.7944 | 10.506 | 32.2684 | 11.8625 | 8.5258 | 9.7388 | 32.3382 | 11.6104 | 8.3446 | 10.0033 | 29.875 | 15.1547 | 10.8919 | 17.9607 | 29.9444 | 14.9831 | 10.7686 | 17.5481 | 30.0168 | 14.8034 | 10.6395 | 17.4034 | 30.0991 | 14.5983 | 10.4921 | 17.2787 | 30.2082 | 14.6966 | 10.5627 | 17.1184 | 30.3705 | 14.8565 | 10.6777 | 16.9462 | 30.5696 | 14.8451 | 10.6694 | 16.7529 | 30.7281 | 14.7294 | 10.5863 | 16.5048 | 30.8528 | 14.4905 | 10.4146 | 16.1831 | 30.9771 | 14.33 | 10.2993 | 15.8633 | 31.3739 | 13.8468 | 9.952 | 14.778 | 31.7852 | 13.4125 | 9.6398 | 13.4619 | 32.0866 | 13.0863 | 9.4054 | 12.5154 | 32.3548 | 12.9191 | 9.2852 | 11.6329 | 32.4967 | 12.701 | 9.1284 | 11.2033 | 29.875 | 15.1547 | 10.8919 | 17.9607 | 29.9079 | 14.9026 | 10.7108 | 17.2399 | 30.0022 | 14.6463 | 10.5266 | 17.0041 | 30.1284 | 14.375 | 10.3316 | 16.8083 | 30.287 | 14.6885 | 10.5569 | 16.539 | 30.4673 | 14.6806 | 10.5512 | 16.2752 | 30.62 | 14.4343 | 10.3742 | 15.941 | 30.8061 | 14.0769 | 10.1173 | 15.3016 | 30.9531 | 13.6449 | 9.8069 | 14.0585 | 31.0949 | 13.2734 | 9.5399 | 12.8259 | 31.5095 | 12.5645 | 9.0304 | 9.182 | 31.8989 | 11.6354 | 8.3626 | 5.5627 | 32.1708 | 10.8119 | 7.7707 | 2.4097 | 32.3696 | 9.9883 | 7.1788 | -0.91359 | 32.442 | 9.1894 | 6.6046 | -3.8204
PRESTON EAST | PRESTON EAST | PENWORTHAM EAST / ROCHDALE | 356777 | 432926 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 7.2154 | 1.1704 | 0.85379 | 7.2154 | 34.833 | 8.5632 | 6.2468 | 7.8035 | 35.3675 | 18.6817 | 13.6281 | 6.0127 | 35.6746 | 22.6575 | 16.5283 | 4.5431 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 12.6194 | 2.047 | 1.4933 | 12.6194 | 32.8075 | 9.8068 | 7.1539 | 13.7804 | 33.628 | 12.7115 | 9.2729 | 13.1755 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 6.5436 | 1.0614 | 0.7743 | 6.5436 | 34.8262 | 8.4095 | 6.1346 | 7.848 | 35.3441 | 18.516 | 13.5072 | 6.3147 | 35.567 | 22.4962 | 16.4107 | 5.2392 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.2414 | 0.36358 | 0.26523 | 2.2414 | 13.4677 | 2.1846 | 1.5936 | 13.4677 | 32.6097 | 20.7195 | 15.1146 | 11.1513 | 34.0002 | 20.4825 | 14.9417 | 8.9665 | 34.7086 | 20.5335 | 14.9789 | 7.3807 | 35.0852 | 22.7344 | 16.5845 | 6.5315 | 35.0405 | 22.686 | 16.5491 | 7.2852 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 10.2421 | 1.6614 | 1.2119 | 10.2421 | 33.3621 | 9.1659 | 6.6864 | 14.3762 | 34.1681 | 19.411 | 14.16 | 13.757 | 34.4957 | 23.5337 | 17.1675 | 13.7067 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 0.94461 | 0.15323 | 0.11178 | 0.94461 | 12.1754 | 1.975 | 1.4407 | 11.2969 | 32.4461 | 20.4987 | 14.9535 | 8.8268 | 33.9799 | 20.245 | 14.7684 | 6.5378 | 34.939 | 20.2822 | 14.7956 | 4.8355 | 35.415 | 22.4695 | 16.3912 | 3.9014 | 35.4239 | 22.3912 | 16.334 | 4.5698
PRESTON OLD RD | BLACKPOOL | PENWORTHAM WEST / STANAH | 332562 | 434929 | 30.0819 | 12.3701 | 9.0238 | 16.9321 | 30.1152 | 11.9995 | 8.7534 | 15.4377 | 30.1573 | 11.9039 | 8.6837 | 15.1851 | 30.2138 | 11.8161 | 8.6197 | 15.1917 | 30.2944 | 11.6683 | 8.5119 | 15.1399 | 30.3911 | 11.5167 | 8.4013 | 15.0734 | 30.5048 | 11.3864 | 8.3062 | 15.01 | 30.644 | 11.2717 | 8.2226 | 14.9496 | 30.7465 | 11.1959 | 8.1673 | 14.8551 | 30.8416 | 11.1307 | 8.1197 | 14.7813 | 31.255 | 10.7528 | 7.844 | 13.6346 | 31.7858 | 10.1934 | 7.4359 | 11.2669 | 32.0542 | 9.7375 | 7.1033 | 9.2312 | 32.2981 | 9.309 | 6.7908 | 6.9659 | 32.452 | 8.8252 | 6.4379 | 5.0834 | 30.0581 | 12.3701 | 9.0238 | 16.9321 | 30.1031 | 12.2601 | 8.9436 | 16.5389 | 30.132 | 12.197 | 8.8975 | 16.4498 | 30.1712 | 12.124 | 8.8443 | 16.408 | 30.2319 | 12.0451 | 8.7868 | 16.3155 | 30.3094 | 11.9452 | 8.7139 | 16.2047 | 30.4083 | 11.6683 | 8.5119 | 16.0434 | 30.5249 | 11.5471 | 8.4235 | 15.843 | 30.5806 | 11.4648 | 8.3634 | 15.6909 | 30.6385 | 11.3876 | 8.3071 | 15.5341 | 30.8191 | 11.1734 | 8.1508 | 15.0511 | 30.9964 | 11.0347 | 8.0496 | 14.5714 | 31.1665 | 10.8976 | 7.9497 | 14.0657 | 31.3456 | 10.8225 | 7.8948 | 13.5072 | 31.4839 | 10.7187 | 7.8191 | 13.0862 | 30.0867 | 12.3701 | 9.0238 | 16.9321 | 30.1249 | 11.945 | 8.7137 | 15.2101 | 30.1749 | 11.8042 | 8.611 | 14.9356 | 30.2434 | 11.6937 | 8.5304 | 14.974 | 30.3389 | 11.5489 | 8.4248 | 14.9574 | 30.4535 | 11.3954 | 8.3128 | 14.9316 | 30.5896 | 11.2608 | 8.2146 | 14.9271 | 30.7557 | 11.1553 | 8.1376 | 14.9273 | 30.8743 | 11.0742 | 8.0785 | 14.898 | 30.984 | 10.9968 | 8.022 | 14.8804 | 31.4399 | 10.6058 | 7.7368 | 13.9122 | 31.999 | 10.0385 | 7.3229 | 11.6974 | 32.2863 | 9.5881 | 6.9944 | 9.7943 | 32.4868 | 9.0977 | 6.6367 | 7.675 | 32.5884 | 8.7496 | 6.3827 | 5.9492 | 30.0867 | 12.3701 | 9.0238 | 16.9321 | 30.0423 | 12.1075 | 8.8323 | 15.9691 | 30.0487 | 12.0316 | 8.7769 | 15.846 | 30.0758 | 11.8997 | 8.6807 | 15.8824 | 30.1351 | 11.8018 | 8.6092 | 15.8401 | 30.2341 | 11.6954 | 8.5316 | 15.7681 | 30.3815 | 11.5478 | 8.4239 | 15.5563 | 30.5753 | 11.282 | 8.2301 | 14.8591 | 30.7168 | 11.0846 | 8.0861 | 14.1261 | 30.8547 | 10.8741 | 7.9325 | 13.3982 | 31.2791 | 10.4391 | 7.6152 | 11.273 | 31.6867 | 9.9 | 7.2219 | 9.189 | 31.9556 | 9.4399 | 6.8863 | 7.4861 | 32.1557 | 9.1725 | 6.6912 | 6.407 | 32.1158 | 9.1724 | 6.6912 | 7.308 | 30.0819 | 12.3701 | 9.0238 | 16.9321 | 30.1089 | 12.1635 | 8.8731 | 16.2385 | 30.1309 | 12.1133 | 8.8365 | 16.1585 | 30.1553 | 12.043 | 8.7852 | 16.2221 | 30.1989 | 11.9103 | 8.6884 | 16.2545 | 30.2764 | 11.7686 | 8.5851 | 16.2552 | 30.3845 | 11.6459 | 8.4955 | 16.2301 | 30.5051 | 11.5345 | 8.4143 | 16.1998 | 30.5933 | 11.4615 | 8.361 | 16.1194 | 30.68 | 11.395 | 8.3125 | 16.044 | 30.9708 | 11.169 | 8.1476 | 15.6741 | 31.3019 | 10.98 | 8.0098 | 15.1325 | 31.5492 | 10.8469 | 7.9127 | 14.7397 | 31.7837 | 10.7863 | 7.8684 | 14.3148 | 31.924 | 10.7136 | 7.8155 | 14.0608 | 30.0819 | 12.3701 | 9.0238 | 16.9321 | 30.0572 | 11.9429 | 8.7122 | 15.1913 | 30.0935 | 11.8146 | 8.6186 | 14.8723 | 30.1571 | 11.6621 | 8.5074 | 14.8285 | 30.2477 | 11.5556 | 8.4297 | 14.7134 | 30.3521 | 11.4415 | 8.3464 | 14.5938 | 30.4963 | 11.2817 | 8.2298 | 14.3219 | 30.7239 | 11.0083 | 8.0304 | 13.5423 | 30.8779 | 10.7952 | 7.8749 | 12.746 | 31.025 | 10.5685 | 7.7095 | 11.955 | 31.4488 | 10.0928 | 7.3625 | 9.6436 | 31.8311 | 9.518 | 6.9433 | 7.416 | 32.0728 | 9.0289 | 6.5865 | 5.5702 | 32.2449 | 8.7321 | 6.3699 | 4.3059 | 32.2357 | 8.6621 | 6.3189 | 4.9869
PRESTWICH | AGECROFT | KEARSLEY | 381392 | 404001 | 31.5283 | 8.1021 | 5.9104 | 12.7547 | 31.649 | 7.7507 | 5.654 | 11.7762 | 31.8148 | 7.3954 | 5.3948 | 11.3745 | 32.0189 | 7.0674 | 5.1555 | 11.0518 | 32.2615 | 6.685 | 4.8766 | 10.6414 | 32.5368 | 6.2908 | 4.589 | 10.213 | 32.8105 | 6.1064 | 4.4545 | 9.7921 | 33.1384 | 5.9712 | 4.3559 | 9.3846 | 33.394 | 5.8216 | 4.2468 | 8.9543 | 33.6097 | 5.684 | 4.1464 | 8.5192 | 31.7484 | 5.1499 | 3.7568 | 6.3436 | 28.267 | 4.5852 | 3.3448 | 3.1921 | 26.6065 | 4.3158 | 3.1483 | 0.82746 | 25.1467 | 4.079 | 2.9756 | -1.3862 | 22.2869 | 3.6152 | 2.6372 | -3.0113 | 31.4849 | 8.1021 | 5.9104 | 12.7547 | 31.5953 | 7.9084 | 5.769 | 12.3336 | 31.6842 | 7.6001 | 5.5442 | 12.1119 | 31.7774 | 7.27 | 5.3034 | 11.9024 | 31.9037 | 6.9184 | 5.0469 | 11.5778 | 32.048 | 6.5793 | 4.7995 | 11.2256 | 32.2255 | 6.1906 | 4.516 | 10.7895 | 32.434 | 5.9457 | 4.3373 | 10.2706 | 32.586 | 5.7131 | 4.1677 | 9.8799 | 32.7463 | 5.4898 | 4.0047 | 9.4758 | 30.9884 | 5.0266 | 3.6669 | 8.2608 | 28.926 | 4.6921 | 3.4228 | 7.0689 | 28.5535 | 4.6317 | 3.3787 | 5.9637 | 29.2566 | 4.7457 | 3.4619 | 4.788 | 28.0296 | 4.5467 | 3.3167 | 3.9238 | 31.5446 | 8.1021 | 5.9104 | 12.7547 | 31.6932 | 7.6938 | 5.6126 | 11.5776 | 31.8968 | 7.2924 | 5.3197 | 11.0711 | 32.1507 | 6.8688 | 5.0107 | 10.6712 | 32.4522 | 6.397 | 4.6665 | 10.1789 | 32.7951 | 6.1059 | 4.4542 | 9.6657 | 33.1641 | 5.8372 | 4.2582 | 9.1739 | 33.5204 | 5.6674 | 4.1343 | 8.6506 | 33.7342 | 5.4809 | 3.9983 | 8.0781 | 32.6442 | 5.2952 | 3.8628 | 7.5128 | 28.2582 | 4.5838 | 3.3438 | 4.9946 | 24.0699 | 3.9044 | 2.8482 | 1.8264 | 22.012 | 3.5706 | 2.6047 | -0.33044 | 20.1844 | 3.2741 | 2.3884 | -2.1096 | 17.9845 | 2.9173 | 2.1281 | -2.9707 | 31.5446 | 8.1021 | 5.9104 | 12.7547 | 31.5516 | 7.8133 | 5.6997 | 12.2084 | 31.647 | 7.6035 | 5.5467 | 11.8808 | 31.7776 | 7.2955 | 5.322 | 11.571 | 31.9661 | 6.9803 | 5.092 | 11.1264 | 32.2486 | 6.6968 | 4.8852 | 10.6051 | 32.5978 | 6.4633 | 4.7149 | 9.9479 | 32.9934 | 6.114 | 4.4601 | 8.8459 | 33.3012 | 5.7888 | 4.2228 | 7.7389 | 33.587 | 5.4595 | 3.9826 | 6.6646 | 31.8937 | 5.1735 | 3.774 | 3.5962 | 27.1626 | 4.406 | 3.2141 | 0.87076 | 23.4474 | 3.8034 | 2.7745 | -0.83231 | 20.2676 | 3.2876 | 2.3983 | -1.7058 | 19.0064 | 3.083 | 2.249 | -1.2286 | 31.5283 | 8.1021 | 5.9104 | 12.7547 | 31.6332 | 7.8182 | 5.7032 | 12.0995 | 31.7497 | 7.4964 | 5.4685 | 11.8326 | 31.8797 | 7.1847 | 5.2411 | 11.6383 | 32.0469 | 6.8409 | 4.9903 | 11.3921 | 32.2956 | 6.4522 | 4.7068 | 11.0868 | 32.6011 | 6.2993 | 4.5952 | 10.7479 | 32.8996 | 6.1744 | 4.5041 | 10.4022 | 33.1283 | 6.0311 | 4.3996 | 9.991 | 33.3554 | 5.8967 | 4.3016 | 9.5749 | 33.8717 | 5.502 | 4.0136 | 8.0805 | 32.2678 | 5.2342 | 3.8182 | 6.4843 | 32.0955 | 5.2062 | 3.7978 | 5.3365 | 31.9806 | 5.1876 | 3.7843 | 4.1968 | 29.7138 | 4.8199 | 3.516 | 3.3934 | 31.5283 | 8.1021 | 5.9104 | 12.7547 | 31.5893 | 7.7282 | 5.6376 | 11.7635 | 31.7609 | 7.4668 | 5.4469 | 11.2042 | 31.9808 | 7.134 | 5.2041 | 10.7371 | 32.2441 | 6.791 | 4.9539 | 10.1569 | 32.5388 | 6.4844 | 4.7303 | 9.5606 | 32.881 | 6.2375 | 4.5502 | 8.8139 | 33.2835 | 5.864 | 4.2777 | 7.5722 | 33.583 | 5.5209 | 4.0274 | 6.3601 | 31.9387 | 5.1808 | 3.7793 | 5.1835 | 29.7646 | 4.8281 | 3.522 | 1.8483 | 24.8116 | 4.0247 | 2.936 | -1.0218 | 20.8812 | 3.3871 | 2.4709 | -2.8753 | 17.4852 | 2.8363 | 2.069 | -3.9141 | 15.9536 | 2.5878 | 1.8878 | -3.6743
PRINGLE ST | BLACKBURN | PENWORTHAM EAST / ROCHDALE | 369088 | 427387 | 29.3636 | 13.2791 | 9.6869 | 17.0381 | 29.7326 | 13.0246 | 9.5013 | 16.1179 | 30.01 | 11.1776 | 8.1539 | 15.7145 | 30.3213 | 9.1964 | 6.7087 | 15.4065 | 30.5421 | 7.4793 | 5.4561 | 14.9807 | 30.7691 | 5.7058 | 4.1623 | 14.5336 | 22.9715 | 3.7262 | 2.7182 | 14.1032 | 20.1746 | 3.2725 | 2.3873 | 13.7034 | 19.4775 | 3.1594 | 2.3048 | 13.3089 | 19.6495 | 3.1873 | 2.3251 | 12.9313 | 18.5001 | 3.0009 | 2.1891 | 11.1334 | 21.1116 | 3.4245 | 2.4981 | 8.2661 | 32.538 | 5.278 | 3.8502 | 5.7323 | 33.7929 | 7.9077 | 5.7685 | 3.2202 | 34.0321 | 8.2056 | 5.9859 | 1.019 | 29.3453 | 13.2791 | 9.6869 | 17.0381 | 29.5568 | 13.1688 | 9.6064 | 16.5935 | 29.6896 | 11.5164 | 8.401 | 16.3681 | 29.8596 | 9.8286 | 7.1698 | 16.184 | 30.0823 | 8.0219 | 5.8519 | 15.9585 | 30.3453 | 6.1665 | 4.4984 | 15.708 | 27.5598 | 4.4705 | 3.2611 | 15.3981 | 26.6161 | 4.3174 | 3.1495 | 15.0268 | 25.8404 | 4.1916 | 3.0577 | 14.7666 | 24.9798 | 4.052 | 2.9559 | 14.5011 | 22.7384 | 3.6884 | 2.6906 | 13.7833 | 19.6345 | 3.1849 | 2.3234 | 12.928 | 27.769 | 4.5044 | 3.2859 | 11.4727 | 33.0208 | 6.747 | 4.9218 | 9.82 | 33.2263 | 7.2932 | 5.3203 | 8.8271 | 29.3704 | 13.2791 | 9.6869 | 17.0381 | 29.6715 | 12.9806 | 9.4692 | 16.0295 | 29.9112 | 11.0553 | 8.0647 | 15.5619 | 30.2272 | 8.8644 | 6.4664 | 15.2109 | 30.4509 | 7.3453 | 5.3583 | 14.7481 | 30.6823 | 5.4442 | 3.9715 | 14.2696 | 20.6383 | 3.3477 | 2.4421 | 13.8124 | 18.7035 | 3.0339 | 2.2132 | 13.3957 | 18.3811 | 2.9816 | 2.175 | 12.9908 | 18.2139 | 2.9545 | 2.1552 | 12.6013 | 15.9789 | 2.5919 | 1.8908 | 10.8063 | 17.6804 | 2.8679 | 2.0921 | 8.2181 | 28.3046 | 4.5913 | 3.3493 | 5.9031 | 33.6493 | 7.3157 | 5.3367 | 3.4481 | 33.824 | 7.505 | 5.4748 | 1.3663 | 29.3711 | 13.2791 | 9.6869 | 17.0381 | 29.6559 | 13.0659 | 9.5314 | 16.472 | 29.8888 | 12.7987 | 9.3365 | 16.1079 | 30.169 | 12.3122 | 8.9816 | 15.7809 | 30.3722 | 11.8958 | 8.6778 | 15.3221 | 30.6213 | 11.382 | 8.303 | 14.8307 | 30.9302 | 11.324 | 8.2607 | 14.1811 | 31.3031 | 11.0766 | 8.0802 | 13.0071 | 31.6248 | 10.7354 | 7.8313 | 11.8066 | 31.9532 | 10.3702 | 7.5649 | 10.6219 | 32.4197 | 9.9116 | 7.2304 | 7.5495 | 32.8666 | 9.1499 | 6.6747 | 5.1192 | 33.1878 | 8.4488 | 6.1633 | 2.9432 | 33.3868 | 7.8167 | 5.7022 | 1.6111 | 33.2992 | 7.6457 | 5.5775 | 2.4122 | 29.363 | 13.2791 | 9.6869 | 17.0381 | 29.6403 | 13.0634 | 9.5295 | 16.244 | 29.8297 | 11.2336 | 8.1948 | 15.8912 | 30.0542 | 9.2405 | 6.7409 | 15.6569 | 30.2973 | 7.6001 | 5.5442 | 15.3968 | 30.4524 | 5.8372 | 4.2582 | 15.1134 | 23.8513 | 3.8689 | 2.8223 | 14.7943 | 21.0048 | 3.4072 | 2.4855 | 14.4378 | 20.6333 | 3.3469 | 2.4415 | 14.0358 | 20.7862 | 3.3717 | 2.4596 | 13.6224 | 20.5171 | 3.3281 | 2.4278 | 12.5563 | 25.3185 | 4.1069 | 2.9959 | 11.6116 | 32.9518 | 6.2052 | 4.5266 | 10.396 | 33.2088 | 9.1602 | 6.6822 | 9.0002 | 33.2744 | 9.7258 | 7.0948 | 8.4517 | 29.363 | 13.2791 | 9.6869 | 17.0381 | 29.5935 | 12.9927 | 9.478 | 16.1433 | 29.8142 | 12.7052 | 9.2683 | 15.6704 | 30.1223 | 12.2021 | 8.9013 | 15.2767 | 30.3472 | 11.7895 | 8.6002 | 14.7577 | 30.575 | 11.2048 | 8.1738 | 14.2281 | 30.8554 | 11.1654 | 8.145 | 13.5434 | 31.2107 | 10.9048 | 7.9549 | 12.3067 | 31.4968 | 10.5659 | 7.7077 | 11.0731 | 31.8018 | 10.1961 | 7.4379 | 9.8532 | 32.751 | 9.7044 | 7.0792 | 6.6586 | 33.2049 | 8.9089 | 6.4989 | 4.0864 | 33.5324 | 8.1627 | 5.9546 | 1.6982 | 33.7291 | 7.4797 | 5.4564 | 0.084533 | 33.6618 | 7.2533 | 5.2912 | 0.59756
GRANE RD & PRINNY HILL | ROSSENDALE | PADIHAM | 378328 | 423395 | 24.3676 | 11.8952 | 8.6774 | 15.3903 | 24.4795 | 11.6878 | 8.5261 | 15.1367 | 24.5723 | 11.6764 | 8.5178 | 14.6661 | 24.6547 | 11.4139 | 8.3263 | 14.5378 | 24.7849 | 11.1857 | 8.1598 | 14.3485 | 24.9502 | 10.6664 | 7.781 | 14.0962 | 25.1375 | 10.1392 | 7.3964 | 13.7707 | 25.354 | 9.8705 | 7.2004 | 13.3426 | 25.5795 | 9.7007 | 7.0765 | 12.8058 | 25.8251 | 9.5385 | 6.9582 | 12.2147 | 26.6431 | 8.9579 | 6.5347 | 9.9348 | 27.3976 | 8.3802 | 6.1133 | 7.4359 | 27.8943 | 7.993 | 5.8308 | 5.6444 | 28.2682 | 8.021 | 5.8512 | 4.0849 | 28.5006 | 7.6569 | 5.5856 | 2.9789 | 24.3463 | 11.8952 | 8.6774 | 15.3903 | 24.4145 | 11.7823 | 8.595 | 15.1396 | 24.4892 | 11.5677 | 8.4385 | 14.8362 | 24.5644 | 11.4648 | 8.3634 | 14.7371 | 24.6213 | 11.3662 | 8.2915 | 14.6145 | 24.6907 | 11.2302 | 8.1923 | 14.4583 | 24.7822 | 10.8943 | 7.9472 | 14.2561 | 24.8999 | 10.8086 | 7.8847 | 14.005 | 25.0168 | 10.7139 | 7.8156 | 13.7391 | 25.1514 | 10.593 | 7.7274 | 13.4373 | 25.6664 | 10.3465 | 7.5476 | 12.3029 | 26.3057 | 10.1245 | 7.3857 | 10.8979 | 26.8796 | 9.8327 | 7.1728 | 9.4401 | 27.4639 | 9.7083 | 7.082 | 7.8666 | 27.8438 | 9.6286 | 7.0239 | 6.8299 | 24.3785 | 11.8952 | 8.6774 | 15.3903 | 24.4993 | 11.7428 | 8.5662 | 15.1369 | 24.581 | 11.6734 | 8.5156 | 14.67 | 24.6662 | 11.2713 | 8.2222 | 14.551 | 24.7973 | 11.0348 | 8.0497 | 14.3807 | 24.9592 | 10.4635 | 7.633 | 14.1608 | 25.1239 | 9.9923 | 7.2892 | 13.8857 | 25.3183 | 9.7155 | 7.0873 | 13.5308 | 25.5126 | 9.5525 | 6.9684 | 13.1 | 25.7279 | 9.3926 | 6.8518 | 12.6118 | 26.5287 | 8.7567 | 6.3879 | 10.4458 | 27.3623 | 8.1136 | 5.9188 | 7.8047 | 27.9408 | 7.6688 | 5.5943 | 5.8544 | 28.3454 | 7.7014 | 5.6181 | 4.2636 | 28.5113 | 7.3574 | 5.3671 | 3.2812 | 24.3785 | 11.8952 | 8.6774 | 15.3903 | 24.412 | 11.761 | 8.5795 | 15.2579 | 24.5007 | 11.8024 | 8.6097 | 14.84 | 24.5692 | 11.4502 | 8.3527 | 14.7493 | 24.6918 | 11.2041 | 8.1733 | 14.5877 | 24.8574 | 10.934 | 7.9762 | 14.3411 | 25.0308 | 10.4342 | 7.6116 | 13.9348 | 25.2647 | 9.8493 | 7.1849 | 13.1936 | 25.5174 | 9.2436 | 6.7431 | 12.3527 | 25.792 | 9.0221 | 6.5815 | 11.4574 | 26.6501 | 8.6977 | 6.3449 | 8.7216 | 27.3894 | 8.1564 | 5.95 | 6.3596 | 27.8643 | 7.6633 | 5.5903 | 4.7283 | 28.117 | 7.2277 | 5.2725 | 3.7373 | 28.1261 | 7.0699 | 5.1574 | 4.019 | 24.3676 | 11.8952 | 8.6774 | 15.3903 | 24.4597 | 11.7144 | 8.5455 | 15.1515 | 24.5467 | 11.6846 | 8.5237 | 14.7121 | 24.5969 | 11.4445 | 8.3486 | 14.6369 | 24.6739 | 11.2537 | 8.2094 | 14.5305 | 24.7919 | 10.7678 | 7.8549 | 14.3529 | 24.9557 | 10.2509 | 7.4779 | 14.0918 | 25.1487 | 9.982 | 7.2818 | 13.7538 | 25.3571 | 9.8232 | 7.1659 | 13.3208 | 25.5858 | 9.6942 | 7.0718 | 12.83 | 26.3018 | 9.2217 | 6.7271 | 11.0712 | 26.9998 | 8.8357 | 6.4455 | 9.3475 | 27.4726 | 8.5823 | 6.2607 | 8.1924 | 27.7954 | 8.7426 | 6.3776 | 7.4168 | 27.9174 | 8.6942 | 6.3423 | 7.1561 | 24.3676 | 11.8952 | 8.6774 | 15.3903 | 24.4421 | 11.775 | 8.5897 | 15.2299 | 24.528 | 11.7836 | 8.596 | 14.7721 | 24.6167 | 11.3985 | 8.315 | 14.641 | 24.7512 | 11.1281 | 8.1178 | 14.4546 | 24.913 | 10.8559 | 7.9192 | 14.2228 | 25.068 | 10.3799 | 7.572 | 13.8556 | 25.2976 | 9.8011 | 7.1498 | 13.151 | 25.5312 | 9.2316 | 6.7343 | 12.3707 | 25.7844 | 8.9925 | 6.5599 | 11.5334 | 26.6385 | 8.6613 | 6.3183 | 8.792 | 27.4503 | 8.0696 | 5.8867 | 6.1845 | 28.01 | 7.5284 | 5.4918 | 4.2759 | 28.3537 | 7.0602 | 5.1503 | 3.0827 | 28.3837 | 6.808 | 4.9663 | 3.246
QUEENS PARK | STUART ST | STALYBRIDGE | 385893 | 400645 | 21.8922 | 13.2241 | 9.6468 | 12.5872 | 21.9705 | 11.7397 | 8.5639 | 4.5321 | 22.1057 | 11.2303 | 8.1924 | 2.2086 | 22.2762 | 10.9862 | 8.0143 | 1.2552 | 22.4878 | 10.6759 | 7.7879 | 0.12044 | 22.7516 | 10.3558 | 7.5544 | -1.0348 | 23.0829 | 10.0438 | 7.3268 | -2.2044 | 23.4038 | 9.7439 | 7.1081 | -3.4012 | 23.6933 | 9.4151 | 6.8682 | -4.6486 | 24.0069 | 9.2247 | 6.7293 | -5.8943 | 24.8933 | 8.4218 | 6.1436 | -9.7173 | 25.6761 | 7.6503 | 5.5808 | -13.402 | 26.1793 | 7.0013 | 5.1074 | -16.6451 | 26.5273 | 6.4877 | 4.7327 | -20.4188 | 26.685 | 6.2508 | 4.5599 | -21.9421 | 21.863 | 13.2241 | 9.6468 | 12.5872 | 21.9189 | 12.6997 | 9.2643 | 9.8165 | 21.9852 | 12.4445 | 9.0781 | 8.6383 | 22.0601 | 12.2371 | 8.9268 | 7.7774 | 22.1571 | 12.0201 | 8.7685 | 6.9054 | 22.2832 | 11.8117 | 8.6164 | 6.0121 | 22.4367 | 11.4997 | 8.3889 | 5.0902 | 22.6169 | 11.2962 | 8.2405 | 4.1404 | 22.8007 | 11.0868 | 8.0876 | 3.1412 | 23.0097 | 10.8822 | 7.9384 | 2.13 | 23.777 | 10.2427 | 7.4719 | -0.92925 | 24.5416 | 9.6851 | 7.0651 | -3.9947 | 25.1765 | 9.127 | 6.658 | -6.9847 | 25.7596 | 8.5269 | 6.2202 | -10.7288 | 26.1249 | 8.1187 | 5.9224 | -12.2634 | 21.9015 | 13.2241 | 9.6468 | 12.5872 | 21.9918 | 11.5198 | 8.4035 | 3.3748 | 22.1451 | 10.9514 | 7.9889 | 0.78858 | 22.3376 | 10.6714 | 7.7847 | -0.20334 | 22.5718 | 10.3366 | 7.5404 | -1.3754 | 22.8562 | 10.0089 | 7.3014 | -2.5673 | 23.1736 | 9.6353 | 7.0289 | -3.7724 | 23.4103 | 9.3684 | 6.8342 | -5.0038 | 23.6671 | 9.098 | 6.6368 | -6.2613 | 23.9499 | 8.8084 | 6.4256 | -7.5194 | 24.8422 | 7.9381 | 5.7908 | -11.4152 | 25.6654 | 7.1499 | 5.2158 | -15.1084 | 26.1978 | 6.5403 | 4.7711 | -18.2791 | 26.4878 | 6.0147 | 4.3876 | -21.8655 | 26.4152 | 5.8389 | 4.2594 | -23.0219 | 21.9015 | 13.2241 | 9.6468 | 12.5872 | 21.9385 | 11.9573 | 8.7227 | 5.7385 | 22.0393 | 11.5341 | 8.4139 | 3.6733 | 22.1684 | 11.2836 | 8.2312 | 2.7393 | 22.349 | 10.9579 | 7.9936 | 1.6082 | 22.6247 | 10.5321 | 7.683 | 0.41756 | 22.9852 | 10.3038 | 7.5165 | -0.84315 | 23.3275 | 9.8968 | 7.2196 | -2.2535 | 23.6223 | 9.6084 | 7.0092 | -3.6869 | 23.9249 | 9.2121 | 6.7201 | -5.1117 | 24.8039 | 8.6292 | 6.2949 | -9.1679 | 25.5277 | 7.8492 | 5.7259 | -12.6715 | 25.9573 | 7.1961 | 5.2495 | -15.6498 | 26.1496 | 6.6603 | 4.8586 | -18.9345 | 25.9716 | 6.4376 | 4.6962 | -19.6689 | 21.8922 | 13.2241 | 9.6468 | 12.5872 | 21.9597 | 12.4221 | 9.0617 | 8.2873 | 22.0603 | 12.0472 | 8.7882 | 6.7643 | 22.1739 | 11.8319 | 8.6312 | 5.8797 | 22.3204 | 11.5445 | 8.4216 | 4.8421 | 22.5447 | 11.2372 | 8.1974 | 3.756 | 22.8466 | 10.9403 | 7.9808 | 2.6257 | 23.2057 | 10.6564 | 7.7737 | 1.4645 | 23.4514 | 10.295 | 7.5101 | 0.24016 | 23.7136 | 10.1324 | 7.3914 | -0.99665 | 24.5559 | 9.3886 | 6.8489 | -4.6312 | 25.3084 | 8.7085 | 6.3527 | -7.9257 | 25.8185 | 8.1063 | 5.9135 | -10.8795 | 26.1784 | 7.7138 | 5.6271 | -14.4251 | 26.3011 | 7.5522 | 5.5093 | -15.6512 | 21.8922 | 13.2241 | 9.6468 | 12.5872 | 21.9526 | 11.3328 | 8.2671 | 2.3397 | 22.0889 | 10.7676 | 7.8548 | -0.46538 | 22.2604 | 10.5005 | 7.66 | -1.4641 | 22.4691 | 10.1611 | 7.4124 | -2.6464 | 22.7217 | 9.7047 | 7.0795 | -3.8448 | 23.0334 | 9.5019 | 6.9315 | -5.1013 | 23.3472 | 9.0901 | 6.6311 | -6.536 | 23.6134 | 8.8019 | 6.4208 | -7.989 | 23.9055 | 8.4099 | 6.1349 | -9.4303 | 24.8577 | 7.7876 | 5.6809 | -13.5518 | 25.7104 | 6.9922 | 5.1007 | -17.1308 | 26.2266 | 6.3188 | 4.6095 | -20.1894 | 26.4866 | 5.7628 | 4.2039 | -23.5287 | 26.4796 | 5.5243 | 4.0299 | -24.3308
RADCLIFFE | - | KEARSLEY | 377524 | 406160 | 44.8756 | 13.6937 | 9.8419 | 8.5587 | 45.0841 | 13.2855 | 9.5486 | 6.2427 | 45.3831 | 12.7397 | 9.1563 | 5.5268 | 45.7576 | 12.2322 | 8.7915 | 5.0325 | 46.2017 | 11.6743 | 8.3905 | 4.3609 | 46.5537 | 11.0841 | 7.9664 | 3.6603 | 46.9724 | 10.5185 | 7.5598 | 2.9865 | 47.4879 | 10.3278 | 7.4228 | 2.327 | 47.9293 | 10.1121 | 7.2678 | 1.487 | 48.3686 | 9.8993 | 7.1148 | 0.67347 | 50.0951 | 8.845 | 6.357 | -4.4055 | 45.9505 | 7.5654 | 5.4374 | -11.0301 | 38.7722 | 6.3835 | 4.588 | -16.0103 | 31.0014 | 5.1041 | 3.6684 | -20.6205 | 24.8807 | 4.0964 | 2.9442 | -23.8178 | 44.8119 | 13.6937 | 9.8419 | 8.5587 | 44.9692 | 13.5254 | 9.7209 | 7.6647 | 45.1421 | 13.4337 | 9.6551 | 7.3988 | 45.3623 | 13.3045 | 9.5622 | 7.0684 | 45.6 | 13.138 | 9.4425 | 6.6126 | 45.8598 | 12.9845 | 9.3322 | 6.0917 | 46.1791 | 11.2207 | 8.0645 | 5.4206 | 46.5498 | 11.0156 | 7.9171 | 4.5918 | 46.8231 | 10.8266 | 7.7813 | 3.8429 | 47.1151 | 10.687 | 7.6809 | 3.0131 | 48.4142 | 10.2365 | 7.3572 | 0.11898 | 49.3389 | 10.4492 | 7.51 | -2.5147 | 50.2251 | 10.2847 | 7.3918 | -5.0634 | 51.3901 | 9.6303 | 6.9215 | -7.9863 | 51.9543 | 9.0846 | 6.5293 | -9.7724 | 44.9025 | 13.6937 | 9.8419 | 8.5587 | 45.1609 | 13.1993 | 9.4866 | 5.8113 | 45.5282 | 12.5569 | 9.0249 | 4.8801 | 45.9916 | 11.9836 | 8.6129 | 4.2456 | 46.4296 | 11.3552 | 8.1612 | 3.4264 | 46.8571 | 10.7303 | 7.7121 | 2.5767 | 47.3615 | 10.1298 | 7.2805 | 1.784 | 47.9723 | 9.8864 | 7.1056 | 0.99243 | 48.4732 | 9.6259 | 6.9184 | 0.077124 | 48.9352 | 9.3546 | 6.7233 | -0.88554 | 48.8071 | 8.0357 | 5.7754 | -6.8787 | 40.189 | 6.6168 | 4.7556 | -13.5736 | 32.519 | 5.354 | 3.848 | -18.139 | 25.4601 | 4.1918 | 3.0127 | -21.7991 | 20.4026 | 3.3591 | 2.4143 | -23.4355 | 44.9025 | 13.6937 | 9.8419 | 8.5587 | 44.9233 | 13.4046 | 9.6342 | 7.0788 | 45.1086 | 12.8577 | 9.2411 | 6.4846 | 45.7765 | 12.239 | 8.7964 | 5.5263 | 46.5368 | 11.5614 | 8.3094 | 4.333 | 46.9207 | 10.9394 | 7.8624 | 3.4863 | 47.3445 | 10.2453 | 7.3635 | 2.3263 | 47.8612 | 9.7521 | 7.009 | 0.11643 | 48.3403 | 9.2625 | 6.6571 | -2.1543 | 48.8266 | 8.615 | 6.1918 | -4.368 | 42.9005 | 7.0632 | 5.0765 | -10.6144 | 34.2653 | 5.6415 | 4.0547 | -15.8547 | 27.2513 | 4.4867 | 3.2247 | -19.2585 | 20.9114 | 3.4429 | 2.4745 | -21.0917 | 17.5441 | 2.8885 | 2.076 | -20.0509 | 44.8756 | 13.6937 | 9.8419 | 8.5587 | 45.0548 | 13.431 | 9.6531 | 7.1456 | 45.263 | 12.9453 | 9.3041 | 6.723 | 45.4983 | 12.4695 | 8.9621 | 6.4221 | 45.8071 | 11.9711 | 8.6039 | 6.0552 | 46.231 | 11.4184 | 8.2066 | 5.5818 | 46.645 | 10.8721 | 7.814 | 5.0251 | 47.1065 | 10.6904 | 7.6834 | 4.432 | 47.4911 | 10.483 | 7.5343 | 3.6245 | 47.8866 | 10.2653 | 7.3779 | 2.7751 | 49.5314 | 9.467 | 6.8041 | -0.74418 | 50.7144 | 8.6915 | 6.2468 | -4.298 | 47.996 | 7.9022 | 5.6795 | -6.825 | 42.6869 | 7.0281 | 5.0512 | -9.16 | 38.5186 | 6.3418 | 4.558 | -10.6388 | 44.8756 | 13.6937 | 9.8419 | 8.5587 | 44.9805 | 13.2373 | 9.5139 | 6.0493 | 45.2909 | 12.6186 | 9.0692 | 5.0546 | 46.1074 | 11.9532 | 8.591 | 3.846 | 46.9578 | 11.239 | 8.0777 | 2.431 | 47.2849 | 10.5964 | 7.6159 | 1.445 | 47.6946 | 9.8755 | 7.0977 | 0.11369 | 48.2523 | 9.3428 | 6.7148 | -2.3413 | 48.7462 | 8.8233 | 6.3415 | -4.7987 | 49.2407 | 8.1582 | 5.8634 | -7.1975 | 39.3164 | 6.4731 | 4.6524 | -14.0517 | 30.0754 | 4.9517 | 3.5589 | -19.8335 | 22.71 | 3.739 | 2.6873 | -23.5544 | 16.0189 | 2.6374 | 1.8955 | -25.7242 | 12.203 | 2.0091 | 1.444 | -25.1549
RANDAL ST | BLACKBURN | PENWORTHAM EAST / ROCHDALE | 368092 | 428515 | 32.4462 | 13.7225 | 10.0104 | 17.5698 | 32.533 | 13.4459 | 9.8086 | 17.2432 | 32.6548 | 13.1227 | 9.5729 | 16.7762 | 32.8075 | 12.6996 | 9.2642 | 16.366 | 32.9843 | 12.2835 | 8.9606 | 15.9787 | 33.1778 | 12.2975 | 8.9708 | 15.5939 | 33.3909 | 12.1591 | 8.8699 | 15.2235 | 33.6444 | 11.9842 | 8.7423 | 14.84 | 33.8066 | 11.7466 | 8.569 | 14.4211 | 33.9598 | 11.46 | 8.3599 | 14.0188 | 34.4325 | 10.8377 | 7.9059 | 12.7011 | 34.877 | 10.3913 | 7.5803 | 11.2037 | 35.2001 | 9.8842 | 7.2104 | 9.1836 | 35.4883 | 9.3032 | 6.7866 | 7.0415 | 35.6836 | 8.7466 | 6.3805 | 5.4177 | 32.4262 | 13.7225 | 10.0104 | 17.5698 | 32.5351 | 13.6038 | 9.9238 | 17.3487 | 32.6585 | 13.4159 | 9.7867 | 16.9904 | 32.8055 | 13.1776 | 9.6128 | 16.6672 | 32.9869 | 12.8608 | 9.3818 | 16.3446 | 33.2092 | 12.4746 | 9.1 | 15.9728 | 33.3962 | 12.2644 | 8.9467 | 15.5432 | 33.5751 | 12.0662 | 8.8021 | 15.0514 | 33.6807 | 11.9182 | 8.6942 | 14.7601 | 33.7901 | 11.7819 | 8.5947 | 14.4696 | 34.1163 | 11.3979 | 8.3146 | 13.7341 | 34.4225 | 11.034 | 8.0492 | 13.194 | 34.6165 | 10.8012 | 7.8793 | 12.7364 | 34.7929 | 10.9209 | 7.9667 | 12.3033 | 34.9213 | 10.8166 | 7.8906 | 12.0387 | 32.4546 | 13.7225 | 10.0104 | 17.5698 | 32.5493 | 13.4191 | 9.789 | 17.238 | 32.6838 | 12.9954 | 9.48 | 16.71 | 32.8555 | 12.4681 | 9.0953 | 16.2368 | 33.0556 | 12.2032 | 8.9021 | 15.7886 | 33.277 | 12.1055 | 8.8308 | 15.3434 | 33.5234 | 11.9069 | 8.6859 | 14.9115 | 33.8185 | 11.6104 | 8.4696 | 14.4674 | 34.0093 | 11.2972 | 8.2411 | 14.0368 | 34.1884 | 10.8525 | 7.9168 | 13.6292 | 34.6649 | 10.3337 | 7.5383 | 12.3632 | 35.1422 | 9.7469 | 7.1103 | 11.0534 | 35.496 | 9.1423 | 6.6692 | 9.3577 | 35.8069 | 8.487 | 6.1911 | 7.4901 | 36.0134 | 7.9013 | 5.7639 | 6.2141 | 32.4546 | 13.7225 | 10.0104 | 17.5698 | 32.4856 | 13.4471 | 9.8094 | 17.3529 | 32.5459 | 13.2089 | 9.6357 | 16.9184 | 32.6297 | 12.8569 | 9.3789 | 16.531 | 32.7449 | 12.7605 | 9.3086 | 16.1602 | 32.9144 | 12.4241 | 9.0632 | 15.7592 | 33.1208 | 11.8107 | 8.6157 | 15.2765 | 33.3607 | 11.7308 | 8.5575 | 14.5351 | 33.5409 | 11.4125 | 8.3253 | 13.7505 | 33.7143 | 11.0457 | 8.0577 | 12.9878 | 34.2383 | 10.145 | 7.4006 | 10.4632 | 34.7904 | 9.3978 | 6.8555 | 8.3346 | 35.1345 | 8.7405 | 6.3761 | 6.6327 | 35.4138 | 8.1956 | 5.9786 | 5.6433 | 35.4867 | 7.9868 | 5.8263 | 6.804 | 32.4462 | 13.7225 | 10.0104 | 17.5698 | 32.523 | 13.4702 | 9.8263 | 17.264 | 32.614 | 13.1509 | 9.5934 | 16.8364 | 32.7199 | 12.7376 | 9.2919 | 16.4852 | 32.8482 | 12.3642 | 9.0195 | 16.1778 | 33.0259 | 12.376 | 9.0281 | 15.8386 | 33.2438 | 12.2615 | 8.9446 | 15.4745 | 33.4781 | 12.0826 | 8.8141 | 15.1023 | 33.622 | 11.8463 | 8.6417 | 14.6894 | 33.764 | 11.5478 | 8.4239 | 14.2804 | 34.2052 | 10.9304 | 7.9736 | 13.3369 | 34.6318 | 10.7994 | 7.878 | 12.7575 | 34.918 | 10.5793 | 7.7175 | 12.3836 | 35.1749 | 10.348 | 7.5487 | 12.1227 | 35.315 | 10.1153 | 7.379 | 12.2418 | 32.4462 | 13.7225 | 10.0104 | 17.5698 | 32.5216 | 13.4226 | 9.7916 | 17.2744 | 32.6423 | 13.1601 | 9.6001 | 16.7461 | 32.7967 | 12.7705 | 9.3159 | 16.2541 | 32.9753 | 12.6515 | 9.2291 | 15.7866 | 33.1702 | 12.3223 | 8.9889 | 15.3246 | 33.3919 | 11.7703 | 8.5863 | 14.7844 | 33.6777 | 11.5617 | 8.4341 | 13.949 | 33.8734 | 11.2501 | 8.2068 | 13.1267 | 34.0585 | 10.8792 | 7.9362 | 12.3302 | 34.5841 | 9.9725 | 7.2748 | 9.755 | 35.0143 | 9.194 | 6.7069 | 7.5527 | 35.3237 | 8.5076 | 6.2062 | 5.7403 | 35.5615 | 7.9363 | 5.7894 | 4.6155 | 35.6301 | 7.6973 | 5.6151 | 5.6135
RAWTENSTALL RD | ROSSENDALE | PADIHAM | 379395 | 422143 | 30.4563 | 17.2672 | 12.5962 | 15.515 | 30.5123 | 17.1328 | 12.4982 | 15.161 | 30.5728 | 16.8024 | 12.2571 | 14.8719 | 30.6372 | 16.6645 | 12.1565 | 14.6533 | 30.7285 | 16.4337 | 11.9881 | 14.3892 | 30.836 | 16.1566 | 11.786 | 14.1054 | 30.9597 | 15.974 | 11.6528 | 13.8307 | 31.1045 | 15.8003 | 11.5261 | 13.5525 | 31.2328 | 15.6795 | 11.4379 | 13.2403 | 31.3625 | 15.5581 | 11.3494 | 12.9379 | 31.8983 | 15.0196 | 10.9566 | 11.1653 | 32.3059 | 14.5283 | 10.5982 | 8.4215 | 32.5881 | 14.12 | 10.3004 | 6.3311 | 32.8355 | 13.6567 | 9.9624 | 4.3064 | 33.0033 | 13.2692 | 9.6797 | 2.8977 | 30.4464 | 17.2672 | 12.5962 | 15.515 | 30.4983 | 17.1886 | 12.5389 | 15.2958 | 30.5498 | 17.0511 | 12.4385 | 15.1032 | 30.6061 | 16.9138 | 12.3384 | 14.9432 | 30.6791 | 16.7616 | 12.2273 | 14.7852 | 30.7659 | 16.5936 | 12.1048 | 14.6137 | 30.8769 | 16.3147 | 11.9014 | 14.3651 | 31.0075 | 16.1817 | 11.8043 | 14.0224 | 31.0813 | 16.0761 | 11.7273 | 13.7838 | 31.1594 | 15.9683 | 11.6487 | 13.537 | 31.4116 | 15.6432 | 11.4115 | 12.7449 | 31.6933 | 15.3378 | 11.1887 | 11.8621 | 31.9735 | 15.2362 | 11.1146 | 11.0016 | 32.2843 | 15.0401 | 10.9716 | 10.0244 | 32.5126 | 14.794 | 10.792 | 9.2924 | 30.4593 | 17.2672 | 12.5962 | 15.515 | 30.5366 | 17.0929 | 12.4691 | 15.0614 | 30.6225 | 16.6595 | 12.1529 | 14.5311 | 30.7162 | 16.5022 | 12.0382 | 14.0775 | 30.8395 | 16.2193 | 11.8317 | 13.568 | 30.9817 | 15.931 | 11.6215 | 13.0318 | 31.1441 | 15.6494 | 11.416 | 12.51 | 31.3254 | 15.375 | 11.2158 | 11.9693 | 31.4831 | 15.1642 | 11.0621 | 11.4187 | 31.644 | 15.0492 | 10.9782 | 10.8514 | 32.221 | 14.441 | 10.5345 | 8.4782 | 32.7132 | 13.8339 | 10.0916 | 5.7595 | 33.0572 | 13.3576 | 9.7442 | 3.9273 | 33.3492 | 12.9404 | 9.4398 | 2.4368 | 33.5096 | 12.611 | 9.1996 | 1.8498 | 30.4593 | 17.2672 | 12.5962 | 15.515 | 30.4521 | 17.1523 | 12.5124 | 15.3786 | 30.5015 | 16.9619 | 12.3735 | 14.9284 | 30.5655 | 16.6013 | 12.1104 | 14.5038 | 30.6644 | 16.4344 | 11.9886 | 14.0047 | 30.7921 | 16.2473 | 11.8521 | 13.468 | 30.9665 | 16.0184 | 11.6852 | 12.7869 | 31.2083 | 15.5803 | 11.3656 | 11.6188 | 31.4013 | 15.1786 | 11.0726 | 10.4699 | 31.5585 | 14.8306 | 10.8187 | 9.3448 | 32.0455 | 14.0601 | 10.2567 | 6.3232 | 32.4851 | 13.5103 | 9.8556 | 4.0556 | 32.7767 | 13.037 | 9.5103 | 2.6821 | 33.0009 | 12.655 | 9.2317 | 2.1104 | 33.0817 | 12.5663 | 9.1669 | 2.8155 | 30.4563 | 17.2672 | 12.5962 | 15.515 | 30.507 | 17.1527 | 12.5127 | 15.209 | 30.5562 | 16.8281 | 12.2759 | 14.9534 | 30.6014 | 16.7052 | 12.1862 | 14.7821 | 30.6638 | 16.4963 | 12.0338 | 14.6177 | 30.7492 | 16.2326 | 11.8415 | 14.425 | 30.8576 | 16.0649 | 11.7191 | 14.2035 | 30.9827 | 15.8951 | 11.5953 | 13.953 | 31.0989 | 15.7745 | 11.5073 | 13.639 | 31.2202 | 15.6499 | 11.4164 | 13.3202 | 31.6257 | 15.2584 | 11.1308 | 12.258 | 32.0409 | 15.0534 | 10.9812 | 11.139 | 32.3386 | 14.8897 | 10.8618 | 10.3611 | 32.5559 | 14.695 | 10.7198 | 9.5764 | 32.6985 | 14.4814 | 10.5639 | 8.9842 | 30.4563 | 17.2672 | 12.5962 | 15.515 | 30.466 | 17.1208 | 12.4894 | 15.2519 | 30.537 | 16.9172 | 12.3409 | 14.7306 | 30.6259 | 16.5454 | 12.0696 | 14.2428 | 30.7466 | 16.362 | 11.9358 | 13.6854 | 30.882 | 16.1753 | 11.7997 | 13.108 | 31.0592 | 15.9285 | 11.6196 | 12.3752 | 31.3136 | 15.4773 | 11.2905 | 11.1416 | 31.526 | 15.068 | 10.9919 | 9.9524 | 31.6826 | 14.7105 | 10.7311 | 8.785 | 32.1731 | 13.911 | 10.1479 | 5.6155 | 32.6219 | 13.329 | 9.7233 | 3.2118 | 32.9303 | 12.8239 | 9.3549 | 1.6944 | 33.1666 | 12.4083 | 9.0517 | 0.94159 | 33.2887 | 12.2805 | 8.9584 | 1.425
REDDISH VALE | VERNON PARK | BREDBURY | 390147 | 393309 | 29.6548 | 9.7675 | 7.1252 | 17.5292 | 29.7234 | 9.4927 | 6.9248 | 17.3776 | 29.8068 | 8.8514 | 6.457 | 17.237 | 29.8953 | 8.9502 | 6.5291 | 17.0708 | 30.0048 | 8.4307 | 6.1501 | 16.8219 | 30.1282 | 8.4965 | 6.1981 | 16.5738 | 30.2695 | 8.3997 | 6.1275 | 16.3522 | 30.4387 | 8.2462 | 6.0155 | 16.1536 | 30.5629 | 8.0738 | 5.8897 | 15.9156 | 30.6797 | 7.9112 | 5.7711 | 15.7042 | 31.0645 | 7.3735 | 5.3789 | 14.041 | 31.4998 | 6.642 | 4.8452 | 10.981 | 31.834 | 5.9597 | 4.3475 | 8.3791 | 31.9032 | 5.175 | 3.7751 | 5.5354 | 28.2313 | 4.5794 | 3.3406 | 2.9528 | 29.6359 | 9.7675 | 7.1252 | 17.5292 | 29.7082 | 9.5791 | 6.9878 | 17.3654 | 29.7772 | 9.0453 | 6.5984 | 17.2174 | 29.8628 | 9.034 | 6.5901 | 17.0568 | 29.9772 | 8.8135 | 6.4293 | 16.8436 | 30.1134 | 8.509 | 6.2072 | 16.6221 | 30.2715 | 8.3101 | 6.0621 | 16.3391 | 30.4537 | 8.2225 | 5.9982 | 15.9836 | 30.5304 | 8.1359 | 5.935 | 15.6789 | 30.6091 | 8.0506 | 5.8728 | 15.3694 | 30.8477 | 7.7746 | 5.6715 | 14.4507 | 31.0752 | 7.5178 | 5.4841 | 13.5562 | 31.275 | 7.1978 | 5.2507 | 12.6928 | 31.4795 | 7.0482 | 5.1415 | 11.7335 | 31.6429 | 6.7891 | 4.9526 | 10.9925 | 29.661 | 9.7675 | 7.1252 | 17.5292 | 29.7365 | 9.4467 | 6.8912 | 17.3938 | 29.8241 | 8.9357 | 6.5185 | 17.2766 | 29.9242 | 8.7723 | 6.3992 | 17.1581 | 30.048 | 8.4599 | 6.1714 | 16.9548 | 30.1885 | 8.43 | 6.1496 | 16.7601 | 30.3514 | 8.2833 | 6.0425 | 16.6117 | 30.5463 | 8.0647 | 5.8831 | 16.4934 | 30.6867 | 7.8972 | 5.7609 | 16.2635 | 30.8181 | 7.7165 | 5.6291 | 16.107 | 31.2458 | 7.0957 | 5.1762 | 14.6683 | 31.7177 | 6.2862 | 4.5857 | 11.8126 | 32.0768 | 5.5576 | 4.0542 | 9.3563 | 29.6071 | 4.8026 | 3.5034 | 6.6674 | 25.5032 | 4.1369 | 3.0178 | 4.2944 | 29.661 | 9.7675 | 7.1252 | 17.5292 | 29.657 | 9.4947 | 6.9263 | 17.6355 | 29.6944 | 9.0978 | 6.6367 | 17.5929 | 29.7375 | 8.7581 | 6.3889 | 17.498 | 29.8094 | 8.6547 | 6.3135 | 17.2942 | 29.9207 | 8.5849 | 6.2626 | 17.0653 | 30.0659 | 8.4434 | 6.1593 | 16.6905 | 30.2456 | 8.1419 | 5.9394 | 15.7626 | 30.3917 | 7.8412 | 5.7201 | 14.7117 | 30.5339 | 7.5329 | 5.4952 | 13.725 | 30.965 | 6.6847 | 4.8764 | 10.9005 | 31.4173 | 5.8733 | 4.2845 | 8.1433 | 31.7581 | 5.1556 | 3.7609 | 5.8745 | 27.8691 | 4.5206 | 3.2978 | 4.328 | 27.3935 | 4.4435 | 3.2415 | 5.0643 | 29.6548 | 9.7675 | 7.1252 | 17.5292 | 29.7153 | 9.5254 | 6.9487 | 17.4008 | 29.7777 | 8.8388 | 6.4478 | 17.3001 | 29.832 | 9.0104 | 6.573 | 17.2247 | 29.9052 | 8.544 | 6.2327 | 17.1095 | 30.0144 | 8.5934 | 6.2688 | 16.9714 | 30.1568 | 8.5234 | 6.2177 | 16.8165 | 30.3116 | 8.3869 | 6.1182 | 16.6569 | 30.4226 | 8.21 | 5.9891 | 16.4249 | 30.5319 | 8.051 | 5.8731 | 16.1967 | 30.8769 | 7.6745 | 5.5984 | 15.3966 | 31.2443 | 7.333 | 5.3493 | 14.4555 | 31.5227 | 7.0068 | 5.1114 | 13.7709 | 31.7899 | 6.5907 | 4.8078 | 13.0011 | 31.9638 | 6.4245 | 4.6866 | 12.5141 | 29.6548 | 9.7675 | 7.1252 | 17.5292 | 29.6783 | 9.4538 | 6.8964 | 17.5777 | 29.7529 | 9.0622 | 6.6107 | 17.4448 | 29.8408 | 8.6924 | 6.341 | 17.2404 | 29.9521 | 8.5655 | 6.2484 | 16.9446 | 30.0754 | 8.4812 | 6.1869 | 16.6562 | 30.2243 | 8.3248 | 6.0728 | 16.2096 | 30.4302 | 8.0077 | 5.8415 | 15.1771 | 30.59 | 7.6874 | 5.6079 | 14.0443 | 30.743 | 7.3638 | 5.3718 | 12.9817 | 31.1817 | 6.4784 | 4.7259 | 9.9552 | 31.5999 | 5.6364 | 4.1117 | 7.0255 | 30.1123 | 4.8845 | 3.5632 | 4.5715 | 25.8829 | 4.1985 | 3.0627 | 2.7828 | 25.0117 | 4.0571 | 2.9596 | 3.2325
RIBBLESDALE T13 & RIBBLESDALE T14 | PADIHAM | PADIHAM | 374759 | 443587 | 22.7599 | 17.2335 | 12.386 | 4.6917 | 22.8404 | 16.9323 | 12.1696 | 3.3553 | 22.9326 | 16.5491 | 11.8941 | 2.9941 | 23.0059 | 16.0837 | 11.5597 | 2.8525 | 23.097 | 15.8092 | 11.3624 | 2.6887 | 23.2038 | 14.9844 | 10.7696 | 2.5213 | 23.3285 | 14.958 | 10.7506 | 2.365 | 23.4763 | 15.2098 | 10.9316 | 2.2105 | 23.8555 | 15.1115 | 10.861 | 1.7695 | 23.9955 | 15.0294 | 10.8019 | 1.5861 | 24.5383 | 14.5476 | 10.4557 | 0.47301 | 25.2243 | 13.8913 | 9.984 | -1.4344 | 25.8876 | 13.2928 | 9.5538 | -3.1482 | 26.3062 | 12.7354 | 9.1532 | -4.9235 | 26.502 | 12.0383 | 8.6522 | -6.5944 | 22.7466 | 17.2335 | 12.386 | 4.6917 | 22.8228 | 17.0778 | 12.2741 | 4.0232 | 22.9201 | 16.9869 | 12.2088 | 3.7591 | 23.0171 | 16.8879 | 12.1377 | 3.5867 | 23.106 | 16.7614 | 12.0467 | 3.4281 | 23.2078 | 16.5914 | 11.9245 | 3.2711 | 23.3352 | 16.4295 | 11.8082 | 3.0689 | 23.4935 | 16.3011 | 11.7159 | 2.7998 | 23.5902 | 16.2029 | 11.6453 | 2.5622 | 23.6917 | 16.0758 | 11.554 | 2.3293 | 24.2445 | 15.6291 | 11.233 | 1.4378 | 24.6633 | 15.2192 | 10.9384 | 0.72257 | 25.0181 | 14.5162 | 10.433 | 0.10407 | 25.4007 | 14.5364 | 10.4476 | -0.6112 | 25.8452 | 14.0751 | 10.1161 | -1.3494 | 22.7655 | 17.2335 | 12.386 | 4.6917 | 22.8437 | 16.8587 | 12.1167 | 3.1581 | 22.9358 | 16.3785 | 11.7716 | 2.7625 | 23.0117 | 15.9644 | 11.4739 | 2.6184 | 23.1045 | 15.4992 | 11.1396 | 2.4544 | 23.2119 | 14.721 | 10.5803 | 2.2877 | 23.3369 | 14.9417 | 10.7389 | 2.1309 | 23.7223 | 14.9651 | 10.7557 | 1.7397 | 23.8447 | 14.7616 | 10.6094 | 1.5851 | 23.969 | 14.6398 | 10.5219 | 1.4521 | 24.5447 | 13.9298 | 10.0117 | 0.4412 | 25.6098 | 13.1141 | 9.4253 | -1.6703 | 26.0868 | 12.627 | 9.0753 | -3.0163 | 26.4952 | 11.866 | 8.5284 | -4.3434 | 26.6959 | 11.1973 | 8.0477 | -5.5559 | 22.7655 | 17.2335 | 12.386 | 4.6917 | 22.781 | 16.9546 | 12.1856 | 3.7174 | 22.8385 | 16.6849 | 11.9918 | 3.4438 | 22.8891 | 16.0916 | 11.5653 | 3.3225 | 22.9586 | 15.878 | 11.4118 | 3.1835 | 23.3606 | 15.5585 | 11.1822 | 2.7274 | 23.4873 | 14.7472 | 10.5991 | 2.4872 | 23.6982 | 14.9007 | 10.7094 | 1.9115 | 24.3613 | 14.3569 | 10.3186 | 0.84353 | 24.5576 | 14.2714 | 10.2572 | 0.26273 | 25.1818 | 13.5659 | 9.7501 | -1.4267 | 25.7334 | 12.9145 | 9.2819 | -3.0298 | 26.079 | 12.1818 | 8.7553 | -4.5392 | 26.3005 | 11.4991 | 8.2647 | -5.4858 | 26.2345 | 11.2386 | 8.0774 | -4.5748 | 22.7599 | 17.2335 | 12.386 | 4.6917 | 22.8262 | 16.979 | 12.2031 | 3.5758 | 22.9087 | 16.616 | 11.9422 | 3.2635 | 22.9648 | 16.1514 | 11.6083 | 3.147 | 23.025 | 15.8923 | 11.4221 | 3.052 | 23.1035 | 15.0759 | 10.8353 | 2.9576 | 23.2039 | 15.0627 | 10.8259 | 2.8466 | 23.3226 | 15.3349 | 11.0215 | 2.7133 | 23.681 | 15.2294 | 10.9456 | 2.2652 | 23.8057 | 15.1343 | 10.8774 | 2.0607 | 24.2411 | 14.7568 | 10.606 | 1.386 | 24.7346 | 14.303 | 10.2799 | 0.60546 | 25.2354 | 13.9575 | 10.0316 | -0.071691 | 25.4844 | 13.6754 | 9.8288 | -0.51667 | 25.5642 | 13.2877 | 9.5501 | -0.64049 | 22.7599 | 17.2335 | 12.386 | 4.6917 | 22.7909 | 16.8414 | 12.1042 | 3.101 | 22.8712 | 16.5116 | 11.8672 | 2.684 | 22.9453 | 15.9407 | 11.4569 | 2.5151 | 23.0344 | 15.7191 | 11.2977 | 2.3321 | 23.4411 | 15.3918 | 11.0624 | 1.8477 | 23.5651 | 14.608 | 10.4991 | 1.5827 | 23.7826 | 14.6931 | 10.5602 | 0.96464 | 24.4379 | 14.1982 | 10.2045 | -0.11836 | 24.6275 | 14.0808 | 10.1202 | -0.71308 | 25.2455 | 13.328 | 9.5791 | -2.4451 | 25.804 | 12.6488 | 9.091 | -4.0963 | 26.1804 | 11.9042 | 8.5558 | -5.7676 | 26.4216 | 11.1772 | 8.0333 | -6.9376 | 26.379 | 10.8648 | 7.8088 | -6.3264
RIBBLETON | PRESTON EAST | PENWORTHAM EAST / ROCHDALE | 356730 | 431506 | 28.7025 | 7.8456 | 5.7233 | 17.8384 | 28.7329 | 7.4404 | 5.4276 | 15.3515 | 28.7656 | 7.1155 | 5.1906 | 13.3925 | 28.823 | 6.8508 | 4.9976 | 11.8437 | 28.9259 | 6.5624 | 4.7871 | 10.1925 | 29.0655 | 6.2157 | 4.5342 | 8.5096 | 29.2487 | 6.1461 | 4.4835 | 8.2862 | 29.4816 | 6.0731 | 4.4302 | 8.0249 | 29.7313 | 5.9785 | 4.3612 | 7.7069 | 30.0067 | 5.8757 | 4.2862 | 7.3848 | 31.0044 | 5.4464 | 3.9731 | 5.7514 | 31.1935 | 5.0599 | 3.6911 | 3.428 | 29.8643 | 4.8443 | 3.5338 | 1.6077 | 32.7696 | 6.1955 | 4.5196 | -0.046036 | 32.9716 | 7.5022 | 5.4728 | -1.5279 | 28.6901 | 7.8456 | 5.7233 | 17.8384 | 28.7288 | 7.8002 | 5.6901 | 17.5884 | 28.7572 | 7.695 | 5.6134 | 16.9966 | 28.7988 | 7.5772 | 5.5275 | 16.4341 | 28.8627 | 7.4519 | 5.4361 | 15.8377 | 28.9457 | 7.3266 | 5.3447 | 15.2222 | 29.0546 | 7.1769 | 5.2354 | 15.0303 | 29.1901 | 7.1003 | 5.1795 | 14.7734 | 29.2896 | 7.0309 | 5.1289 | 14.5395 | 29.4069 | 6.9599 | 5.0771 | 14.2895 | 29.8745 | 6.7355 | 4.9134 | 13.4488 | 30.4786 | 6.5281 | 4.7621 | 12.5189 | 31.1187 | 6.3837 | 4.6568 | 11.5875 | 31.8125 | 7.4668 | 5.4469 | 10.6109 | 32.2633 | 8.4733 | 6.1812 | 10.0005 | 28.705 | 7.8456 | 5.7233 | 17.8384 | 28.736 | 7.3661 | 5.3735 | 14.9568 | 28.7698 | 7.0094 | 5.1133 | 12.9426 | 28.8267 | 6.7274 | 4.9076 | 11.4212 | 28.926 | 6.4127 | 4.678 | 9.8002 | 29.0567 | 6.0863 | 4.4398 | 8.1552 | 29.224 | 6.0292 | 4.3983 | 8.0215 | 29.4319 | 5.9325 | 4.3277 | 7.8375 | 29.6463 | 5.8118 | 4.2396 | 7.6174 | 29.8881 | 5.6892 | 4.1502 | 7.379 | 30.8795 | 5.3366 | 3.893 | 5.9126 | 30.0234 | 4.8701 | 3.5527 | 3.6128 | 28.4099 | 4.6084 | 3.3617 | 1.792 | 32.8892 | 5.9002 | 4.3041 | 0.1992 | 33.0896 | 7.2413 | 5.2825 | -1.1523 | 28.705 | 7.8456 | 5.7233 | 17.8384 | 28.6704 | 7.5282 | 5.4917 | 15.9917 | 28.6768 | 7.2326 | 5.2761 | 14.1751 | 28.7134 | 6.9668 | 5.0822 | 12.6666 | 28.8012 | 6.6269 | 4.8342 | 11.0372 | 28.9381 | 6.353 | 4.6345 | 9.3664 | 29.1425 | 6.2639 | 4.5695 | 9.0958 | 29.4571 | 6.1067 | 4.4548 | 8.4233 | 29.7985 | 5.9283 | 4.3246 | 7.6747 | 30.1689 | 5.7559 | 4.1988 | 6.9008 | 31.133 | 5.7193 | 4.1721 | 4.5951 | 31.875 | 5.2701 | 3.8445 | 2.4798 | 31.9153 | 5.177 | 3.7765 | 0.88646 | 32.6054 | 7.646 | 5.5777 | 0.030573 | 32.6511 | 7.5776 | 5.5277 | 0.59672 | 28.7025 | 7.8456 | 5.7233 | 17.8384 | 28.7269 | 7.7582 | 5.6595 | 17.4259 | 28.745 | 7.4949 | 5.4674 | 15.851 | 28.774 | 7.2429 | 5.2836 | 14.3657 | 28.8311 | 6.9815 | 5.0929 | 12.8539 | 28.9277 | 6.6608 | 4.859 | 11.3106 | 29.0702 | 6.6054 | 4.8185 | 11.1974 | 29.2543 | 6.5485 | 4.777 | 11.0134 | 29.4542 | 6.4619 | 4.7139 | 10.7479 | 29.6826 | 6.3667 | 4.6444 | 10.4613 | 30.51 | 6.0316 | 4.3999 | 9.4098 | 31.3241 | 5.8614 | 4.2758 | 8.316 | 31.8777 | 5.8415 | 4.2613 | 7.5821 | 32.2576 | 7.409 | 5.4047 | 7.0427 | 32.4096 | 9.0029 | 6.5675 | 6.8983 | 28.7025 | 7.8456 | 5.7233 | 17.8384 | 28.6821 | 7.3294 | 5.3467 | 14.7301 | 28.7072 | 6.9912 | 5.1 | 12.6508 | 28.763 | 6.7144 | 4.898 | 11.0875 | 28.8626 | 6.1901 | 4.5156 | 8.2047 | 28.9907 | 5.8578 | 4.2732 | 6.2049 | 29.173 | 5.7178 | 4.1711 | 5.6008 | 29.4675 | 5.5109 | 4.0201 | 4.6084 | 29.7761 | 5.2861 | 3.8561 | 3.5499 | 30.1147 | 5.1044 | 3.7236 | 2.7616 | 31.0399 | 5.035 | 3.6729 | 0.33411 | 28.0212 | 4.5453 | 3.3157 | -1.9769 | 27.2269 | 4.4165 | 3.2218 | -3.7727 | 32.8214 | 6.8407 | 4.9902 | -4.8055 | 32.8859 | 6.7466 | 4.9215 | -4.3922
RINGLEY | KEARSLEY LOCAL | KEARSLEY | 376120 | 405531 | 18.7172 | 12.4375 | 8.9391 | 16.1459 | 18.7488 | 11.9933 | 8.6198 | 13.6385 | 18.7924 | 11.6397 | 8.3657 | 13.0913 | 18.8581 | 11.3604 | 8.165 | 13.0648 | 18.9556 | 11.0722 | 7.9578 | 13.0214 | 19.0746 | 10.7502 | 7.7264 | 12.9684 | 19.2167 | 10.4408 | 7.504 | 12.9106 | 19.393 | 10.3819 | 7.4617 | 12.8436 | 19.5173 | 10.3234 | 7.4196 | 12.7508 | 19.6101 | 10.2651 | 7.3777 | 12.6615 | 19.9933 | 10.0366 | 7.2135 | 12.1292 | 20.3786 | 9.7254 | 6.9899 | 11.063 | 20.6361 | 9.401 | 6.7566 | 9.8435 | 20.8583 | 8.9723 | 6.4486 | 8.5156 | 21.0189 | 8.6786 | 6.2375 | 7.3225 | 18.7067 | 12.4375 | 8.9391 | 16.1459 | 18.725 | 12.3067 | 8.8451 | 15.3798 | 18.7395 | 12.2517 | 8.8056 | 15.1746 | 18.7634 | 12.2219 | 8.7841 | 15.1326 | 18.8028 | 12.1824 | 8.7557 | 15.0856 | 18.8536 | 12.1178 | 8.7093 | 15.0242 | 18.918 | 12.0663 | 8.6723 | 14.9412 | 18.9944 | 12.0131 | 8.634 | 14.84 | 19.0592 | 11.9451 | 8.5852 | 14.7559 | 19.132 | 11.8906 | 8.546 | 14.6695 | 19.3952 | 11.7967 | 8.4785 | 14.3985 | 19.7038 | 11.6769 | 8.3924 | 14.1174 | 20.0106 | 11.5603 | 8.3086 | 13.8501 | 20.2343 | 11.3995 | 8.1931 | 13.397 | 20.3842 | 11.247 | 8.0835 | 13.1032 | 18.7216 | 12.4375 | 8.9391 | 16.1459 | 18.7579 | 11.9145 | 8.5632 | 13.2235 | 18.8084 | 11.5362 | 8.2913 | 12.592 | 18.8839 | 11.2251 | 8.0677 | 12.5654 | 18.9923 | 10.922 | 7.8499 | 12.5231 | 19.1227 | 10.5873 | 7.6093 | 12.4723 | 19.277 | 10.2651 | 7.3777 | 12.4169 | 19.4249 | 10.2022 | 7.3325 | 12.3549 | 19.512 | 10.1366 | 7.2854 | 12.2854 | 19.597 | 10.0796 | 7.2444 | 12.2207 | 19.9793 | 9.8212 | 7.0587 | 11.7504 | 20.3886 | 9.5127 | 6.837 | 10.945 | 20.6698 | 9.1592 | 6.5829 | 9.9375 | 20.8985 | 8.7792 | 6.3098 | 8.7607 | 21.0445 | 8.5013 | 6.11 | 7.6976 | 18.7216 | 12.4375 | 8.9391 | 16.1459 | 18.7133 | 12.0791 | 8.6815 | 14.1526 | 18.7355 | 11.7633 | 8.4545 | 13.726 | 18.783 | 11.455 | 8.2329 | 13.7226 | 18.8678 | 11.1587 | 8.02 | 13.696 | 18.9947 | 10.8244 | 7.7797 | 13.6489 | 19.1734 | 10.462 | 7.5192 | 13.5469 | 19.4407 | 10.3344 | 7.4276 | 13.2939 | 19.5741 | 10.2216 | 7.3465 | 13.0184 | 19.6991 | 10.1021 | 7.2606 | 12.7443 | 20.084 | 9.5654 | 6.8748 | 11.6016 | 20.4339 | 9.2735 | 6.6651 | 10.2385 | 20.6763 | 8.9746 | 6.4503 | 9.1331 | 20.8351 | 8.7665 | 6.3006 | 8.4518 | 20.8314 | 8.7586 | 6.2949 | 8.9286 | 18.7172 | 12.4375 | 8.9391 | 16.1459 | 18.7431 | 12.1756 | 8.7509 | 14.6647 | 18.7697 | 11.8468 | 8.5145 | 14.3402 | 18.8056 | 11.5909 | 8.3306 | 14.3413 | 18.8622 | 11.3054 | 8.1254 | 14.3435 | 18.9531 | 11.0033 | 7.9083 | 14.3261 | 19.0778 | 10.709 | 7.6968 | 14.2868 | 19.2256 | 10.6547 | 7.6577 | 14.2347 | 19.3582 | 10.6007 | 7.6189 | 14.1516 | 19.486 | 10.5437 | 7.5779 | 14.0657 | 19.774 | 10.365 | 7.4496 | 13.7626 | 20.0682 | 10.2153 | 7.3419 | 13.4333 | 20.2738 | 10.0738 | 7.2402 | 13.2099 | 20.4326 | 9.8256 | 7.0618 | 13.0324 | 20.4987 | 9.7831 | 7.0313 | 13.0222 | 18.7172 | 12.4375 | 8.9391 | 16.1459 | 18.7195 | 11.8647 | 8.5274 | 12.8895 | 18.7599 | 11.4884 | 8.2569 | 12.182 | 18.8293 | 11.173 | 8.0303 | 12.1466 | 18.9301 | 10.8621 | 7.8068 | 12.0919 | 19.0488 | 10.5229 | 7.563 | 12.032 | 19.2082 | 10.1597 | 7.302 | 11.9213 | 19.4684 | 10.0321 | 7.2103 | 11.647 | 19.6114 | 9.9116 | 7.1237 | 11.3622 | 19.7323 | 9.7889 | 7.0354 | 11.0802 | 20.1193 | 9.2539 | 6.651 | 9.9164 | 20.4885 | 8.9294 | 6.4177 | 8.4448 | 20.7547 | 8.6027 | 6.1829 | 7.2323 | 20.9244 | 8.3724 | 6.0174 | 6.4383 | 20.9282 | 8.3409 | 5.9948 | 6.8029
RISLEY | - | BOLD | 365181 | 392989 | 8.8525 | 1.4575 | 1.0475 | 8.8525 | 5.5912 | 0.92055 | 0.66162 | 5.5912 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 1.273 | 8.8525 | 1.4575 | 1.0475 | 8.8525 | 7.6192 | 1.2544 | 0.9016 | 7.6192 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 8.8525 | 1.4575 | 1.0475 | 8.8525 | 5.0416 | 0.83007 | 0.59659 | 5.0416 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.5653 | 8.8525 | 1.4575 | 1.0475 | 8.8525 | 5.9045 | 0.97213 | 0.69869 | 5.9045 | 4.6852 | 0.77138 | 0.5544 | 4.6852 | 3.3237 | 0.54722 | 0.3933 | 3.3237 | 1.3784 | 0.22694 | 0.16311 | 1.3784 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 8.8525 | 1.4575 | 1.0475 | 8.8525 | 6.6039 | 1.0873 | 0.78145 | 6.6039 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 8.8525 | 1.4575 | 1.0475 | 8.8525 | 4.6543 | 0.7663 | 0.55075 | 4.6543 | 3.0815 | 0.50734 | 0.36464 | 3.0815 | 1.5933 | 0.26232 | 0.18854 | 1.5933 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.5108 | 2.6844 | 0.44197 | 0.31765 | 1.2086 | 2.6844 | 0.44197 | 0.31765 | 1.8165
ROBERT HALL ST | FREDERICK RD | KEARSLEY | 381359 | 397718 | 30.7755 | 9.2865 | 6.7744 | 13.2195 | 30.9327 | 8.6345 | 6.2988 | 9.8122 | 31.1086 | 8.3201 | 6.0694 | 8.4163 | 31.2942 | 8.1106 | 5.9166 | 7.6311 | 31.4909 | 7.8696 | 5.7408 | 6.8029 | 31.6949 | 7.6085 | 5.5503 | 5.9735 | 31.9122 | 7.3594 | 5.3686 | 5.0273 | 32.1538 | 7.1086 | 5.1856 | 4.0868 | 32.364 | 6.8572 | 5.0022 | 3.0907 | 32.5663 | 6.6957 | 4.8844 | 2.5942 | 33.1573 | 6.1944 | 4.5187 | 0.85566 | 33.681 | 5.7983 | 4.2298 | -1.4144 | 33.9385 | 5.5052 | 4.0159 | -3.1562 | 32.31 | 5.241 | 3.8232 | -5.0009 | 29.76 | 4.8274 | 3.5215 | -6.8566 | 30.7706 | 9.2865 | 6.7744 | 13.2195 | 30.9367 | 9.0431 | 6.5968 | 12.0047 | 31.1064 | 8.8914 | 6.4861 | 11.3847 | 31.2943 | 8.7606 | 6.3907 | 10.951 | 31.5135 | 8.6314 | 6.2965 | 10.5629 | 31.7632 | 8.4945 | 6.1966 | 10.1754 | 32.0451 | 8.2041 | 5.9848 | 9.736 | 32.3584 | 8.0532 | 5.8747 | 9.2018 | 32.5376 | 7.9148 | 5.7737 | 8.6917 | 32.7186 | 7.7811 | 5.6762 | 8.1656 | 33.2488 | 7.3777 | 5.382 | 6.6111 | 33.6558 | 7.0667 | 5.1551 | 5.0295 | 33.9797 | 6.8246 | 4.9784 | 3.5877 | 34.3432 | 6.6223 | 4.8309 | 1.9233 | 34.7161 | 6.3211 | 4.6112 | 0.26517 | 30.7781 | 9.2865 | 6.7744 | 13.2195 | 30.9434 | 8.537 | 6.2276 | 9.2986 | 31.1289 | 8.1669 | 5.9577 | 7.7541 | 31.3274 | 7.8846 | 5.7517 | 6.9188 | 31.5388 | 7.6501 | 5.5806 | 6.0263 | 31.7595 | 7.3663 | 5.3736 | 5.1241 | 31.9978 | 6.7816 | 4.9471 | 2.4511 | 32.2626 | 6.1597 | 4.4934 | -0.53927 | 32.4891 | 5.5204 | 4.0271 | -3.5489 | 32.6553 | 5.297 | 3.8641 | -4.8791 | 29.2384 | 4.7428 | 3.4598 | -6.8629 | 26.0231 | 4.2212 | 3.0793 | -9.1108 | 23.8034 | 3.8611 | 2.8166 | -10.8944 | 21.6143 | 3.5061 | 2.5576 | -12.7501 | 18.4638 | 2.995 | 2.1848 | -14.5472 | 30.7781 | 9.2865 | 6.7744 | 13.2195 | 30.8564 | 8.7467 | 6.3806 | 10.4193 | 30.9794 | 8.4877 | 6.1916 | 9.1334 | 31.1103 | 8.2495 | 6.0179 | 8.3484 | 31.2625 | 7.9869 | 5.8264 | 7.4924 | 31.4497 | 7.6407 | 5.5738 | 6.6117 | 31.6585 | 7.205 | 5.256 | 3.9172 | 31.8737 | 6.5776 | 4.7983 | 0.78209 | 32.0731 | 5.959 | 4.347 | -2.3789 | 32.2685 | 5.6214 | 4.1007 | -3.8785 | 32.3428 | 5.2463 | 3.8271 | -6.1778 | 28.0438 | 4.549 | 3.3184 | -8.3874 | 25.3937 | 4.1191 | 3.0048 | -9.9595 | 23.6513 | 3.8365 | 2.7987 | -11.3866 | 21.273 | 3.4507 | 2.5172 | -12.5929 | 30.7755 | 9.2865 | 6.7744 | 13.2195 | 30.9238 | 8.8656 | 6.4673 | 11.099 | 31.0729 | 8.627 | 6.2933 | 9.9827 | 31.2206 | 8.4252 | 6.146 | 9.234 | 31.3818 | 8.1874 | 5.9726 | 8.4636 | 31.5775 | 7.9566 | 5.8043 | 7.6846 | 31.8022 | 7.713 | 5.6266 | 6.7795 | 32.0329 | 7.4686 | 5.4482 | 5.8665 | 32.2301 | 7.2098 | 5.2595 | 4.8662 | 32.4248 | 7.048 | 5.1414 | 4.3545 | 33.0114 | 6.5851 | 4.8038 | 2.7987 | 33.5995 | 6.3316 | 4.6188 | 1.1443 | 33.9351 | 6.1473 | 4.4844 | -0.10364 | 34.2941 | 5.9689 | 4.3542 | -1.5092 | 34.1892 | 5.5458 | 4.0456 | -2.9676 | 30.7755 | 9.2865 | 6.7744 | 13.2195 | 30.8904 | 8.4765 | 6.1835 | 8.9639 | 31.0634 | 8.1405 | 5.9384 | 7.3374 | 31.2516 | 7.8921 | 5.7572 | 6.4933 | 31.4537 | 7.6145 | 5.5547 | 5.5836 | 31.6619 | 7.2613 | 5.297 | 4.6688 | 31.8848 | 6.8102 | 4.968 | 1.927 | 32.1397 | 6.1669 | 4.4987 | -1.2654 | 32.3591 | 5.5448 | 4.0448 | -4.462 | 32.078 | 5.2034 | 3.7958 | -5.9759 | 29.6194 | 4.8046 | 3.5049 | -8.3921 | 25.4016 | 4.1204 | 3.0058 | -10.6737 | 22.2654 | 3.6117 | 2.6347 | -12.3161 | 20.4338 | 3.3146 | 2.4179 | -13.8384 | 17.8311 | 2.8924 | 2.11 | -15.1908
ROCHDALE CENTRAL | ROCHDALE CENTRAL | ROCHDALE | 389111 | 413393 | 5.3563 | 0.86885 | 0.63381 | 5.3563 | 4.0363 | 0.65473 | 0.47762 | 4.0363 | 3.3591 | 0.54489 | 0.39749 | 3.3591 | 2.1688 | 0.3518 | 0.25664 | 2.1688 | 0.60774 | 0.098582 | 0.071914 | 0.60774 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 5.3563 | 0.86885 | 0.63381 | 5.3563 | 4.7037 | 0.76298 | 0.55659 | 4.7037 | 3.8809 | 0.62953 | 0.45923 | 3.8809 | 2.983 | 0.48387 | 0.35298 | 2.983 | 1.9614 | 0.31815 | 0.23209 | 1.9614 | 0.79668 | 0.12923 | 0.094271 | 0.79668 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 5.3563 | 0.86885 | 0.63381 | 5.3563 | 3.6998 | 0.60014 | 0.4378 | 3.6998 | 2.6598 | 0.43145 | 0.31473 | 2.6598 | 0.9639 | 0.15635 | 0.11406 | 0.9639 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 5.3563 | 0.86885 | 0.63381 | 5.3563 | 4.4974 | 0.72952 | 0.53218 | 4.4974 | 3.8582 | 0.62584 | 0.45654 | 3.8582 | 2.4886 | 0.40368 | 0.29448 | 2.4886 | 1.0194 | 0.16536 | 0.12063 | 1.0194 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 5.3563 | 0.86885 | 0.63381 | 5.3563 | 4.4038 | 0.71433 | 0.5211 | 4.4038 | 3.9118 | 0.63454 | 0.46289 | 3.9118 | 2.8667 | 0.465 | 0.33921 | 2.8667 | 1.564 | 0.2537 | 0.18507 | 1.564 | 0.37287 | 0.060483 | 0.044122 | 0.37287 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 5.3563 | 0.86885 | 0.63381 | 5.3563 | 4.0052 | 0.64968 | 0.47393 | 4.0052 | 3.203 | 0.51955 | 0.37901 | 3.203 | 1.6031 | 0.26004 | 0.1897 | 1.6031 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914
ROMAN RD | LOWER DARWEN | ROCHDALE | 369058 | 426505 | 29.5576 | 16.2325 | 11.8414 | 12.7738 | 29.6347 | 16.0113 | 11.68 | 12.1745 | 29.7403 | 15.9638 | 11.6453 | 11.7576 | 29.8618 | 15.9242 | 11.6165 | 11.5105 | 30.0117 | 15.7726 | 11.5059 | 11.3909 | 30.1994 | 15.7057 | 11.4571 | 11.2657 | 30.4368 | 15.5502 | 11.3436 | 11.1418 | 30.7395 | 15.4444 | 11.2665 | 11.012 | 31.0593 | 15.3312 | 11.1839 | 10.7848 | 31.3977 | 15.2159 | 11.0998 | 10.5612 | 32.0859 | 14.8729 | 10.8496 | 9.6298 | 32.7921 | 14.5719 | 10.63 | 8.4277 | 33.3221 | 14.4047 | 10.508 | 7.1155 | 33.7279 | 14.6652 | 10.6981 | 5.8413 | 33.7722 | 14.4702 | 10.5558 | 4.7794 | 29.5451 | 16.2325 | 11.8414 | 12.7738 | 29.5941 | 16.1138 | 11.7548 | 12.5834 | 29.6589 | 16.198 | 11.8162 | 12.4145 | 29.7244 | 16.1703 | 11.796 | 12.3446 | 29.8043 | 16.1125 | 11.7539 | 12.3062 | 29.9077 | 16.0369 | 11.6987 | 12.2539 | 30.0364 | 15.7922 | 11.5202 | 12.175 | 30.1904 | 15.764 | 11.4996 | 12.0663 | 30.3381 | 15.7243 | 11.4706 | 11.8881 | 30.506 | 15.6445 | 11.4124 | 11.7068 | 31.1404 | 15.5494 | 11.3431 | 11.1606 | 31.9009 | 15.4442 | 11.2663 | 10.6054 | 32.3223 | 15.4189 | 11.2478 | 10.1085 | 32.682 | 15.6446 | 11.4125 | 9.6103 | 32.9161 | 15.7132 | 11.4625 | 9.3075 | 29.563 | 16.2325 | 11.8414 | 12.7738 | 29.6345 | 15.9871 | 11.6624 | 12.077 | 29.7407 | 15.9542 | 11.6383 | 11.6434 | 29.8644 | 15.8092 | 11.5326 | 11.395 | 30.014 | 15.7079 | 11.4587 | 11.277 | 30.1969 | 15.5791 | 11.3647 | 11.1556 | 30.4241 | 15.4103 | 11.2416 | 11.0362 | 30.7131 | 15.2519 | 11.1261 | 10.9151 | 30.9978 | 15.1402 | 11.0446 | 10.7474 | 31.3057 | 15.0364 | 10.9689 | 10.5884 | 31.9673 | 14.6196 | 10.6648 | 9.8322 | 32.6598 | 14.2971 | 10.4296 | 8.7901 | 33.1741 | 14.1438 | 10.3177 | 7.6372 | 33.6007 | 14.4634 | 10.5508 | 6.6163 | 33.5797 | 14.273 | 10.4119 | 5.8762 | 29.5631 | 16.2325 | 11.8414 | 12.7738 | 29.5915 | 16.0534 | 11.7107 | 12.3901 | 29.6651 | 16.078 | 11.7286 | 12.0383 | 29.7525 | 16.0133 | 11.6815 | 11.8254 | 29.8748 | 15.8485 | 11.5613 | 11.7334 | 30.0608 | 15.7389 | 11.4813 | 11.6211 | 30.3093 | 15.6222 | 11.3962 | 11.4426 | 30.6202 | 15.4454 | 11.2672 | 11.0688 | 30.9423 | 15.2594 | 11.1315 | 10.6265 | 31.2843 | 15.1078 | 11.0209 | 10.1896 | 32.3393 | 15.4548 | 11.2741 | 8.6982 | 33.0028 | 15.0494 | 10.9783 | 7.2884 | 33.2735 | 14.695 | 10.7198 | 6.1831 | 33.3689 | 14.448 | 10.5396 | 5.6208 | 33.2374 | 14.4297 | 10.5263 | 6.4268 | 29.5576 | 16.2325 | 11.8414 | 12.7738 | 29.6161 | 16.0674 | 11.7209 | 12.4475 | 29.692 | 16.019 | 11.6856 | 12.0969 | 29.7678 | 15.9925 | 11.6663 | 11.8896 | 29.8623 | 15.8509 | 11.563 | 11.8425 | 30.0074 | 15.8431 | 11.5573 | 11.7767 | 30.2059 | 15.6878 | 11.444 | 11.6847 | 30.4442 | 15.578 | 11.3639 | 11.5742 | 30.6951 | 15.471 | 11.2859 | 11.3555 | 30.9723 | 15.3635 | 11.2075 | 11.1309 | 31.7984 | 15.085 | 11.0043 | 10.4763 | 32.2539 | 14.9505 | 10.9062 | 9.9395 | 32.5622 | 14.964 | 10.9161 | 9.6082 | 32.7937 | 15.4977 | 11.3054 | 9.3993 | 32.8326 | 15.5101 | 11.3144 | 9.5346 | 29.5576 | 16.2325 | 11.8414 | 12.7738 | 29.5918 | 15.9908 | 11.6651 | 12.0774 | 29.6844 | 15.9697 | 11.6497 | 11.638 | 29.7934 | 15.9053 | 11.6027 | 11.3823 | 29.9263 | 15.7376 | 11.4803 | 11.2536 | 30.088 | 15.6256 | 11.3987 | 11.1256 | 30.2933 | 15.5024 | 11.3088 | 10.9376 | 30.571 | 15.3078 | 11.1668 | 10.5383 | 30.8547 | 15.149 | 11.051 | 10.0874 | 31.1636 | 14.9753 | 10.9242 | 9.6436 | 32.2053 | 15.27 | 11.1393 | 8.1907 | 33.025 | 14.8872 | 10.86 | 6.7314 | 33.3672 | 14.5292 | 10.5989 | 5.6122 | 33.508 | 14.2689 | 10.409 | 4.9843 | 33.3975 | 14.2306 | 10.381 | 5.7004
ROMILEY | VERNON PARK | BREDBURY | 393626 | 390716 | 22.306 | 11.1093 | 7.9845 | 6.8393 | 22.3696 | 10.8208 | 7.7771 | 6.208 | 22.4534 | 10.3614 | 7.4469 | 6.0444 | 22.5659 | 9.8556 | 7.0834 | 5.9775 | 22.7213 | 9.2569 | 6.6531 | 5.7978 | 22.9035 | 8.6791 | 6.2378 | 5.6015 | 23.0885 | 8.2813 | 5.952 | 5.4206 | 23.2951 | 8.119 | 5.8353 | 5.2634 | 25.2337 | 7.6367 | 5.4887 | 3.2583 | 25.3601 | 7.489 | 5.3825 | 3.1186 | 27.7204 | 6.6735 | 4.7964 | -0.46073 | 28.5038 | 6.0561 | 4.3527 | -4.1277 | 28.7861 | 5.8513 | 4.2054 | -7.1782 | 30.437 | 6.2753 | 4.5102 | -11.9585 | 30.5222 | 6.6294 | 4.7647 | -14.8986 | 22.2746 | 11.1093 | 7.9845 | 6.8393 | 22.3432 | 10.9593 | 7.8766 | 6.5939 | 22.3979 | 10.5058 | 7.5507 | 6.4699 | 22.469 | 10.0353 | 7.2125 | 6.3622 | 22.5716 | 9.5185 | 6.8411 | 6.1933 | 22.699 | 8.9372 | 6.4234 | 6.0037 | 22.8573 | 8.2714 | 5.9448 | 5.7428 | 23.0434 | 8.179 | 5.8784 | 5.4155 | 23.1462 | 8.0823 | 5.8089 | 5.1622 | 23.2552 | 7.966 | 5.7253 | 4.8883 | 23.6103 | 7.6139 | 5.4722 | 4.053 | 23.9366 | 7.2774 | 5.2304 | 3.2185 | 24.2616 | 7.4297 | 5.3399 | 2.36 | 26.201 | 8.0917 | 5.8157 | -0.21422 | 26.3638 | 8.6416 | 6.2109 | -0.84238 | 22.3142 | 11.1093 | 7.9845 | 6.8393 | 22.3845 | 10.7596 | 7.7331 | 6.1401 | 22.4802 | 10.2508 | 7.3674 | 5.9859 | 22.6101 | 9.6934 | 6.9669 | 5.9712 | 22.7865 | 9.0511 | 6.5052 | 5.8429 | 22.9783 | 8.5605 | 6.1526 | 5.6461 | 24.9862 | 7.78 | 5.5916 | 3.6101 | 25.0988 | 7.5926 | 5.457 | 3.565 | 26.8943 | 7.1049 | 5.1065 | 1.7232 | 26.9832 | 6.9689 | 5.0087 | 1.6822 | 29.3753 | 6.0823 | 4.3715 | -1.6346 | 30.187 | 5.411 | 3.889 | -5.0689 | 30.4501 | 5.1446 | 3.6976 | -7.8657 | 30.3997 | 5.7741 | 4.1499 | -10.6635 | 30.496 | 6.0709 | 4.3633 | -13.3509 | 22.3142 | 11.1093 | 7.9845 | 6.8393 | 22.28 | 10.8615 | 7.8064 | 6.6744 | 22.3123 | 10.7323 | 7.7135 | 6.6441 | 26.8998 | 9.6221 | 6.9156 | 2.0344 | 26.7233 | 9.4615 | 6.8001 | 2.184 | 26.6392 | 9.311 | 6.692 | 2.204 | 26.6309 | 9.2045 | 6.6154 | 1.9613 | 26.7367 | 8.8992 | 6.396 | 1.0014 | 27.0816 | 8.5438 | 6.1406 | -0.30545 | 27.2441 | 8.2184 | 5.9067 | -1.414 | 27.9894 | 7.2316 | 5.1975 | -4.9866 | 28.4638 | 6.3883 | 4.5914 | -8.1687 | 28.7159 | 5.8055 | 4.1725 | -10.7319 | 28.7086 | 6.8307 | 4.9093 | -12.182 | 28.566 | 6.7132 | 4.8249 | -10.8545 | 22.306 | 11.1093 | 7.9845 | 6.8393 | 22.3591 | 10.9007 | 7.8345 | 6.5235 | 22.4114 | 10.4653 | 7.5217 | 6.4664 | 22.4722 | 9.9768 | 7.1705 | 6.4963 | 22.5632 | 9.4065 | 6.7607 | 6.4787 | 22.7078 | 8.8518 | 6.362 | 6.4232 | 22.8981 | 8.4888 | 6.101 | 6.3371 | 23.0717 | 8.3441 | 5.9971 | 6.238 | 24.9852 | 7.8637 | 5.6518 | 4.2514 | 25.0944 | 7.7139 | 5.5441 | 4.1026 | 27.2519 | 7.1077 | 5.1085 | 1.6705 | 27.7607 | 6.9973 | 5.0291 | 0.76048 | 28.0163 | 7.2449 | 5.2071 | 0.22176 | 29.6513 | 8.1932 | 5.8886 | -1.7526 | 29.6948 | 9.0649 | 6.5151 | -1.9088 | 22.306 | 11.1093 | 7.9845 | 6.8393 | 22.3013 | 10.7973 | 7.7603 | 6.3344 | 22.3778 | 10.6251 | 7.6365 | 6.1489 | 27.0184 | 9.4909 | 6.8213 | 1.429 | 26.8857 | 9.3138 | 6.694 | 1.4791 | 26.8047 | 9.1491 | 6.5757 | 1.4338 | 26.7777 | 9.0216 | 6.484 | 1.1107 | 26.9018 | 8.6936 | 6.2482 | 0.039574 | 27.2689 | 8.3232 | 5.982 | -1.3489 | 27.4575 | 7.9823 | 5.737 | -2.5388 | 28.2068 | 6.9441 | 4.9909 | -6.3638 | 28.6611 | 6.0564 | 4.3529 | -9.7653 | 28.905 | 5.4302 | 3.9028 | -12.5482 | 28.8758 | 6.4002 | 4.6 | -14.271 | 28.7385 | 6.2238 | 4.4732 | -13.2531
ROSSALL | THORNTON | PENWORTHAM WEST / STANAH | 331916 | 445505 | -6.0777 | -6.0777 | -6.0777 | -6.0777 | -6.0408 | -6.0408 | -6.0408 | -6.0408 | -6.0164 | -6.0164 | -6.0164 | -6.0164 | -5.9856 | -5.9856 | -5.9856 | -5.9856 | -5.9403 | -5.9403 | -5.9403 | -5.9403 | -5.8923 | -5.8923 | -5.8923 | -5.8923 | -5.8458 | -5.8458 | -5.8458 | -5.8458 | -5.7945 | -5.7945 | -5.7945 | -5.7945 | -5.7399 | -5.7399 | -5.7399 | -5.7399 | -5.6862 | -5.6862 | -5.6862 | -5.6862 | -5.4088 | -5.4088 | -5.4088 | -5.4088 | -5.1783 | -5.1783 | -5.1783 | -5.1783 | -4.9983 | -4.9983 | -4.9983 | -4.9983 | -4.8192 | -4.8192 | -4.8192 | -4.8192 | -4.7133 | -4.7133 | -4.7133 | -4.7133 | -6.0772 | -6.0772 | -6.0772 | -6.0772 | -6.0445 | -6.0445 | -6.0445 | -6.0445 | -6.0258 | -6.0258 | -6.0258 | -6.0258 | -6.0023 | -6.0023 | -6.0023 | -6.0023 | -5.9707 | -5.9707 | -5.9707 | -5.9707 | -5.9337 | -5.9337 | -5.9337 | -5.9337 | -5.8906 | -5.8906 | -5.8906 | -5.8906 | -5.8427 | -5.8427 | -5.8427 | -5.8427 | -5.8028 | -5.8028 | -5.8028 | -5.8028 | -5.7614 | -5.7614 | -5.7614 | -5.7614 | -5.6323 | -5.6323 | -5.6323 | -5.6323 | -5.4982 | -5.4982 | -5.4982 | -5.4982 | -5.378 | -5.378 | -5.378 | -5.378 | -5.2529 | -5.2529 | -5.2529 | -5.2529 | -5.1543 | -5.1543 | -5.1543 | -5.1543 | -6.0779 | -6.0779 | -6.0779 | -6.0779 | -6.0408 | -6.0408 | -6.0408 | -6.0408 | -6.0167 | -6.0167 | -6.0167 | -6.0167 | -5.9862 | -5.9862 | -5.9862 | -5.9862 | -5.9418 | -5.9418 | -5.9418 | -5.9418 | -5.8953 | -5.8953 | -5.8953 | -5.8953 | -5.8506 | -5.8506 | -5.8506 | -5.8506 | -5.8022 | -5.8022 | -5.8022 | -5.8022 | -5.751 | -5.751 | -5.751 | -5.751 | -5.7013 | -5.7013 | -5.7013 | -5.7013 | -5.4318 | -5.4318 | -5.4318 | -5.4318 | -5.2081 | -5.2081 | -5.2081 | -5.2081 | -5.0362 | -5.0362 | -5.0362 | -5.0362 | -4.8748 | -4.8748 | -4.8748 | -4.8748 | -4.7503 | -4.7503 | -4.7503 | -4.7503 | -6.0779 | -6.0779 | -6.0779 | -6.0779 | -6.0649 | -6.0649 | -6.0649 | -6.0649 | -6.0516 | -6.0516 | -6.0516 | -6.0516 | -6.0258 | -6.0258 | -6.0258 | -6.0258 | -5.984 | -5.984 | -5.984 | -5.984 | -5.9338 | -5.9338 | -5.9338 | -5.9338 | -5.8565 | -5.8565 | -5.8565 | -5.8565 | -5.6993 | -5.6993 | -5.6993 | -5.6993 | -5.6111 | -5.6111 | -5.6111 | -5.6111 | -5.5345 | -5.5345 | -5.5345 | -5.5345 | -5.3095 | -5.3095 | -5.3095 | -5.3095 | -5.0961 | -5.0961 | -5.0961 | -5.0961 | -4.9363 | -4.9363 | -4.9363 | -4.9363 | -4.8283 | -4.8283 | -4.8283 | -4.8283 | -4.8406 | -4.8406 | -4.8406 | -4.8406 | -6.0777 | -6.0777 | -6.0777 | -6.0777 | -6.0458 | -6.0458 | -6.0458 | -6.0458 | -6.0292 | -6.0292 | -6.0292 | -6.0292 | -6.0117 | -6.0117 | -6.0117 | -6.0117 | -5.9885 | -5.9885 | -5.9885 | -5.9885 | -5.9567 | -5.9567 | -5.9567 | -5.9567 | -5.9158 | -5.9158 | -5.9158 | -5.9158 | -5.8675 | -5.8675 | -5.8675 | -5.8675 | -5.8148 | -5.8148 | -5.8148 | -5.8148 | -5.7597 | -5.7597 | -5.7597 | -5.7597 | -5.5705 | -5.5705 | -5.5705 | -5.5705 | -5.3632 | -5.3632 | -5.3632 | -5.3632 | -5.2529 | -5.2529 | -5.2529 | -5.2529 | -5.1664 | -5.1664 | -5.1664 | -5.1664 | -5.1361 | -5.1361 | -5.1361 | -5.1361 | -6.0777 | -6.0777 | -6.0777 | -6.0777 | -6.0574 | -6.0574 | -6.0574 | -6.0574 | -6.0332 | -6.0332 | -6.0332 | -6.0332 | -5.9948 | -5.9948 | -5.9948 | -5.9948 | -5.9426 | -5.9426 | -5.9426 | -5.9426 | -5.8896 | -5.8896 | -5.8896 | -5.8896 | -5.8115 | -5.8115 | -5.8115 | -5.8115 | -5.6477 | -5.6477 | -5.6477 | -5.6477 | -5.5547 | -5.5547 | -5.5547 | -5.5547 | -5.4749 | -5.4749 | -5.4749 | -5.4749 | -5.2404 | -5.2404 | -5.2404 | -5.2404 | -5.0201 | -5.0201 | -5.0201 | -5.0201 | -4.8605 | -4.8605 | -4.8605 | -4.8605 | -4.7759 | -4.7759 | -4.7759 | -4.7759 | -4.779 | -4.779 | -4.779 | -4.779
ROYTON | ROYTON | WHITEGATE | 392426 | 407533 | 29.8551 | 12.7899 | 9.3301 | 16.8222 | 29.9478 | 12.5895 | 9.1838 | 16.0041 | 30.0601 | 12.4437 | 9.0775 | 15.6883 | 30.194 | 12.3963 | 9.0429 | 15.4816 | 30.3442 | 12.2726 | 8.9527 | 15.1626 | 30.5012 | 12.1348 | 8.8521 | 14.823 | 30.6696 | 11.9913 | 8.7475 | 14.4941 | 30.8535 | 11.8737 | 8.6617 | 14.1646 | 31.0088 | 11.7577 | 8.5771 | 13.821 | 31.1628 | 11.6585 | 8.5047 | 13.4932 | 31.6651 | 11.1977 | 8.1686 | 11.5313 | 32.1749 | 10.6702 | 7.7837 | 8.4616 | 32.5412 | 10.4171 | 7.5991 | 6.0828 | 32.8609 | 10.1817 | 7.4274 | 3.7982 | 33.0826 | 9.7199 | 7.0906 | 2.0541 | 29.8334 | 12.7899 | 9.3301 | 16.8222 | 29.9066 | 12.7234 | 9.2816 | 16.5833 | 29.9749 | 12.655 | 9.2316 | 16.4349 | 30.055 | 12.5802 | 9.1771 | 16.2941 | 30.16 | 12.4899 | 9.1112 | 16.102 | 30.2678 | 12.4041 | 9.0486 | 15.8954 | 30.3864 | 12.2119 | 8.9084 | 15.6269 | 30.53 | 12.1105 | 8.8345 | 15.2786 | 30.622 | 12.0315 | 8.7768 | 15.0129 | 30.7209 | 11.9448 | 8.7136 | 14.7343 | 31.0506 | 11.6889 | 8.5269 | 13.867 | 31.4095 | 11.4526 | 8.3545 | 12.9118 | 31.7553 | 11.3898 | 8.3087 | 11.9536 | 32.1233 | 11.388 | 8.3074 | 10.8833 | 32.3943 | 11.1579 | 8.1395 | 10.0549 | 29.8619 | 12.7899 | 9.3301 | 16.8222 | 29.972 | 12.5471 | 9.1529 | 15.8322 | 30.1083 | 12.3483 | 9.0079 | 15.4212 | 30.273 | 12.2518 | 8.9375 | 15.0637 | 30.4682 | 12.0758 | 8.8091 | 14.5904 | 30.6252 | 11.876 | 8.6634 | 14.0637 | 30.8087 | 11.6895 | 8.5273 | 13.5537 | 31.026 | 11.5234 | 8.4062 | 13.0487 | 31.2045 | 11.3607 | 8.2875 | 12.532 | 31.3834 | 11.2023 | 8.1719 | 12.0081 | 31.9888 | 10.5685 | 7.7096 | 9.5036 | 32.5977 | 9.9412 | 7.252 | 6.333 | 33.0342 | 9.6485 | 7.0384 | 4.2508 | 33.4092 | 9.327 | 6.8039 | 2.5425 | 33.6008 | 9.1522 | 6.6764 | 1.7359 | 29.8619 | 12.7899 | 9.3301 | 16.8222 | 29.8943 | 12.6297 | 9.2132 | 16.3201 | 29.9771 | 12.5061 | 9.123 | 16.0272 | 30.0817 | 12.3984 | 9.0445 | 15.6943 | 30.2265 | 12.2235 | 8.9169 | 15.2092 | 30.3853 | 12.0205 | 8.7688 | 14.6533 | 30.5578 | 11.7841 | 8.5963 | 13.9525 | 30.7688 | 11.5501 | 8.4256 | 12.7496 | 30.9588 | 11.3021 | 8.2447 | 11.5643 | 31.1502 | 11.0693 | 8.0749 | 10.4127 | 31.7387 | 10.9713 | 8.0034 | 7.1631 | 32.2898 | 10.3269 | 7.5334 | 4.4793 | 32.6691 | 9.8379 | 7.1766 | 2.8987 | 32.9716 | 9.4673 | 6.9063 | 2.2139 | 33.1191 | 9.3238 | 6.8016 | 2.8821 | 29.8551 | 12.7899 | 9.3301 | 16.8222 | 29.9349 | 12.6823 | 9.2516 | 16.473 | 30.0172 | 12.563 | 9.1646 | 16.2848 | 30.1047 | 12.52 | 9.1332 | 16.1492 | 30.2153 | 12.4328 | 9.0696 | 15.9731 | 30.3516 | 12.3203 | 8.9875 | 15.7643 | 30.5035 | 12.1948 | 8.8959 | 15.527 | 30.6734 | 12.0854 | 8.8161 | 15.2488 | 30.8268 | 11.9713 | 8.7329 | 14.9123 | 30.9778 | 11.8681 | 8.6576 | 14.5689 | 31.4315 | 11.5512 | 8.4264 | 13.3948 | 31.893 | 11.3449 | 8.276 | 12.1377 | 32.2343 | 11.358 | 8.2855 | 11.2313 | 32.5442 | 11.3443 | 8.2755 | 10.2966 | 32.7475 | 11.1729 | 8.1505 | 9.5593 | 29.8551 | 12.7899 | 9.3301 | 16.8222 | 29.9079 | 12.5656 | 9.1664 | 15.9723 | 30.0259 | 12.417 | 9.0581 | 15.5482 | 30.173 | 12.2868 | 8.9631 | 15.1358 | 30.3515 | 12.0978 | 8.8252 | 14.5764 | 30.5088 | 11.8837 | 8.669 | 13.9733 | 30.6796 | 11.6381 | 8.4898 | 13.2135 | 30.9065 | 11.389 | 8.3081 | 11.9292 | 31.099 | 11.1319 | 8.1206 | 10.6849 | 31.2921 | 10.8906 | 7.9446 | 9.4727 | 31.8872 | 10.7517 | 7.8432 | 6.0267 | 32.4362 | 10.0633 | 7.3411 | 3.1723 | 32.8229 | 9.5383 | 6.958 | 1.4246 | 33.126 | 9.135 | 6.6638 | 0.54175 | 33.2954 | 8.9569 | 6.5339 | 0.97594
SALE | SALE | CARRINGTON | 378952 | 392177 | 29.8136 | 9.0456 | 6.5986 | 16.0912 | 29.9316 | 8.7486 | 6.382 | 14.6815 | 30.0904 | 8.5892 | 6.2657 | 14.1499 | 30.2903 | 8.4436 | 6.1595 | 13.8387 | 30.5254 | 8.2849 | 6.0438 | 13.4596 | 30.7875 | 8.1527 | 5.9473 | 13.0697 | 31.082 | 7.9958 | 5.8328 | 12.7004 | 31.4354 | 7.866 | 5.7381 | 12.3492 | 31.6931 | 7.7228 | 5.6337 | 11.9958 | 31.9405 | 7.5869 | 5.5345 | 11.6667 | 32.6623 | 7.0696 | 5.1572 | 9.8983 | 33.1827 | 6.4668 | 4.7174 | 7.2426 | 33.5257 | 5.9703 | 4.3552 | 5.2705 | 33.8327 | 5.5569 | 4.0537 | 3.3909 | 32.4825 | 5.269 | 3.8436 | 2.0001 | 29.7732 | 9.0456 | 6.5986 | 16.0912 | 29.8761 | 8.917 | 6.5048 | 15.5831 | 29.9856 | 8.8381 | 6.4473 | 15.2711 | 30.1319 | 8.7172 | 6.3591 | 14.9807 | 30.3208 | 8.5696 | 6.2514 | 14.6247 | 30.5493 | 8.4221 | 6.1438 | 14.2671 | 30.8182 | 8.0948 | 5.9051 | 13.8364 | 31.1251 | 7.9247 | 5.781 | 13.3207 | 31.2512 | 7.8087 | 5.6963 | 13.0164 | 31.3838 | 7.6943 | 5.6129 | 12.7005 | 31.7943 | 7.3503 | 5.362 | 11.7435 | 32.1951 | 7.074 | 5.1604 | 10.7607 | 32.555 | 6.8174 | 4.9732 | 9.8754 | 32.9267 | 6.6731 | 4.8679 | 8.9194 | 33.222 | 6.5151 | 4.7527 | 8.1736 | 29.8308 | 9.0456 | 6.5986 | 16.0912 | 29.971 | 8.6916 | 6.3404 | 14.4284 | 30.1625 | 8.4676 | 6.177 | 13.7894 | 30.4057 | 8.2718 | 6.0342 | 13.4133 | 30.692 | 8.1014 | 5.9099 | 12.9657 | 31.0127 | 7.9179 | 5.776 | 12.5055 | 31.375 | 7.7406 | 5.6466 | 12.0761 | 31.8089 | 7.5734 | 5.5247 | 11.6563 | 32.1257 | 7.3896 | 5.3906 | 11.2376 | 32.431 | 7.2145 | 5.2629 | 10.8189 | 33.0994 | 6.5851 | 4.8037 | 8.8107 | 33.6991 | 5.895 | 4.3003 | 6.2348 | 32.9378 | 5.3428 | 3.8975 | 4.4936 | 30.5325 | 4.9527 | 3.6129 | 3.0212 | 28.7685 | 4.6665 | 3.4042 | 2.2275 | 29.8308 | 9.0456 | 6.5986 | 16.0912 | 29.8601 | 8.8083 | 6.4255 | 15.0724 | 29.9565 | 8.6735 | 6.3272 | 14.6158 | 30.0933 | 8.5023 | 6.2023 | 14.3113 | 30.2812 | 8.3294 | 6.0762 | 13.9083 | 30.5502 | 8.1547 | 5.9488 | 13.4613 | 30.8744 | 7.8984 | 5.7617 | 12.9059 | 31.2377 | 7.5196 | 5.4855 | 11.952 | 31.5211 | 7.2032 | 5.2546 | 10.9948 | 31.7998 | 6.8784 | 5.0177 | 10.0639 | 32.6391 | 6.1111 | 4.458 | 7.4617 | 33.2429 | 5.5095 | 4.0191 | 5.2848 | 31.2875 | 5.0751 | 3.7022 | 3.9788 | 30.422 | 4.9347 | 3.5998 | 3.4003 | 29.196 | 4.7359 | 3.4548 | 3.7971 | 29.8136 | 9.0456 | 6.5986 | 16.0912 | 29.9166 | 8.8603 | 6.4635 | 15.3249 | 30.0302 | 8.7431 | 6.3779 | 14.9687 | 30.1628 | 8.6099 | 6.2808 | 14.7348 | 30.3301 | 8.4747 | 6.1822 | 14.4728 | 30.5688 | 8.3652 | 6.1023 | 14.1909 | 30.8665 | 8.2237 | 5.999 | 13.9022 | 31.1884 | 8.1031 | 5.9111 | 13.6031 | 31.4169 | 7.9649 | 5.8103 | 13.2616 | 31.6451 | 7.8298 | 5.7117 | 12.9178 | 32.3633 | 7.4341 | 5.4231 | 11.7956 | 32.9533 | 7.0957 | 5.1762 | 10.532 | 33.2899 | 6.7908 | 4.9538 | 9.5732 | 33.6057 | 6.5667 | 4.7903 | 8.6135 | 33.7976 | 6.4025 | 4.6705 | 7.914 | 29.8136 | 9.0456 | 6.5986 | 16.0912 | 29.8961 | 8.6926 | 6.3411 | 14.4328 | 30.0662 | 8.5138 | 6.2107 | 13.7566 | 30.2803 | 8.3235 | 6.0719 | 13.3346 | 30.533 | 8.1278 | 5.9291 | 12.8251 | 30.8119 | 7.9373 | 5.7902 | 12.3056 | 31.1294 | 7.6653 | 5.5917 | 11.6639 | 31.5276 | 7.2694 | 5.3029 | 10.5903 | 31.8287 | 6.932 | 5.0568 | 9.5571 | 32.12 | 6.5941 | 4.8103 | 8.5511 | 32.9118 | 5.779 | 4.2157 | 5.7269 | 31.6877 | 5.1401 | 3.7496 | 3.3752 | 28.7531 | 4.664 | 3.4024 | 1.9052 | 27.6565 | 4.4862 | 3.2726 | 1.1358 | 26.3337 | 4.2716 | 3.1161 | 1.4548
SALE MOOR | SALE | CARRINGTON | 379671 | 391133 | 11.6769 | 11.6769 | 11.6769 | 2.3351 | 11.7414 | 11.7414 | 11.7414 | 2.2793 | 11.8233 | 11.8233 | 11.8233 | 2.2166 | 11.9172 | 11.9172 | 11.9172 | 2.1468 | 12.0336 | 12.0336 | 12.0336 | 1.9904 | 12.167 | 12.167 | 12.167 | 1.8294 | 12.3206 | 12.3206 | 12.3206 | 1.6892 | 12.4968 | 12.4968 | 12.4968 | 1.5744 | 12.5992 | 12.5992 | 12.5992 | 1.4382 | 12.6951 | 12.6951 | 12.6951 | 1.3265 | 13.0602 | 13.0602 | 13.0602 | 0.29394 | 13.5263 | 13.5263 | 13.5263 | -1.6683 | 13.7944 | 13.7944 | 13.7944 | -3.3342 | 13.9904 | 13.9904 | 13.9904 | -5.0499 | 14.1203 | 14.1203 | 14.1203 | -6.6109 | 11.6526 | 11.6526 | 11.6526 | 2.3351 | 11.6973 | 11.6973 | 11.6973 | 2.2753 | 11.7374 | 11.7374 | 11.7374 | 2.2083 | 11.7796 | 11.7796 | 11.7796 | 2.1335 | 11.8417 | 11.8417 | 11.8417 | 2.0283 | 11.9214 | 11.9214 | 11.9214 | 1.9158 | 12.0173 | 12.0173 | 12.0173 | 1.7542 | 12.1252 | 12.1252 | 12.1252 | 1.5738 | 12.1981 | 12.1981 | 12.1981 | 1.409 | 12.2752 | 12.2752 | 12.2752 | 1.2412 | 12.5246 | 12.5246 | 12.5246 | 0.74534 | 12.7149 | 12.7149 | 12.7149 | 0.29101 | 12.894 | 12.894 | 12.894 | -0.12295 | 13.0638 | 13.0638 | 13.0638 | -0.53569 | 13.1816 | 13.1816 | 13.1816 | -0.81021 | 11.687 | 11.687 | 11.687 | 2.3351 | 11.7558 | 11.7558 | 11.7558 | 2.2953 | 11.8455 | 11.8455 | 11.8455 | 2.2513 | 11.9537 | 11.9537 | 11.9537 | 2.2067 | 12.0876 | 12.0876 | 12.0876 | 2.0798 | 12.2414 | 12.2414 | 12.2414 | 1.9527 | 12.4195 | 12.4195 | 12.4195 | 1.8591 | 12.5817 | 12.5817 | 12.5817 | 1.7945 | 12.6936 | 12.6936 | 12.6936 | 1.7176 | 12.7724 | 12.7724 | 12.7724 | 1.6506 | 13.1165 | 13.1165 | 13.1165 | 0.69175 | 13.6587 | 13.6587 | 13.6587 | -1.1703 | 13.8927 | 13.8927 | 13.8927 | -2.7363 | 14.085 | 14.085 | 14.085 | -4.3202 | 14.1963 | 14.1963 | 14.1963 | -5.7134 | 11.687 | 11.687 | 11.687 | 2.3351 | 11.6916 | 11.6916 | 11.6916 | 2.4652 | 11.7344 | 11.7344 | 11.7344 | 2.4756 | 11.7934 | 11.7934 | 11.7934 | 2.4557 | 11.8804 | 11.8804 | 11.8804 | 2.3527 | 12.0173 | 12.0173 | 12.0173 | 2.209 | 12.191 | 12.191 | 12.191 | 1.9665 | 12.3982 | 12.3982 | 12.3982 | 1.3676 | 12.563 | 12.563 | 12.563 | 0.73695 | 12.7246 | 12.7246 | 12.7246 | 0.10957 | 13.1838 | 13.1838 | 13.1838 | -1.7179 | 13.5295 | 13.5295 | 13.5295 | -3.4796 | 13.7392 | 13.7392 | 13.7392 | -4.9567 | 13.8853 | 13.8853 | 13.8853 | -5.8418 | 13.8646 | 13.8646 | 13.8646 | -5.0867 | 11.6768 | 11.6768 | 11.6768 | 2.3351 | 11.7281 | 11.7281 | 11.7281 | 2.2971 | 11.7829 | 11.7829 | 11.7829 | 2.2706 | 11.8341 | 11.8341 | 11.8341 | 2.2676 | 11.9046 | 11.9046 | 11.9046 | 2.2536 | 12.0173 | 12.0173 | 12.0173 | 2.1963 | 12.1657 | 12.1657 | 12.1657 | 2.1277 | 12.3289 | 12.3289 | 12.3289 | 2.0619 | 12.4278 | 12.4278 | 12.4278 | 1.9478 | 12.5141 | 12.5141 | 12.5141 | 1.8378 | 12.7754 | 12.7754 | 12.7754 | 1.4355 | 12.9998 | 12.9998 | 12.9998 | 0.90412 | 13.1674 | 13.1674 | 13.1674 | 0.51537 | 13.329 | 13.329 | 13.329 | 0.15954 | 13.4077 | 13.4077 | 13.4077 | 0.031531 | 11.6768 | 11.6768 | 11.6768 | 2.3351 | 11.7054 | 11.7054 | 11.7054 | 2.4204 | 11.7796 | 11.7796 | 11.7796 | 2.3712 | 11.8708 | 11.8708 | 11.8708 | 2.2795 | 11.9853 | 11.9853 | 11.9853 | 2.0971 | 12.1148 | 12.1148 | 12.1148 | 1.9145 | 12.2694 | 12.2694 | 12.2694 | 1.6351 | 12.481 | 12.481 | 12.481 | 0.97177 | 12.6515 | 12.6515 | 12.6515 | 0.28821 | 12.8175 | 12.8175 | 12.8175 | -0.39089 | 13.2755 | 13.2755 | 13.2755 | -2.36 | 13.6166 | 13.6166 | 13.6166 | -4.2225 | 13.8161 | 13.8161 | 13.8161 | -5.7968 | 13.9489 | 13.9489 | 13.9489 | -6.8224 | 13.9336 | 13.9336 | 13.9336 | -6.2538
SALFORD QUAYS | FREDERICK RD | KEARSLEY | 380334 | 397555 | 30.6987 | 14.5835 | 10.6385 | 18.2734 | 30.7494 | 14.2168 | 10.371 | 16.4286 | 30.8347 | 13.9108 | 10.1477 | 15.0839 | 30.9118 | 13.6078 | 9.9267 | 13.5232 | 30.9856 | 13.2671 | 9.6782 | 11.7947 | 31.0657 | 12.9052 | 9.4142 | 10.0713 | 31.1563 | 12.4697 | 9.0965 | 7.9359 | 31.264 | 12.197 | 8.8976 | 6.7062 | 31.3795 | 11.9166 | 8.693 | 5.4096 | 31.4947 | 11.7092 | 8.5417 | 4.6037 | 31.8367 | 11.1924 | 8.1647 | 1.9485 | 32.1464 | 10.7067 | 7.8104 | -0.37315 | 32.3596 | 10.4611 | 7.6312 | -1.3263 | 32.5335 | 10.1803 | 7.4264 | -2.3451 | 32.6465 | 9.8721 | 7.2016 | -3.2707 | 30.689 | 14.5835 | 10.6385 | 18.2734 | 30.7413 | 14.4593 | 10.5479 | 17.7249 | 30.8174 | 14.3866 | 10.4948 | 17.4417 | 30.883 | 14.3108 | 10.4396 | 17.282 | 30.9457 | 14.2384 | 10.3867 | 17.1458 | 31.0166 | 14.1582 | 10.3282 | 17.0097 | 31.0964 | 13.9777 | 10.1965 | 16.859 | 31.1855 | 13.9072 | 10.1451 | 16.6823 | 31.2705 | 13.8334 | 10.0913 | 16.4504 | 31.3576 | 13.7561 | 10.0349 | 16.2198 | 31.6276 | 13.5328 | 9.872 | 15.5482 | 31.9023 | 13.3683 | 9.752 | 14.8882 | 32.1542 | 13.2134 | 9.639 | 14.272 | 32.4262 | 13.0235 | 9.5005 | 13.5531 | 32.658 | 12.8693 | 9.388 | 12.8903 | 30.7016 | 14.5835 | 10.6385 | 18.2734 | 30.7563 | 14.1527 | 10.3242 | 16.1434 | 30.846 | 13.8446 | 10.0994 | 14.7414 | 30.9303 | 13.5078 | 9.8537 | 13.1784 | 31.0116 | 13.126 | 9.5752 | 11.4492 | 31.0997 | 12.7598 | 9.3081 | 9.7256 | 31.1997 | 12.2899 | 8.9653 | 7.5888 | 31.3178 | 11.9669 | 8.7297 | 6.3592 | 31.4284 | 11.756 | 8.5759 | 5.0939 | 31.5357 | 11.5868 | 8.4524 | 4.3241 | 31.8652 | 10.9811 | 8.0105 | 1.7782 | 32.174 | 10.487 | 7.6501 | -0.42014 | 32.3791 | 10.2261 | 7.4598 | -1.2378 | 32.5197 | 9.9194 | 7.236 | -2.0569 | 32.5691 | 9.6182 | 7.0163 | -2.7124 | 30.7016 | 14.5835 | 10.6385 | 18.2734 | 30.7287 | 14.2767 | 10.4147 | 16.7648 | 30.7961 | 14.0281 | 10.2333 | 15.5042 | 30.8547 | 13.6974 | 9.9921 | 13.9606 | 30.9126 | 13.3258 | 9.721 | 12.2469 | 30.9891 | 12.9453 | 9.4434 | 10.5297 | 31.0818 | 12.548 | 9.1536 | 8.3435 | 31.1868 | 12.2298 | 8.9215 | 6.9092 | 31.2941 | 11.8934 | 8.6761 | 5.4295 | 31.3998 | 11.6459 | 8.4955 | 4.4439 | 31.7136 | 10.9504 | 7.9882 | 1.5506 | 31.9998 | 10.3618 | 7.5588 | -0.61237 | 32.1823 | 10.0885 | 7.3594 | -1.3841 | 32.3029 | 9.9446 | 7.2544 | -1.9098 | 32.3157 | 9.8386 | 7.1771 | -1.7775 | 30.6987 | 14.5835 | 10.6385 | 18.2734 | 30.746 | 14.388 | 10.4958 | 17.3294 | 30.821 | 14.1188 | 10.2995 | 16.1777 | 30.8822 | 13.8298 | 10.0886 | 14.637 | 30.939 | 13.4979 | 9.8465 | 12.9452 | 31.0118 | 13.1411 | 9.5863 | 11.2522 | 31.1004 | 12.7188 | 9.2782 | 9.1307 | 31.1965 | 12.4425 | 9.0766 | 7.9068 | 31.2998 | 12.1642 | 8.8736 | 6.6059 | 31.4046 | 11.9624 | 8.7264 | 5.7892 | 31.7305 | 11.478 | 8.373 | 3.3359 | 32.0454 | 11.102 | 8.0987 | 1.5481 | 32.2706 | 10.9646 | 7.9985 | 1.0949 | 32.4579 | 10.7855 | 7.8679 | 0.64763 | 32.5683 | 10.5491 | 7.6954 | 0.37069 | 30.6987 | 14.5835 | 10.6385 | 18.2734 | 30.7366 | 14.1087 | 10.2921 | 15.9073 | 30.8195 | 13.8151 | 10.0779 | 14.4533 | 30.8962 | 13.4813 | 9.8344 | 12.8846 | 30.9689 | 13.1007 | 9.5568 | 11.1491 | 31.0464 | 12.7222 | 9.2806 | 9.4222 | 31.1345 | 12.3166 | 8.9848 | 7.2292 | 31.2435 | 11.9874 | 8.7446 | 5.7773 | 31.3496 | 11.6045 | 8.4653 | 3.9865 | 31.4531 | 11.3025 | 8.2451 | 2.6909 | 31.762 | 10.4546 | 7.6265 | -1.1289 | 32.0418 | 9.7147 | 7.0867 | -4.2161 | 32.2249 | 9.2973 | 6.7822 | -5.9177 | 32.3379 | 8.9008 | 6.493 | -7.6831 | 32.3526 | 8.5276 | 6.2207 | -9.1093
SAMLESBURY ENTERPRISE ZONE | PRESTON EAST | PENWORTHAM EAST / ROCHDALE | 362105 | 431439 | 27.5 | 18.802 | 13.5134 | 26.8333 | 27.5 | 18.6387 | 13.396 | 26.8333 | 27.5 | 18.4372 | 13.2512 | 26.7711 | 27.5 | 18.1394 | 13.0372 | 26.7089 | 27.5 | 18.014 | 12.947 | 26.6468 | 27.5 | 18.0874 | 12.9998 | 26.5846 | 27.5 | 18.0856 | 12.9985 | 26.5224 | 27.5 | 17.9952 | 12.9335 | 26.4602 | 27.5 | 17.8772 | 12.8487 | 26.4292 | 27.5 | 17.7156 | 12.7325 | 26.3981 | 27.5 | 17.3999 | 12.5056 | 26.3981 | 27.5 | 17.4941 | 12.5734 | 26.3981 | 27.5 | 17.4199 | 12.52 | 26.3981 | 27.5 | 17.3553 | 12.4736 | 26.3981 | 27.5 | 17.2605 | 12.4054 | 26.3981 | 27.5 | 18.802 | 13.5134 | 26.8333 | 27.5 | 18.7438 | 13.4716 | 26.8333 | 27.5 | 18.6594 | 13.4108 | 26.8229 | 27.5 | 18.5482 | 13.3309 | 26.8125 | 27.5 | 18.3832 | 13.2124 | 26.8022 | 27.5 | 18.131 | 13.0311 | 26.7918 | 27.5 | 18.1125 | 13.0178 | 26.7815 | 27.5 | 18.0462 | 12.9702 | 26.7711 | 27.5 | 18.0269 | 12.9563 | 26.7711 | 27.5 | 18.0078 | 12.9425 | 26.7711 | 27.5 | 17.9052 | 12.8688 | 26.7711 | 27.5 | 17.7678 | 12.7701 | 26.7711 | 27.5 | 17.8787 | 12.8497 | 26.7711 | 27.5 | 18.047 | 12.9707 | 26.7711 | 27.5 | 18.1207 | 13.0237 | 26.7711 | 27.5 | 18.802 | 13.5134 | 26.8333 | 27.5 | 18.6339 | 13.3925 | 26.8333 | 27.5 | 18.3864 | 13.2147 | 26.7711 | 27.5 | 18.0098 | 12.944 | 26.7089 | 27.5 | 18.0933 | 13.004 | 26.6468 | 27.5 | 18.1236 | 13.0258 | 26.5846 | 27.5 | 18.0229 | 12.9534 | 26.5224 | 27.5 | 17.8751 | 12.8472 | 26.4602 | 27.5 | 17.7084 | 12.7274 | 26.4292 | 27.5 | 17.559 | 12.62 | 26.3981 | 27.5 | 17.4967 | 12.5752 | 26.3981 | 27.5 | 17.3516 | 12.471 | 26.3981 | 27.5 | 17.2755 | 12.4163 | 26.3981 | 27.5 | 17.226 | 12.3807 | 26.3981 | 27.5 | 17.1436 | 12.3214 | 26.3981 | 27.5 | 18.802 | 13.5134 | 26.8333 | 27.5 | 18.6477 | 13.4025 | 26.8333 | 27.5 | 18.4839 | 13.2847 | 26.7711 | 27.5 | 18.3974 | 13.2226 | 26.7089 | 27.5 | 18.4255 | 13.2428 | 26.6468 | 27.5 | 18.1434 | 13.04 | 26.5846 | 27.5 | 17.9144 | 12.8754 | 26.5224 | 27.5 | 17.919 | 12.8787 | 26.4602 | 27.5 | 17.7857 | 12.7829 | 26.4292 | 27.5 | 17.6445 | 12.6815 | 26.3981 | 27.5 | 17.4478 | 12.5401 | 26.3981 | 27.5 | 17.3116 | 12.4422 | 26.3981 | 27.5 | 17.2114 | 12.3701 | 26.3981 | 27.5 | 17.1069 | 12.2951 | 26.3981 | 27.5 | 17.0462 | 12.2514 | 26.3981 | 27.5 | 18.802 | 13.5134 | 26.8333 | 27.5 | 18.6566 | 13.4089 | 26.8333 | 27.5 | 18.4485 | 13.2593 | 26.7711 | 27.5 | 18.1461 | 13.042 | 26.7089 | 27.5 | 18.0436 | 12.9683 | 26.6468 | 27.5 | 18.116 | 13.0203 | 26.5846 | 27.5 | 18.1168 | 13.0209 | 26.5224 | 27.5 | 18.0311 | 12.9593 | 26.4602 | 27.5 | 17.9078 | 12.8707 | 26.4292 | 27.5 | 17.7309 | 12.7436 | 26.3981 | 27.5 | 17.554 | 12.6164 | 26.3981 | 27.5 | 17.5976 | 12.6477 | 26.3981 | 27.5 | 17.544 | 12.6092 | 26.3981 | 27.5 | 17.5124 | 12.5865 | 26.3981 | 27.5 | 17.4503 | 12.5419 | 26.3981 | 27.5 | 18.802 | 13.5134 | 26.8333 | 27.5 | 18.636 | 13.3941 | 26.8333 | 27.5 | 18.4729 | 13.2768 | 26.7711 | 27.5 | 18.3682 | 13.2016 | 26.7089 | 27.5 | 18.395 | 13.2208 | 26.6468 | 27.5 | 18.1407 | 13.0381 | 26.5846 | 27.5 | 17.8235 | 12.8101 | 26.5224 | 27.5 | 17.8706 | 12.844 | 26.4602 | 27.5 | 17.7472 | 12.7553 | 26.4292 | 27.5 | 17.6099 | 12.6566 | 26.3981 | 27.5 | 17.4121 | 12.5144 | 26.3981 | 27.5 | 17.2755 | 12.4162 | 26.3981 | 27.5 | 17.1725 | 12.3422 | 26.3981 | 27.5 | 17.0696 | 12.2683 | 26.3981 | 27.5 | 16.9992 | 12.2177 | 26.3981
SANDGATE | BARROW & SANDGATE | HARKER / HUTTON | 321492 | 468870 | 29.4718 | 11.149 | 8.013 | 15.5782 | 29.5435 | 10.8308 | 7.7843 | 14.1789 | 29.6421 | 10.5231 | 7.5632 | 13.1941 | 29.7661 | 10.2513 | 7.3678 | 12.436 | 29.9245 | 9.9819 | 7.1742 | 11.4391 | 30.1127 | 9.72 | 6.9859 | 10.4283 | 30.3388 | 9.4731 | 6.8085 | 9.4278 | 30.5306 | 9.241 | 6.6417 | 8.4408 | 30.6799 | 9.0714 | 6.5198 | 7.8589 | 30.828 | 8.9175 | 6.4092 | 7.2942 | 31.3312 | 8.2139 | 5.9035 | 4.3123 | 31.8728 | 7.2077 | 5.1804 | -0.86601 | 32.2402 | 6.4786 | 4.6563 | -4.5958 | 32.5178 | 6.9142 | 4.9694 | -8.0953 | 32.6706 | 6.2278 | 4.4761 | -10.9347 | 29.4477 | 11.149 | 8.013 | 15.5782 | 29.537 | 10.8832 | 7.822 | 14.8473 | 29.6291 | 10.6374 | 7.6453 | 14.3349 | 29.7433 | 10.3791 | 7.4597 | 13.8869 | 29.8912 | 10.0966 | 7.2567 | 13.3667 | 30.0683 | 9.7935 | 7.0388 | 12.7961 | 30.2236 | 9.4385 | 6.7837 | 12.1215 | 30.4053 | 9.229 | 6.633 | 11.3474 | 30.4984 | 9.0948 | 6.5366 | 11.021 | 30.5987 | 8.9644 | 6.4429 | 10.6902 | 30.9297 | 8.5962 | 6.1782 | 9.6978 | 31.2527 | 8.3187 | 5.9788 | 8.7061 | 31.534 | 8.1003 | 5.8218 | 8.0722 | 31.813 | 8.613 | 6.1903 | 7.6238 | 31.9816 | 9.1257 | 6.5588 | 7.4011 | 29.4792 | 11.149 | 8.013 | 15.5782 | 29.5587 | 10.7677 | 7.7389 | 13.9808 | 29.6707 | 10.39 | 7.4675 | 12.9781 | 29.814 | 10.0916 | 7.2531 | 12.251 | 29.9962 | 9.8221 | 7.0593 | 11.2869 | 30.2123 | 9.5531 | 6.866 | 10.3147 | 30.4221 | 9.2983 | 6.6829 | 9.3724 | 30.624 | 9.048 | 6.5029 | 8.4452 | 30.7776 | 8.8693 | 6.3745 | 7.9354 | 30.922 | 8.6959 | 6.2499 | 7.4318 | 31.3614 | 7.8311 | 5.6284 | 4.6119 | 31.9183 | 6.6976 | 4.8137 | -0.4366 | 32.3311 | 6.0064 | 4.3169 | -4.0516 | 32.646 | 6.3382 | 4.5554 | -7.4061 | 32.7767 | 5.5715 | 4.0043 | -10.074 | 29.4792 | 11.149 | 8.013 | 15.5782 | 29.4487 | 10.9028 | 7.8361 | 14.734 | 29.4842 | 10.5806 | 7.6045 | 13.922 | 29.5404 | 10.3091 | 7.4094 | 13.2699 | 29.6413 | 10.0039 | 7.19 | 12.358 | 29.8103 | 9.778 | 7.0276 | 11.4185 | 30.0227 | 9.3062 | 6.6886 | 10.2681 | 30.2656 | 8.8861 | 6.3866 | 8.1663 | 30.4723 | 8.4473 | 6.0712 | 6.4263 | 30.6818 | 8.0688 | 5.7992 | 4.7077 | 31.2583 | 7.9391 | 5.706 | -0.26995 | 31.7214 | 6.8313 | 4.9098 | -5.0784 | 32.0374 | 5.9666 | 4.2883 | -8.3911 | 32.2283 | 5.3292 | 3.8302 | -10.1443 | 32.1452 | 5.3273 | 3.8288 | -8.5147 | 29.4718 | 11.149 | 8.013 | 15.5782 | 29.5336 | 10.8964 | 7.8314 | 14.4281 | 29.6008 | 10.6026 | 7.6203 | 13.5182 | 29.6736 | 10.3388 | 7.4307 | 12.8248 | 29.7744 | 10.0904 | 7.2522 | 11.953 | 29.9356 | 9.8508 | 7.08 | 11.0565 | 30.156 | 9.6162 | 6.9113 | 10.1149 | 30.3464 | 9.3872 | 6.7468 | 9.1441 | 30.4744 | 9.2143 | 6.6225 | 8.5489 | 30.6073 | 9.0548 | 6.5079 | 7.9489 | 31.0555 | 8.5388 | 6.137 | 6.0188 | 31.448 | 8.0885 | 5.8133 | 3.9958 | 31.6949 | 7.9123 | 5.6867 | 3.1055 | 31.8839 | 8.8912 | 6.3903 | 2.7481 | 31.9213 | 8.7281 | 6.2731 | 2.8281 | 29.4718 | 11.149 | 8.013 | 15.5782 | 29.4779 | 10.7664 | 7.738 | 14.0116 | 29.5672 | 10.4069 | 7.4797 | 12.9816 | 29.6883 | 10.1166 | 7.271 | 12.2095 | 29.8463 | 9.79 | 7.0363 | 11.1819 | 30.0303 | 9.5462 | 6.8611 | 10.1504 | 30.262 | 9.0856 | 6.53 | 8.9261 | 30.5535 | 8.6318 | 6.2039 | 6.8158 | 30.7651 | 8.1816 | 5.8803 | 5.0148 | 30.9767 | 7.79 | 5.5989 | 3.2331 | 31.5223 | 7.6207 | 5.4772 | -1.9543 | 31.9849 | 6.4641 | 4.6459 | -6.9611 | 32.3105 | 5.5544 | 3.992 | -10.5046 | 29.4316 | 4.8457 | 3.4827 | -12.5877 | 28.9936 | 4.7736 | 3.4309 | -11.3511
SCARISBRICK | SKELMERSDALE | WASHWAY FARM / KIRKBY | 338069 | 412086 | 6.1552 | 6.1552 | 6.1552 | 3.7568 | 6.1979 | 6.1979 | 6.1979 | 3.7293 | 6.2699 | 6.2699 | 6.2699 | 3.6738 | 6.3709 | 6.3709 | 6.3709 | 3.6252 | 6.4435 | 6.4435 | 6.4435 | 3.563 | 6.5174 | 6.5174 | 6.5174 | 3.4969 | 6.5952 | 6.5952 | 6.5952 | 3.4344 | 6.6862 | 6.6862 | 6.6862 | 3.3644 | 6.7695 | 6.7695 | 6.7695 | 3.2769 | 6.8527 | 6.8527 | 6.8527 | 3.19 | 7.1988 | 7.1988 | 7.1988 | 2.6184 | 7.4875 | 7.4875 | 7.4875 | 1.9225 | 7.6327 | 7.6327 | 7.6327 | 1.417 | 7.7369 | 7.7369 | 7.7369 | 1.0063 | 7.7932 | 7.7932 | 7.7932 | 0.72103 | 6.1366 | 6.1366 | 6.1366 | 3.7568 | 6.1584 | 6.1584 | 6.1584 | 3.7322 | 6.1839 | 6.1839 | 6.1839 | 3.6853 | 6.2239 | 6.2239 | 6.2239 | 3.6441 | 6.2827 | 6.2827 | 6.2827 | 3.5992 | 6.3593 | 6.3593 | 6.3593 | 3.5487 | 6.4235 | 6.4235 | 6.4235 | 3.4849 | 6.4725 | 6.4725 | 6.4725 | 3.3944 | 6.5144 | 6.5144 | 6.5144 | 3.3179 | 6.5591 | 6.5591 | 6.5591 | 3.2364 | 6.71 | 6.71 | 6.71 | 2.7915 | 6.8759 | 6.8759 | 6.8759 | 2.3803 | 7.046 | 7.046 | 7.046 | 2.0289 | 7.2426 | 7.2426 | 7.2426 | 1.6975 | 7.3866 | 7.3866 | 7.3866 | 1.5195 | 6.1641 | 6.1641 | 6.1641 | 3.7568 | 6.2137 | 6.2137 | 6.2137 | 3.7288 | 6.2973 | 6.2973 | 6.2973 | 3.6733 | 6.3887 | 6.3887 | 6.3887 | 3.6245 | 6.4569 | 6.4569 | 6.4569 | 3.563 | 6.5347 | 6.5347 | 6.5347 | 3.4982 | 6.6167 | 6.6167 | 6.6167 | 3.4373 | 6.7119 | 6.7119 | 6.7119 | 3.3702 | 6.7948 | 6.7948 | 6.7948 | 3.2973 | 6.8771 | 6.8771 | 6.8771 | 3.2318 | 7.2352 | 7.2352 | 7.2352 | 2.874 | 7.5051 | 7.5051 | 7.5051 | 2.2359 | 7.6513 | 7.6513 | 7.6513 | 1.775 | 7.7501 | 7.7501 | 7.7501 | 1.3546 | 7.7899 | 7.7899 | 7.7899 | 1.0477 | 6.1641 | 6.1641 | 6.1641 | 3.7568 | 6.1798 | 6.1798 | 6.1798 | 3.7744 | 6.2232 | 6.2232 | 6.2232 | 3.7418 | 6.2909 | 6.2909 | 6.2909 | 3.7073 | 6.39 | 6.39 | 6.39 | 3.6614 | 6.4812 | 6.4812 | 6.4812 | 3.6017 | 6.5833 | 6.5833 | 6.5833 | 3.5137 | 6.7499 | 6.7499 | 6.7499 | 3.3401 | 6.8839 | 6.8839 | 6.8839 | 3.1547 | 6.9778 | 6.9778 | 6.9778 | 2.9749 | 7.2383 | 7.2383 | 7.2383 | 2.4596 | 7.4533 | 7.4533 | 7.4533 | 1.9206 | 7.5807 | 7.5807 | 7.5807 | 1.5108 | 7.6552 | 7.6552 | 7.6552 | 1.3068 | 7.6407 | 7.6407 | 7.6407 | 1.5239 | 6.1552 | 6.1552 | 6.1552 | 3.7568 | 6.1898 | 6.1898 | 6.1898 | 3.7365 | 6.2375 | 6.2375 | 6.2375 | 3.6926 | 6.3006 | 6.3006 | 6.3006 | 3.6625 | 6.3852 | 6.3852 | 6.3852 | 3.6338 | 6.445 | 6.445 | 6.445 | 3.5946 | 6.51 | 6.51 | 6.51 | 3.5415 | 6.5919 | 6.5919 | 6.5919 | 3.4733 | 6.6713 | 6.6713 | 6.6713 | 3.3816 | 6.7553 | 6.7553 | 6.7553 | 3.2894 | 7.0459 | 7.0459 | 7.0459 | 2.8626 | 7.3534 | 7.3534 | 7.3534 | 2.3487 | 7.5243 | 7.5243 | 7.5243 | 2.0049 | 7.6235 | 7.6235 | 7.6235 | 1.7503 | 7.6463 | 7.6463 | 7.6463 | 1.7212 | 6.1552 | 6.1552 | 6.1552 | 3.7568 | 6.1885 | 6.1885 | 6.1885 | 3.7588 | 6.259 | 6.259 | 6.259 | 3.7044 | 6.3599 | 6.3599 | 6.3599 | 3.6447 | 6.4423 | 6.4423 | 6.4423 | 3.5771 | 6.5161 | 6.5161 | 6.5161 | 3.5091 | 6.6115 | 6.6115 | 6.6115 | 3.416 | 6.7777 | 6.7777 | 6.7777 | 3.226 | 6.9342 | 6.9342 | 6.9342 | 3.0295 | 7.0257 | 7.0257 | 7.0257 | 2.84 | 7.2832 | 7.2832 | 7.2832 | 2.1267 | 7.5047 | 7.5047 | 7.5047 | 1.4566 | 7.6517 | 7.6517 | 7.6517 | 0.9878 | 7.7271 | 7.7271 | 7.7271 | 0.74058 | 7.7149 | 7.7149 | 7.7149 | 0.91314
SEBERGHAM | CARLISLE | HARKER / HUTTON | 335344 | 542653 | 1.7205 | 1.7205 | 1.7205 | 0.7012 | 1.7471 | 1.7471 | 1.7471 | 0.53399 | 1.7891 | 1.7891 | 1.7891 | 0.44512 | 1.844 | 1.844 | 1.844 | 0.38314 | 1.912 | 1.912 | 1.912 | 0.294 | 1.9929 | 1.9929 | 1.9929 | 0.19951 | 2.0886 | 2.0886 | 2.0886 | 0.11658 | 2.2077 | 2.2077 | 2.2077 | 0.038518 | 2.3076 | 2.3076 | 2.3076 | -0.057446 | 2.3903 | 2.3903 | 2.3903 | -0.14353 | 2.6354 | 2.6354 | 2.6354 | -0.60757 | 2.8308 | 2.8308 | 2.8308 | -1.3309 | 2.9482 | 2.9482 | 2.9482 | -1.9015 | 3.024 | 3.024 | 3.024 | -2.4011 | 3.0598 | 3.0598 | 3.0598 | -2.8656 | 1.7082 | 1.7082 | 1.7082 | 0.7012 | 1.7386 | 1.7386 | 1.7386 | 0.61301 | 1.771 | 1.771 | 1.771 | 0.52456 | 1.8103 | 1.8103 | 1.8103 | 0.4378 | 1.8611 | 1.8611 | 1.8611 | 0.33958 | 1.9236 | 1.9236 | 1.9236 | 0.24642 | 1.9843 | 1.9843 | 1.9843 | 0.13565 | 2.0396 | 2.0396 | 2.0396 | 0.0066165 | 2.0808 | 2.0808 | 2.0808 | -0.092395 | 2.1256 | 2.1256 | 2.1256 | -0.193 | 2.2769 | 2.2769 | 2.2769 | -0.49483 | 2.4404 | 2.4404 | 2.4404 | -0.78287 | 2.5974 | 2.5974 | 2.5974 | -1.0664 | 2.77 | 2.77 | 2.77 | -1.4226 | 2.9095 | 2.9095 | 2.9095 | -1.7337 | 1.723 | 1.723 | 1.723 | 0.7012 | 1.7528 | 1.7528 | 1.7528 | 0.5227 | 1.7994 | 1.7994 | 1.7994 | 0.43884 | 1.8611 | 1.8611 | 1.8611 | 0.39223 | 1.9375 | 1.9375 | 1.9375 | 0.31916 | 2.0282 | 2.0282 | 2.0282 | 0.24405 | 2.1349 | 2.1349 | 2.1349 | 0.18709 | 2.2661 | 2.2661 | 2.2661 | 0.14008 | 2.3346 | 2.3346 | 2.3346 | 0.085167 | 2.3979 | 2.3979 | 2.3979 | 0.03212 | 2.5911 | 2.5911 | 2.5911 | -0.3396 | 2.8243 | 2.8243 | 2.8243 | -0.9835 | 2.9839 | 2.9839 | 2.9839 | -1.4838 | 3.0931 | 3.0931 | 3.0931 | -1.8922 | 3.1233 | 3.1233 | 3.1233 | -2.2453 | 1.723 | 1.723 | 1.723 | 0.7012 | 1.7332 | 1.7332 | 1.7332 | 0.60694 | 1.7581 | 1.7581 | 1.7581 | 0.54591 | 1.7938 | 1.7938 | 1.7938 | 0.48185 | 1.8442 | 1.8442 | 1.8442 | 0.40776 | 1.9216 | 1.9216 | 1.9216 | 0.32647 | 2.0195 | 2.0195 | 2.0195 | 0.22306 | 2.1331 | 2.1331 | 2.1331 | 0.02173 | 2.2312 | 2.2312 | 2.2312 | -0.20561 | 2.3319 | 2.3319 | 2.3319 | -0.4377 | 2.5797 | 2.5797 | 2.5797 | -1.1036 | 2.7673 | 2.7673 | 2.7673 | -1.7157 | 2.8839 | 2.8839 | 2.8839 | -2.1398 | 2.9539 | 2.9539 | 2.9539 | -2.3082 | 2.9599 | 2.9599 | 2.9599 | -2.0401 | 1.7205 | 1.7205 | 1.7205 | 0.7012 | 1.7438 | 1.7438 | 1.7438 | 0.60947 | 1.775 | 1.775 | 1.775 | 0.53913 | 1.8125 | 1.8125 | 1.8125 | 0.48681 | 1.8605 | 1.8605 | 1.8605 | 0.4326 | 1.9311 | 1.9311 | 1.9311 | 0.38334 | 2.0224 | 2.0224 | 2.0224 | 0.3339 | 2.1264 | 2.1264 | 2.1264 | 0.27941 | 2.206 | 2.206 | 2.206 | 0.19417 | 2.2716 | 2.2716 | 2.2716 | 0.10777 | 2.5168 | 2.5168 | 2.5168 | -0.22556 | 2.7525 | 2.7525 | 2.7525 | -0.63177 | 2.8832 | 2.8832 | 2.8832 | -0.89475 | 2.9769 | 2.9769 | 2.9769 | -1.1417 | 3.0119 | 3.0119 | 3.0119 | -1.2584 | 1.7205 | 1.7205 | 1.7205 | 0.7012 | 1.7413 | 1.7413 | 1.7413 | 0.52817 | 1.7826 | 1.7826 | 1.7826 | 0.42722 | 1.8384 | 1.8384 | 1.8384 | 0.32885 | 1.9057 | 1.9057 | 1.9057 | 0.2229 | 1.9845 | 1.9845 | 1.9845 | 0.11921 | 2.0775 | 2.0775 | 2.0775 | -0.0086372 | 2.1956 | 2.1956 | 2.1956 | -0.2449 | 2.2931 | 2.2931 | 2.2931 | -0.49381 | 2.3921 | 2.3921 | 2.3921 | -0.74671 | 2.6288 | 2.6288 | 2.6288 | -1.4795 | 2.8181 | 2.8181 | 2.8181 | -2.1576 | 2.9401 | 2.9401 | 2.9401 | -2.6395 | 3.0072 | 3.0072 | 3.0072 | -2.8624 | 3.0131 | 3.0131 | 3.0131 | -2.6457
SEDBERGH | KENDAL (PARKSIDE RD) | HARKER / HUTTON | 365151 | 491747 | 18.5719 | 18.5719 | 18.5719 | 12.9069 | 18.6844 | 18.6844 | 18.6844 | 12.6071 | 18.8334 | 18.8334 | 18.8334 | 12.4883 | 18.998 | 18.998 | 18.998 | 12.3852 | 19.1384 | 19.1384 | 19.1384 | 12.2341 | 19.3241 | 19.3241 | 19.1817 | 12.0553 | 19.5549 | 19.5549 | 19.1038 | 11.8588 | 19.8397 | 19.8397 | 19.0292 | 11.6153 | 20.1496 | 20.1496 | 18.9474 | 11.3169 | 20.4904 | 20.4904 | 18.8641 | 11.0041 | 21.3136 | 21.3136 | 18.4678 | 8.9743 | 21.9728 | 21.9728 | 18.0969 | 6.9492 | 22.3643 | 22.3643 | 17.8009 | 5.5809 | 22.6277 | 22.6277 | 17.474 | 4.543 | 22.7622 | 22.7622 | 17.2349 | 3.8437 | 18.5648 | 18.5648 | 18.5648 | 12.9069 | 18.6495 | 18.6495 | 18.6495 | 12.725 | 18.726 | 18.726 | 18.726 | 12.613 | 18.8376 | 18.8376 | 18.8376 | 12.4863 | 18.9918 | 18.9918 | 18.9918 | 12.3306 | 19.1325 | 19.1325 | 19.1325 | 12.1549 | 19.2711 | 19.2711 | 19.1666 | 11.9404 | 19.4307 | 19.4307 | 19.0896 | 11.6789 | 19.5796 | 19.5796 | 19.0242 | 11.4687 | 19.754 | 19.754 | 18.9552 | 11.2395 | 20.34 | 20.34 | 18.7383 | 10.4477 | 21.074 | 21.074 | 18.5201 | 9.5733 | 21.7365 | 21.7365 | 18.2592 | 8.303 | 22.2231 | 22.2231 | 17.9775 | 6.8616 | 22.529 | 22.529 | 17.7344 | 5.9052 | 18.5757 | 18.5757 | 18.5757 | 12.9069 | 18.6806 | 18.6806 | 18.6806 | 12.5832 | 18.8262 | 18.8262 | 18.8262 | 12.4709 | 18.9981 | 18.9981 | 18.9981 | 12.3916 | 19.1341 | 19.1341 | 19.1341 | 12.2689 | 19.3094 | 19.3094 | 19.1195 | 12.1277 | 19.5168 | 19.5168 | 19.0375 | 11.9851 | 19.7729 | 19.7729 | 18.9599 | 11.8198 | 20.0388 | 20.0388 | 18.8769 | 11.6162 | 20.3396 | 20.3396 | 18.7718 | 11.2377 | 21.1823 | 21.1823 | 18.3416 | 9.3434 | 21.8842 | 21.8842 | 17.897 | 7.193 | 22.3188 | 22.3188 | 17.4995 | 5.621 | 22.5949 | 22.5949 | 16.8594 | 4.4897 | 22.6997 | 22.6997 | 16.6674 | 3.8338 | 18.5757 | 18.5757 | 18.5757 | 12.9069 | 18.6334 | 18.6334 | 18.6334 | 12.7389 | 18.7243 | 18.7243 | 18.7243 | 12.6762 | 18.8613 | 18.8613 | 18.8613 | 12.6064 | 19.0307 | 19.0307 | 19.0307 | 12.4957 | 19.2083 | 19.2083 | 19.1182 | 12.3477 | 19.4522 | 19.4522 | 18.9406 | 12.1273 | 19.7499 | 19.7499 | 18.731 | 11.7025 | 20.073 | 20.073 | 18.5176 | 11.2137 | 20.3584 | 20.3584 | 18.1918 | 10.6967 | 21.14 | 21.14 | 17.6438 | 8.441 | 21.771 | 21.771 | 17.1816 | 6.487 | 22.131 | 22.131 | 16.5684 | 5.2136 | 22.342 | 21.8853 | 15.7294 | 4.474 | 22.3521 | 21.2373 | 15.2636 | 4.5424 | 18.5719 | 18.5719 | 18.5719 | 12.9069 | 18.6606 | 18.6606 | 18.6606 | 12.6749 | 18.7627 | 18.7627 | 18.7627 | 12.5863 | 18.8941 | 18.8941 | 18.8941 | 12.5149 | 19.035 | 19.035 | 19.035 | 12.4259 | 19.1855 | 19.1855 | 19.1855 | 12.3093 | 19.3915 | 19.3915 | 19.1545 | 12.1575 | 19.6213 | 19.6213 | 19.0875 | 11.9695 | 19.8641 | 19.8641 | 19.0121 | 11.7184 | 20.1398 | 20.1398 | 18.9334 | 11.4417 | 20.9984 | 20.9984 | 18.607 | 9.9147 | 21.6467 | 21.6467 | 18.2849 | 8.2087 | 22.0686 | 22.0686 | 18.023 | 7.0663 | 22.3617 | 22.3617 | 17.7571 | 6.3007 | 22.4649 | 22.4649 | 17.5623 | 6.0161 | 18.5719 | 18.5719 | 18.5719 | 12.9069 | 18.6574 | 18.6574 | 18.6574 | 12.5976 | 18.7956 | 18.7956 | 18.7956 | 12.4708 | 18.9625 | 18.9625 | 18.9625 | 12.3512 | 19.0879 | 19.0879 | 19.0879 | 12.1983 | 19.2492 | 19.2492 | 19.0643 | 12.0295 | 19.4591 | 19.4591 | 18.885 | 11.7926 | 19.7275 | 19.7275 | 18.6734 | 11.3425 | 20.007 | 20.007 | 18.4617 | 10.8551 | 20.3224 | 20.3224 | 18.2009 | 10.3363 | 21.3 | 21.3 | 17.6276 | 8.4249 | 21.9558 | 21.9558 | 17.1443 | 6.2336 | 22.3834 | 22.3834 | 16.562 | 4.6972 | 22.6284 | 21.7936 | 15.6635 | 3.7828 | 22.6544 | 21.076 | 15.1477 | 3.7703
SELSMIRE | PENRITH & SHAP | HARKER / HUTTON | 361018 | 507505 | 4.4707 | 4.4707 | 4.4707 | 1.1663 | 4.5069 | 4.5069 | 4.5069 | 0.46943 | 4.5839 | 4.5839 | 4.5839 | 0.22562 | 4.7133 | 4.7133 | 4.7133 | 0.018774 | 4.9167 | 4.9167 | 4.9167 | -0.32149 | 5.1734 | 5.1734 | 5.1734 | -0.85014 | 5.4893 | 5.4893 | 5.4893 | -1.6258 | 5.7953 | 5.7953 | 5.7953 | -2.6977 | 6.1728 | 6.1728 | 6.1728 | -4.0554 | 6.6008 | 6.6008 | 6.6008 | -5.6187 | 7.9833 | 7.9833 | 7.9833 | -10.7084 | 9.1207 | 9.1207 | 9.1207 | -14.8451 | 9.8053 | 9.8053 | 9.8053 | -17.2984 | 10.2224 | 10.2224 | 10.2224 | -18.7247 | 10.4322 | 10.4322 | 10.4322 | -19.4133 | 4.4707 | 4.4707 | 4.4707 | 1.1663 | 4.5038 | 4.5038 | 4.5038 | 0.85841 | 4.5583 | 4.5583 | 4.5583 | 0.7253 | 4.6369 | 4.6369 | 4.6369 | 0.60052 | 4.7471 | 4.7471 | 4.7471 | 0.43648 | 4.8894 | 4.8894 | 4.8894 | 0.22415 | 5.0289 | 5.0289 | 5.0289 | -0.060661 | 5.1947 | 5.1947 | 5.1947 | -0.43512 | 5.3861 | 5.3861 | 5.3861 | -0.90852 | 5.6125 | 5.6125 | 5.6125 | -1.4982 | 6.3325 | 6.3325 | 6.3325 | -4.0277 | 7.2757 | 7.2757 | 7.2757 | -7.4802 | 8.2777 | 8.2777 | 8.2777 | -11.2362 | 9.3635 | 9.3635 | 9.3635 | -15.3743 | 10.0608 | 10.0608 | 10.0608 | -18.0605 | 4.4707 | 4.4707 | 4.4707 | 1.1663 | 4.5034 | 4.5034 | 4.5034 | 0.36583 | 4.5733 | 4.5733 | 4.5733 | 0.11467 | 4.6839 | 4.6839 | 4.6839 | -0.05851 | 4.8524 | 4.8524 | 4.8524 | -0.33665 | 5.0786 | 5.0786 | 5.0786 | -0.76011 | 5.3555 | 5.3555 | 5.3555 | -1.3692 | 5.6395 | 5.6395 | 5.6395 | -2.2042 | 5.9434 | 5.9434 | 5.9434 | -3.2695 | 6.3019 | 6.3019 | 6.3019 | -4.5568 | 7.6369 | 7.6369 | 7.6369 | -9.4565 | 8.9437 | 8.9437 | 8.9437 | -14.2648 | 9.815 | 9.815 | 9.815 | -17.4599 | 10.3388 | 10.3388 | 10.3388 | -19.3142 | 10.554 | 10.554 | 10.554 | -20.0341 | 4.4707 | 4.4707 | 4.4707 | 1.1663 | 4.4882 | 4.4882 | 4.4882 | 0.61488 | 4.5476 | 4.5476 | 4.5476 | 0.40453 | 4.6579 | 4.6579 | 4.6579 | 0.20028 | 4.8437 | 4.8437 | 4.8437 | -0.1295 | 5.1373 | 5.1373 | 5.1373 | -0.6554 | 5.4329 | 5.4329 | 5.4329 | -1.4457 | 5.7481 | 5.7481 | 5.7481 | -2.5677 | 6.1337 | 6.1337 | 6.1337 | -3.9769 | 6.5713 | 6.5713 | 6.5713 | -5.5955 | 7.9622 | 7.9622 | 7.9622 | -10.7593 | 9.0861 | 9.0861 | 9.0861 | -14.8501 | 9.7545 | 9.7545 | 9.7545 | -17.2364 | 10.1338 | 10.1338 | 10.1338 | -18.5151 | 10.25 | 10.25 | 10.25 | -18.8727 | 4.4707 | 4.4707 | 4.4707 | 1.1663 | 4.4999 | 4.4999 | 4.4999 | 0.6017 | 4.5599 | 4.5599 | 4.5599 | 0.40534 | 4.656 | 4.656 | 4.656 | 0.24491 | 4.8102 | 4.8102 | 4.8102 | -0.0094267 | 5.0447 | 5.0447 | 5.0447 | -0.4082 | 5.3215 | 5.3215 | 5.3215 | -0.99723 | 5.5779 | 5.5779 | 5.5779 | -1.802 | 5.8701 | 5.8701 | 5.8701 | -2.8348 | 6.2107 | 6.2107 | 6.2107 | -4.0603 | 7.4435 | 7.4435 | 7.4435 | -8.5695 | 8.6209 | 8.6209 | 8.6209 | -12.8633 | 9.4003 | 9.4003 | 9.4003 | -15.6829 | 9.8772 | 9.8772 | 9.8772 | -17.347 | 10.0478 | 10.0478 | 10.0478 | -17.9261 | 4.4707 | 4.4707 | 4.4707 | 1.1663 | 4.496 | 4.496 | 4.496 | 0.28052 | 4.5651 | 4.5651 | 4.5651 | 0.0077017 | 4.6762 | 4.6762 | 4.6762 | -0.18517 | 4.845 | 4.845 | 4.845 | -0.47257 | 5.0638 | 5.0638 | 5.0638 | -0.90137 | 5.3486 | 5.3486 | 5.3486 | -1.5306 | 5.6608 | 5.6608 | 5.6608 | -2.4325 | 5.9853 | 5.9853 | 5.9853 | -3.5709 | 6.3651 | 6.3651 | 6.3651 | -4.9347 | 7.7345 | 7.7345 | 7.7345 | -9.9631 | 9.0383 | 9.0383 | 9.0383 | -14.7641 | 9.9034 | 9.9034 | 9.9034 | -17.932 | 10.3992 | 10.3992 | 10.3992 | -19.6904 | 10.5437 | 10.5437 | 10.5437 | -20.1573
SETTLE | PADIHAM | PADIHAM | 381588 | 463721 | 13.5014 | 13.5014 | 13.5014 | 8.2564 | 13.5237 | 13.5237 | 13.5237 | 8.2052 | 13.5486 | 13.5486 | 13.5486 | 8.1588 | 13.5794 | 13.5794 | 13.5794 | 8.1215 | 13.628 | 13.628 | 13.628 | 8.057 | 13.6842 | 13.6842 | 13.6842 | 7.9852 | 13.7456 | 13.7456 | 13.7456 | 7.9207 | 13.8177 | 13.8177 | 13.8177 | 7.8558 | 13.8853 | 13.8853 | 13.8853 | 7.7878 | 13.9529 | 13.9529 | 13.9529 | 7.7264 | 14.2333 | 14.2333 | 14.2333 | 7.2345 | 14.428 | 14.428 | 14.428 | 6.286 | 14.5433 | 14.5433 | 14.5433 | 5.4973 | 14.6274 | 14.6274 | 14.6274 | 4.6939 | 14.6764 | 14.6764 | 14.6764 | 3.9554 | 13.5015 | 13.5015 | 13.5015 | 8.2564 | 13.5251 | 13.5251 | 13.5251 | 8.1925 | 13.5484 | 13.5484 | 13.5484 | 8.123 | 13.5793 | 13.5793 | 13.5793 | 8.0575 | 13.6209 | 13.6209 | 13.6209 | 7.9879 | 13.6689 | 13.6689 | 13.6689 | 7.9177 | 13.7284 | 13.7284 | 13.7284 | 7.8283 | 13.8022 | 13.8022 | 13.8022 | 7.7069 | 13.8482 | 13.8482 | 13.8482 | 7.6376 | 13.8965 | 13.8965 | 13.8965 | 7.5697 | 14.056 | 14.056 | 14.056 | 7.3636 | 14.2282 | 14.2282 | 14.2282 | 7.1033 | 14.3963 | 14.3963 | 14.3963 | 6.8399 | 14.539 | 14.539 | 14.539 | 6.5039 | 14.6301 | 14.6301 | 14.6301 | 6.2218 | 13.501 | 13.501 | 13.501 | 8.2564 | 13.5241 | 13.5241 | 13.5241 | 8.204 | 13.5477 | 13.5477 | 13.5477 | 8.1577 | 13.5767 | 13.5767 | 13.5767 | 8.12 | 13.6229 | 13.6229 | 13.6229 | 8.0558 | 13.6757 | 13.6757 | 13.6757 | 7.9846 | 13.7324 | 13.7324 | 13.7324 | 7.9209 | 13.7966 | 13.7966 | 13.7966 | 7.8576 | 13.8569 | 13.8569 | 13.8569 | 7.8011 | 13.9174 | 13.9174 | 13.9174 | 7.7523 | 14.1906 | 14.1906 | 14.1906 | 7.3598 | 14.4439 | 14.4439 | 14.4439 | 6.4659 | 14.5695 | 14.5695 | 14.5695 | 5.7109 | 14.6528 | 14.6528 | 14.6528 | 4.9606 | 14.6877 | 14.6877 | 14.6877 | 4.2962 | 13.501 | 13.501 | 13.501 | 8.2564 | 13.4865 | 13.4865 | 13.4865 | 8.2783 | 13.4924 | 13.4924 | 13.4924 | 8.2508 | 13.511 | 13.511 | 13.511 | 8.2135 | 13.5467 | 13.5467 | 13.5467 | 8.1564 | 13.5947 | 13.5947 | 13.5947 | 8.0942 | 13.6618 | 13.6618 | 13.6618 | 7.9925 | 13.7756 | 13.7756 | 13.7756 | 7.749 | 13.8931 | 13.8931 | 13.8931 | 7.4539 | 14.0126 | 14.0126 | 14.0126 | 7.1418 | 14.2104 | 14.2104 | 14.2104 | 6.241 | 14.3741 | 14.3741 | 14.3741 | 5.3799 | 14.4766 | 14.4766 | 14.4766 | 4.7102 | 14.5323 | 14.5323 | 14.5323 | 4.3049 | 14.5173 | 14.5173 | 14.5173 | 4.5679 | 13.5014 | 13.5014 | 13.5014 | 8.2564 | 13.5203 | 13.5203 | 13.5203 | 8.2106 | 13.5391 | 13.5391 | 13.5391 | 8.1653 | 13.5604 | 13.5604 | 13.5604 | 8.1323 | 13.5918 | 13.5918 | 13.5918 | 8.0969 | 13.6332 | 13.6332 | 13.6332 | 8.0622 | 13.6858 | 13.6858 | 13.6858 | 8.0203 | 13.7501 | 13.7501 | 13.7501 | 7.961 | 13.8138 | 13.8138 | 13.8138 | 7.8854 | 13.8807 | 13.8807 | 13.8807 | 7.8098 | 14.1131 | 14.1131 | 14.1131 | 7.5447 | 14.3448 | 14.3448 | 14.3448 | 7.1738 | 14.4558 | 14.4558 | 14.4558 | 6.9147 | 14.5308 | 14.5308 | 14.5308 | 6.6533 | 14.5566 | 14.5566 | 14.5566 | 6.5105 | 13.5014 | 13.5014 | 13.5014 | 8.2564 | 13.4978 | 13.4978 | 13.4978 | 8.2662 | 13.5179 | 13.5179 | 13.5179 | 8.2242 | 13.5525 | 13.5525 | 13.5525 | 8.1706 | 13.6023 | 13.6023 | 13.6023 | 8.0978 | 13.657 | 13.657 | 13.657 | 8.0232 | 13.7287 | 13.7287 | 13.7287 | 7.9098 | 13.8512 | 13.8512 | 13.8512 | 7.6406 | 13.9679 | 13.9679 | 13.9679 | 7.3226 | 14.05 | 14.05 | 14.05 | 7.0036 | 14.2385 | 14.2385 | 14.2385 | 6.0691 | 14.4154 | 14.4154 | 14.4154 | 5.1689 | 14.5333 | 14.5333 | 14.5333 | 4.4526 | 14.5985 | 14.5985 | 14.5985 | 3.9843 | 14.5928 | 14.5928 | 14.5928 | 4.1755
MOSS SIDE (Leyland) & SEVEN STARS | LEYLAND | PENWORTHAM WEST / STANAH | 352653 | 421636 | 31.2714 | 14.2896 | 10.2702 | 10.238 | 31.3646 | 13.3703 | 9.6095 | 6.8138 | 31.498 | 12.7247 | 9.1455 | 6.0171 | 31.6599 | 12.3605 | 8.8838 | 5.8515 | 31.8778 | 11.7936 | 8.4763 | 5.5695 | 32.1556 | 11.1011 | 7.9786 | 5.2319 | 32.5082 | 10.4446 | 7.5067 | 4.8274 | 32.9545 | 10.0386 | 7.215 | 4.3914 | 33.3926 | 9.7125 | 6.9806 | 3.7028 | 33.8504 | 9.4085 | 6.7621 | 3.0111 | 35.3091 | 8.3292 | 5.9864 | 0.22556 | 36.458 | 7.275 | 5.2287 | -3.2017 | 37.1917 | 6.5485 | 4.7065 | -5.7707 | 34.9436 | 5.7532 | 4.1349 | -7.9914 | 30.3702 | 5.0002 | 3.5938 | -9.7309 | 31.2381 | 14.2896 | 10.2702 | 10.238 | 31.3199 | 13.866 | 9.9658 | 8.7557 | 31.4022 | 13.6594 | 9.8173 | 8.2982 | 31.4894 | 13.4679 | 9.6796 | 8.1341 | 31.6001 | 13.4178 | 9.6436 | 7.9374 | 31.7415 | 13.2445 | 9.5191 | 7.6807 | 31.9209 | 12.9592 | 9.314 | 7.3534 | 32.1375 | 12.756 | 9.168 | 6.9101 | 32.3594 | 12.5637 | 9.0298 | 6.3888 | 32.6117 | 12.336 | 8.8661 | 5.84 | 33.5643 | 11.6276 | 8.357 | 4.057 | 34.6398 | 11.0336 | 7.93 | 2.0893 | 35.6521 | 10.4319 | 7.4976 | 0.26947 | 36.5579 | 9.7483 | 7.0063 | -1.5923 | 37.0967 | 9.0361 | 6.4944 | -2.8015 | 31.2783 | 14.2896 | 10.2702 | 10.238 | 31.3679 | 13.198 | 9.4856 | 6.2577 | 31.5032 | 12.5243 | 9.0015 | 5.3659 | 31.6669 | 12.0526 | 8.6624 | 5.2015 | 31.8822 | 11.4767 | 8.2485 | 5.0245 | 32.1499 | 10.7492 | 7.7257 | 4.83 | 32.4828 | 10.097 | 7.2569 | 4.6168 | 32.8977 | 9.6683 | 6.9488 | 4.3519 | 33.2661 | 9.3168 | 6.6962 | 3.8675 | 33.6689 | 9.1252 | 6.5585 | 3.3345 | 35.1236 | 8.2331 | 5.9173 | 0.86847 | 36.3191 | 7.1033 | 5.1053 | -2.4616 | 37.0995 | 6.1505 | 4.4205 | -4.9724 | 31.603 | 5.2032 | 3.7396 | -7.0252 | 26.951 | 4.4373 | 3.1892 | -8.4546 | 31.2784 | 14.2896 | 10.2702 | 10.238 | 31.2825 | 13.5169 | 9.7148 | 7.5843 | 31.3686 | 13.0652 | 9.3902 | 6.9788 | 31.4857 | 12.5304 | 9.0059 | 6.8887 | 31.6691 | 12.0091 | 8.6312 | 6.7649 | 31.9469 | 11.5218 | 8.281 | 6.5834 | 32.3326 | 10.8607 | 7.8058 | 6.1679 | 32.8624 | 10.3582 | 7.4446 | 5.2686 | 33.4249 | 9.8712 | 7.0946 | 4.2166 | 33.923 | 9.263 | 6.6575 | 3.0851 | 35.2123 | 8.0871 | 5.8123 | -0.27335 | 36.3178 | 6.9424 | 4.9896 | -3.3308 | 36.8403 | 6.0655 | 4.3594 | -5.5225 | 32.7978 | 5.3999 | 3.881 | -6.7192 | 31.8311 | 5.2408 | 3.7666 | -5.9672 | 31.2713 | 14.2896 | 10.2702 | 10.238 | 31.3443 | 13.5037 | 9.7054 | 7.4218 | 31.4396 | 12.974 | 9.3246 | 6.7727 | 31.5379 | 12.604 | 9.0588 | 6.6849 | 31.6698 | 12.0908 | 8.6899 | 6.619 | 31.8762 | 11.448 | 8.2279 | 6.5 | 32.163 | 10.8255 | 7.7805 | 6.2728 | 32.5135 | 10.4232 | 7.4914 | 5.9479 | 32.8993 | 10.1259 | 7.2777 | 5.4038 | 33.3052 | 9.8284 | 7.0639 | 4.7896 | 34.6619 | 9.0828 | 6.528 | 2.6849 | 35.7846 | 8.4918 | 6.1032 | 0.56642 | 36.4939 | 8.0335 | 5.7738 | -0.8718 | 36.9563 | 7.514 | 5.4005 | -1.9158 | 37.1005 | 7.1413 | 5.1326 | -2.2137 | 31.2713 | 14.2896 | 10.2702 | 10.238 | 31.2921 | 13.1339 | 9.4396 | 5.8697 | 31.4099 | 12.4875 | 8.975 | 4.9003 | 31.5615 | 11.9714 | 8.6041 | 4.7249 | 31.7637 | 11.2991 | 8.1209 | 3.9275 | 32.0121 | 10.617 | 7.6307 | 3.0229 | 32.3412 | 9.8462 | 7.0766 | 1.9693 | 32.8266 | 9.1516 | 6.5774 | 0.41572 | 33.335 | 8.668 | 6.2299 | -0.66873 | 33.8857 | 8.0916 | 5.8156 | -1.807 | 35.1989 | 6.6427 | 4.7743 | -5.3191 | 33.363 | 5.493 | 3.9479 | -8.6962 | 27.1045 | 4.4626 | 3.2073 | -11.2025 | 22.8269 | 3.7583 | 2.7011 | -12.6417 | 21.7157 | 3.5753 | 2.5697 | -12.0711
SHANNON ST SOUTH | BLACKPOOL | PENWORTHAM WEST / STANAH | 330806 | 435291 | 31.8792 | 11.3573 | 8.285 | 11.9696 | 32.2135 | 10.8991 | 7.9507 | 9.9631 | 32.4572 | 10.7218 | 7.8214 | 9.5681 | 32.6286 | 10.5948 | 7.7287 | 9.4927 | 32.893 | 10.4239 | 7.6041 | 9.3176 | 33.2016 | 10.2088 | 7.4472 | 9.1097 | 33.5351 | 10.0386 | 7.323 | 8.9099 | 33.8795 | 9.8526 | 7.1873 | 8.7245 | 34.1805 | 9.7152 | 7.0871 | 8.5423 | 34.4784 | 9.5869 | 6.9935 | 8.3807 | 36.101 | 8.944 | 6.5245 | 6.6036 | 37.0789 | 8.0127 | 5.8452 | 2.354 | 37.6698 | 7.3223 | 5.3415 | -1.1444 | 38.1115 | 6.5765 | 4.7975 | -4.8083 | 36.1399 | 5.8622 | 4.2764 | -7.8821 | 31.8594 | 11.3573 | 8.285 | 11.9696 | 32.1562 | 11.1588 | 8.1402 | 11.1201 | 32.3736 | 11.0198 | 8.0388 | 10.794 | 32.5061 | 10.8258 | 7.8973 | 10.4748 | 32.6821 | 10.5412 | 7.6896 | 9.5103 | 32.8439 | 10.2254 | 7.4593 | 8.3377 | 33.0512 | 9.683 | 7.0636 | 6.9211 | 33.3055 | 9.2778 | 6.768 | 5.2324 | 33.4601 | 9.1406 | 6.6679 | 5.0883 | 33.6361 | 9.0116 | 6.5738 | 4.9419 | 34.3349 | 8.622 | 6.2897 | 4.4997 | 35.1767 | 8.3157 | 6.0662 | 4.0826 | 35.9777 | 8.0879 | 5.9 | 3.7589 | 36.7755 | 7.9399 | 5.792 | 2.9888 | 37.31 | 7.6801 | 5.6025 | 1.9832 | 31.8865 | 11.3573 | 8.285 | 11.9696 | 32.1636 | 10.8198 | 7.8929 | 9.6888 | 32.394 | 10.5735 | 7.7132 | 9.2678 | 32.5798 | 10.4206 | 7.6017 | 9.235 | 32.8239 | 10.2108 | 7.4486 | 9.1034 | 33.1051 | 9.9946 | 7.2909 | 8.9463 | 33.4056 | 9.801 | 7.1497 | 8.822 | 33.7118 | 9.5971 | 7.0009 | 8.712 | 33.9706 | 9.4322 | 6.8806 | 8.6298 | 34.2406 | 9.2634 | 6.7575 | 8.5466 | 35.8619 | 8.573 | 6.2539 | 7.0402 | 36.9362 | 7.6538 | 5.5834 | 3.0697 | 37.594 | 6.8054 | 4.9644 | -0.3355 | 36.7384 | 5.9593 | 4.3472 | -3.8514 | 31.9229 | 5.1782 | 3.7774 | -6.6762 | 31.8871 | 11.3573 | 8.285 | 11.9696 | 32.0915 | 11.0133 | 8.034 | 10.6404 | 32.2641 | 10.8792 | 7.9363 | 10.43 | 32.4547 | 10.7474 | 7.8401 | 10.438 | 32.7224 | 10.5865 | 7.7227 | 10.3262 | 33.0514 | 10.4503 | 7.6234 | 10.1758 | 33.5421 | 10.2278 | 7.461 | 9.8365 | 34.0586 | 9.9129 | 7.2314 | 8.8231 | 34.5468 | 9.5926 | 6.9977 | 7.6338 | 34.947 | 9.2027 | 6.7132 | 6.3009 | 35.893 | 8.3939 | 6.1232 | 2.4368 | 36.7141 | 7.423 | 5.415 | -1.4003 | 37.2607 | 6.5812 | 4.8009 | -4.4129 | 37.1422 | 6.0248 | 4.395 | -6.2415 | 36.2615 | 5.882 | 4.2908 | -4.8887 | 31.8786 | 11.3573 | 8.285 | 11.9696 | 32.1374 | 11.0478 | 8.0592 | 10.6501 | 32.3232 | 10.9066 | 7.9562 | 10.4073 | 32.4801 | 10.7876 | 7.8694 | 10.4003 | 32.6306 | 10.6429 | 7.7639 | 10.3563 | 32.7897 | 10.454 | 7.626 | 10.3012 | 32.9768 | 10.3061 | 7.5181 | 10.21 | 33.2001 | 10.125 | 7.3861 | 10.0546 | 33.4161 | 9.9928 | 7.2896 | 9.908 | 33.6567 | 9.8605 | 7.1931 | 9.7318 | 34.5689 | 9.4089 | 6.8637 | 9.006 | 35.5531 | 8.999 | 6.5646 | 7.5468 | 36.285 | 8.5937 | 6.269 | 5.3589 | 36.9386 | 8.2061 | 5.9863 | 3.5237 | 37.1972 | 7.9497 | 5.7992 | 2.6657 | 31.8786 | 11.3573 | 8.285 | 11.9696 | 32.0805 | 10.8138 | 7.8885 | 9.6566 | 32.2893 | 10.6293 | 7.7539 | 9.1908 | 32.4769 | 10.4737 | 7.6404 | 9.0915 | 32.7497 | 10.2899 | 7.5064 | 8.8777 | 33.0535 | 10.1356 | 7.3938 | 8.6465 | 33.4738 | 9.8939 | 7.2174 | 8.2112 | 33.9391 | 9.5545 | 6.9699 | 7.0826 | 34.3748 | 9.2332 | 6.7355 | 5.9104 | 34.8525 | 8.8344 | 6.4446 | 4.531 | 35.9509 | 7.9657 | 5.8109 | 0.47929 | 36.8755 | 6.9597 | 5.077 | -3.4417 | 37.3141 | 6.0527 | 4.4154 | -6.7539 | 33.4533 | 5.4265 | 3.9585 | -8.9623 | 32.1234 | 5.2107 | 3.8012 | -8.0037
SHAP | PENRITH & SHAP | HARKER / HUTTON | 356910 | 513357 | 12.4481 | 12.4481 | 12.4481 | 6.1616 | 12.4696 | 12.4696 | 12.4696 | 5.9407 | 12.4945 | 12.4945 | 12.4945 | 5.8502 | 12.5217 | 12.5217 | 12.5217 | 5.829 | 12.5611 | 12.5611 | 12.5611 | 5.8194 | 12.5924 | 12.5924 | 12.5924 | 5.808 | 12.6267 | 12.6267 | 12.6267 | 5.7989 | 12.6669 | 12.6669 | 12.6669 | 5.7871 | 12.7128 | 12.7128 | 12.7128 | 5.7261 | 12.7602 | 12.7602 | 12.7602 | 5.6674 | 14.9789 | 14.9789 | 14.8496 | 3.3523 | 15.2887 | 15.2887 | 14.7013 | 2.8956 | 17.3891 | 17.3891 | 14.3103 | 0.65294 | 17.4699 | 17.4699 | 14.2489 | 0.42518 | 17.5795 | 17.5795 | 14.1375 | 0.21199 | 12.4469 | 12.4469 | 12.4469 | 6.1616 | 12.4655 | 12.4655 | 12.4655 | 6.1377 | 12.4873 | 12.4873 | 12.4873 | 6.0817 | 12.5082 | 12.5082 | 12.5082 | 6.0621 | 12.5307 | 12.5307 | 12.5307 | 6.0649 | 12.5501 | 12.5501 | 12.5501 | 6.0223 | 12.5748 | 12.5748 | 12.5748 | 5.9372 | 12.607 | 12.607 | 12.607 | 5.8345 | 12.6463 | 12.6463 | 12.6463 | 5.7793 | 12.6892 | 12.6892 | 12.6892 | 5.725 | 12.8418 | 12.8418 | 12.8418 | 5.5616 | 13.0243 | 13.0243 | 13.0243 | 5.4047 | 13.2164 | 13.2164 | 13.2164 | 5.2695 | 13.4131 | 13.4131 | 13.4131 | 5.1467 | 17.6452 | 17.6452 | 14.3829 | 0.88849 | 12.4486 | 12.4486 | 12.4486 | 6.1616 | 12.4712 | 12.4712 | 12.4712 | 5.9032 | 12.4969 | 12.4969 | 12.4969 | 5.806 | 12.5172 | 12.5172 | 12.5172 | 5.784 | 12.5377 | 12.5377 | 12.5377 | 5.7748 | 12.5596 | 12.5596 | 12.5596 | 5.7647 | 12.581 | 12.581 | 12.581 | 5.7578 | 12.6058 | 12.6058 | 12.6058 | 5.7496 | 12.6361 | 12.6361 | 12.6361 | 5.7146 | 12.6689 | 12.6689 | 12.6689 | 5.6838 | 12.8064 | 12.8064 | 12.8064 | 5.5036 | 14.6075 | 14.6075 | 14.5572 | 3.5913 | 16.1967 | 16.1967 | 14.2875 | 1.9284 | 16.2731 | 16.2731 | 14.1384 | 1.7974 | 16.3494 | 16.3494 | 14.0084 | 1.733 | 12.4486 | 12.4486 | 12.4486 | 6.1616 | 12.4573 | 12.4573 | 12.4573 | 5.9928 | 12.4632 | 12.4632 | 12.4632 | 5.9134 | 12.4702 | 12.4702 | 12.4702 | 5.8885 | 13.7881 | 13.7881 | 13.7881 | 4.562 | 13.7491 | 13.7491 | 13.7491 | 4.608 | 13.7126 | 13.7126 | 13.7126 | 4.6433 | 13.6947 | 13.6947 | 13.6947 | 4.6313 | 13.6858 | 13.6858 | 13.6858 | 4.5918 | 13.6762 | 13.6762 | 13.6762 | 4.5573 | 15.1001 | 15.1001 | 14.6045 | 2.9884 | 15.3166 | 15.3166 | 14.4363 | 2.6244 | 15.4944 | 15.4944 | 14.2869 | 2.3512 | 15.5281 | 15.5281 | 14.1595 | 2.348 | 15.4878 | 15.4878 | 14.0904 | 2.6578 | 12.4481 | 12.4481 | 12.4481 | 6.1616 | 12.4669 | 12.4669 | 12.4669 | 6.115 | 12.4902 | 12.4902 | 12.4902 | 6.0566 | 12.5129 | 12.5129 | 12.5129 | 6.0397 | 12.5354 | 12.5354 | 12.5354 | 6.0441 | 12.561 | 12.561 | 12.561 | 6.0497 | 12.5916 | 12.5916 | 12.5916 | 6.0524 | 12.6267 | 12.6267 | 12.6267 | 6.0479 | 12.6663 | 12.6663 | 12.6663 | 5.9907 | 12.7088 | 12.7088 | 12.7088 | 5.9327 | 14.9002 | 14.9002 | 14.9002 | 3.6759 | 15.1797 | 15.1797 | 14.7948 | 3.354 | 17.2643 | 17.2643 | 14.41 | 1.2419 | 17.3261 | 17.3261 | 14.3863 | 1.2022 | 17.3957 | 17.3957 | 14.3112 | 1.2287 | 12.4481 | 12.4481 | 12.4481 | 6.1616 | 12.4596 | 12.4596 | 12.4596 | 5.8789 | 12.4863 | 12.4863 | 12.4863 | 5.7749 | 12.5169 | 12.5169 | 12.5169 | 5.7438 | 13.8512 | 13.8512 | 13.8512 | 4.4126 | 13.8246 | 13.8246 | 13.8246 | 4.4585 | 13.8014 | 13.8014 | 13.8014 | 4.4959 | 13.8002 | 13.8002 | 13.8002 | 4.4842 | 13.7883 | 13.7883 | 13.7883 | 4.4476 | 13.7751 | 13.7751 | 13.7751 | 4.4159 | 15.2167 | 15.2167 | 14.5779 | 2.8385 | 15.4608 | 15.4608 | 14.402 | 2.4471 | 15.6636 | 15.6636 | 14.2462 | 2.1532 | 15.7141 | 15.7141 | 14.1134 | 2.1316 | 15.6844 | 15.6844 | 14.0407 | 2.4237
SHAW | ROYTON | WHITEGATE | 394298 | 409450 | 30.3066 | 11.2311 | 8.1929 | 15.7185 | 30.3616 | 11.1213 | 8.1128 | 15.4905 | 30.4354 | 10.9542 | 7.991 | 15.4253 | 30.5367 | 10.7523 | 7.8436 | 15.3928 | 30.6796 | 10.6647 | 7.7797 | 15.2694 | 30.8577 | 10.7304 | 7.8277 | 15.1241 | 31.0792 | 10.6832 | 7.7932 | 14.979 | 31.3618 | 10.6309 | 7.7551 | 14.8299 | 31.6219 | 10.5495 | 7.6957 | 14.5654 | 31.8899 | 10.4708 | 7.6383 | 14.2684 | 32.7775 | 10.07 | 7.3459 | 12.3045 | 33.628 | 9.5345 | 6.9553 | 9.0079 | 34.1322 | 9.186 | 6.7011 | 6.2314 | 34.5639 | 8.8078 | 6.4252 | 3.2751 | 34.8634 | 8.2543 | 6.0214 | 0.61704 | 30.2769 | 11.2311 | 8.1929 | 15.7185 | 30.3306 | 11.185 | 8.1593 | 15.5959 | 30.3683 | 11.1176 | 8.1101 | 15.5178 | 30.4196 | 11.0471 | 8.0587 | 15.434 | 30.4991 | 10.9584 | 7.994 | 15.2934 | 30.6045 | 10.8536 | 7.9176 | 15.119 | 30.738 | 10.7617 | 7.8505 | 14.8833 | 30.8956 | 10.664 | 7.7792 | 14.5937 | 31.0132 | 10.5817 | 7.7192 | 14.3612 | 31.1431 | 10.4934 | 7.6548 | 14.1202 | 31.6039 | 10.198 | 7.4393 | 13.1686 | 32.1355 | 9.8831 | 7.2096 | 12.1389 | 32.6696 | 9.7374 | 7.1033 | 11.1451 | 33.2387 | 9.8121 | 7.1578 | 10.1118 | 33.6075 | 9.6849 | 7.065 | 9.413 | 30.3137 | 11.2311 | 8.1929 | 15.7185 | 30.3754 | 11.0897 | 8.0898 | 15.4857 | 30.4598 | 10.8558 | 7.9191 | 15.4421 | 30.5752 | 10.7036 | 7.8081 | 15.4132 | 30.7345 | 10.6829 | 7.793 | 15.2992 | 30.9297 | 10.6688 | 7.7828 | 15.1727 | 31.1694 | 10.6028 | 7.7346 | 15.0719 | 31.4708 | 10.5346 | 7.6848 | 14.974 | 31.7304 | 10.4604 | 7.6307 | 14.8062 | 31.998 | 10.3726 | 7.5667 | 14.5973 | 32.8546 | 9.894 | 7.2176 | 12.7937 | 33.7 | 9.2844 | 6.7728 | 9.6052 | 34.2579 | 8.8791 | 6.4771 | 6.9368 | 34.7086 | 8.4195 | 6.1419 | 4.167 | 34.9837 | 7.8774 | 5.7464 | 1.8543 | 30.3137 | 11.2311 | 8.1929 | 15.7185 | 30.2748 | 11.1589 | 8.1403 | 15.8569 | 30.3016 | 10.9163 | 7.9633 | 15.908 | 30.3576 | 10.8372 | 7.9056 | 15.9 | 30.4673 | 10.8919 | 7.9455 | 15.7743 | 30.6475 | 10.8476 | 7.9132 | 15.6102 | 30.9059 | 10.7359 | 7.8317 | 15.2517 | 31.2738 | 10.5532 | 7.6984 | 14.2267 | 31.6169 | 10.357 | 7.5553 | 13.1446 | 31.9727 | 10.1543 | 7.4074 | 12.1004 | 32.8916 | 10.0049 | 7.2984 | 9.0358 | 33.5893 | 9.2646 | 6.7584 | 6.0781 | 34.0696 | 8.6296 | 6.2951 | 3.6017 | 34.3983 | 8.0701 | 5.887 | 1.8946 | 34.4226 | 7.9914 | 5.8296 | 2.8286 | 30.3066 | 11.2311 | 8.1929 | 15.7185 | 30.3518 | 11.16 | 8.1411 | 15.6269 | 30.3953 | 11.0092 | 8.031 | 15.6287 | 30.4476 | 10.8128 | 7.8878 | 15.6695 | 30.5326 | 10.7575 | 7.8475 | 15.6734 | 30.6781 | 10.8303 | 7.9006 | 15.6319 | 30.8824 | 10.8007 | 7.8789 | 15.5442 | 31.1217 | 10.7522 | 7.8435 | 15.4313 | 31.3373 | 10.687 | 7.796 | 15.246 | 31.5669 | 10.6131 | 7.7421 | 14.9832 | 32.3493 | 10.374 | 7.5677 | 13.9528 | 33.0412 | 10.1967 | 7.4384 | 12.7393 | 33.5153 | 10.1777 | 7.4245 | 11.8345 | 33.896 | 10.1772 | 7.4241 | 11.0481 | 34.0831 | 10.0338 | 7.3195 | 10.6863 | 30.3066 | 11.2311 | 8.1929 | 15.7185 | 30.2909 | 11.1256 | 8.116 | 15.7268 | 30.3547 | 10.8692 | 7.929 | 15.6813 | 30.4545 | 10.7729 | 7.8587 | 15.5818 | 30.5974 | 10.8099 | 7.8857 | 15.3745 | 30.7693 | 10.7642 | 7.8524 | 15.1577 | 31.0014 | 10.6372 | 7.7597 | 14.7336 | 31.3655 | 10.4317 | 7.6098 | 13.6214 | 31.7004 | 10.2248 | 7.4589 | 12.4793 | 32.0458 | 10.0132 | 7.3045 | 11.3739 | 32.9916 | 9.8151 | 7.16 | 8.0929 | 33.7168 | 9.0406 | 6.595 | 4.9124 | 34.2364 | 8.3487 | 6.0903 | 2.166 | 34.5788 | 7.7423 | 5.6479 | 0.18283 | 34.6171 | 7.6149 | 5.5549 | 0.82331
Siddick | STAINBURN & SIDDICK | HARKER / HUTTON | 300289 | 530805 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844
SILLOTH | CARLISLE | HARKER / HUTTON | 311307 | 553464 | 37.0722 | 20.6356 | 14.8312 | 37.0722 | 37.1087 | 20.5927 | 14.8004 | 37.1087 | 37.1652 | 20.5409 | 14.7632 | 37.1652 | 37.2312 | 20.4964 | 14.7312 | 37.2312 | 37.3104 | 20.4358 | 14.6876 | 37.3104 | 37.406 | 20.3683 | 14.6391 | 37.406 | 37.521 | 20.3072 | 14.5952 | 37.521 | 37.6528 | 20.2066 | 14.5229 | 37.6528 | 37.7668 | 20.1344 | 14.471 | 37.7668 | 37.875 | 20.0631 | 14.4197 | 37.875 | 38.1864 | 19.7738 | 14.2118 | 38.1864 | 38.4921 | 19.4318 | 13.966 | 38.4921 | 38.6988 | 19.0879 | 13.7189 | 38.0027 | 38.8487 | 18.9807 | 13.6418 | 37.0477 | 38.9248 | 18.8139 | 13.5219 | 36.261 | 37.0649 | 20.6356 | 14.8312 | 37.0649 | 37.0941 | 20.601 | 14.8063 | 37.0941 | 37.133 | 20.5463 | 14.7671 | 37.133 | 37.1745 | 20.4804 | 14.7196 | 37.1745 | 37.2256 | 20.408 | 14.6676 | 37.2256 | 37.2905 | 20.3328 | 14.6136 | 37.2905 | 37.3689 | 20.246 | 14.5512 | 37.3689 | 37.4597 | 20.1645 | 14.4926 | 37.4597 | 37.5244 | 20.1008 | 14.4469 | 37.5244 | 37.5944 | 20.0339 | 14.3988 | 37.5944 | 37.8231 | 19.8099 | 14.2378 | 37.8231 | 38.0555 | 19.5859 | 14.0767 | 38.0555 | 38.2717 | 19.397 | 13.941 | 38.2717 | 38.4621 | 19.4609 | 13.987 | 38.4621 | 38.5831 | 19.5421 | 14.0453 | 38.468 | 37.0752 | 20.6356 | 14.8312 | 37.0752 | 37.1133 | 20.5801 | 14.7913 | 37.1133 | 37.1739 | 20.4978 | 14.7322 | 37.1739 | 37.2467 | 20.4259 | 14.6805 | 37.2467 | 37.3337 | 20.3479 | 14.6244 | 37.3337 | 37.4377 | 20.2697 | 14.5682 | 37.4377 | 37.5623 | 20.2031 | 14.5204 | 37.5623 | 37.6912 | 20.0911 | 14.4399 | 37.6912 | 37.7992 | 20.0132 | 14.3839 | 37.7992 | 37.8891 | 19.9349 | 14.3276 | 37.8891 | 38.2031 | 19.5278 | 14.035 | 38.2031 | 38.5319 | 19.0661 | 13.7032 | 38.5319 | 38.7573 | 18.6433 | 13.3993 | 38.1407 | 38.9104 | 18.4322 | 13.2476 | 37.4704 | 38.9685 | 18.179 | 13.0656 | 37.086 | 37.0753 | 20.6356 | 14.8312 | 37.0753 | 37.0847 | 20.6077 | 14.8112 | 37.0847 | 37.1203 | 20.5615 | 14.7779 | 37.1203 | 37.1637 | 20.5032 | 14.7361 | 37.1637 | 37.2227 | 20.4431 | 14.6928 | 37.2227 | 37.3149 | 20.3283 | 14.6103 | 37.3149 | 37.4351 | 20.2331 | 14.542 | 37.4351 | 37.5794 | 20.0583 | 14.4163 | 37.5794 | 37.7122 | 19.9051 | 14.3062 | 37.7122 | 37.8444 | 19.7571 | 14.1998 | 37.8444 | 38.1725 | 19.3515 | 13.9083 | 38.1725 | 38.4713 | 18.9255 | 13.6021 | 38.1581 | 38.6639 | 18.5651 | 13.3431 | 37.4017 | 38.7729 | 18.4323 | 13.2477 | 37.0072 | 38.7335 | 18.2291 | 13.1016 | 37.4925 | 37.0722 | 20.6356 | 14.8312 | 37.0722 | 37.1022 | 20.6004 | 14.8059 | 37.1022 | 37.1438 | 20.5533 | 14.7721 | 37.1438 | 37.1861 | 20.5147 | 14.7443 | 37.1861 | 37.2381 | 20.4693 | 14.7117 | 37.2381 | 37.3177 | 20.4189 | 14.6755 | 37.3177 | 37.4241 | 20.3691 | 14.6397 | 37.4241 | 37.5472 | 20.272 | 14.5699 | 37.5472 | 37.6439 | 20.2082 | 14.524 | 37.6439 | 37.7445 | 20.1396 | 14.4747 | 37.7445 | 38.0453 | 19.8955 | 14.2993 | 38.0453 | 38.3276 | 19.6649 | 14.1336 | 38.3276 | 38.5208 | 19.4197 | 13.9573 | 38.5208 | 38.6617 | 19.4347 | 13.9681 | 38.6617 | 38.7017 | 19.4271 | 13.9626 | 38.5925 | 37.0722 | 20.6356 | 14.8312 | 37.0722 | 37.0908 | 20.5933 | 14.8008 | 37.0908 | 37.1435 | 20.5344 | 14.7585 | 37.1435 | 37.2079 | 20.4633 | 14.7074 | 37.2079 | 37.2838 | 20.3908 | 14.6553 | 37.2838 | 37.3733 | 20.2665 | 14.5659 | 37.3733 | 37.4822 | 20.1676 | 14.4949 | 37.4822 | 37.6263 | 19.9864 | 14.3646 | 37.6263 | 37.7552 | 19.8303 | 14.2524 | 37.7552 | 37.8858 | 19.6758 | 14.1414 | 37.8858 | 38.2164 | 19.2375 | 13.8264 | 38.2164 | 38.5211 | 18.7766 | 13.4951 | 37.6712 | 38.7258 | 18.386 | 13.2143 | 36.8022 | 38.8394 | 18.2338 | 13.105 | 36.2995 | 38.8091 | 18.0188 | 12.9505 | 36.6894
SKELMERSDALE | SKELMERSDALE | WASHWAY FARM / KIRKBY | 347198 | 407434 | 12.8615 | 2.1175 | 1.5219 | 12.8615 | 11.6355 | 1.9157 | 1.3769 | 11.6355 | 6.8276 | 1.1241 | 0.80792 | 6.8276 | 2.1713 | 0.35749 | 0.25693 | 2.1713 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 13.1769 | 2.1695 | 1.5592 | 2.8515 | 12.9851 | 2.1379 | 1.5366 | 1.8324 | 12.8615 | 2.1175 | 1.5219 | 12.8615 | 12.4155 | 2.0441 | 1.4691 | 12.4155 | 7.9654 | 1.3114 | 0.94255 | 7.9654 | 3.5317 | 0.58147 | 0.41791 | 3.5317 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 1.2265 | 0.20193 | 0.14513 | 1.2265 | 16.951 | 2.7909 | 2.0058 | 6.4168 | 12.8615 | 2.1175 | 1.5219 | 12.8615 | 11.2843 | 1.8579 | 1.3353 | 11.2843 | 6.0185 | 0.9909 | 0.71218 | 6.0185 | 0.97463 | 0.16047 | 0.11533 | 0.97463 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 7.0257 | 1.1567 | 0.83137 | 2.7969 | 6.7912 | 1.1181 | 0.80361 | 2.2932 | 12.8615 | 2.1175 | 1.5219 | 12.8615 | 11.8832 | 1.9565 | 1.4062 | 11.8832 | 10.9262 | 1.7989 | 1.2929 | 10.9262 | 19.4944 | 3.2512 | 2.3367 | 12.6843 | 18.5188 | 3.049 | 2.1914 | 12.4143 | 17.5785 | 2.8942 | 2.0801 | 12.1014 | 16.0143 | 2.6366 | 1.895 | 11.6764 | 15.2597 | 2.5124 | 1.8057 | 10.8793 | 13.725 | 2.2597 | 1.6241 | 10.0214 | 12.0004 | 1.9758 | 1.42 | 9.1417 | 17.5985 | 2.8975 | 2.0825 | 6.6358 | 13.0955 | 2.1561 | 1.5496 | 4.6474 | 9.6306 | 1.5856 | 1.1396 | 3.4728 | 8.1171 | 1.3364 | 0.96051 | 3.1273 | 6.1961 | 1.0201 | 0.7332 | 3.4552 | 12.8615 | 2.1175 | 1.5219 | 12.8615 | 12.0444 | 1.983 | 1.4252 | 12.0444 | 7.3507 | 1.2102 | 0.86982 | 7.3507 | 2.7754 | 0.45696 | 0.32842 | 2.7754 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 18.6032 | 3.0629 | 2.2013 | 6.7278 | 19.2669 | 3.1721 | 2.2799 | 6.267 | 12.8615 | 2.1175 | 1.5219 | 12.8615 | 11.4033 | 1.8775 | 1.3494 | 11.4033 | 10.2933 | 1.6947 | 1.218 | 10.2933 | 18.985 | 3.1257 | 2.2465 | 12.1652 | 17.697 | 2.9137 | 2.0941 | 11.8538 | 16.7215 | 2.7531 | 1.9787 | 11.5218 | 15.1187 | 2.4892 | 1.789 | 11.0754 | 14.3347 | 2.3601 | 1.6962 | 10.2559 | 12.8001 | 2.1074 | 1.5147 | 9.4 | 10.8914 | 1.7932 | 1.2888 | 8.5186 | 16.4976 | 2.7162 | 1.9522 | 5.9002 | 11.7534 | 1.9351 | 1.3908 | 3.6933 | 7.9147 | 1.3031 | 0.93656 | 2.2696 | 6.2035 | 1.0214 | 0.73407 | 1.7551 | 4.0443 | 0.66586 | 0.47857 | 1.9396
HUTTON END & SKELTON C | PENRITH & SHAP | HARKER / HUTTON | 342672 | 538337 | 29.2443 | 28.8363 | 20.7252 | 19.8878 | 29.3163 | 28.7891 | 20.6913 | 19.7962 | 29.4216 | 28.2972 | 20.3378 | 19.6044 | 29.5507 | 27.7985 | 19.9793 | 19.4081 | 29.7337 | 27.2698 | 19.5993 | 19.1111 | 29.9941 | 26.7416 | 19.2197 | 18.8282 | 30.2191 | 26.1909 | 18.8239 | 18.4081 | 30.4766 | 25.9992 | 18.6861 | 17.64 | 30.7817 | 25.7749 | 18.5249 | 16.6873 | 31.1189 | 25.5292 | 18.3483 | 15.6082 | 32.2162 | 24.6846 | 17.7413 | 11.8877 | 33.1596 | 23.8801 | 17.1631 | 8.4734 | 33.7419 | 23.2711 | 16.7254 | 6.2863 | 34.1129 | 22.6877 | 16.3061 | 4.8452 | 34.3109 | 21.6521 | 15.5618 | 3.8394 | 29.2451 | 28.8363 | 20.7252 | 19.8878 | 29.3161 | 28.7996 | 20.6989 | 19.7703 | 29.3936 | 28.7388 | 20.6551 | 19.5868 | 29.4841 | 28.6646 | 20.6018 | 19.3941 | 29.5975 | 28.5766 | 20.5386 | 19.1736 | 29.7423 | 28.4873 | 20.4744 | 18.9577 | 29.9261 | 28.365 | 20.3865 | 18.6841 | 30.1549 | 28.2628 | 20.313 | 18.355 | 30.3614 | 28.1785 | 20.2524 | 18.1061 | 30.5659 | 28.0878 | 20.1873 | 17.8267 | 31.1785 | 27.6759 | 19.8912 | 16.1633 | 31.9331 | 27.1411 | 19.5068 | 13.7622 | 32.7233 | 26.5436 | 19.0774 | 11.104 | 33.5621 | 25.8269 | 18.5623 | 8.0666 | 34.0992 | 25.1917 | 18.1058 | 5.9417 | 29.244 | 28.8363 | 20.7252 | 19.8878 | 29.3123 | 28.7645 | 20.6736 | 19.8145 | 29.4146 | 28.2115 | 20.2762 | 19.6391 | 29.5483 | 27.6564 | 19.8772 | 19.4762 | 29.7189 | 27.0918 | 19.4714 | 19.2191 | 29.9539 | 26.5407 | 19.0753 | 18.9916 | 30.1529 | 25.9682 | 18.6638 | 18.6512 | 30.3682 | 25.7604 | 18.5145 | 18.0354 | 30.6173 | 25.5233 | 18.3441 | 17.2874 | 30.9003 | 25.2583 | 18.1536 | 16.4053 | 31.9494 | 24.2968 | 17.4626 | 12.8603 | 32.9969 | 23.2883 | 16.7378 | 9.0724 | 33.6948 | 22.3704 | 16.078 | 6.4719 | 34.1172 | 20.9318 | 15.0441 | 4.8507 | 34.2876 | 20.0522 | 14.4119 | 3.9532 | 29.244 | 28.8363 | 20.7252 | 19.8878 | 29.2602 | 28.7767 | 20.6824 | 19.8849 | 29.3351 | 28.2452 | 20.3004 | 19.7027 | 29.4693 | 27.6535 | 19.8751 | 19.4894 | 29.6307 | 27.0898 | 19.4699 | 19.2228 | 29.8693 | 26.4768 | 19.0294 | 18.9298 | 30.0673 | 25.7404 | 18.5002 | 18.4328 | 30.3367 | 25.3074 | 18.1889 | 17.4831 | 30.6523 | 24.8408 | 17.8535 | 16.3212 | 31.0022 | 23.5998 | 16.9616 | 15.0293 | 32.1041 | 22.4896 | 16.1637 | 10.991 | 33.0145 | 21.5551 | 15.4921 | 7.695 | 33.5582 | 20.782 | 14.9364 | 5.7098 | 33.8505 | 20.1252 | 14.4644 | 4.7383 | 33.8822 | 19.7475 | 14.1929 | 4.7788 | 29.2443 | 28.8363 | 20.7252 | 19.8878 | 29.3048 | 28.795 | 20.6956 | 19.8064 | 29.3908 | 28.3053 | 20.3436 | 19.619 | 29.4868 | 27.8096 | 19.9873 | 19.4326 | 29.6203 | 27.2957 | 19.6179 | 19.2106 | 29.8262 | 26.7914 | 19.2555 | 19.0567 | 30.0708 | 26.2803 | 18.8881 | 18.861 | 30.2778 | 26.126 | 18.7773 | 18.3028 | 30.5182 | 25.941 | 18.6443 | 17.5705 | 30.7916 | 25.7348 | 18.4961 | 16.7123 | 31.7704 | 24.9778 | 17.9521 | 13.4852 | 32.7182 | 24.2337 | 17.4173 | 10.2809 | 33.3448 | 23.624 | 16.979 | 8.176 | 33.7428 | 22.9994 | 16.5301 | 6.7939 | 33.8744 | 21.9573 | 15.7812 | 6.2332 | 29.2443 | 28.8363 | 20.7252 | 19.8878 | 29.2802 | 28.7727 | 20.6795 | 19.8777 | 29.3803 | 28.2375 | 20.2949 | 19.6804 | 29.5133 | 27.6349 | 19.8618 | 19.4055 | 29.6741 | 27.0609 | 19.4492 | 19.0817 | 29.895 | 26.4506 | 19.0106 | 18.802 | 30.1313 | 25.7416 | 18.501 | 18.441 | 30.3757 | 25.3473 | 18.2176 | 17.6648 | 30.6556 | 24.9172 | 17.9085 | 16.6763 | 30.9712 | 23.7671 | 17.0819 | 15.5519 | 32.0714 | 22.5642 | 16.2173 | 11.5823 | 33.1118 | 21.5669 | 15.5005 | 7.8167 | 33.7963 | 20.6936 | 14.8729 | 5.3151 | 34.1689 | 19.981 | 14.3607 | 4.0231 | 34.2245 | 19.5825 | 14.0743 | 3.9724
SLIPWAY | EGREMONT | HARKER / HUTTON | 297180 | 518183 | 16.6266 | 16.6266 | 12.821 | 7.4927 | 16.6523 | 16.6523 | 12.747 | 7.1146 | 16.6824 | 16.6824 | 12.6595 | 7.0067 | 16.7213 | 16.7213 | 12.5481 | 6.9525 | 16.7766 | 16.7766 | 12.3528 | 6.8343 | 16.8413 | 16.8413 | 12.3346 | 6.7048 | 16.9135 | 16.9135 | 12.3579 | 6.5943 | 16.9965 | 16.9965 | 12.3439 | 6.5141 | 17.0506 | 17.0506 | 12.306 | 6.4487 | 17.0993 | 17.0424 | 12.2487 | 6.403 | 17.3062 | 16.8402 | 12.1034 | 5.6274 | 17.5984 | 16.5094 | 11.8656 | 3.986 | 17.8241 | 16.1258 | 11.59 | 2.6288 | 18.0328 | 15.5579 | 11.1818 | 1.2626 | 18.1933 | 14.7516 | 10.6023 | 0.080889 | 16.6219 | 16.6219 | 12.821 | 7.4927 | 16.6559 | 16.6559 | 12.8008 | 7.3858 | 16.6902 | 16.6902 | 12.7734 | 7.3063 | 16.7339 | 16.7339 | 12.7284 | 7.2249 | 16.7935 | 16.7935 | 12.6703 | 7.116 | 16.867 | 16.867 | 12.5987 | 6.9984 | 16.9585 | 16.9585 | 12.4194 | 6.7938 | 17.0694 | 17.0694 | 12.3055 | 6.1544 | 17.101 | 17.0555 | 12.2582 | 6.0811 | 17.1326 | 16.9876 | 12.2093 | 6.0095 | 17.2279 | 16.7653 | 12.0496 | 5.8038 | 17.3203 | 16.5573 | 11.9 | 5.6181 | 17.4008 | 16.4339 | 11.8113 | 5.476 | 17.4766 | 16.6413 | 11.9604 | 5.3699 | 17.5194 | 16.804 | 12.0774 | 5.3121 | 16.6287 | 16.6287 | 12.821 | 7.4927 | 16.6572 | 16.6572 | 12.7322 | 7.0639 | 16.6914 | 16.6914 | 12.6146 | 6.9532 | 16.7364 | 16.7364 | 12.4685 | 6.9074 | 16.7993 | 16.7993 | 12.2516 | 6.8009 | 16.8729 | 16.8729 | 12.3197 | 6.6856 | 16.9566 | 16.9566 | 12.3086 | 6.5909 | 17.0532 | 17.0417 | 12.2482 | 6.5321 | 17.1152 | 16.98 | 12.2038 | 6.4935 | 17.171 | 16.9551 | 12.186 | 6.4756 | 17.3988 | 16.6872 | 11.9934 | 5.7846 | 17.7081 | 16.1951 | 11.6397 | 4.2381 | 17.945 | 15.656 | 11.2523 | 2.9716 | 18.161 | 14.6029 | 10.4954 | 1.7185 | 18.3149 | 13.8641 | 9.9644 | 0.66906 | 16.6287 | 16.6287 | 12.821 | 7.4927 | 16.603 | 16.603 | 12.7685 | 7.3429 | 16.6071 | 16.6071 | 12.6812 | 7.3013 | 16.6215 | 16.6215 | 12.5073 | 7.2733 | 16.6566 | 16.6566 | 12.4063 | 7.1732 | 16.7131 | 16.7131 | 12.4362 | 7.0566 | 16.7924 | 16.7924 | 12.2638 | 6.8457 | 16.9115 | 15.6386 | 11.2398 | 6.2965 | 17.0124 | 15.0365 | 10.807 | 5.733 | 17.1095 | 14.9761 | 10.7637 | 5.1895 | 17.3964 | 13.844 | 9.95 | 3.6535 | 17.6893 | 13.3154 | 9.57 | 2.2051 | 17.9022 | 12.8378 | 9.2268 | 1.0714 | 17.9876 | 12.4167 | 8.9241 | 0.51896 | 17.9544 | 12.3819 | 8.8991 | 1.3302 | 16.6266 | 16.6266 | 12.821 | 7.4927 | 16.648 | 16.648 | 12.7831 | 7.3909 | 16.6674 | 16.6674 | 12.7068 | 7.344 | 16.6878 | 16.6878 | 12.6032 | 7.3292 | 16.7185 | 16.7185 | 12.4267 | 7.3033 | 16.767 | 16.767 | 12.4111 | 7.2751 | 16.8307 | 16.8307 | 12.4477 | 7.2424 | 16.9024 | 16.9024 | 12.4392 | 7.1929 | 16.9506 | 16.9506 | 12.4025 | 7.1172 | 16.9974 | 16.9974 | 12.3427 | 7.0439 | 17.1506 | 17.0627 | 12.2633 | 6.7601 | 17.3211 | 16.9718 | 12.198 | 6.4058 | 17.442 | 16.8094 | 12.0812 | 6.1959 | 17.5499 | 16.4755 | 11.8412 | 6.0205 | 17.5943 | 15.6642 | 11.2582 | 6.0995 | 16.6266 | 16.6266 | 12.821 | 7.4927 | 16.6163 | 16.6163 | 12.7435 | 7.1521 | 16.6422 | 16.6422 | 12.636 | 6.9774 | 16.6825 | 16.6825 | 12.4442 | 6.8377 | 16.741 | 16.741 | 12.3353 | 6.6282 | 16.8076 | 16.8076 | 12.3492 | 6.4135 | 16.8928 | 16.8928 | 12.1849 | 6.1033 | 17.0295 | 15.9796 | 11.4849 | 5.4978 | 17.1375 | 15.3668 | 11.0444 | 4.9055 | 17.2401 | 14.8336 | 10.6612 | 4.3343 | 17.5319 | 13.6723 | 9.8266 | 2.7193 | 17.81 | 13.1266 | 9.4344 | 1.1914 | 18.02 | 12.6293 | 9.0769 | -0.030544 | 18.1275 | 12.075 | 8.6785 | -0.70603 | 18.0967 | 12.0801 | 8.6822 | -0.045698
SNIPE | DROYLSDEN | STALYBRIDGE | 391844 | 398322 | 30.6089 | 7.6914 | 5.6108 | 14.044 | 30.6566 | 7.3253 | 5.3437 | 12.9337 | 30.7362 | 7.0713 | 5.1584 | 12.5828 | 30.8299 | 6.8739 | 5.0144 | 12.4593 | 30.9448 | 6.6134 | 4.8244 | 12.1149 | 31.0846 | 6.3752 | 4.6506 | 11.753 | 31.2575 | 6.2327 | 4.5466 | 11.3849 | 31.4771 | 6.1177 | 4.4628 | 11.0045 | 31.6898 | 5.9623 | 4.3494 | 10.55 | 31.9073 | 5.8346 | 4.2562 | 10.1114 | 32.5932 | 5.3601 | 3.9101 | 8.2289 | 29.5692 | 4.7964 | 3.4989 | 5.5971 | 26.4335 | 4.2878 | 3.1279 | 3.3893 | 26.0274 | 4.2219 | 3.0798 | 1.2339 | 22.7841 | 3.6958 | 2.696 | -0.69591 | 30.5945 | 7.6914 | 5.6108 | 14.044 | 30.6369 | 7.4817 | 5.4578 | 13.6678 | 30.6878 | 7.2833 | 5.313 | 13.5001 | 30.7435 | 7.0958 | 5.1763 | 13.4229 | 30.8163 | 6.9194 | 5.0476 | 13.3397 | 30.9113 | 6.7641 | 4.9343 | 13.2418 | 31.029 | 6.5496 | 4.7779 | 13.1035 | 31.1674 | 6.4957 | 4.7386 | 12.9174 | 31.2774 | 6.422 | 4.6848 | 12.6531 | 31.3962 | 6.3429 | 4.627 | 12.3865 | 31.8021 | 6.1083 | 4.4559 | 11.5667 | 32.2552 | 5.9161 | 4.3157 | 10.6003 | 32.6949 | 5.6785 | 4.1424 | 9.6414 | 33.1583 | 5.6771 | 4.1414 | 8.5827 | 33.4823 | 5.7006 | 4.1585 | 7.8075 | 30.6135 | 7.6914 | 5.6108 | 14.044 | 30.6669 | 7.2803 | 5.3109 | 12.7622 | 30.7545 | 7.0049 | 5.11 | 12.3768 | 30.8597 | 6.7833 | 4.9483 | 12.2518 | 30.9871 | 6.5224 | 4.758 | 11.9083 | 31.1398 | 6.2774 | 4.5793 | 11.549 | 31.3263 | 6.1171 | 4.4623 | 11.1838 | 31.5603 | 5.9699 | 4.355 | 10.8093 | 31.769 | 5.8218 | 4.247 | 10.3974 | 31.9806 | 5.6966 | 4.1556 | 10.0061 | 31.963 | 5.1847 | 3.7822 | 8.2545 | 27.8746 | 4.5215 | 3.2984 | 5.7488 | 25.7935 | 4.184 | 3.0521 | 3.9117 | 25.0081 | 4.0566 | 2.9592 | 2.1441 | 23.1061 | 3.748 | 2.7341 | 0.545 | 30.6135 | 7.6914 | 5.6108 | 14.044 | 30.5996 | 7.3872 | 5.3889 | 13.2942 | 30.6408 | 7.1595 | 5.2227 | 13.0498 | 30.694 | 6.9308 | 5.0559 | 12.9727 | 30.7761 | 6.7149 | 4.8984 | 12.6595 | 30.9112 | 6.436 | 4.695 | 12.2985 | 31.0933 | 6.2614 | 4.5676 | 11.8191 | 31.3187 | 5.9961 | 4.3741 | 11.0175 | 31.5346 | 5.7831 | 4.2187 | 10.1669 | 31.7576 | 5.6084 | 4.0913 | 9.3316 | 32.4427 | 5.2811 | 3.8525 | 6.7844 | 29.3853 | 4.7666 | 3.4772 | 4.0805 | 26.4701 | 4.2937 | 3.1322 | 2.1432 | 24.2024 | 3.9259 | 2.8639 | 1.0751 | 23.999 | 3.8929 | 2.8398 | 1.6703 | 30.6089 | 7.6914 | 5.6108 | 14.044 | 30.649 | 7.4207 | 5.4133 | 13.3703 | 30.7046 | 7.1864 | 5.2424 | 13.1415 | 30.76 | 7.0066 | 5.1112 | 13.0837 | 30.8329 | 6.7739 | 4.9415 | 12.8446 | 30.9519 | 6.559 | 4.7847 | 12.5649 | 31.1157 | 6.4299 | 4.6905 | 12.2439 | 31.3044 | 6.3157 | 4.6072 | 11.8983 | 31.4835 | 6.1691 | 4.5003 | 11.4542 | 31.672 | 6.0318 | 4.4001 | 11.0083 | 32.3027 | 5.651 | 4.1223 | 9.5745 | 32.7514 | 5.3126 | 3.8755 | 8.0509 | 31.2855 | 5.0748 | 3.702 | 7.1258 | 32.3471 | 5.247 | 3.8276 | 6.501 | 31.6636 | 5.1361 | 3.7467 | 6.2225 | 30.6089 | 7.6914 | 5.6108 | 14.044 | 30.6147 | 7.2763 | 5.3079 | 12.7518 | 30.6876 | 7.0253 | 5.1249 | 12.3491 | 30.7785 | 6.7761 | 4.9431 | 12.2074 | 30.8905 | 6.5483 | 4.7769 | 11.8406 | 31.0229 | 6.2686 | 4.5728 | 11.4649 | 31.1891 | 6.0907 | 4.4431 | 10.9799 | 31.4167 | 5.8319 | 4.2543 | 10.142 | 31.6285 | 5.5851 | 4.0743 | 9.2609 | 31.8453 | 5.4152 | 3.9503 | 8.3984 | 31.4569 | 5.1026 | 3.7223 | 5.6994 | 27.7329 | 4.4985 | 3.2816 | 2.8645 | 24.6599 | 4.0001 | 2.918 | 0.75311 | 22.1811 | 3.598 | 2.6247 | -0.50192 | 21.7402 | 3.5265 | 2.5725 | -0.11002
S.E. MACCLESFIELD | MACCLESFIELD | MACCLESFIELD | 392001 | 372504 | 29.5714 | 12.3285 | 8.8607 | 13.7631 | 29.7185 | 12.2018 | 8.7696 | 13.4551 | 29.9113 | 12.0722 | 8.6766 | 13.1291 | 30.0506 | 11.9382 | 8.5802 | 12.8469 | 30.2303 | 11.7948 | 8.4771 | 12.5122 | 30.4383 | 11.643 | 8.3681 | 12.1626 | 30.6609 | 11.5159 | 8.2767 | 11.8245 | 30.9013 | 11.3772 | 8.177 | 11.4833 | 31.1224 | 11.2247 | 8.0674 | 11.1188 | 31.3452 | 11.0744 | 7.9594 | 10.7761 | 32.1881 | 10.455 | 7.5142 | 8.6226 | 33.1305 | 9.6897 | 6.9642 | 5.3398 | 33.6345 | 8.9999 | 6.4684 | 2.648 | 34.0258 | 8.2059 | 5.8978 | -0.054753 | 34.2715 | 7.4778 | 5.3744 | -2.3863 | 29.5343 | 12.3285 | 8.8607 | 13.7631 | 29.6745 | 12.2552 | 8.808 | 13.5242 | 29.8285 | 12.1564 | 8.737 | 13.2291 | 29.9752 | 12.0324 | 8.6479 | 12.9322 | 30.1151 | 11.8959 | 8.5498 | 12.5846 | 30.2663 | 11.7537 | 8.4476 | 12.2149 | 30.444 | 11.5745 | 8.3188 | 11.7609 | 30.6538 | 11.3979 | 8.1919 | 11.1929 | 30.7881 | 11.2542 | 8.0886 | 10.79 | 30.9316 | 11.1061 | 7.9822 | 10.3834 | 31.4098 | 10.6523 | 7.656 | 9.1002 | 31.9165 | 10.1988 | 7.3301 | 7.6598 | 32.3924 | 9.7529 | 7.0096 | 6.3396 | 32.8929 | 9.3617 | 6.7284 | 4.9433 | 33.2503 | 8.9535 | 6.4351 | 3.9966 | 29.5869 | 12.3285 | 8.8607 | 13.7631 | 29.7384 | 12.1725 | 8.7486 | 13.4345 | 29.9269 | 11.9777 | 8.6086 | 13.1054 | 30.0728 | 11.787 | 8.4716 | 12.8229 | 30.2619 | 11.5922 | 8.3315 | 12.4907 | 30.4794 | 11.45 | 8.2293 | 12.1454 | 30.7007 | 11.2577 | 8.0911 | 11.8115 | 30.9371 | 11.0765 | 7.9609 | 11.4788 | 31.1494 | 10.8878 | 7.8252 | 11.1601 | 31.3638 | 10.7293 | 7.7114 | 10.8694 | 32.2183 | 10.0686 | 7.2365 | 9.2923 | 33.275 | 9.214 | 6.6223 | 6.378 | 33.8329 | 8.4133 | 6.0468 | 3.9661 | 34.2806 | 7.5222 | 5.4064 | 1.6483 | 34.5424 | 6.7282 | 4.8357 | -0.3892 | 29.5869 | 12.3285 | 8.8607 | 13.7631 | 29.6361 | 12.2251 | 8.7864 | 13.672 | 29.7441 | 12.097 | 8.6943 | 13.4491 | 29.8758 | 11.928 | 8.5729 | 13.2338 | 30.0155 | 11.8034 | 8.4834 | 12.9595 | 30.2129 | 11.6095 | 8.344 | 12.6338 | 30.4749 | 11.3986 | 8.1924 | 12.1768 | 30.8016 | 11.1222 | 7.9938 | 11.3192 | 31.107 | 10.8217 | 7.7778 | 10.412 | 31.3788 | 10.5213 | 7.5619 | 9.3491 | 32.1604 | 9.6009 | 6.9004 | 6.2777 | 32.8926 | 8.7277 | 6.2728 | 3.3459 | 33.3871 | 7.9355 | 5.7034 | 1.0927 | 33.7382 | 7.242 | 5.2049 | -0.29533 | 33.8225 | 7.021 | 5.0461 | 0.57394 | 29.5713 | 12.3285 | 8.8607 | 13.7631 | 29.6946 | 12.2318 | 8.7912 | 13.5278 | 29.8337 | 12.1151 | 8.7074 | 13.2558 | 29.9634 | 11.9986 | 8.6236 | 13.0488 | 30.0836 | 11.8824 | 8.5401 | 12.8438 | 30.2489 | 11.7478 | 8.4433 | 12.6045 | 30.4558 | 11.6444 | 8.369 | 12.331 | 30.6769 | 11.5116 | 8.2736 | 12.0323 | 30.8726 | 11.3676 | 8.1701 | 11.6756 | 31.0779 | 11.2123 | 8.0585 | 11.32 | 31.7667 | 10.7613 | 7.7343 | 10.0636 | 32.4754 | 10.3234 | 7.4196 | 8.4582 | 32.9801 | 9.9218 | 7.131 | 7.2984 | 33.4121 | 9.4483 | 6.7906 | 6.2902 | 33.6293 | 9.0352 | 6.4938 | 5.8131 | 29.5713 | 12.3285 | 8.8607 | 13.7631 | 29.6705 | 12.1907 | 8.7617 | 13.5497 | 29.8518 | 12.0359 | 8.6505 | 13.2256 | 29.9912 | 11.844 | 8.5125 | 12.9083 | 30.1708 | 11.7015 | 8.4101 | 12.5439 | 30.3732 | 11.4946 | 8.2614 | 12.1741 | 30.6049 | 11.2793 | 8.1066 | 11.6813 | 30.936 | 10.9698 | 7.8842 | 10.6654 | 31.2384 | 10.6318 | 7.6413 | 9.5426 | 31.5453 | 10.313 | 7.4122 | 8.398 | 32.4005 | 9.3419 | 6.7142 | 5.0632 | 33.1418 | 8.4139 | 6.0472 | 1.8804 | 33.6595 | 7.5765 | 5.4454 | -0.61511 | 34.0124 | 6.8306 | 4.9093 | -2.2647 | 34.1115 | 6.5401 | 4.7005 | -1.6933
SOUTH PARK | LYTHAM | PENWORTHAM WEST / STANAH | 336410 | 427512 | 29.41 | 12.8205 | 9.2144 | 19.7453 | 29.448 | 12.5213 | 8.9993 | 19.3264 | 29.4959 | 11.9382 | 8.5802 | 19.1471 | 29.5488 | 11.8869 | 8.5434 | 19.0352 | 29.6122 | 11.5683 | 8.3144 | 18.8905 | 29.6852 | 11.2497 | 8.0854 | 18.7422 | 29.7709 | 11.0903 | 7.9708 | 18.6059 | 29.8743 | 10.9264 | 7.853 | 18.4764 | 29.9495 | 10.7997 | 7.7619 | 18.3287 | 30.023 | 10.7204 | 7.7049 | 18.1963 | 30.2648 | 10.3875 | 7.4657 | 17.2916 | 30.5191 | 9.9681 | 7.1643 | 15.7131 | 30.7009 | 9.5997 | 6.8995 | 14.4398 | 30.8606 | 9.1604 | 6.5838 | 13.0973 | 30.967 | 8.8202 | 6.3392 | 11.8883 | 29.3994 | 12.8205 | 9.2144 | 19.7453 | 29.4587 | 12.6487 | 9.0909 | 19.5385 | 29.5228 | 11.8338 | 8.5052 | 19.3881 | 29.5964 | 11.9832 | 8.6126 | 19.2536 | 29.6873 | 11.8223 | 8.4969 | 19.0932 | 29.7882 | 11.5815 | 8.3239 | 18.9312 | 29.8944 | 11.3591 | 8.164 | 18.7295 | 29.9724 | 11.2477 | 8.0839 | 18.4771 | 30.0203 | 11.1674 | 8.0262 | 18.3015 | 30.0693 | 11.0852 | 7.9671 | 18.1257 | 30.223 | 10.8482 | 7.7968 | 17.6058 | 30.3848 | 10.6829 | 7.678 | 17.0934 | 30.5304 | 10.5081 | 7.5523 | 16.6397 | 30.6838 | 10.3304 | 7.4247 | 16.1653 | 30.798 | 10.1405 | 7.2882 | 15.853 | 29.4129 | 12.8205 | 9.2144 | 19.7453 | 29.4538 | 12.4667 | 8.96 | 19.2842 | 29.5057 | 11.9156 | 8.564 | 19.1066 | 29.5646 | 11.7853 | 8.4703 | 19.0144 | 29.6349 | 11.4585 | 8.2355 | 18.8878 | 29.7155 | 11.1483 | 8.0125 | 18.7601 | 29.8105 | 10.96 | 7.8771 | 18.6551 | 29.9243 | 10.7967 | 7.7598 | 18.5572 | 30.0024 | 10.6632 | 7.6638 | 18.4601 | 30.0777 | 10.576 | 7.6012 | 18.3663 | 30.3321 | 10.1868 | 7.3214 | 17.5777 | 30.6058 | 9.7346 | 6.9964 | 16.0931 | 30.8018 | 9.2923 | 6.6786 | 14.8849 | 30.9656 | 8.8632 | 6.3701 | 13.5569 | 31.0629 | 8.4378 | 6.0644 | 12.4467 | 29.4129 | 12.8205 | 9.2144 | 19.7453 | 29.3994 | 12.5354 | 9.0095 | 19.5473 | 29.4168 | 12.0497 | 8.6604 | 19.4481 | 29.4387 | 11.9023 | 8.5544 | 19.3988 | 29.4749 | 11.6035 | 8.3397 | 19.2995 | 29.5323 | 11.3243 | 8.139 | 19.1812 | 29.6098 | 11.1455 | 8.0105 | 18.9888 | 29.7087 | 10.9161 | 7.8456 | 18.5069 | 29.7938 | 10.7034 | 7.6928 | 18.0056 | 29.8787 | 10.5184 | 7.5598 | 17.5034 | 30.1374 | 10.034 | 7.2116 | 15.9964 | 30.3911 | 9.5982 | 6.8984 | 14.5242 | 30.5671 | 9.1842 | 6.6008 | 13.3639 | 30.696 | 8.8369 | 6.3513 | 12.6036 | 30.7072 | 8.7298 | 6.2743 | 13.1365 | 29.41 | 12.8205 | 9.2144 | 19.7453 | 29.4442 | 12.5797 | 9.0413 | 19.4764 | 29.4807 | 11.9992 | 8.6241 | 19.3458 | 29.5165 | 11.9623 | 8.5975 | 19.2725 | 29.5619 | 11.6533 | 8.3755 | 19.1894 | 29.6268 | 11.344 | 8.1531 | 19.0985 | 29.7108 | 11.1913 | 8.0434 | 19.0008 | 29.8038 | 11.0307 | 7.928 | 18.9006 | 29.8685 | 10.9106 | 7.8417 | 18.7644 | 29.934 | 10.831 | 7.7844 | 18.6333 | 30.1463 | 10.5938 | 7.614 | 18.2014 | 30.3647 | 10.3955 | 7.4715 | 17.7246 | 30.5211 | 10.2043 | 7.334 | 17.4169 | 30.6548 | 10.0328 | 7.2107 | 17.1398 | 30.7281 | 9.8713 | 7.0947 | 17.0094 | 29.41 | 12.8205 | 9.2144 | 19.7453 | 29.4166 | 12.4713 | 8.9634 | 19.3478 | 29.4596 | 11.9721 | 8.6046 | 19.1675 | 29.5109 | 11.8108 | 8.4887 | 19.0589 | 29.5736 | 11.5035 | 8.2678 | 18.9064 | 29.6442 | 11.2207 | 8.0646 | 18.7546 | 29.7306 | 11.0318 | 7.9288 | 18.5231 | 29.8496 | 10.7927 | 7.7569 | 17.9856 | 29.9372 | 10.5724 | 7.5986 | 17.4511 | 30.0235 | 10.3829 | 7.4624 | 16.9158 | 30.2824 | 9.8898 | 7.108 | 15.3629 | 30.5278 | 9.4436 | 6.7873 | 13.8795 | 30.7014 | 9.022 | 6.4843 | 12.6621 | 30.8227 | 8.6258 | 6.1995 | 11.7545 | 30.8385 | 8.4956 | 6.1059 | 12.1292
S.W. MACCLESFIELD | MACCLESFIELD | MACCLESFIELD | 390968 | 373004 | 20.9459 | 3.4486 | 2.4786 | 8.3496 | 18.7857 | 3.0929 | 2.2229 | 6.7214 | 17.6308 | 2.9028 | 2.0863 | 6.1707 | 16.6195 | 2.7363 | 1.9666 | 5.9068 | 15.3457 | 2.5266 | 1.8159 | 5.5089 | 14.3398 | 2.3609 | 1.6969 | 5.0917 | 13.9306 | 2.2936 | 1.6484 | 4.7061 | 13.4407 | 2.2129 | 1.5905 | 4.3437 | 12.7014 | 2.0912 | 1.503 | 3.9192 | 12.0513 | 1.9842 | 1.426 | 3.5433 | 7.6284 | 1.256 | 0.90268 | 0.9534 | 2.5641 | 0.42215 | 0.30341 | -3.6245 | 2.6844 | 0.44197 | 0.31765 | -7.4495 | 2.6844 | 0.44197 | 0.31765 | -11.5042 | 2.6844 | 0.44197 | 0.31765 | -15.1526 | 20.9459 | 3.4486 | 2.4786 | 8.3496 | 20.1627 | 3.3196 | 2.3859 | 7.8458 | 19.6437 | 3.2342 | 2.3245 | 7.5397 | 18.9647 | 3.1224 | 2.2441 | 7.2691 | 18.1211 | 2.9835 | 2.1443 | 6.9168 | 17.1414 | 2.8222 | 2.0284 | 6.5347 | 16.5536 | 2.7254 | 1.9588 | 6.0492 | 15.3437 | 2.5262 | 1.8156 | 5.4369 | 14.3054 | 2.3553 | 1.6928 | 4.9269 | 13.2204 | 2.1766 | 1.5644 | 4.4152 | 10.0572 | 1.6558 | 1.1901 | 2.8929 | 6.8675 | 1.1307 | 0.81265 | 1.3866 | 3.9529 | 0.65082 | 0.46775 | -0.039527 | 4.5317 | 0.7461 | 0.53624 | -1.6267 | 4.634 | 0.76296 | 0.54835 | -2.7955 | 20.9459 | 3.4486 | 2.4786 | 8.3496 | 18.3823 | 3.0265 | 2.1752 | 6.5226 | 16.7403 | 2.7562 | 1.9809 | 5.9626 | 15.2449 | 2.5099 | 1.804 | 5.7611 | 14.4861 | 2.385 | 1.7142 | 5.4289 | 13.9191 | 2.2917 | 1.6471 | 5.0878 | 13.3179 | 2.1927 | 1.5759 | 4.8111 | 12.4997 | 2.058 | 1.4791 | 4.5647 | 11.2643 | 1.8546 | 1.3329 | 4.2792 | 10.8275 | 1.7827 | 1.2812 | 4.0186 | 6.8457 | 1.1271 | 0.81006 | 1.7831 | 0.59801 | 0.098458 | 0.070764 | -2.4912 | 2.6844 | 0.44197 | 0.31765 | -6.0462 | 2.6844 | 0.44197 | 0.31765 | -9.7745 | 2.6844 | 0.44197 | 0.31765 | -13.0476 | 20.9459 | 3.4486 | 2.4786 | 8.3496 | 19.3562 | 3.1869 | 2.2905 | 7.4262 | 17.9618 | 2.9573 | 2.1254 | 7.1045 | 17.2934 | 2.8472 | 2.0464 | 6.9567 | 16.7237 | 2.7534 | 1.9789 | 6.6431 | 16.0151 | 2.6368 | 1.8951 | 6.2703 | 14.7654 | 2.431 | 1.7472 | 5.6909 | 13.1087 | 2.1583 | 1.5512 | 4.3245 | 11.0539 | 1.8199 | 1.308 | 2.8877 | 8.9812 | 1.4787 | 1.0628 | 1.46 | 2.707 | 0.44568 | 0.32032 | -2.6839 | 2.6844 | 0.44197 | 0.31765 | -6.7524 | 2.6844 | 0.44197 | 0.31765 | -10.007 | 2.6844 | 0.44197 | 0.31765 | -12.1408 | 2.6844 | 0.44197 | 0.31765 | -11.0403 | 20.9459 | 3.4486 | 2.4786 | 8.3496 | 19.7836 | 3.2572 | 2.341 | 7.6439 | 18.9094 | 3.1133 | 2.2376 | 7.3467 | 18.0699 | 2.9751 | 2.1382 | 7.2057 | 17.0787 | 2.8119 | 2.021 | 7.0233 | 16.1962 | 2.6666 | 1.9165 | 6.789 | 15.9362 | 2.6238 | 1.8858 | 6.5161 | 15.5469 | 2.5597 | 1.8397 | 6.224 | 14.8514 | 2.4452 | 1.7574 | 5.813 | 14.1827 | 2.3351 | 1.6783 | 5.4149 | 11.0982 | 1.8272 | 1.3133 | 4.0268 | 9.3889 | 1.5458 | 1.111 | 2.3903 | 7.4774 | 1.2311 | 0.88481 | 1.2454 | 7.5158 | 1.2374 | 0.88935 | 0.10898 | 8.0808 | 1.3304 | 0.95621 | -0.56071 | 20.9459 | 3.4486 | 2.4786 | 8.3496 | 18.487 | 3.0437 | 2.1876 | 6.6251 | 16.7677 | 2.7607 | 1.9841 | 6.0154 | 15.903 | 2.6183 | 1.8818 | 5.7024 | 15.1382 | 2.4924 | 1.7913 | 5.2417 | 14.3263 | 2.3587 | 1.6953 | 4.7778 | 12.9262 | 2.1282 | 1.5296 | 4.0892 | 11.0544 | 1.82 | 1.3081 | 2.5622 | 8.8464 | 1.4565 | 1.0468 | 1.0073 | 6.6321 | 1.0919 | 0.78479 | -0.53649 | 2.6844 | 0.44197 | 0.31765 | -5.0222 | 2.6844 | 0.44197 | 0.31765 | -9.358 | 2.6844 | 0.44197 | 0.31765 | -12.8729 | 2.6844 | 0.44197 | 0.31765 | -15.3214 | 2.6844 | 0.44197 | 0.31765 | -14.5919
SPA RD | BOLTON | KEARSLEY | 371065 | 409109 | 37.6186 | 8.569 | 6.2509 | 7.7306 | 37.7453 | 8.255 | 6.0219 | 5.9991 | 37.902 | 8.0417 | 5.8663 | 5.1773 | 38.0711 | 7.8909 | 5.7563 | 4.6744 | 38.2803 | 7.7056 | 5.6211 | 4.1145 | 38.5307 | 7.456 | 5.4391 | 3.5317 | 38.7942 | 7.2152 | 5.2634 | 2.9609 | 39.1015 | 6.9995 | 5.106 | 2.3792 | 39.4096 | 6.7787 | 4.945 | 1.7349 | 39.7337 | 6.5557 | 4.7823 | 1.0932 | 35.1051 | 5.6944 | 4.154 | -1.7226 | 29.1907 | 4.735 | 3.4541 | -5.4945 | 23.6976 | 3.844 | 2.8041 | -8.3445 | 22.1156 | 3.5874 | 2.6169 | -10.7598 | 20.8706 | 3.3854 | 2.4696 | -12.348 | 37.6103 | 8.569 | 6.2509 | 7.7306 | 37.7508 | 8.4071 | 6.1329 | 7.1596 | 37.9226 | 8.3281 | 6.0752 | 6.6847 | 38.1095 | 8.1782 | 5.9659 | 6.3048 | 38.331 | 7.995 | 5.8322 | 5.8992 | 38.557 | 7.7772 | 5.6734 | 5.4578 | 38.8313 | 7.4496 | 5.4344 | 4.9317 | 39.1593 | 7.2169 | 5.2646 | 4.3095 | 39.3294 | 7.0585 | 5.1491 | 3.8614 | 39.5193 | 6.8712 | 5.0124 | 3.3856 | 38.8549 | 6.3026 | 4.5977 | 1.9572 | 35.8927 | 5.8221 | 4.2472 | 0.51406 | 33.1332 | 5.3745 | 3.9206 | -0.79223 | 32.8247 | 5.3245 | 3.8841 | -2.0896 | 32.2038 | 5.2238 | 3.8107 | -3.0508 | 37.6221 | 8.569 | 6.2509 | 7.7306 | 37.7644 | 8.1604 | 5.9529 | 5.6331 | 37.9403 | 7.8654 | 5.7377 | 4.6249 | 38.1311 | 7.5713 | 5.5232 | 3.9664 | 38.3601 | 7.2933 | 5.3204 | 3.2445 | 38.6175 | 6.9596 | 5.077 | 2.4902 | 38.8877 | 6.6638 | 4.8612 | 1.7335 | 39.2011 | 6.366 | 4.6439 | 0.9525 | 37.3509 | 6.0587 | 4.4197 | 0.14379 | 35.3946 | 5.7414 | 4.1882 | -0.66685 | 28.0797 | 4.5548 | 3.3227 | -4.0337 | 20.4355 | 3.3148 | 2.4181 | -7.9133 | 14.7878 | 2.3987 | 1.7498 | -10.551 | 12.3278 | 1.9997 | 1.4587 | -12.4404 | 10.8935 | 1.767 | 1.289 | -13.0509 | 37.6221 | 8.569 | 6.2509 | 7.7306 | 37.6535 | 8.3023 | 6.0564 | 6.3941 | 37.7635 | 8.1291 | 5.93 | 5.6152 | 37.8899 | 7.8735 | 5.7436 | 5.0707 | 38.0646 | 7.6137 | 5.5541 | 4.4416 | 38.2992 | 7.2979 | 5.3237 | 3.7324 | 38.5777 | 6.9328 | 5.0574 | 2.8275 | 38.924 | 6.4867 | 4.7319 | 1.4306 | 37.2553 | 6.0432 | 4.4084 | -0.028408 | 33.988 | 5.5132 | 4.0218 | -1.4504 | 27.719 | 4.4963 | 3.28 | -5.4784 | 20.9865 | 3.4042 | 2.4833 | -8.8581 | 16.0177 | 2.5982 | 1.8954 | -10.9944 | 16.6391 | 2.699 | 1.9689 | -11.912 | 13.7155 | 2.2248 | 1.623 | -11.1165 | 37.6186 | 8.569 | 6.2509 | 7.7306 | 37.7287 | 8.3992 | 6.1271 | 6.847 | 37.8561 | 8.2485 | 6.0172 | 6.2505 | 37.9777 | 8.1165 | 5.9209 | 5.8552 | 38.1228 | 7.9642 | 5.8098 | 5.4715 | 38.3165 | 7.7544 | 5.6568 | 5.0386 | 38.5424 | 7.5311 | 5.4938 | 4.5534 | 38.8028 | 7.3266 | 5.3447 | 4.0156 | 39.0719 | 7.1034 | 5.1819 | 3.3714 | 39.3689 | 6.8756 | 5.0157 | 2.6991 | 37.9179 | 6.1507 | 4.4868 | 0.52216 | 34.049 | 5.5231 | 4.029 | -1.6309 | 29.9761 | 4.8624 | 3.5471 | -3.2199 | 30.0621 | 4.8764 | 3.5572 | -4.5169 | 30.1725 | 4.8943 | 3.5703 | -5.0767 | 37.6186 | 8.569 | 6.2509 | 7.7306 | 37.685 | 8.1612 | 5.9535 | 5.6256 | 37.8452 | 7.9352 | 5.7886 | 4.5888 | 38.0269 | 7.648 | 5.5791 | 3.9084 | 38.2481 | 7.3494 | 5.3613 | 3.1584 | 38.5021 | 7.0236 | 5.1237 | 2.3873 | 38.8124 | 6.6518 | 4.8524 | 1.4509 | 38.1299 | 6.185 | 4.5119 | -0.039543 | 35.355 | 5.7349 | 4.1835 | -1.5162 | 32.0257 | 5.1949 | 3.7896 | -2.9749 | 25.457 | 4.1294 | 3.0123 | -7.1368 | 18.4765 | 2.9971 | 2.1863 | -10.6236 | 13.2912 | 2.156 | 1.5727 | -12.885 | 13.7316 | 2.2274 | 1.6249 | -13.9425 | 10.535 | 1.7089 | 1.2466 | -13.3791
SPADEADAM 132/11KV | - | HARKER / HUTTON | 361282 | 570359 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795
SPOTLAND | ROCHDALE CENTRAL | ROCHDALE | 387882 | 414309 | 22.5198 | 13.2926 | 9.6968 | 11.5181 | 22.6126 | 13.2491 | 9.665 | 11.155 | 22.7489 | 13.2256 | 9.6479 | 11.0277 | 22.8732 | 13.2098 | 9.6364 | 10.9578 | 22.9958 | 13.0915 | 9.5501 | 10.8085 | 23.1351 | 12.9881 | 9.4746 | 10.6555 | 23.2923 | 12.9133 | 9.4201 | 10.5266 | 23.4825 | 12.8332 | 9.3616 | 10.4134 | 23.63 | 12.7485 | 9.2998 | 10.2616 | 23.7681 | 12.6671 | 9.2405 | 10.1321 | 24.2502 | 12.2693 | 8.9503 | 8.7588 | 24.6537 | 11.6294 | 8.4835 | 6.0578 | 24.9605 | 11.1863 | 8.1602 | 3.7197 | 25.2468 | 10.5664 | 7.7081 | 1.1605 | 25.4537 | 9.9998 | 7.2947 | -1.074 | 22.4857 | 13.2926 | 9.6968 | 11.5181 | 22.5479 | 13.2503 | 9.6659 | 11.3721 | 22.6094 | 13.2024 | 9.6309 | 11.2847 | 22.6948 | 13.1372 | 9.5834 | 11.1999 | 22.7832 | 13.071 | 9.5351 | 11.0701 | 22.8917 | 13.0017 | 9.4845 | 10.9157 | 22.9909 | 12.7634 | 9.3107 | 10.7108 | 23.1064 | 12.6976 | 9.2627 | 10.452 | 23.1992 | 12.6434 | 9.2232 | 10.2315 | 23.2834 | 12.5954 | 9.1882 | 10.0084 | 23.5402 | 12.4375 | 9.073 | 9.3402 | 23.7878 | 12.328 | 8.9931 | 8.6777 | 24.0117 | 12.193 | 8.8946 | 7.9922 | 24.2436 | 11.9943 | 8.7497 | 7.2194 | 24.4226 | 11.7681 | 8.5847 | 6.6987 | 22.5343 | 13.2926 | 9.6968 | 11.5181 | 22.6399 | 13.2412 | 9.6593 | 11.1249 | 22.7982 | 13.2109 | 9.6372 | 11.0119 | 22.9145 | 13.135 | 9.5818 | 10.8271 | 23.0574 | 12.9851 | 9.4725 | 10.567 | 23.2212 | 12.8903 | 9.4033 | 10.3099 | 23.4085 | 12.7363 | 9.2909 | 10.0956 | 23.6353 | 12.6237 | 9.2088 | 9.9023 | 23.8053 | 12.5044 | 9.1218 | 9.6716 | 23.9393 | 12.4096 | 9.0526 | 9.4537 | 24.4218 | 11.8577 | 8.65 | 8.1272 | 24.8274 | 11.3814 | 8.3026 | 5.602 | 25.1237 | 10.8281 | 7.8989 | 3.4166 | 25.3991 | 10.1799 | 7.4261 | 1.0301 | 25.5901 | 9.6281 | 7.0236 | -1.0192 | 22.5343 | 13.2926 | 9.6968 | 11.5181 | 22.5428 | 13.3119 | 9.7109 | 11.4655 | 22.6132 | 13.3327 | 9.726 | 11.4424 | 22.7186 | 13.2514 | 9.6667 | 11.2767 | 22.8181 | 13.142 | 9.5869 | 11.0088 | 22.9617 | 13.0351 | 9.5089 | 10.7196 | 23.1544 | 12.692 | 9.2587 | 10.2926 | 23.4216 | 12.5159 | 9.1301 | 9.3295 | 23.6126 | 12.2158 | 8.9112 | 8.326 | 23.7701 | 11.8917 | 8.6748 | 7.3316 | 24.1638 | 11.1547 | 8.1372 | 4.7305 | 24.5789 | 10.5845 | 7.7212 | 2.3355 | 24.8869 | 10.0632 | 7.341 | 0.33243 | 25.1318 | 9.6305 | 7.0253 | -1.0065 | 25.1562 | 9.6269 | 7.0227 | -0.18174 | 22.5198 | 13.2926 | 9.6968 | 11.5181 | 22.5979 | 13.2862 | 9.6921 | 11.3446 | 22.687 | 13.285 | 9.6912 | 11.2919 | 22.7876 | 13.2777 | 9.6859 | 11.2895 | 22.8641 | 13.1909 | 9.6226 | 11.2637 | 22.9802 | 13.0988 | 9.5554 | 11.2067 | 23.1344 | 13.0398 | 9.5124 | 11.1258 | 23.3031 | 12.9666 | 9.459 | 11.0423 | 23.4335 | 12.8835 | 9.3983 | 10.8991 | 23.5614 | 12.8004 | 9.3377 | 10.7631 | 23.9528 | 12.561 | 9.1631 | 10.2513 | 24.3301 | 12.2676 | 8.949 | 9.3618 | 24.6124 | 12.1035 | 8.8293 | 8.6903 | 24.8571 | 11.8363 | 8.6344 | 8.0545 | 24.9678 | 11.5945 | 8.458 | 7.6908 | 22.5198 | 13.2926 | 9.6968 | 11.5181 | 22.5653 | 13.2734 | 9.6828 | 11.2712 | 22.6951 | 13.2737 | 9.683 | 11.1453 | 22.8174 | 13.174 | 9.6103 | 10.8963 | 22.9447 | 13.0528 | 9.5218 | 10.5532 | 23.0869 | 12.9401 | 9.4396 | 10.2134 | 23.2666 | 12.6217 | 9.2073 | 9.7229 | 23.547 | 12.3778 | 9.0295 | 8.6716 | 23.783 | 12.0654 | 8.8015 | 7.5995 | 23.9429 | 11.7325 | 8.5587 | 6.5367 | 24.3427 | 10.9687 | 8.0015 | 3.7321 | 24.7225 | 10.3664 | 7.5621 | 1.1661 | 25.0041 | 9.8188 | 7.1627 | -1.0082 | 25.2171 | 9.2988 | 6.7833 | -2.5706 | 25.2641 | 9.2772 | 6.7676 | -2.0033
SPRING COTTAGE | NELSON | PADIHAM | 385446 | 437481 | -9.0095 | -1.4614 | -1.0661 | -9.0095 | -9.9408 | -1.6125 | -1.1763 | -9.9408 | -10.7609 | -1.7455 | -1.2733 | -10.7609 | -12.7387 | -2.0663 | -1.5074 | -12.7387 | -15.7725 | -2.5584 | -1.8664 | -15.7725 | -16.5266 | -2.6808 | -1.9556 | -16.5266 | -16.9301 | -2.7462 | -2.0033 | -16.9301 | -17.4087 | -2.8239 | -2.06 | -17.4087 | -17.8394 | -2.8937 | -2.1109 | -17.8394 | -18.2431 | -2.9592 | -2.1587 | -18.2431 | -19.9035 | -3.2285 | -2.3552 | -19.9035 | -21.7106 | -3.5217 | -2.569 | -21.7106 | -23.2213 | -3.7667 | -2.7478 | -23.2213 | -25.4343 | -4.1257 | -3.0096 | -25.4343 | -26.624 | -4.3187 | -3.1504 | -26.624 | -9.0095 | -1.4614 | -1.0661 | -9.0095 | -9.3251 | -1.5126 | -1.1034 | -9.3251 | -10.1018 | -1.6386 | -1.1953 | -10.1018 | -10.6997 | -1.7356 | -1.2661 | -10.6997 | -11.292 | -1.8317 | -1.3362 | -11.292 | -11.9729 | -1.9421 | -1.4167 | -11.9729 | -13.4174 | -2.1764 | -1.5877 | -13.4174 | -13.8653 | -2.2491 | -1.6407 | -13.8653 | -14.1588 | -2.2967 | -1.6754 | -14.1588 | -14.4437 | -2.3429 | -1.7091 | -14.4437 | -15.3438 | -2.4889 | -1.8156 | -15.3438 | -16.1603 | -2.6214 | -1.9122 | -16.1603 | -17.2098 | -2.7916 | -2.0364 | -17.2098 | -19.0894 | -3.0965 | -2.2588 | -19.0894 | -19.5719 | -3.1747 | -2.3159 | -19.5719 | -9.0095 | -1.4614 | -1.0661 | -9.0095 | -9.9955 | -1.6214 | -1.1828 | -9.9955 | -11.0904 | -1.799 | -1.3123 | -11.0904 | -13.3856 | -2.1713 | -1.5839 | -13.3856 | -17.2961 | -2.8056 | -2.0466 | -17.2961 | -16.8247 | -2.7291 | -1.9909 | -16.8247 | -17.4768 | -2.8349 | -2.068 | -17.4768 | -18.1135 | -2.9382 | -2.1434 | -18.1135 | -18.5345 | -3.0065 | -2.1932 | -18.5345 | -18.9817 | -3.079 | -2.2461 | -18.9817 | -20.5324 | -3.3305 | -2.4296 | -20.5324 | -22.4943 | -3.6488 | -2.6618 | -22.4943 | -24.1928 | -3.9243 | -2.8627 | -24.1928 | -25.8568 | -4.1942 | -3.0596 | -25.8568 | -27.5634 | -4.4711 | -3.2616 | -27.5634 | -9.0095 | -1.4614 | -1.0661 | -9.0095 | -9.692 | -1.5721 | -1.1469 | -9.692 | -10.039 | -1.6284 | -1.1879 | -10.039 | -12.1988 | -1.9788 | -1.4435 | -12.1988 | -13.6259 | -2.2103 | -1.6124 | -13.6259 | -15.2636 | -2.4759 | -1.8061 | -15.2636 | -15.2481 | -2.4734 | -1.8043 | -15.2481 | -16.1499 | -2.6197 | -1.911 | -16.1499 | -17.3366 | -2.8122 | -2.0514 | -17.3366 | -18.3123 | -2.9704 | -2.1669 | -18.3123 | -20.9704 | -3.4016 | -2.4814 | -20.9704 | -23.0379 | -3.737 | -2.7261 | -23.0379 | -24.8494 | -4.0308 | -2.9404 | -24.8494 | -26.4262 | -4.2866 | -3.127 | -26.4262 | -26.2453 | -4.2573 | -3.1056 | -26.2453 | -9.0095 | -1.4614 | -1.0661 | -9.0095 | -9.62 | -1.5605 | -1.1383 | -9.62 | -10.3564 | -1.6799 | -1.2255 | -10.3564 | -12.1641 | -1.9731 | -1.4394 | -12.1641 | -15.1525 | -2.4579 | -1.793 | -15.1525 | -15.9007 | -2.5792 | -1.8815 | -15.9007 | -16.2604 | -2.6376 | -1.9241 | -16.2604 | -16.6927 | -2.7077 | -1.9752 | -16.6927 | -17.1245 | -2.7778 | -2.0263 | -17.1245 | -17.5441 | -2.8458 | -2.076 | -17.5441 | -18.8474 | -3.0572 | -2.2302 | -18.8474 | -19.5593 | -3.1727 | -2.3144 | -19.5593 | -20.1249 | -3.2645 | -2.3814 | -20.1249 | -20.8166 | -3.3767 | -2.4632 | -20.8166 | -21.4411 | -3.478 | -2.5371 | -21.4411 | -9.0095 | -1.4614 | -1.0661 | -9.0095 | -9.9494 | -1.6139 | -1.1773 | -9.9494 | -10.4372 | -1.693 | -1.235 | -10.4372 | -12.6624 | -2.054 | -1.4983 | -12.6624 | -14.0973 | -2.2867 | -1.6681 | -14.0973 | -15.7381 | -2.5529 | -1.8623 | -15.7381 | -15.8557 | -2.572 | -1.8762 | -15.8557 | -16.7293 | -2.7137 | -1.9796 | -16.7293 | -17.9541 | -2.9123 | -2.1245 | -17.9541 | -18.9073 | -3.0669 | -2.2373 | -18.9073 | -21.6676 | -3.5147 | -2.5639 | -21.6676 | -23.7543 | -3.8532 | -2.8108 | -23.7543 | -25.5852 | -4.1502 | -3.0275 | -25.5852 | -27.3143 | -4.4307 | -3.2321 | -27.3143 | -27.2644 | -4.4225 | -3.2262 | -27.2644 | Switchgear to be replaced in RIIO-ED2
SPRING GARDEN ST 11kV | LANCASTER | HEYSHAM | 347661 | 461494 | 40.1974 | 10.1727 | 7.3113 | 28.6133 | 40.2359 | 10.0321 | 7.2103 | 28.4786 | 40.2868 | 9.7644 | 7.0179 | 27.7477 | 40.3434 | 9.4854 | 6.8173 | 27.0242 | 40.4154 | 9.1282 | 6.5606 | 26.2307 | 40.496 | 8.6874 | 6.2438 | 25.4287 | 40.5846 | 8.2516 | 5.9306 | 24.6486 | 42.9458 | 7.6092 | 5.4689 | 22.209 | 42.9667 | 7.3822 | 5.3058 | 22.1035 | 42.9924 | 7.3032 | 5.249 | 22.0114 | 41.7835 | 6.8793 | 4.9443 | 20.8586 | 38.1832 | 6.2866 | 4.5183 | 18.5907 | 35.1174 | 5.7818 | 4.1555 | 16.7228 | 31.979 | 5.2651 | 3.7841 | 14.3517 | 28.7007 | 4.7253 | 3.3962 | 12.5904 | 40.1869 | 10.1727 | 7.3113 | 28.6133 | 40.2293 | 10.0906 | 7.2523 | 28.4588 | 40.2736 | 9.8546 | 7.0827 | 28.3058 | 40.3219 | 9.6214 | 6.9151 | 28.151 | 40.3825 | 9.3491 | 6.7194 | 27.9616 | 40.4527 | 9.1423 | 6.5707 | 27.7693 | 40.5367 | 8.8182 | 6.3378 | 27.532 | 40.6356 | 8.6957 | 6.2498 | 27.2324 | 40.6962 | 8.5955 | 6.1777 | 27.0182 | 40.757 | 8.4994 | 6.1087 | 26.809 | 40.9376 | 8.234 | 5.9179 | 26.2165 | 41.1159 | 8.0323 | 5.773 | 25.6297 | 41.2766 | 7.8313 | 5.6285 | 25.1036 | 41.8493 | 7.6056 | 5.4663 | 24.1283 | 42.661 | 7.2918 | 5.2407 | 23.0093 | 40.2003 | 10.1727 | 7.3113 | 28.6133 | 40.2418 | 9.9952 | 7.1837 | 28.4898 | 40.2971 | 9.6729 | 6.9521 | 27.7705 | 40.3601 | 9.343 | 6.715 | 27.0673 | 40.4399 | 8.9728 | 6.4489 | 26.293 | 40.5295 | 8.5549 | 6.1486 | 25.5126 | 40.6295 | 8.0706 | 5.8005 | 24.7684 | 42.9299 | 7.4122 | 5.3273 | 22.4364 | 42.9486 | 7.1959 | 5.1718 | 22.3872 | 42.9708 | 7.0895 | 5.0954 | 22.342 | 38.5042 | 6.3394 | 4.5563 | 20.1154 | 34.2084 | 5.6322 | 4.0479 | 17.5111 | 30.6974 | 5.0541 | 3.6325 | 15.7937 | 27.3001 | 4.4948 | 3.2305 | 14.0816 | 23.4554 | 3.8618 | 2.7755 | 12.5176 | 40.2003 | 10.1727 | 7.3113 | 28.6133 | 40.1869 | 10.0671 | 7.2354 | 28.7036 | 40.2125 | 9.7924 | 7.038 | 28.0485 | 40.8445 | 9.3418 | 6.7141 | 26.7776 | 43.7043 | 8.5875 | 6.172 | 23.1872 | 44.6996 | 8.0944 | 5.8176 | 21.4902 | 44.5784 | 7.6041 | 5.4652 | 20.8386 | 42.8575 | 7.0562 | 5.0714 | 20.351 | 40.3438 | 6.6423 | 4.7739 | 19.7378 | 37.8147 | 6.2259 | 4.4747 | 19.1232 | 32.9638 | 5.4272 | 3.9007 | 17.1305 | 28.7554 | 4.7344 | 3.4027 | 15.1012 | 24.8693 | 4.0945 | 2.9428 | 13.3771 | 21.8947 | 3.6048 | 2.5908 | 12.4795 | 20.783 | 3.4218 | 2.4593 | 13.2714 | 40.1974 | 10.1727 | 7.3113 | 28.6133 | 40.2311 | 10.0615 | 7.2314 | 28.4956 | 40.2697 | 9.8022 | 7.045 | 27.7859 | 40.3064 | 9.5328 | 6.8514 | 27.1015 | 40.3533 | 9.1939 | 6.6079 | 26.3945 | 40.4183 | 8.7731 | 6.3054 | 25.6819 | 40.4999 | 8.3513 | 6.0022 | 24.9583 | 42.8481 | 7.7129 | 5.5434 | 22.5447 | 42.8603 | 7.4827 | 5.378 | 22.4373 | 42.8807 | 7.4001 | 5.3186 | 22.33 | 43.0808 | 7.1109 | 5.1107 | 21.846 | 41.4403 | 6.8228 | 4.9037 | 21.2117 | 40.2411 | 6.6254 | 4.7618 | 20.8001 | 39.0246 | 6.4251 | 4.6178 | 20.0035 | 37.4899 | 6.1724 | 4.4362 | 19.6815 | 40.1974 | 10.1727 | 7.3113 | 28.6133 | 40.1978 | 10.0245 | 7.2048 | 28.6642 | 40.2432 | 9.7374 | 6.9985 | 27.9581 | 40.8986 | 9.2763 | 6.667 | 26.6302 | 43.7797 | 8.5044 | 6.1123 | 22.9865 | 44.7777 | 8.009 | 5.7562 | 21.251 | 44.6552 | 7.5029 | 5.3925 | 20.5504 | 42.2124 | 6.9499 | 4.9951 | 20.0013 | 39.6479 | 6.5277 | 4.6916 | 19.3519 | 37.0754 | 6.1042 | 4.3872 | 18.6991 | 32.083 | 5.2822 | 3.7964 | 16.5811 | 27.7249 | 4.5647 | 3.2807 | 14.4449 | 23.664 | 3.8961 | 2.8002 | 12.5944 | 20.4365 | 3.3647 | 2.4183 | 11.5078 | 19.0461 | 3.1358 | 2.2538 | 12.0645
SPRING GARDEN ST 6.6KV | LANCASTER | HEYSHAM | 347651 | 461484 | 29.6427 | 8.4949 | 6.1969 | 15.6949 | 29.7187 | 8.3429 | 6.086 | 15.4198 | 29.8157 | 8.169 | 5.9592 | 15.0779 | 29.9142 | 7.9628 | 5.8087 | 14.7665 | 30.0224 | 7.7026 | 5.619 | 14.4276 | 30.1399 | 7.3011 | 5.3261 | 14.0892 | 30.2695 | 7.0226 | 5.1229 | 13.7701 | 30.4174 | 6.7485 | 4.9229 | 13.4552 | 30.5386 | 6.4699 | 4.7197 | 13.1046 | 30.6592 | 6.2872 | 4.5864 | 12.776 | 31.0221 | 5.8418 | 4.2615 | 11.4377 | 31.3652 | 5.2814 | 3.8527 | 9.4773 | 29.1854 | 4.7342 | 3.4535 | 7.7345 | 25.4655 | 4.1308 | 3.0133 | 5.8623 | 21.1642 | 3.433 | 2.5044 | 4.0537 | 29.6375 | 8.4949 | 6.1969 | 15.6949 | 29.7486 | 8.3971 | 6.1256 | 15.4067 | 29.8831 | 8.1536 | 5.9479 | 15.0648 | 30.0283 | 7.907 | 5.7681 | 14.7436 | 30.1946 | 7.6417 | 5.5745 | 14.4107 | 30.3844 | 7.3228 | 5.3419 | 14.0741 | 30.5602 | 7.0777 | 5.1631 | 13.6877 | 30.7299 | 6.908 | 5.0393 | 13.1977 | 30.826 | 6.7642 | 4.9344 | 12.8262 | 30.9219 | 6.6254 | 4.8331 | 12.4666 | 31.2035 | 6.2227 | 4.5394 | 11.4706 | 31.4934 | 5.8811 | 4.2902 | 10.4853 | 31.7664 | 5.5562 | 4.0532 | 9.5891 | 32.0671 | 5.2177 | 3.8062 | 8.4255 | 29.7446 | 4.8249 | 3.5197 | 7.492 | 29.6449 | 8.4949 | 6.1969 | 15.6949 | 29.7233 | 8.2974 | 6.0529 | 15.4162 | 29.8233 | 8.0324 | 5.8595 | 15.0738 | 29.9263 | 7.7572 | 5.6588 | 14.7605 | 30.039 | 7.4573 | 5.44 | 14.4212 | 30.1611 | 7.062 | 5.1516 | 14.0828 | 30.2956 | 6.7181 | 4.9007 | 13.762 | 30.4481 | 6.3989 | 4.6679 | 13.448 | 30.5636 | 6.105 | 4.4535 | 13.1307 | 30.6781 | 5.932 | 4.3273 | 12.8391 | 31.039 | 5.2578 | 3.8355 | 11.6105 | 27.7582 | 4.5027 | 3.2846 | 9.7788 | 23.4839 | 3.8093 | 2.7788 | 8.1588 | 18.6257 | 3.0213 | 2.204 | 6.4666 | 13.3276 | 2.1619 | 1.577 | 4.8976 | 29.6449 | 8.4949 | 6.1969 | 15.6949 | 29.6697 | 8.35 | 6.0912 | 15.5498 | 29.7308 | 8.1505 | 5.9457 | 15.2695 | 29.7921 | 7.8685 | 5.7399 | 15.0057 | 29.865 | 7.6192 | 5.5581 | 14.7104 | 29.9555 | 7.365 | 5.3727 | 14.4064 | 30.0625 | 6.9237 | 5.0508 | 14.0313 | 30.189 | 6.3881 | 4.66 | 13.4001 | 30.3124 | 5.9687 | 4.3541 | 12.7232 | 30.4364 | 5.5619 | 4.0573 | 12.0694 | 29.1642 | 4.7307 | 3.451 | 10.2255 | 24.2136 | 3.9277 | 2.8652 | 8.2133 | 19.6302 | 3.1842 | 2.3228 | 6.7084 | 14.7518 | 2.3929 | 1.7456 | 5.6154 | 11.4369 | 1.8552 | 1.3533 | 5.6218 | 29.6427 | 8.4949 | 6.1969 | 15.6949 | 29.7151 | 8.3702 | 6.106 | 15.441 | 29.8032 | 8.203 | 5.984 | 15.1146 | 29.888 | 8.0025 | 5.8377 | 14.8318 | 29.9806 | 7.7556 | 5.6576 | 14.5526 | 30.0894 | 7.3522 | 5.3634 | 14.2772 | 30.2141 | 7.1029 | 5.1815 | 14.0047 | 30.3497 | 6.8313 | 4.9833 | 13.7145 | 30.4582 | 6.54 | 4.7708 | 13.3558 | 30.5679 | 6.3855 | 4.6582 | 13.008 | 30.9038 | 5.9978 | 4.3753 | 12.0148 | 31.2296 | 5.6338 | 4.1098 | 11.0134 | 31.463 | 5.2718 | 3.8457 | 10.3381 | 30.4437 | 4.9383 | 3.6024 | 9.6637 | 27.6843 | 4.4907 | 3.2759 | 9.0716 | 29.6427 | 8.4949 | 6.1969 | 15.6949 | 29.6932 | 8.3134 | 6.0645 | 15.5106 | 29.7853 | 8.0981 | 5.9075 | 15.1814 | 29.881 | 7.8033 | 5.6924 | 14.863 | 29.9867 | 7.5424 | 5.5021 | 14.516 | 30.0995 | 7.2827 | 5.3126 | 14.1755 | 30.2253 | 6.8293 | 4.9819 | 13.7669 | 30.3793 | 6.2878 | 4.5868 | 13.0843 | 30.4997 | 5.8663 | 4.2794 | 12.3937 | 30.6201 | 5.4537 | 3.9784 | 11.728 | 28.3884 | 4.6049 | 3.3592 | 9.8048 | 23.3155 | 3.782 | 2.7589 | 7.741 | 18.6091 | 3.0186 | 2.202 | 6.1717 | 13.6138 | 2.2083 | 1.6109 | 4.9863 | 10.1026 | 1.6387 | 1.1954 | 4.867
SQUIRES GATE | BLACKPOOL | PENWORTHAM WEST / STANAH | 332037 | 432063 | 22.04 | 3.5751 | 2.608 | 15.8871 | 19.0562 | 3.0911 | 2.2549 | 12.8783 | 18.2483 | 2.9601 | 2.1593 | 12.2468 | 17.3303 | 2.8111 | 2.0507 | 12.1265 | 15.5542 | 2.523 | 1.8405 | 11.9387 | 13.7223 | 2.2259 | 1.6238 | 11.7343 | 12.4241 | 2.0153 | 1.4701 | 11.5195 | 11.132 | 1.8057 | 1.3172 | 11.132 | 10.0928 | 1.6372 | 1.1943 | 10.0928 | 9.1316 | 1.4812 | 1.0805 | 9.1316 | 9.5209 | 1.5444 | 1.1266 | 9.2736 | 12.9216 | 2.096 | 1.529 | 7.5148 | 25.1119 | 4.0734 | 2.9715 | 5.9148 | 27.662 | 6.6041 | 4.8176 | 4.2888 | 27.8174 | 7.2145 | 5.2629 | 2.9316 | 22.04 | 3.5751 | 2.608 | 15.8871 | 21.1327 | 3.4279 | 2.5006 | 14.783 | 20.7658 | 3.3684 | 2.4572 | 14.4859 | 20.4219 | 3.3126 | 2.4165 | 14.3397 | 19.6616 | 3.1893 | 2.3266 | 14.1001 | 18.6411 | 3.0238 | 2.2058 | 13.8121 | 16.9362 | 2.7472 | 2.0041 | 13.4624 | 16.0761 | 2.6077 | 1.9023 | 13.0496 | 15.3406 | 2.4884 | 1.8152 | 12.7 | 14.5241 | 2.3559 | 1.7186 | 12.3386 | 12.4335 | 2.0168 | 1.4712 | 11.2275 | 10.8346 | 1.7575 | 1.2821 | 10.1252 | 17.9633 | 2.9138 | 2.1256 | 9.1284 | 27.106 | 4.7983 | 3.5003 | 8.133 | 27.4593 | 5.2813 | 3.8527 | 7.5056 | 22.04 | 3.5751 | 2.608 | 15.8871 | 18.5027 | 3.0013 | 2.1894 | 12.4197 | 17.1763 | 2.7862 | 2.0325 | 11.7288 | 15.9868 | 2.5932 | 1.8917 | 11.6516 | 14.238 | 2.3095 | 1.6848 | 11.5239 | 12.6011 | 2.044 | 1.4911 | 11.3756 | 11.1822 | 1.8139 | 1.3232 | 11.1822 | 9.1726 | 1.4879 | 1.0854 | 9.1726 | 9.0196 | 1.4631 | 1.0673 | 9.0196 | 9.0715 | 1.4715 | 1.0734 | 9.0715 | 8.1606 | 1.3237 | 0.96564 | 8.1606 | 11.4701 | 1.8606 | 1.3573 | 7.3942 | 23.3241 | 3.7834 | 2.7599 | 5.7423 | 27.8062 | 6.2591 | 4.5659 | 4.0536 | 27.932 | 6.8904 | 5.0264 | 2.9649 | 22.04 | 3.5751 | 2.608 | 15.8871 | 19.7892 | 3.21 | 2.3417 | 13.5664 | 18.8298 | 3.0544 | 2.2281 | 13.106 | 17.8339 | 2.8928 | 2.1103 | 13.0527 | 16.1921 | 2.6265 | 1.916 | 12.9565 | 14.9597 | 2.4266 | 1.7702 | 12.8349 | 13.6888 | 2.2205 | 1.6198 | 12.6342 | 15.4395 | 2.5044 | 1.827 | 12.0729 | 16.2329 | 2.6331 | 1.9208 | 11.4334 | 18.5189 | 3.004 | 2.1913 | 10.7879 | 26.0469 | 8.5033 | 6.2031 | 8.8068 | 26.7043 | 7.9926 | 5.8305 | 6.8389 | 27.1169 | 7.5864 | 5.5342 | 5.34 | 27.3807 | 7.4395 | 5.427 | 4.2674 | 27.4213 | 7.3668 | 5.374 | 4.7218 | 22.04 | 3.5751 | 2.608 | 15.8871 | 20.1557 | 3.2695 | 2.385 | 13.8489 | 19.594 | 3.1783 | 2.3186 | 13.4177 | 18.884 | 3.0632 | 2.2345 | 13.3506 | 17.3122 | 2.8082 | 2.0485 | 13.2797 | 15.471 | 2.5095 | 1.8307 | 13.123 | 14.1886 | 2.3015 | 1.6789 | 12.92 | 12.8631 | 2.0865 | 1.5221 | 12.7129 | 11.7732 | 1.9097 | 1.3931 | 11.7732 | 11.0287 | 1.789 | 1.305 | 11.0287 | 11.9347 | 1.9359 | 1.4122 | 11.0907 | 16.4373 | 2.6663 | 1.945 | 10.0261 | 27.1056 | 4.8437 | 3.5334 | 9.2724 | 27.4374 | 7.6012 | 5.545 | 8.666 | 27.5464 | 8.4438 | 6.1596 | 8.4272 | 22.04 | 3.5751 | 2.608 | 15.8871 | 18.1961 | 2.9516 | 2.1531 | 12.0739 | 16.6461 | 2.7002 | 1.9697 | 11.2922 | 15.5515 | 2.5226 | 1.8402 | 11.1594 | 13.8584 | 2.248 | 1.6399 | 10.9676 | 12.5135 | 2.0298 | 1.4807 | 10.7593 | 11.2108 | 1.8185 | 1.3266 | 10.4941 | 12.9484 | 2.1004 | 1.5322 | 9.9302 | 13.7419 | 2.2291 | 1.6261 | 9.2494 | 15.7859 | 2.5606 | 1.8679 | 8.5492 | 26.1349 | 8.0302 | 5.8579 | 6.3637 | 26.8148 | 7.479 | 5.4558 | 4.1863 | 27.2635 | 7.0377 | 5.1339 | 2.5077 | 27.5309 | 6.8584 | 5.0031 | 1.2721 | 27.5741 | 6.7543 | 4.9272 | 1.5785
ST ANNES | LYTHAM | PENWORTHAM WEST / STANAH | 331716 | 429849 | 22.1106 | 11.0319 | 8.0476 | 14.6263 | 22.1548 | 10.6592 | 7.7757 | 13.8681 | 22.2159 | 9.9888 | 7.2867 | 13.6399 | 22.2948 | 9.9193 | 7.236 | 13.5273 | 22.3919 | 9.6857 | 7.0656 | 13.3701 | 22.5042 | 9.4018 | 6.8585 | 13.2094 | 22.6349 | 9.2669 | 6.76 | 13.0593 | 22.7957 | 9.1278 | 6.6586 | 12.9222 | 22.9271 | 9.0075 | 6.5708 | 12.7674 | 23.0561 | 8.949 | 6.5282 | 12.6299 | 23.4608 | 8.6567 | 6.3149 | 11.6843 | 23.8334 | 8.2606 | 6.026 | 10.0173 | 24.0968 | 7.9154 | 5.7741 | 8.6573 | 24.3251 | 7.4713 | 5.4502 | 7.1889 | 24.4862 | 7.1887 | 5.244 | 5.8348 | 22.0895 | 11.0319 | 8.0476 | 14.6263 | 22.129 | 10.7791 | 7.8632 | 14.2518 | 22.1627 | 10.2861 | 7.5036 | 14.0993 | 22.2042 | 10.0883 | 7.3593 | 13.992 | 22.262 | 9.9672 | 7.271 | 13.8608 | 22.3327 | 9.7896 | 7.1414 | 13.741 | 22.417 | 9.6124 | 7.0121 | 13.5899 | 22.5132 | 9.5228 | 6.9467 | 13.3933 | 22.5775 | 9.4558 | 6.8978 | 13.2239 | 22.6457 | 9.3871 | 6.8477 | 13.0466 | 22.8657 | 9.2027 | 6.7132 | 12.5118 | 23.0941 | 9.073 | 6.6187 | 11.9824 | 23.3074 | 8.9265 | 6.5118 | 11.4725 | 23.5297 | 8.7503 | 6.3832 | 10.9065 | 23.694 | 8.5799 | 6.2589 | 10.4932 | 22.1161 | 11.0319 | 8.0476 | 14.6263 | 22.165 | 10.6212 | 7.748 | 13.7693 | 22.2343 | 9.8329 | 7.173 | 13.5345 | 22.3249 | 9.868 | 7.1986 | 13.4426 | 22.4364 | 9.6055 | 7.0071 | 13.3117 | 22.5652 | 9.332 | 6.8076 | 13.1779 | 22.7156 | 9.1918 | 6.7053 | 13.0663 | 22.8998 | 9.0439 | 6.5974 | 12.9707 | 23.0441 | 8.9326 | 6.5162 | 12.8662 | 23.1849 | 8.866 | 6.4676 | 12.7705 | 23.6038 | 8.549 | 6.2363 | 11.9488 | 24.0202 | 8.145 | 5.9417 | 10.3817 | 24.3213 | 7.7756 | 5.6722 | 9.1093 | 24.5764 | 7.3876 | 5.3892 | 7.7491 | 24.6919 | 7.0459 | 5.1399 | 6.5216 | 22.1161 | 11.0319 | 8.0476 | 14.6263 | 22.1211 | 10.6953 | 7.8021 | 14.1217 | 22.1548 | 9.8142 | 7.1593 | 13.9653 | 22.2041 | 9.9857 | 7.2844 | 13.8814 | 22.2783 | 9.7257 | 7.0948 | 13.7416 | 22.3916 | 9.4931 | 6.9251 | 13.5864 | 22.5357 | 9.3079 | 6.79 | 13.3578 | 22.7076 | 9.1094 | 6.6452 | 12.8484 | 22.85 | 8.9088 | 6.4988 | 12.3152 | 22.9928 | 8.7469 | 6.3807 | 11.7836 | 23.4307 | 8.3217 | 6.0705 | 10.2408 | 23.8262 | 7.9413 | 5.7931 | 8.7446 | 24.1037 | 7.6036 | 5.5467 | 7.5773 | 24.3236 | 7.3028 | 5.3273 | 6.8041 | 24.3996 | 7.2683 | 5.3021 | 7.1972 | 22.1106 | 11.0319 | 8.0476 | 14.6263 | 22.1489 | 10.7019 | 7.8069 | 13.9971 | 22.1909 | 10.0163 | 7.3068 | 13.8108 | 22.2401 | 9.9808 | 7.2809 | 13.735 | 22.3059 | 9.7662 | 7.1243 | 13.6456 | 22.4047 | 9.49 | 6.9228 | 13.5479 | 22.5329 | 9.3661 | 6.8325 | 13.4515 | 22.6752 | 9.2359 | 6.7375 | 13.3531 | 22.7886 | 9.1183 | 6.6516 | 13.2109 | 22.9038 | 9.0579 | 6.6076 | 13.0724 | 23.2755 | 8.8599 | 6.4631 | 12.5973 | 23.639 | 8.6808 | 6.3325 | 12.051 | 23.8878 | 8.5205 | 6.2156 | 11.685 | 24.1026 | 8.3443 | 6.0871 | 11.333 | 24.2289 | 8.2474 | 6.0163 | 11.1246 | 22.1106 | 11.0319 | 8.0476 | 14.6263 | 22.1307 | 10.6106 | 7.7403 | 13.7628 | 22.1883 | 9.7682 | 7.1258 | 13.5069 | 22.2666 | 9.8742 | 7.2031 | 13.371 | 22.3638 | 9.6077 | 7.0086 | 13.1866 | 22.4743 | 9.3719 | 6.8367 | 13.0038 | 22.6062 | 9.1842 | 6.6997 | 12.7415 | 22.7826 | 8.9716 | 6.5447 | 12.1839 | 22.9288 | 8.7631 | 6.3926 | 11.6146 | 23.0733 | 8.5966 | 6.2711 | 11.0471 | 23.5057 | 8.1509 | 5.946 | 9.3923 | 23.8775 | 7.7483 | 5.6523 | 7.7992 | 24.1435 | 7.3952 | 5.3947 | 6.5366 | 24.342 | 7.0565 | 5.1476 | 5.6493 | 24.4156 | 7.006 | 5.1108 | 5.9113
ST MARYS | GREENHILL | WHITEGATE | 392582 | 405316 | 29.6288 | 11.5751 | 8.4439 | 19.0298 | 29.6922 | 11.3483 | 8.2784 | 17.9035 | 29.7702 | 9.91 | 7.2292 | 16.6556 | 29.8415 | 8.5369 | 6.2275 | 15.9394 | 29.9058 | 7.2164 | 5.2643 | 15.2339 | 29.9756 | 5.8018 | 4.2324 | 14.5274 | 27.2113 | 4.4139 | 3.2199 | 13.8294 | 26.0256 | 4.2216 | 3.0796 | 13.1355 | 24.9412 | 4.0457 | 2.9513 | 12.4488 | 24.7087 | 4.008 | 2.9238 | 12.2259 | 23.7326 | 3.8497 | 2.8083 | 11.388 | 25.9342 | 4.2068 | 3.0688 | 10.3777 | 30.9311 | 5.5618 | 4.0572 | 9.6102 | 31.0751 | 7.4246 | 5.4162 | 8.8462 | 31.195 | 7.729 | 5.6382 | 8.1465 | 29.6255 | 11.5751 | 8.4439 | 19.0298 | 29.7035 | 11.4712 | 8.3681 | 18.5744 | 29.7907 | 10.0989 | 7.367 | 18.0733 | 29.8673 | 8.9096 | 6.4995 | 17.7624 | 29.9485 | 7.6162 | 5.5559 | 17.4648 | 30.039 | 6.3926 | 4.6633 | 17.1634 | 30.1309 | 4.927 | 3.5942 | 16.843 | 29.6471 | 4.809 | 3.5081 | 16.4858 | 28.9993 | 4.704 | 3.4315 | 16.1671 | 28.4518 | 4.6152 | 3.3667 | 15.9321 | 26.8499 | 4.3553 | 3.1771 | 15.2347 | 25.732 | 4.174 | 3.0449 | 14.535 | 30.9341 | 5.0178 | 3.6604 | 13.881 | 31.1786 | 6.3508 | 4.6328 | 13.155 | 31.3696 | 6.4472 | 4.7032 | 12.491 | 29.6302 | 11.5751 | 8.4439 | 19.0298 | 29.7028 | 11.2893 | 8.2354 | 17.6982 | 29.7867 | 9.7934 | 7.1441 | 16.396 | 29.864 | 8.4199 | 6.1422 | 15.6473 | 29.9357 | 7.0157 | 5.1179 | 14.9048 | 30.0138 | 5.5733 | 4.0656 | 14.1565 | 25.5344 | 4.1419 | 3.0215 | 13.4097 | 24.1815 | 3.9225 | 2.8614 | 12.6617 | 22.8625 | 3.7085 | 2.7053 | 11.9454 | 22.346 | 3.6247 | 2.6442 | 11.6911 | 20.4239 | 3.313 | 2.4168 | 10.7427 | 22.0912 | 3.5834 | 2.614 | 9.7109 | 31.056 | 5.0376 | 3.6749 | 8.9938 | 31.2407 | 6.7502 | 4.9242 | 8.3415 | 31.3512 | 7.0222 | 5.1226 | 7.8532 | 29.6302 | 11.5751 | 8.4439 | 19.0298 | 29.6686 | 11.3726 | 8.2962 | 18.0646 | 29.7253 | 11.0337 | 8.0489 | 16.8555 | 29.7777 | 10.8076 | 7.884 | 16.1308 | 29.8343 | 10.5207 | 7.6747 | 15.4092 | 29.9063 | 10.1085 | 7.374 | 14.6755 | 29.9907 | 9.6172 | 7.0156 | 13.9118 | 30.0811 | 9.4297 | 6.8789 | 13.0599 | 30.1643 | 9.1854 | 6.7006 | 12.2251 | 30.2489 | 8.9764 | 6.5482 | 11.8583 | 30.5121 | 8.5032 | 6.203 | 10.7895 | 30.7513 | 8.0358 | 5.862 | 9.8589 | 30.904 | 7.6463 | 5.5779 | 9.2481 | 31.0281 | 7.2449 | 5.285 | 8.8109 | 31.1144 | 6.9301 | 5.0554 | 8.621 | 29.6288 | 11.5751 | 8.4439 | 19.0298 | 29.6901 | 11.4258 | 8.335 | 18.2688 | 29.7612 | 10.0029 | 7.297 | 17.1036 | 29.8241 | 8.6269 | 6.2932 | 16.4062 | 29.882 | 7.3321 | 5.3487 | 15.7351 | 29.9431 | 5.9372 | 4.3311 | 15.0626 | 28.06 | 4.5516 | 3.3203 | 14.3896 | 26.9062 | 4.3644 | 3.1838 | 13.7094 | 25.7934 | 4.1839 | 3.0521 | 13.0207 | 25.5467 | 4.1439 | 3.0229 | 12.788 | 24.843 | 4.0298 | 2.9397 | 12.0615 | 27.6217 | 4.4805 | 3.2685 | 11.3474 | 30.8583 | 5.9189 | 4.3177 | 10.8229 | 31.0179 | 7.8723 | 5.7427 | 10.2731 | 31.1476 | 8.2317 | 6.0049 | 9.8068 | 29.6288 | 11.5751 | 8.4439 | 19.0298 | 29.6844 | 11.2822 | 8.2302 | 17.6074 | 29.7629 | 10.9142 | 7.9618 | 16.2821 | 29.8401 | 10.6777 | 7.7892 | 15.5264 | 29.9118 | 10.3785 | 7.571 | 14.7758 | 29.9868 | 9.9645 | 7.269 | 14.0225 | 30.0698 | 9.4659 | 6.9053 | 13.2408 | 30.1704 | 9.2728 | 6.7644 | 12.3605 | 30.2595 | 9.0237 | 6.5826 | 11.5162 | 30.3459 | 8.8128 | 6.4288 | 11.1411 | 30.6083 | 8.3292 | 6.0761 | 10.0515 | 30.8498 | 7.8546 | 5.7298 | 9.1042 | 31.0202 | 7.4501 | 5.4347 | 8.4731 | 31.1521 | 7.0391 | 5.1349 | 8.0103 | 31.2456 | 6.708 | 4.8934 | 7.772
ST MARYS ST | RIBBLE | PENWORTHAM EAST / ROCHDALE | 354932 | 429640 | 23.8624 | 12.7702 | 9.3157 | 10.2868 | 23.9755 | 12.6332 | 9.2157 | 9.2051 | 24.0715 | 12.3632 | 9.0188 | 8.4313 | 24.1767 | 12.0424 | 8.7848 | 7.8256 | 24.2995 | 11.9774 | 8.7373 | 7.2095 | 24.4297 | 11.9413 | 8.711 | 6.5874 | 24.5706 | 11.7778 | 8.5917 | 5.9669 | 24.7392 | 11.6308 | 8.4845 | 5.4993 | 24.9115 | 11.4627 | 8.3619 | 4.9976 | 25.0846 | 11.3362 | 8.2696 | 4.5062 | 25.5632 | 10.8201 | 7.8931 | 2.6152 | 26.0293 | 10.389 | 7.5786 | 1.1673 | 26.3323 | 9.9432 | 7.2534 | 0.12246 | 26.5602 | 9.695 | 7.0723 | -0.79632 | 26.6597 | 9.3086 | 6.7905 | -1.341 | 23.8519 | 12.7702 | 9.3157 | 10.2868 | 23.9662 | 12.8298 | 9.3591 | 9.8994 | 24.0694 | 12.8782 | 9.3945 | 9.6427 | 24.1778 | 12.8494 | 9.3735 | 9.436 | 24.2673 | 12.7261 | 9.2835 | 9.217 | 24.3695 | 12.6155 | 9.2028 | 8.9927 | 24.494 | 12.381 | 9.0317 | 8.7249 | 24.6412 | 12.2589 | 8.9427 | 8.4596 | 24.7444 | 12.1601 | 8.8706 | 8.2811 | 24.8585 | 12.0566 | 8.7951 | 8.0988 | 25.2366 | 11.7395 | 8.5638 | 7.5489 | 25.5785 | 11.4827 | 8.3765 | 6.9937 | 25.8044 | 11.0606 | 8.0686 | 6.5015 | 26.0163 | 11.1076 | 8.1028 | 5.6573 | 26.1649 | 10.9061 | 7.9558 | 5.0499 | 23.865 | 12.7702 | 9.3157 | 10.2868 | 23.969 | 12.5538 | 9.1579 | 9.0176 | 24.0633 | 12.1272 | 8.8466 | 8.168 | 24.1663 | 12.0148 | 8.7646 | 7.5022 | 24.2835 | 11.9303 | 8.703 | 6.8237 | 24.4173 | 11.7671 | 8.5839 | 6.1351 | 24.548 | 11.5432 | 8.4206 | 5.4418 | 24.7032 | 11.3656 | 8.2911 | 4.8973 | 24.8542 | 11.2049 | 8.1738 | 4.3469 | 25.0181 | 11.0257 | 8.0431 | 3.8048 | 25.5718 | 10.4119 | 7.5954 | 1.8645 | 26.0761 | 9.8618 | 7.1941 | 0.6588 | 26.4148 | 9.5584 | 6.9727 | -0.15693 | 26.6526 | 9.1371 | 6.6654 | -0.69144 | 26.6787 | 8.8767 | 6.4754 | -0.70659 | 23.8651 | 12.7702 | 9.3157 | 10.2868 | 23.933 | 12.6308 | 9.214 | 9.4132 | 24.0054 | 12.4451 | 9.0785 | 8.6612 | 24.0756 | 12.1296 | 8.8484 | 8.0318 | 24.1734 | 12.0627 | 8.7996 | 7.3826 | 24.3007 | 11.9715 | 8.7331 | 6.7118 | 24.4628 | 11.775 | 8.5897 | 5.9718 | 24.6448 | 11.5249 | 8.4072 | 5.197 | 24.8411 | 11.2836 | 8.2312 | 4.3668 | 25.0434 | 11.0608 | 8.0687 | 3.5362 | 25.5669 | 10.325 | 7.5319 | 1.201 | 25.9954 | 9.9484 | 7.2572 | 0.10962 | 26.2551 | 9.5931 | 6.998 | -0.45551 | 26.398 | 9.2832 | 6.772 | -0.48123 | 26.3351 | 9.0922 | 6.6326 | 0.20916 | 23.8619 | 12.7702 | 9.3157 | 10.2868 | 23.9555 | 12.718 | 9.2776 | 9.5597 | 24.0307 | 12.4795 | 9.1036 | 8.8631 | 24.1069 | 12.1922 | 8.894 | 8.2892 | 24.1943 | 12.0439 | 8.7858 | 7.7295 | 24.306 | 12.0699 | 8.8048 | 7.161 | 24.4277 | 11.9189 | 8.6946 | 6.5753 | 24.5591 | 11.7836 | 8.5959 | 6.1247 | 24.6939 | 11.6217 | 8.4778 | 5.6219 | 24.8418 | 11.4801 | 8.3746 | 5.1174 | 25.3224 | 11.0436 | 8.0561 | 3.5822 | 25.726 | 10.7979 | 7.8769 | 2.9747 | 25.9442 | 10.4798 | 7.6449 | 2.566 | 26.1265 | 10.3925 | 7.5812 | 2.2177 | 26.1876 | 10.1483 | 7.4031 | 2.1341 | 23.8619 | 12.7702 | 9.3157 | 10.2868 | 23.9358 | 12.5169 | 9.1309 | 8.98 | 24.0233 | 12.2999 | 8.9726 | 8.117 | 24.1213 | 11.9609 | 8.7253 | 7.4411 | 24.2341 | 11.9365 | 8.7075 | 6.7491 | 24.3649 | 11.8169 | 8.6203 | 6.052 | 24.4988 | 11.6074 | 8.4674 | 5.289 | 24.676 | 11.3508 | 8.2802 | 4.4742 | 24.8491 | 11.1032 | 8.0996 | 3.6104 | 25.0343 | 10.8773 | 7.9348 | 2.7643 | 25.6101 | 10.1143 | 7.3782 | 0.36071 | 26.0875 | 9.7194 | 7.0902 | -0.82476 | 26.4023 | 9.3442 | 6.8165 | -1.4881 | 26.5953 | 9.0096 | 6.5724 | -1.6287 | 26.5923 | 8.7874 | 6.4103 | -1.1398
ST THOMAS RD | LYTHAM | PENWORTHAM WEST / STANAH | 332713 | 428643 | 28.824 | 14.1439 | 10.3178 | 18.6739 | 28.8844 | 13.7578 | 10.0361 | 18.4662 | 28.9648 | 13.5963 | 9.9183 | 18.2042 | 29.0586 | 13.3014 | 9.7032 | 17.8038 | 29.1654 | 12.962 | 9.4556 | 17.3693 | 29.2816 | 12.6243 | 9.2092 | 16.9354 | 29.4089 | 12.4126 | 9.0548 | 16.5374 | 29.5552 | 12.1942 | 8.8955 | 16.1853 | 29.6441 | 12.0285 | 8.7746 | 15.9976 | 29.7272 | 11.9185 | 8.6944 | 15.8365 | 29.9954 | 11.4438 | 8.3481 | 14.5746 | 30.2942 | 10.9027 | 7.9534 | 12.2383 | 30.5133 | 10.4825 | 7.6468 | 10.3899 | 30.7135 | 9.9331 | 7.2461 | 8.4185 | 30.8663 | 9.3639 | 6.8308 | 6.5626 | 28.803 | 14.1439 | 10.3178 | 18.6739 | 28.8922 | 13.8009 | 10.0676 | 18.4324 | 28.9938 | 13.6516 | 9.9586 | 18.137 | 29.1187 | 13.4258 | 9.794 | 17.841 | 29.2645 | 13.1431 | 9.5877 | 17.5235 | 29.4337 | 12.8898 | 9.4029 | 17.2508 | 29.6329 | 12.6607 | 9.2358 | 16.9283 | 29.865 | 12.5122 | 9.1275 | 16.5288 | 29.9152 | 12.4011 | 9.0465 | 16.309 | 29.9667 | 12.2859 | 8.9624 | 16.0913 | 30.1202 | 11.979 | 8.7385 | 15.4646 | 30.2639 | 11.7388 | 8.5633 | 14.8589 | 30.3891 | 11.5069 | 8.3941 | 14.3208 | 30.5173 | 11.2784 | 8.2275 | 13.7199 | 30.6179 | 11.0201 | 8.039 | 13.2568 | 28.8286 | 14.1439 | 10.3178 | 18.6739 | 28.8933 | 13.7394 | 10.0227 | 18.4806 | 28.9804 | 13.5135 | 9.8579 | 18.2313 | 29.0846 | 13.1821 | 9.6162 | 17.8561 | 29.2035 | 12.8194 | 9.3516 | 17.443 | 29.3342 | 12.4726 | 9.0986 | 17.0323 | 29.479 | 12.254 | 8.9391 | 16.6671 | 29.647 | 12.0176 | 8.7667 | 16.35 | 29.7497 | 11.8079 | 8.6137 | 16.2309 | 29.8441 | 11.6533 | 8.5009 | 16.1191 | 30.1447 | 11.1883 | 8.1617 | 15.0144 | 30.4727 | 10.6014 | 7.7336 | 12.8372 | 30.7114 | 10.0631 | 7.3409 | 11.1455 | 30.9254 | 9.3794 | 6.8421 | 9.3786 | 31.0836 | 8.8018 | 6.4208 | 7.7746 | 28.8286 | 14.1439 | 10.3178 | 18.6739 | 28.8452 | 13.7738 | 10.0478 | 18.594 | 28.8858 | 13.6104 | 9.9286 | 18.4009 | 28.9369 | 13.2821 | 9.6891 | 18.0569 | 29.0042 | 12.9547 | 9.4503 | 17.6673 | 29.0991 | 12.6516 | 9.2291 | 17.269 | 29.2148 | 12.4062 | 9.0501 | 16.7768 | 29.3525 | 12.0907 | 8.82 | 15.8762 | 29.4599 | 11.7906 | 8.6011 | 15.102 | 29.5624 | 11.4523 | 8.3543 | 14.3249 | 29.869 | 10.9495 | 7.9875 | 12.1059 | 30.1871 | 10.3403 | 7.5431 | 10.0085 | 30.4169 | 9.7937 | 7.1443 | 8.4351 | 30.6019 | 9.2634 | 6.7575 | 7.4789 | 30.652 | 9.0828 | 6.6258 | 8.2084 | 28.824 | 14.1439 | 10.3178 | 18.6739 | 28.879 | 13.7854 | 10.0563 | 18.4885 | 28.9438 | 13.6375 | 9.9484 | 18.2463 | 29.0137 | 13.3541 | 9.7416 | 17.8816 | 29.0955 | 13.0201 | 9.498 | 17.5198 | 29.2004 | 12.702 | 9.2659 | 17.1961 | 29.3252 | 12.5129 | 9.128 | 16.9092 | 29.4588 | 12.3028 | 8.9747 | 16.6195 | 29.5374 | 12.1327 | 8.8506 | 16.4429 | 29.6143 | 12.0185 | 8.7673 | 16.2705 | 29.8518 | 11.6406 | 8.4916 | 15.7189 | 30.1008 | 11.4766 | 8.372 | 15.1131 | 30.2847 | 11.3165 | 8.2552 | 14.7382 | 30.4554 | 11.05 | 8.0608 | 14.3665 | 30.5615 | 10.8072 | 7.8837 | 14.1996 | 28.824 | 14.1439 | 10.3178 | 18.6739 | 28.8702 | 13.7463 | 10.0278 | 18.5432 | 28.9488 | 13.5558 | 9.8888 | 18.2871 | 29.0436 | 13.2181 | 9.6424 | 17.8734 | 29.1515 | 12.8821 | 9.3973 | 17.4164 | 29.2683 | 12.5656 | 9.1664 | 16.9623 | 29.4013 | 12.3061 | 8.9771 | 16.4068 | 29.5728 | 11.9793 | 8.7387 | 15.4256 | 29.688 | 11.6802 | 8.5205 | 14.6163 | 29.7965 | 11.3677 | 8.2926 | 13.8038 | 30.1039 | 10.7906 | 7.8716 | 11.477 | 30.3922 | 10.1538 | 7.407 | 9.2796 | 30.6 | 9.5811 | 6.9893 | 7.5966 | 30.7599 | 9.0171 | 6.5779 | 6.485 | 30.8096 | 8.8054 | 6.4234 | 7.0216
STAINBURN | STAINBURN & SIDDICK | HARKER / HUTTON | 302535 | 529330 | 14.0994 | 14.0994 | 12.38 | 11.8204 | 14.212 | 14.212 | 12.3161 | 11.4911 | 14.3909 | 14.3909 | 11.2505 | 11.2794 | 14.6246 | 14.2683 | 10.2549 | 11.119 | 14.7501 | 12.8314 | 9.2222 | 10.9397 | 14.8861 | 11.3666 | 8.1694 | 10.7611 | 15.0303 | 9.9617 | 7.1597 | 10.6017 | 15.2004 | 9.8801 | 7.101 | 10.4351 | 15.34 | 9.8072 | 7.0487 | 10.2394 | 15.4743 | 9.7806 | 7.0295 | 9.9893 | 15.8833 | 9.597 | 6.8975 | 8.8664 | 16.2887 | 9.4933 | 6.823 | 7.2385 | 16.5756 | 9.982 | 7.1742 | 5.9713 | 16.8095 | 15.1986 | 10.9236 | 4.7563 | 16.9268 | 14.9508 | 10.7455 | 3.8264 | 14.0702 | 14.0702 | 12.38 | 11.8204 | 14.1263 | 14.1263 | 12.3519 | 11.7567 | 14.1824 | 14.1824 | 11.3823 | 11.6561 | 14.2603 | 14.2603 | 10.3916 | 11.5712 | 14.371 | 13.051 | 9.38 | 11.4823 | 14.5067 | 11.6366 | 8.3634 | 11.3839 | 14.6645 | 10.2234 | 7.3478 | 11.263 | 14.8154 | 10.1984 | 7.3298 | 11.0748 | 14.8942 | 10.1364 | 7.2852 | 10.7965 | 14.9758 | 10.0576 | 7.2286 | 10.509 | 15.2254 | 9.8352 | 7.0687 | 9.6853 | 15.4643 | 9.622 | 6.9155 | 8.9601 | 15.6818 | 9.544 | 6.8595 | 8.334 | 15.9156 | 12.4984 | 8.9828 | 7.7091 | 16.0489 | 15.6592 | 11.2546 | 7.3813 | 14.1132 | 14.1132 | 12.38 | 11.8204 | 14.2409 | 14.2409 | 12.2957 | 11.4477 | 14.4458 | 14.4458 | 11.2404 | 11.2286 | 14.6563 | 14.182 | 10.1929 | 11.0677 | 14.7948 | 12.6988 | 9.1269 | 10.8887 | 14.9485 | 11.2677 | 8.0983 | 10.7108 | 15.1128 | 9.841 | 7.0729 | 10.5522 | 15.3091 | 9.7564 | 7.0121 | 10.387 | 15.4641 | 9.6642 | 6.9458 | 10.2152 | 15.6122 | 9.6184 | 6.913 | 10.0624 | 16.066 | 9.4458 | 6.7889 | 9.2614 | 16.5201 | 9.4055 | 6.7599 | 7.7361 | 16.7782 | 9.8294 | 7.0646 | 6.5745 | 16.9776 | 14.9858 | 10.7706 | 5.5063 | 17.0902 | 14.7073 | 10.5705 | 4.6577 | 14.1132 | 14.1132 | 12.38 | 11.8204 | 14.19 | 14.19 | 12.3092 | 11.5867 | 14.3161 | 14.3161 | 12.2312 | 11.4281 | 14.4892 | 14.4892 | 12.1017 | 11.3004 | 14.6817 | 14.6817 | 12.0062 | 11.1244 | 14.8055 | 14.8055 | 11.9281 | 10.9457 | 14.9566 | 14.9566 | 11.7471 | 10.7147 | 15.1321 | 15.1321 | 11.7155 | 10.3031 | 15.276 | 15.276 | 11.6362 | 9.8823 | 15.4166 | 15.4166 | 11.5632 | 9.4709 | 15.8467 | 15.8254 | 11.374 | 7.9677 | 16.2863 | 15.455 | 11.1078 | 6.5157 | 16.5745 | 15.1271 | 10.8721 | 5.4378 | 16.7547 | 14.8526 | 10.6749 | 4.8001 | 16.7896 | 14.807 | 10.6421 | 5.2737 | 14.0994 | 14.0994 | 12.38 | 11.8204 | 14.1948 | 14.1948 | 12.3433 | 11.7245 | 14.3236 | 14.3236 | 11.2689 | 11.5817 | 14.4763 | 14.3609 | 10.3215 | 11.4718 | 14.6457 | 12.9254 | 9.2897 | 11.371 | 14.7601 | 11.464 | 8.2394 | 11.245 | 14.9004 | 10.0636 | 7.2329 | 11.1033 | 15.054 | 9.9858 | 7.177 | 10.9498 | 15.1831 | 9.9104 | 7.1228 | 10.7541 | 15.3117 | 9.894 | 7.111 | 10.5604 | 15.7108 | 9.759 | 7.014 | 9.7165 | 16.111 | 9.7769 | 7.0268 | 8.8181 | 16.4003 | 10.3905 | 7.4679 | 8.2163 | 16.6487 | 15.7129 | 11.2931 | 7.7125 | 16.7321 | 15.6423 | 11.2424 | 7.5945 | 14.0994 | 14.0994 | 12.38 | 11.8204 | 14.2046 | 14.2046 | 12.2883 | 11.4272 | 14.3847 | 14.3847 | 12.1904 | 11.1972 | 14.6271 | 14.6271 | 12.0594 | 11.0114 | 14.7817 | 14.7817 | 11.959 | 10.7865 | 14.9114 | 14.9114 | 11.881 | 10.5936 | 15.0541 | 15.0541 | 11.6976 | 10.3554 | 15.2409 | 15.2409 | 11.6615 | 9.9077 | 15.3954 | 15.3954 | 11.5633 | 9.3238 | 15.544 | 15.544 | 11.4711 | 8.7411 | 15.9786 | 15.667 | 11.2602 | 7.0796 | 16.3827 | 15.2795 | 10.9817 | 5.5305 | 16.6658 | 14.9325 | 10.7323 | 4.3673 | 16.8205 | 14.6411 | 10.5228 | 3.6469 | 16.852 | 14.5756 | 10.4758 | 4.0084
STANDISH | WRIGHTINGTON | PENWORTHAM WEST / STANAH | 356139 | 410059 | 13.7002 | 12.9659 | 9.3188 | 12.394 | 13.8497 | 12.8533 | 9.2379 | 11.918 | 14.0033 | 11.5996 | 8.3369 | 11.6712 | 14.2013 | 10.4067 | 7.4795 | 11.4467 | 14.4506 | 8.8769 | 6.38 | 11.1192 | 14.7457 | 8.1538 | 5.8603 | 10.7802 | 15.0984 | 7.0403 | 5.06 | 10.4546 | 15.4254 | 6.8874 | 4.9501 | 10.1244 | 15.6967 | 6.7319 | 4.8383 | 9.6699 | 15.9685 | 6.5714 | 4.723 | 9.1095 | 16.7916 | 5.9423 | 4.2708 | 6.4322 | 17.673 | 5.1689 | 3.715 | 2.4221 | 18.3026 | 4.5678 | 3.283 | -0.77725 | 18.8126 | 6.1002 | 4.3843 | -4.1209 | 19.1692 | 7.7472 | 5.568 | -7.3339 | 13.636 | 12.9659 | 9.3188 | 12.394 | 13.7457 | 12.9186 | 9.2848 | 12.1307 | 13.8477 | 11.9945 | 8.6207 | 11.9764 | 13.9667 | 11.0374 | 7.9328 | 11.8196 | 14.1095 | 10.0461 | 7.2203 | 11.5821 | 14.2936 | 9.0334 | 6.4925 | 11.3055 | 14.5179 | 8.028 | 5.7699 | 10.9193 | 14.7785 | 7.8257 | 5.6245 | 10.3707 | 14.9618 | 7.713 | 5.5435 | 9.8565 | 15.1578 | 7.5584 | 5.4324 | 9.3364 | 15.8074 | 7.1095 | 5.1098 | 7.73 | 16.4447 | 6.6026 | 4.7454 | 5.8579 | 16.9847 | 6.1033 | 4.3865 | 4.1297 | 17.5474 | 7.7035 | 5.5366 | 2.3306 | 17.9325 | 9.2698 | 6.6624 | 1.2006 | 13.7298 | 12.9659 | 9.3188 | 12.394 | 13.8759 | 12.8212 | 9.2149 | 11.9029 | 14.0506 | 11.5232 | 8.282 | 11.6844 | 14.279 | 10.2403 | 7.3599 | 11.528 | 14.5652 | 8.9808 | 6.4547 | 11.1494 | 14.9026 | 8.0279 | 5.7698 | 10.7732 | 15.2321 | 6.8579 | 4.9289 | 10.4437 | 15.555 | 6.669 | 4.7931 | 10.1228 | 15.8028 | 6.4794 | 4.6569 | 9.5936 | 16.0388 | 6.2967 | 4.5256 | 9.017 | 16.8803 | 5.5878 | 4.0161 | 6.5553 | 17.8182 | 4.7473 | 3.412 | 2.7085 | 18.4655 | 4.1705 | 2.9974 | -0.36427 | 19.0295 | 5.6629 | 4.0701 | -3.5461 | 19.3902 | 7.3256 | 5.2651 | -6.2425 | 13.7298 | 12.9659 | 9.3188 | 12.394 | 13.745 | 12.9082 | 9.2774 | 12.4154 | 13.8234 | 12.5303 | 9.0058 | 12.3075 | 13.9398 | 12.0408 | 8.654 | 12.1891 | 14.1252 | 11.7544 | 8.4482 | 11.8169 | 14.4195 | 11.6586 | 8.3792 | 11.4008 | 14.8016 | 11.3397 | 8.15 | 10.8049 | 15.1717 | 10.9963 | 7.9032 | 9.5491 | 15.455 | 10.6803 | 7.6762 | 8.2028 | 15.7456 | 10.3807 | 7.4608 | 6.8564 | 16.6467 | 9.6221 | 6.9156 | 3.2165 | 17.5232 | 9.0545 | 6.5076 | -0.37311 | 18.1274 | 8.8902 | 6.3896 | -3.2105 | 18.5766 | 12.0817 | 8.6833 | -5.2239 | 18.6545 | 11.9255 | 8.5711 | -4.6068 | 13.7002 | 12.9659 | 9.3188 | 12.394 | 13.833 | 12.8906 | 9.2647 | 12.0928 | 13.936 | 11.6574 | 8.3784 | 11.9316 | 14.0547 | 10.4901 | 7.5394 | 11.8181 | 14.2187 | 8.9866 | 6.4589 | 11.6499 | 14.478 | 8.2817 | 5.9522 | 11.4242 | 14.8242 | 7.1959 | 5.1719 | 11.1654 | 15.1944 | 7.0529 | 5.069 | 10.8985 | 15.4246 | 6.9035 | 4.9617 | 10.4953 | 15.6629 | 6.7591 | 4.8579 | 10.077 | 16.4201 | 6.2762 | 4.5108 | 8.3048 | 17.1597 | 5.8108 | 4.1763 | 6.3034 | 17.6869 | 5.4619 | 3.9256 | 4.925 | 18.1301 | 7.3586 | 5.2887 | 3.672 | 18.3704 | 9.3849 | 6.7451 | 2.8508 | 13.7002 | 12.9659 | 9.3188 | 12.394 | 13.7704 | 12.8672 | 9.2479 | 12.2048 | 13.9117 | 12.4652 | 8.959 | 11.9434 | 14.1047 | 11.958 | 8.5944 | 11.6867 | 14.3509 | 11.6359 | 8.3629 | 11.1914 | 14.6368 | 11.5212 | 8.2805 | 10.6987 | 14.9841 | 11.1939 | 8.0452 | 10.0097 | 15.3355 | 10.8301 | 7.7838 | 8.6208 | 15.6221 | 10.5018 | 7.5479 | 7.172 | 15.9125 | 10.1815 | 7.3177 | 5.7242 | 16.8135 | 9.3895 | 6.7484 | 1.7647 | 17.6772 | 8.7483 | 6.2875 | -2.1106 | 18.286 | 8.5504 | 6.1454 | -5.215 | 18.72 | 11.6874 | 8.4 | -7.5227 | 18.8731 | 11.485 | 8.2545 | -7.2192
STRANGEWAYS | FREDERICK RD | KEARSLEY | 383780 | 399743 | 33.6435 | 10.0711 | 7.3467 | 15.5928 | 33.7158 | 9.5699 | 6.9811 | 12.3975 | 33.8261 | 9.4045 | 6.8605 | 11.396 | 33.9405 | 9.3117 | 6.7927 | 11.1425 | 34.0631 | 9.2007 | 6.7118 | 10.8699 | 34.2023 | 9.0298 | 6.5871 | 10.5877 | 34.3616 | 8.9242 | 6.5101 | 10.3248 | 34.5515 | 8.7855 | 6.4089 | 10.0657 | 34.7155 | 8.6511 | 6.3108 | 9.7581 | 34.8802 | 8.5323 | 6.2242 | 9.4593 | 35.3803 | 8.0804 | 5.8946 | 8.1227 | 35.8229 | 7.6368 | 5.571 | 6.3044 | 36.0729 | 7.2494 | 5.2883 | 4.9314 | 36.2729 | 6.8747 | 5.015 | 3.658 | 36.3976 | 6.4936 | 4.737 | 2.6693 | 33.6355 | 10.0711 | 7.3467 | 15.5928 | 33.7257 | 9.9451 | 7.2548 | 14.6998 | 33.8481 | 9.8463 | 7.1828 | 14.2667 | 33.9773 | 9.7413 | 7.1061 | 13.991 | 34.1228 | 9.6344 | 7.0281 | 13.7135 | 34.2967 | 9.5301 | 6.9521 | 13.4116 | 34.4889 | 9.1982 | 6.71 | 13.0606 | 34.6478 | 9.0719 | 6.6179 | 12.6477 | 34.7643 | 8.962 | 6.5376 | 12.3433 | 34.8879 | 8.8575 | 6.4615 | 12.0333 | 35.2624 | 8.5633 | 6.2468 | 11.1389 | 35.5933 | 8.325 | 6.0729 | 10.2742 | 35.8935 | 8.1348 | 5.9342 | 9.5455 | 36.2056 | 7.9719 | 5.8154 | 8.7788 | 36.4469 | 7.7403 | 5.6464 | 8.1077 | 33.6468 | 10.0711 | 7.3467 | 15.5928 | 33.7332 | 9.4785 | 6.9144 | 11.8699 | 33.86 | 9.2692 | 6.7618 | 10.7323 | 33.9952 | 9.1355 | 6.6642 | 10.4205 | 34.1411 | 8.9561 | 6.5334 | 10.0909 | 34.3062 | 8.8092 | 6.4262 | 9.7527 | 34.4944 | 8.628 | 6.294 | 9.4247 | 34.7164 | 8.4667 | 6.1764 | 9.1058 | 34.8963 | 8.2868 | 6.0451 | 8.7635 | 35.0764 | 8.1228 | 5.9255 | 8.4283 | 35.6189 | 7.6046 | 5.5474 | 7.012 | 36.0421 | 7.0042 | 5.1094 | 5.2455 | 36.3253 | 6.659 | 4.8576 | 4.0522 | 36.541 | 6.2494 | 4.5589 | 3.1087 | 36.3473 | 5.8959 | 4.301 | 2.6719 | 33.6468 | 10.0711 | 7.3467 | 15.5928 | 33.6736 | 9.6849 | 7.065 | 12.9916 | 33.7535 | 9.5967 | 7.0007 | 12.1075 | 33.8358 | 9.4855 | 6.9195 | 11.8492 | 33.9313 | 9.3656 | 6.8321 | 11.5558 | 34.0625 | 9.2275 | 6.7313 | 11.2433 | 34.2231 | 9.0041 | 6.5684 | 10.8539 | 34.4099 | 8.7614 | 6.3913 | 10.2146 | 34.5861 | 8.5368 | 6.2275 | 9.5353 | 34.7647 | 8.3071 | 6.0599 | 8.8848 | 35.3072 | 7.7476 | 5.6517 | 7.1054 | 35.6944 | 7.1967 | 5.2499 | 5.5602 | 35.9422 | 6.7495 | 4.9236 | 4.6226 | 36.1243 | 6.3845 | 4.6574 | 4.2002 | 36.1969 | 6.2403 | 4.5522 | 4.5064 | 33.6435 | 10.0711 | 7.3467 | 15.5928 | 33.7111 | 9.8339 | 7.1737 | 13.9252 | 33.8056 | 9.7335 | 7.1004 | 13.2349 | 33.8944 | 9.6566 | 7.0443 | 13.025 | 33.9887 | 9.5657 | 6.9781 | 12.8379 | 34.114 | 9.4096 | 6.8641 | 12.6357 | 34.2686 | 9.3154 | 6.7954 | 12.4195 | 34.4417 | 9.1815 | 6.6978 | 12.168 | 34.5887 | 9.044 | 6.5974 | 11.8303 | 34.7404 | 8.9218 | 6.5083 | 11.4857 | 35.2191 | 8.5287 | 6.2216 | 10.417 | 35.6838 | 8.2362 | 6.0082 | 9.3736 | 35.9594 | 7.9903 | 5.8288 | 8.6542 | 36.1742 | 7.7305 | 5.6393 | 7.9775 | 36.2958 | 7.4603 | 5.4422 | 7.6063 | 33.6435 | 10.0711 | 7.3467 | 15.5928 | 33.6975 | 9.4223 | 6.8734 | 11.5262 | 33.8138 | 9.2589 | 6.7542 | 10.3003 | 33.9382 | 9.1208 | 6.6535 | 9.968 | 34.0722 | 8.9917 | 6.5594 | 9.61 | 34.2218 | 8.8418 | 6.45 | 9.2472 | 34.3934 | 8.6105 | 6.2812 | 8.8065 | 34.6062 | 8.3615 | 6.0996 | 8.0949 | 34.7832 | 8.1077 | 5.9144 | 7.3853 | 34.9609 | 7.8822 | 5.7499 | 6.7062 | 35.5031 | 7.2845 | 5.314 | 4.7842 | 35.9175 | 6.71 | 4.8949 | 3.1517 | 36.1756 | 6.241 | 4.5527 | 2.1259 | 35.906 | 5.8243 | 4.2488 | 1.6072 | 34.9297 | 5.6659 | 4.1332 | 1.795
STRAWBERRY BANK | HUNCOAT | PADIHAM | 376338 | 429396 | 19.8953 | 4.3984 | 3.2086 | 17.914 | 20.0084 | 3.6898 | 2.6917 | 13.8244 | 19.0242 | 3.0859 | 2.2511 | 12.3626 | 18.1954 | 2.9515 | 2.1531 | 11.6292 | 16.3093 | 2.6455 | 1.9299 | 10.8702 | 14.4461 | 2.3433 | 1.7094 | 10.1011 | 12.8254 | 2.0804 | 1.5176 | 9.3349 | 11.6379 | 1.8878 | 1.3771 | 8.5587 | 11.1363 | 1.8064 | 1.3178 | 8.3482 | 11.1093 | 1.802 | 1.3146 | 8.146 | 10.3956 | 1.6863 | 1.2301 | 6.9705 | 12.9138 | 2.0947 | 1.5281 | 4.8807 | 23.0094 | 3.8857 | 2.8346 | 2.9027 | 23.4332 | 6.089 | 4.4419 | 0.94414 | 23.7445 | 6.4855 | 4.7311 | -0.64005 | 19.9075 | 4.3984 | 3.2086 | 17.914 | 20.0128 | 4.1614 | 3.0357 | 16.6131 | 20.1126 | 3.9704 | 2.8963 | 16.2828 | 20.2509 | 3.8247 | 2.79 | 16.2016 | 20.4489 | 3.6671 | 2.6751 | 16.1219 | 20.6979 | 3.5074 | 2.5586 | 16.0075 | 20.3943 | 3.3082 | 2.4133 | 15.8295 | 19.7749 | 3.2077 | 2.34 | 15.6072 | 19.241 | 3.1211 | 2.2768 | 15.4152 | 18.6218 | 3.0206 | 2.2035 | 15.1503 | 16.6062 | 2.6937 | 1.965 | 14.2554 | 15.3562 | 2.4909 | 1.8171 | 13.3555 | 22.1392 | 3.6567 | 2.6675 | 12.4589 | 22.4741 | 5.5195 | 4.0264 | 11.643 | 22.6947 | 5.9039 | 4.3068 | 11.1532 | 19.8903 | 4.3984 | 3.2086 | 17.914 | 19.9994 | 3.5487 | 2.5887 | 13.1519 | 18.3408 | 2.9751 | 2.1703 | 11.5745 | 16.8736 | 2.7371 | 1.9966 | 10.8416 | 14.9415 | 2.4237 | 1.768 | 10.0858 | 12.7739 | 2.0721 | 1.5115 | 9.3218 | 11.3615 | 1.8429 | 1.3444 | 8.5617 | 9.9656 | 1.6165 | 1.1792 | 7.7158 | 9.3911 | 1.5233 | 1.1112 | 7.5537 | 9.2575 | 1.5017 | 1.0954 | 7.4028 | 7.7937 | 1.2642 | 0.92223 | 6.3614 | 10.942 | 1.7749 | 1.2948 | 4.5842 | 21.8641 | 3.5466 | 2.5872 | 3.1394 | 23.433 | 5.7004 | 4.1584 | 1.398 | 23.7159 | 6.0713 | 4.4289 | 0.088655 | 19.8903 | 4.3984 | 3.2086 | 17.914 | 19.8948 | 3.7934 | 2.7672 | 14.6293 | 19.95 | 3.345 | 2.4401 | 13.3437 | 20.1206 | 3.2934 | 2.4025 | 12.5579 | 19.0605 | 3.0918 | 2.2554 | 11.8389 | 17.8278 | 2.8918 | 2.1096 | 11.0848 | 16.3902 | 2.6586 | 1.9394 | 10.2183 | 17.5189 | 2.8417 | 2.073 | 9.0178 | 18.1082 | 2.9373 | 2.1427 | 8.4054 | 19.8722 | 3.2235 | 2.3515 | 7.8034 | 22.0794 | 8.1997 | 5.9816 | 5.7403 | 22.6847 | 7.6151 | 5.5551 | 3.7456 | 23.1185 | 7.0455 | 5.1396 | 2.1693 | 23.4184 | 6.5894 | 4.8069 | 1.2195 | 23.3712 | 6.5252 | 4.7601 | 2.1118 | 19.8953 | 4.3984 | 3.2086 | 17.914 | 19.9894 | 3.9497 | 2.8813 | 15.3829 | 20.084 | 3.3957 | 2.4771 | 14.2196 | 20.153 | 3.269 | 2.3847 | 13.5385 | 18.4127 | 2.9867 | 2.1788 | 12.8679 | 16.6139 | 2.6949 | 1.9659 | 12.1679 | 15.0413 | 2.4398 | 1.7798 | 11.4368 | 13.8845 | 2.2522 | 1.6429 | 10.6885 | 13.3963 | 2.173 | 1.5852 | 10.4911 | 13.365 | 2.1679 | 1.5815 | 10.2891 | 13.2767 | 2.1536 | 1.571 | 9.5697 | 17.1553 | 2.7828 | 2.03 | 8.624 | 22.382 | 4.8945 | 3.5705 | 7.9085 | 22.6209 | 7.4036 | 5.4008 | 7.4322 | 22.7208 | 8.1714 | 5.9609 | 7.3375 | 19.8953 | 4.3984 | 3.2086 | 17.914 | 19.9577 | 3.4623 | 2.5257 | 12.584 | 18.2001 | 2.9522 | 2.1536 | 10.9004 | 17.7417 | 2.8779 | 2.0994 | 10.0584 | 16.4239 | 2.6641 | 1.9434 | 9.2919 | 15.174 | 2.4614 | 1.7955 | 8.5208 | 13.7128 | 2.2244 | 1.6226 | 7.6447 | 14.7795 | 2.3974 | 1.7489 | 6.4096 | 15.353 | 2.4904 | 1.8167 | 5.7736 | 16.8754 | 2.7374 | 1.9969 | 5.0777 | 22.2094 | 7.6828 | 5.6045 | 2.8319 | 22.8443 | 7.0625 | 5.152 | 0.67788 | 23.3151 | 6.4448 | 4.7014 | -1.0667 | 23.6402 | 5.9561 | 4.3449 | -2.2228 | 23.6214 | 5.8442 | 4.2633 | -1.554
STUART ST | STUART ST | STALYBRIDGE | 387190 | 398835 | 30.6913 | 10.7343 | 7.8305 | 17.4389 | 30.7722 | 10.0523 | 7.333 | 14.1489 | 30.8742 | 9.889 | 7.2139 | 13.3697 | 30.9916 | 9.8546 | 7.1888 | 13.2322 | 31.1201 | 9.7025 | 7.0778 | 13.018 | 31.252 | 9.5456 | 6.9634 | 12.7803 | 31.4175 | 9.419 | 6.8711 | 12.5507 | 31.5891 | 9.3365 | 6.8108 | 12.3447 | 31.769 | 9.2446 | 6.7438 | 12.1033 | 31.9567 | 9.1521 | 6.6763 | 11.8629 | 32.6104 | 8.778 | 6.4034 | 10.541 | 33.1219 | 8.3618 | 6.0998 | 8.7647 | 33.3891 | 8.0602 | 5.8798 | 7.4289 | 33.5908 | 7.8803 | 5.7486 | 6.325 | 33.6881 | 7.6819 | 5.6039 | 5.5526 | 30.6793 | 10.7343 | 7.8305 | 17.4389 | 30.7358 | 10.5876 | 7.7235 | 16.6641 | 30.8023 | 10.4601 | 7.6305 | 16.4219 | 30.872 | 10.3578 | 7.5558 | 16.3338 | 30.9532 | 10.2279 | 7.4611 | 16.235 | 31.0167 | 10.1141 | 7.3781 | 16.1285 | 31.0959 | 9.8816 | 7.2085 | 15.9901 | 31.1899 | 9.7953 | 7.1455 | 15.8194 | 31.2991 | 9.6798 | 7.0613 | 15.6325 | 31.4218 | 9.6192 | 7.0171 | 15.4316 | 31.8145 | 9.5346 | 6.9554 | 14.7484 | 32.2369 | 9.4238 | 6.8745 | 13.9918 | 32.6505 | 9.3025 | 6.786 | 13.2908 | 33.0802 | 9.2005 | 6.7117 | 12.5806 | 33.3682 | 9.088 | 6.6296 | 12.0854 | 30.6957 | 10.7343 | 7.8305 | 17.4389 | 30.7797 | 9.9002 | 7.2221 | 13.5687 | 30.8909 | 9.7645 | 7.1231 | 12.6217 | 31.0199 | 9.6741 | 7.0571 | 12.4261 | 31.1737 | 9.4996 | 6.9298 | 12.1495 | 31.3414 | 9.3219 | 6.8002 | 11.8484 | 31.5201 | 9.18 | 6.6966 | 11.583 | 31.7004 | 9.0729 | 6.6185 | 11.3313 | 31.8782 | 8.9591 | 6.5355 | 11.0674 | 32.0692 | 8.8487 | 6.455 | 10.7745 | 32.7876 | 8.4067 | 6.1325 | 9.3042 | 33.2217 | 7.9537 | 5.8021 | 7.4849 | 33.4852 | 7.681 | 5.6032 | 6.2975 | 33.6498 | 7.5223 | 5.4874 | 5.4985 | 33.6628 | 7.4108 | 5.4061 | 5.2941 | 30.6958 | 10.7343 | 7.8305 | 17.4389 | 30.7309 | 10.1674 | 7.417 | 14.8022 | 30.8107 | 10.1131 | 7.3774 | 14.1105 | 30.9053 | 10.0782 | 7.3519 | 13.9245 | 31.0322 | 9.9259 | 7.2408 | 13.6434 | 31.2157 | 9.7794 | 7.1339 | 13.3294 | 31.4296 | 9.6301 | 7.025 | 12.9558 | 31.6673 | 9.4256 | 6.8759 | 12.2973 | 31.9171 | 9.2151 | 6.7223 | 11.6139 | 32.1801 | 9.0245 | 6.5833 | 10.9382 | 32.7464 | 8.6212 | 6.2891 | 9.0614 | 33.11 | 8.2041 | 5.9848 | 7.5788 | 33.3179 | 7.8941 | 5.7586 | 6.7388 | 33.4113 | 7.7233 | 5.634 | 6.573 | 33.3417 | 7.6983 | 5.6158 | 7.1152 | 30.6912 | 10.7343 | 7.8305 | 17.4389 | 30.7572 | 10.416 | 7.5983 | 15.9497 | 30.8342 | 10.2668 | 7.4895 | 15.5532 | 30.9122 | 10.2671 | 7.4897 | 15.4672 | 31.0076 | 10.1528 | 7.4063 | 15.3726 | 31.1355 | 10.0156 | 7.3062 | 15.2587 | 31.276 | 9.904 | 7.2249 | 15.1185 | 31.4133 | 9.8311 | 7.1717 | 14.9442 | 31.5652 | 9.7389 | 7.1044 | 14.6978 | 31.7297 | 9.6434 | 7.0347 | 14.4329 | 32.2931 | 9.3404 | 6.8137 | 13.4354 | 32.8318 | 9.086 | 6.6281 | 12.4762 | 33.1413 | 8.9181 | 6.5056 | 11.8307 | 33.3167 | 8.8662 | 6.4678 | 11.2997 | 33.3743 | 8.788 | 6.4107 | 11.094 | 30.6912 | 10.7343 | 7.8305 | 17.4389 | 30.7324 | 9.8117 | 7.1575 | 13.2012 | 30.8301 | 9.76 | 7.1198 | 12.1551 | 30.9458 | 9.6865 | 7.0662 | 11.9317 | 31.0849 | 9.5262 | 6.9492 | 11.6177 | 31.2513 | 9.3763 | 6.8399 | 11.2841 | 31.4207 | 9.2195 | 6.7255 | 10.8845 | 31.6381 | 9.0074 | 6.5708 | 10.1948 | 31.8651 | 8.7958 | 6.4164 | 9.5139 | 32.1078 | 8.6045 | 6.2769 | 8.8207 | 32.8487 | 8.1818 | 5.9685 | 6.8388 | 33.2394 | 7.7474 | 5.6517 | 5.2304 | 33.477 | 7.412 | 5.407 | 4.2607 | 33.5898 | 7.2154 | 5.2635 | 3.9561 | 33.5438 | 7.1682 | 5.2291 | 4.3819
STUBBINS | ROSSENDALE | PADIHAM | 379112 | 418005 | 43.5491 | 12.0344 | 8.6494 | 29.1296 | 43.5647 | 11.8367 | 8.5073 | 28.7379 | 43.6066 | 10.3427 | 7.4335 | 28.5315 | 43.6427 | 8.6379 | 6.2082 | 28.4937 | 42.3083 | 6.9657 | 5.0064 | 28.4975 | 30.2755 | 4.9846 | 3.5826 | 28.4989 | 15.362 | 2.5292 | 1.8178 | 15.362 | 14.2453 | 2.3454 | 1.6857 | 14.2453 | 13.7436 | 2.2628 | 1.6263 | 13.7436 | 13.7669 | 2.2666 | 1.6291 | 13.7669 | 13.3229 | 2.1935 | 1.5765 | 13.3229 | 17.1025 | 2.8158 | 2.0238 | 17.1025 | 29.7311 | 4.895 | 3.5181 | 23.2038 | 45.1416 | 7.4322 | 5.3417 | 22.463 | 47.2955 | 8.0824 | 5.809 | 22.0907 | 43.5377 | 12.0344 | 8.6494 | 29.1296 | 43.5549 | 11.9569 | 8.5936 | 28.9853 | 43.5943 | 10.2732 | 7.3836 | 28.7979 | 43.6212 | 8.6912 | 6.2466 | 28.7137 | 43.3035 | 7.1296 | 5.1242 | 28.6799 | 33.5856 | 5.5296 | 3.9742 | 28.6477 | 22.5476 | 3.7123 | 2.6681 | 22.5476 | 22.1042 | 3.6393 | 2.6156 | 22.1042 | 21.5624 | 3.5501 | 2.5515 | 21.5624 | 20.8919 | 3.4397 | 2.4722 | 20.8919 | 20.0738 | 3.305 | 2.3754 | 20.0738 | 19.5626 | 3.2208 | 2.3149 | 19.5626 | 27.0449 | 4.4527 | 3.2003 | 26.5693 | 39.0683 | 6.4323 | 4.623 | 26.1003 | 39.2822 | 6.4675 | 4.6483 | 23.706 | 43.5504 | 12.0344 | 8.6494 | 29.1296 | 43.5676 | 11.807 | 8.4859 | 28.6967 | 43.611 | 10.3267 | 7.422 | 28.4891 | 43.6494 | 8.49 | 6.102 | 28.4854 | 41.3158 | 6.8023 | 4.889 | 28.5085 | 28.9652 | 4.7689 | 3.4275 | 28.4934 | 14.4895 | 2.3856 | 1.7146 | 14.4895 | 13.3204 | 2.1931 | 1.5762 | 13.3204 | 12.719 | 2.0941 | 1.5051 | 12.719 | 12.6732 | 2.0865 | 1.4996 | 12.6732 | 7.4587 | 1.228 | 0.8826 | 7.4587 | 11.2786 | 1.8569 | 1.3346 | 11.2786 | 24.17 | 3.9794 | 2.8601 | 19.879 | 40.4676 | 6.6627 | 4.7886 | 19.8513 | 44.8238 | 7.3799 | 5.3041 | 20.1028 | 43.5504 | 12.0344 | 8.6494 | 29.1296 | 43.5363 | 11.8164 | 8.4927 | 28.9248 | 43.5675 | 11.9215 | 8.5682 | 28.7746 | 43.5991 | 11.6206 | 8.3519 | 28.7873 | 46.5221 | 10.9353 | 7.8594 | 25.8338 | 46.3969 | 10.7275 | 7.7101 | 26.0158 | 46.3243 | 10.2922 | 7.3972 | 26.132 | 46.2324 | 9.7919 | 7.0376 | 26.0836 | 46.4469 | 9.2199 | 6.6265 | 25.6529 | 46.4737 | 9.061 | 6.5123 | 25.4374 | 47.205 | 8.5459 | 6.1421 | 24.1885 | 47.3101 | 8.2739 | 5.9466 | 23.5635 | 47.3061 | 7.9713 | 5.7291 | 23.1652 | 46.8068 | 7.7064 | 5.5387 | 23.2752 | 46.5807 | 7.6692 | 5.512 | 24.2887 | 43.5491 | 12.0344 | 8.6494 | 29.1296 | 43.5612 | 11.9033 | 8.5551 | 28.9053 | 43.597 | 10.3767 | 7.4579 | 28.7422 | 43.6219 | 8.6896 | 6.2454 | 28.7218 | 42.8279 | 7.0513 | 5.0679 | 28.7603 | 30.9909 | 5.1024 | 3.6672 | 28.7941 | 16.0492 | 2.6424 | 1.8991 | 16.0492 | 14.9145 | 2.4556 | 1.7649 | 14.9145 | 14.4494 | 2.379 | 1.7098 | 14.4494 | 14.4489 | 2.3789 | 1.7098 | 14.4489 | 14.4928 | 2.3861 | 1.715 | 14.4928 | 19.4156 | 3.1966 | 2.2975 | 19.4156 | 32.8955 | 5.416 | 3.8926 | 25.2286 | 47.2446 | 8.0438 | 5.7813 | 25.2104 | 47.127 | 8.9875 | 6.4595 | 25.4817 | 43.5491 | 12.0344 | 8.6494 | 29.1296 | 43.5412 | 11.8154 | 8.492 | 28.7071 | 43.5809 | 11.8683 | 8.53 | 28.4899 | 43.6217 | 11.5388 | 8.2932 | 28.4729 | 46.5517 | 10.8286 | 7.7827 | 25.5088 | 46.4255 | 10.6132 | 7.6279 | 25.6753 | 46.3565 | 10.193 | 7.3259 | 25.7782 | 46.284 | 9.6903 | 6.9646 | 25.707 | 46.4915 | 9.1436 | 6.5717 | 25.2698 | 46.5111 | 8.9585 | 6.4387 | 25.048 | 47.2377 | 8.4226 | 6.0535 | 23.7074 | 47.3587 | 8.1263 | 5.8405 | 23.0006 | 47.3763 | 7.8067 | 5.6108 | 22.528 | 45.7179 | 7.5271 | 5.4099 | 22.5445 | 45.0742 | 7.4211 | 5.3337 | 23.4562
SWINTON | AGECROFT | KEARSLEY | 378367 | 401718 | 30.2368 | 15.0169 | 10.7929 | 18.1608 | 30.3288 | 14.9566 | 10.7496 | 18.0743 | 30.4244 | 13.259 | 9.5295 | 17.9719 | 30.5192 | 11.5218 | 8.281 | 17.8819 | 30.6286 | 9.7273 | 6.9912 | 17.746 | 30.7692 | 7.953 | 5.716 | 17.5926 | 30.9499 | 6.2662 | 4.5037 | 17.4368 | 31.1798 | 6.1693 | 4.434 | 17.2772 | 31.4081 | 6.0672 | 4.3606 | 17.0957 | 31.6499 | 6.0577 | 4.3538 | 16.9245 | 32.364 | 5.9669 | 4.2885 | 15.6175 | 32.9768 | 6.5626 | 4.7167 | 13.2765 | 33.3786 | 8.7716 | 6.3043 | 11.3479 | 33.6696 | 11.4389 | 8.2214 | 9.3628 | 33.8179 | 11.9419 | 8.5829 | 7.6458 | 30.2202 | 15.0169 | 10.7929 | 18.1608 | 30.3156 | 14.9549 | 10.7484 | 18.0651 | 30.4127 | 13.2474 | 9.5212 | 17.9494 | 30.5025 | 11.5163 | 8.277 | 17.8471 | 30.6005 | 9.7543 | 7.0106 | 17.7117 | 30.7236 | 8.009 | 5.7563 | 17.5456 | 30.876 | 6.1315 | 4.4068 | 17.3264 | 31.0573 | 5.9637 | 4.2862 | 17.0553 | 31.1629 | 5.8115 | 4.1769 | 16.8805 | 31.2824 | 5.6725 | 4.077 | 16.697 | 31.7346 | 5.3576 | 3.8506 | 16.0899 | 31.2859 | 5.151 | 3.7021 | 15.423 | 32.811 | 6.575 | 4.7256 | 14.7742 | 33.3039 | 8.8874 | 6.3876 | 13.9892 | 33.6138 | 9.3474 | 6.7181 | 13.496 | 30.2425 | 15.0169 | 10.7929 | 18.1608 | 30.3296 | 14.9594 | 10.7516 | 18.0728 | 30.427 | 13.2195 | 9.5011 | 17.9708 | 30.5228 | 11.439 | 8.2214 | 17.8815 | 30.6321 | 9.6602 | 6.943 | 17.7481 | 30.7694 | 7.8135 | 5.6157 | 17.2972 | 30.9432 | 6.0418 | 4.3423 | 16.8443 | 31.1624 | 5.8675 | 4.2171 | 16.3921 | 31.3657 | 5.7129 | 4.106 | 15.9409 | 31.5857 | 5.6882 | 4.0883 | 15.8035 | 32.286 | 5.6009 | 4.0254 | 14.7867 | 32.9701 | 6.1776 | 4.44 | 12.6978 | 33.4426 | 8.3232 | 5.982 | 10.8283 | 33.771 | 10.9256 | 7.8524 | 8.9442 | 33.9061 | 11.3942 | 8.1893 | 7.3778 | 30.2425 | 15.0169 | 10.7929 | 18.1608 | 30.2614 | 14.9962 | 10.7781 | 18.2419 | 30.3132 | 14.9188 | 10.7224 | 18.1962 | 30.377 | 14.7771 | 10.6206 | 18.138 | 30.4683 | 14.5923 | 10.4878 | 18.0227 | 30.5969 | 14.3209 | 10.2927 | 17.5716 | 30.7769 | 14.1144 | 10.1443 | 17.0071 | 31.0126 | 13.8629 | 9.9635 | 16.1099 | 31.2548 | 13.575 | 9.7566 | 15.1572 | 31.513 | 13.3318 | 9.5818 | 14.3887 | 32.2446 | 12.9159 | 9.2829 | 12.149 | 32.8428 | 12.3788 | 8.8969 | 10.0416 | 33.2233 | 11.8873 | 8.5436 | 8.3745 | 33.4528 | 11.4556 | 8.2334 | 7.3681 | 33.4488 | 11.383 | 8.1812 | 8.0997 | 30.2366 | 15.0169 | 10.7929 | 18.1608 | 30.3122 | 14.9645 | 10.7553 | 18.0878 | 30.386 | 13.2784 | 9.5434 | 18.0098 | 30.4558 | 11.5544 | 8.3044 | 17.966 | 30.5274 | 9.7818 | 7.0304 | 17.916 | 30.6389 | 8.0194 | 5.7637 | 17.8422 | 30.7932 | 6.3481 | 4.5625 | 17.7397 | 30.9789 | 6.2621 | 4.5007 | 17.6122 | 31.1595 | 6.1637 | 4.43 | 17.4401 | 31.3587 | 6.1528 | 4.4222 | 17.2624 | 32.0427 | 6.1806 | 4.4421 | 16.6427 | 32.6291 | 7.0697 | 5.0811 | 15.8159 | 33.0335 | 9.5193 | 6.8417 | 15.1423 | 33.3196 | 12.461 | 8.956 | 14.601 | 33.4265 | 13.2364 | 9.5133 | 14.4376 | 30.2366 | 15.0169 | 10.7929 | 18.1608 | 30.2738 | 14.9867 | 10.7712 | 18.2107 | 30.3575 | 14.8828 | 10.6965 | 18.1219 | 30.4478 | 14.7332 | 10.589 | 18.0148 | 30.5472 | 14.5371 | 10.4481 | 17.8571 | 30.6707 | 14.2545 | 10.245 | 17.3874 | 30.8327 | 14.0494 | 10.0976 | 16.8107 | 31.0592 | 13.7809 | 9.9046 | 15.8677 | 31.2764 | 13.4745 | 9.6844 | 14.78 | 31.5123 | 13.227 | 9.5065 | 13.9847 | 32.2577 | 12.7694 | 9.1776 | 11.6152 | 32.9099 | 12.2019 | 8.7697 | 9.3488 | 33.3564 | 11.6797 | 8.3944 | 7.5131 | 33.6285 | 11.2147 | 8.0602 | 6.3152 | 33.6494 | 11.1034 | 7.9802 | 6.8522
TAME VALLEY | HARTSHEAD-HEYROD | STALYBRIDGE | 395148 | 398108 | 27.8986 | 12.2502 | 8.9363 | 13.4519 | 27.9925 | 11.9609 | 8.7253 | 12.2245 | 28.1136 | 11.1304 | 8.1195 | 11.7287 | 28.2759 | 10.2713 | 7.4927 | 11.516 | 28.4826 | 9.4945 | 6.9261 | 11.1651 | 28.7401 | 8.6336 | 6.2981 | 10.777 | 29.0416 | 7.7741 | 5.6711 | 10.3872 | 29.3536 | 7.6085 | 5.5503 | 10.0049 | 29.657 | 7.4366 | 5.4249 | 9.5839 | 29.9836 | 7.3125 | 5.3343 | 9.1676 | 31.053 | 6.7513 | 4.9249 | 6.7176 | 32.02 | 6.3024 | 4.5975 | 2.9555 | 32.6489 | 6.5044 | 4.7449 | 0.094836 | 33.1147 | 6.9548 | 5.0734 | -2.5295 | 33.397 | 6.9652 | 5.081 | -4.4117 | 27.8774 | 12.2502 | 8.9363 | 13.4519 | 27.9429 | 12.1277 | 8.847 | 13.0593 | 28.0034 | 11.5178 | 8.4021 | 12.8693 | 28.0834 | 10.9125 | 7.9605 | 12.7092 | 28.1991 | 10.2794 | 7.4987 | 12.4878 | 28.3505 | 9.6375 | 7.0304 | 12.2446 | 28.541 | 8.8966 | 6.4899 | 11.9192 | 28.7669 | 8.753 | 6.3852 | 11.506 | 28.9351 | 8.6316 | 6.2967 | 11.2071 | 29.1266 | 8.5118 | 6.2092 | 10.8879 | 29.8353 | 8.1219 | 5.9248 | 9.8424 | 30.6668 | 7.8384 | 5.718 | 8.6753 | 31.4125 | 8.0261 | 5.855 | 7.5059 | 32.1613 | 8.5457 | 6.234 | 6.2082 | 32.6515 | 8.4521 | 6.1657 | 5.2294 | 27.907 | 12.2502 | 8.9363 | 13.4519 | 28.0326 | 11.8648 | 8.6552 | 11.6826 | 28.1937 | 10.9032 | 7.9537 | 10.5992 | 28.4031 | 9.9759 | 7.2773 | 9.83 | 28.6657 | 9.0286 | 6.5862 | 8.9187 | 28.9138 | 8.0848 | 5.8978 | 8.271 | 29.1792 | 7.1818 | 5.239 | 7.6368 | 29.5078 | 6.9582 | 5.0759 | 6.9984 | 29.811 | 6.7351 | 4.9132 | 6.3335 | 30.1405 | 6.5214 | 4.7573 | 5.6452 | 31.3153 | 5.8254 | 4.2496 | 2.8582 | 32.402 | 5.3437 | 3.8981 | -0.79438 | 33.0918 | 5.4584 | 3.9818 | -3.4282 | 33.5907 | 6.061 | 4.4214 | -5.4937 | 33.8307 | 6.1167 | 4.4621 | -6.4449 | 27.907 | 12.2502 | 8.9363 | 13.4519 | 27.9222 | 11.9762 | 8.7365 | 12.3233 | 28.0164 | 11.6049 | 8.4656 | 11.3908 | 28.1523 | 11.2389 | 8.1986 | 10.6514 | 28.3589 | 10.8134 | 7.8882 | 9.7427 | 28.6244 | 10.4003 | 7.5869 | 9.0793 | 28.885 | 9.9428 | 7.2531 | 8.2208 | 29.2233 | 9.5605 | 6.9743 | 6.7345 | 29.5689 | 9.1761 | 6.6938 | 5.2433 | 29.9415 | 8.7878 | 6.4106 | 3.781 | 31.117 | 7.9736 | 5.8166 | 0.091975 | 32.1358 | 7.2462 | 5.286 | -2.9207 | 32.7578 | 6.7135 | 4.8974 | -4.7311 | 33.1066 | 6.5427 | 4.7728 | -5.4571 | 33.1939 | 6.4183 | 4.6821 | -4.8185 | 27.8986 | 12.2502 | 8.9363 | 13.4519 | 27.982 | 12.0392 | 8.7824 | 12.6976 | 28.0692 | 11.2371 | 8.1973 | 12.331 | 28.1745 | 10.4089 | 7.5932 | 12.1973 | 28.3257 | 9.6612 | 7.0477 | 12.0146 | 28.5523 | 8.8353 | 6.4452 | 11.7909 | 28.8494 | 7.999 | 5.8351 | 11.5144 | 29.1416 | 7.8436 | 5.7218 | 11.1882 | 29.3902 | 7.6799 | 5.6024 | 10.7786 | 29.6647 | 7.5466 | 5.5051 | 10.3475 | 30.6229 | 7.1491 | 5.2152 | 8.7895 | 31.5627 | 7.0196 | 5.1207 | 6.8359 | 32.1448 | 7.4952 | 5.4676 | 5.4623 | 32.5625 | 8.2262 | 6.0009 | 4.2396 | 32.7748 | 8.4383 | 6.1557 | 3.4663 | 27.8986 | 12.2502 | 8.9363 | 13.4519 | 27.9392 | 11.8898 | 8.6734 | 11.8324 | 28.0744 | 11.4857 | 8.3787 | 10.7305 | 28.2588 | 11.0987 | 8.0963 | 9.9001 | 28.5011 | 10.6573 | 7.7743 | 8.9083 | 28.7714 | 10.2344 | 7.4658 | 8.1878 | 29.0217 | 9.7681 | 7.1257 | 7.2598 | 29.3615 | 9.3612 | 6.8289 | 5.6885 | 29.6808 | 8.9822 | 6.5524 | 4.1531 | 30.0266 | 8.5857 | 6.2631 | 2.6433 | 31.1883 | 7.7076 | 5.6226 | -1.2525 | 32.278 | 6.9347 | 5.0588 | -4.5052 | 33.0051 | 6.3466 | 4.6297 | -6.6131 | 33.4021 | 6.1278 | 4.4701 | -7.6131 | 33.5255 | 5.9811 | 4.3631 | -7.0747
TARDY GATE | RIBBLE | PENWORTHAM EAST / ROCHDALE | 353958 | 426066 | 29.006 | 12.9325 | 9.2949 | 15.9923 | 29.1005 | 12.8527 | 9.2375 | 15.3495 | 29.2312 | 12.6653 | 9.1028 | 14.6384 | 29.4043 | 12.5973 | 9.0539 | 14.0201 | 29.653 | 12.4237 | 8.9292 | 13.3467 | 29.9305 | 12.1615 | 8.7407 | 12.8234 | 30.2311 | 11.8698 | 8.5311 | 12.6158 | 30.5714 | 11.6799 | 8.3946 | 12.4151 | 30.8773 | 11.4619 | 8.2379 | 12.1376 | 31.1859 | 11.2831 | 8.1094 | 11.8732 | 32.192 | 10.4219 | 7.4904 | 10.2116 | 33.0733 | 10.1266 | 7.2782 | 7.411 | 33.6759 | 9.6151 | 6.9106 | 5.1067 | 34.1526 | 9.4849 | 6.817 | 2.6574 | 34.4598 | 8.9487 | 6.4316 | 0.51873 | 28.9892 | 12.9325 | 9.2949 | 15.9923 | 29.0371 | 12.9223 | 9.2875 | 15.7483 | 29.0752 | 12.9081 | 9.2773 | 15.544 | 29.1309 | 12.7012 | 9.1286 | 15.354 | 29.2158 | 12.6587 | 9.0981 | 15.1302 | 29.3064 | 12.6565 | 9.0965 | 14.9391 | 29.4348 | 12.4203 | 8.9267 | 14.6815 | 29.6267 | 12.3344 | 8.865 | 14.3339 | 29.7975 | 12.2547 | 8.8077 | 14.0088 | 29.9793 | 12.1471 | 8.7303 | 13.6778 | 30.5834 | 11.7859 | 8.4708 | 12.674 | 31.2699 | 11.5523 | 8.3029 | 11.648 | 31.9993 | 11.482 | 8.2523 | 10.645 | 32.5617 | 11.3962 | 8.1907 | 9.5552 | 32.9498 | 11.0482 | 7.9406 | 8.8025 | 29.0131 | 12.9325 | 9.2949 | 15.9923 | 29.1149 | 12.7905 | 9.1928 | 15.2884 | 29.256 | 12.6578 | 9.0974 | 14.5884 | 29.4438 | 12.5194 | 8.998 | 14.0138 | 29.7096 | 12.2491 | 8.8036 | 13.3871 | 30.0055 | 11.9202 | 8.5673 | 12.9194 | 30.3265 | 11.6161 | 8.3488 | 12.7892 | 30.6892 | 11.4009 | 8.1941 | 12.6761 | 31.0017 | 11.1372 | 8.0046 | 12.506 | 31.3161 | 10.7023 | 7.692 | 12.3302 | 32.439 | 10.4526 | 7.5125 | 10.9165 | 33.4437 | 9.69 | 6.9644 | 8.3082 | 33.9717 | 9.4853 | 6.8172 | 6.1685 | 34.3296 | 9.113 | 6.5497 | 3.9294 | 34.5193 | 8.5098 | 6.1162 | 2.0525 | 29.0131 | 12.9325 | 9.2949 | 15.9923 | 29.0265 | 12.8768 | 9.2548 | 15.6762 | 29.1226 | 12.6815 | 9.1144 | 15.0753 | 29.2845 | 12.6279 | 9.0759 | 14.5178 | 29.5327 | 12.4214 | 8.9275 | 13.8818 | 29.8443 | 12.1208 | 8.7114 | 13.3758 | 30.1608 | 11.7996 | 8.4806 | 13.0427 | 30.5043 | 11.5212 | 8.2805 | 12.2348 | 30.8113 | 11.2117 | 8.0581 | 11.3624 | 31.127 | 10.7051 | 7.694 | 10.4814 | 32.1029 | 10.8636 | 7.8079 | 7.9216 | 33.0348 | 10.1053 | 7.2629 | 5.4515 | 33.6686 | 9.5154 | 6.8389 | 3.5077 | 34.122 | 8.9444 | 6.4286 | 2.2486 | 34.0601 | 8.7533 | 6.2912 | 2.9581 | 29.006 | 12.9325 | 9.2949 | 15.9923 | 29.0802 | 12.9141 | 9.2816 | 15.6649 | 29.1803 | 12.6932 | 9.1229 | 15.0446 | 29.2977 | 12.6808 | 9.1139 | 14.4939 | 29.4539 | 12.5348 | 9.009 | 13.9339 | 29.6592 | 12.328 | 8.8604 | 13.4989 | 29.9141 | 12.0456 | 8.6574 | 13.3458 | 30.2017 | 11.8746 | 8.5345 | 13.1853 | 30.4691 | 11.6652 | 8.384 | 12.9216 | 30.7498 | 11.4778 | 8.2493 | 12.6553 | 31.7113 | 10.7099 | 7.6974 | 11.7325 | 32.6532 | 10.8011 | 7.763 | 10.683 | 33.2653 | 10.5202 | 7.5611 | 9.9744 | 33.7492 | 10.7745 | 7.7438 | 9.3479 | 33.9404 | 10.5798 | 7.6039 | 9.0377 | 29.006 | 12.9325 | 9.2949 | 15.9923 | 29.0397 | 12.7522 | 9.1652 | 15.3714 | 29.169 | 12.621 | 9.071 | 14.6486 | 29.3709 | 12.5296 | 9.0053 | 14.0024 | 29.6491 | 12.2578 | 8.8099 | 13.2868 | 29.9504 | 11.9669 | 8.6008 | 12.7293 | 30.2829 | 11.6196 | 8.3512 | 12.3353 | 30.6274 | 11.3411 | 8.1511 | 11.4414 | 30.9302 | 11.0354 | 7.9313 | 10.5088 | 31.2387 | 10.4548 | 7.5141 | 9.5682 | 32.2009 | 10.6164 | 7.6302 | 6.8084 | 33.1097 | 9.8343 | 7.0681 | 4.139 | 33.7428 | 9.1943 | 6.6081 | 2.0037 | 34.1796 | 8.5938 | 6.1765 | 0.51371 | 34.291 | 8.3316 | 5.9881 | 0.9863
TARLETON | WRIGHTINGTON | PENWORTHAM WEST / STANAH | 344741 | 422417 | 18.6825 | 12.2316 | 8.7911 | 10.273 | 18.8816 | 12.0784 | 8.681 | 9.8765 | 19.1801 | 11.8905 | 8.546 | 9.6223 | 19.558 | 11.7084 | 8.4151 | 9.462 | 19.9948 | 11.4323 | 8.2166 | 9.2462 | 20.4478 | 11.0803 | 7.9637 | 9.0315 | 20.9207 | 10.6541 | 7.6573 | 8.8532 | 21.4753 | 10.4358 | 7.5004 | 8.6505 | 22.0769 | 10.1758 | 7.3135 | 8.3013 | 22.6444 | 10.0145 | 7.1976 | 7.977 | 23.7131 | 9.3272 | 6.7036 | 6.3397 | 24.4243 | 8.5833 | 6.169 | 3.8613 | 24.8956 | 10.4406 | 7.5038 | 1.921 | 25.2392 | 13.2923 | 9.5534 | 0.062318 | 25.4031 | 14.5291 | 10.4424 | -1.4486 | 18.7165 | 12.2316 | 8.7911 | 10.273 | 18.8558 | 12.1466 | 8.73 | 10.032 | 18.993 | 12.0576 | 8.666 | 9.8103 | 19.2267 | 11.9555 | 8.5926 | 9.6222 | 19.5844 | 11.8236 | 8.4978 | 9.395 | 20.0379 | 11.6817 | 8.3959 | 9.1386 | 20.4465 | 11.5198 | 8.2795 | 8.8075 | 20.8362 | 11.3578 | 8.163 | 8.3874 | 21.0489 | 11.2082 | 8.0555 | 7.9854 | 21.2769 | 11.0527 | 7.9438 | 7.5799 | 22.0298 | 10.5892 | 7.6107 | 6.2892 | 22.8247 | 10.1528 | 7.297 | 5.0419 | 23.575 | 10.7599 | 7.7333 | 3.9007 | 24.3427 | 13.2064 | 9.4917 | 2.7097 | 24.8637 | 14.5281 | 10.4416 | 1.9521 | 18.6686 | 12.2316 | 8.7911 | 10.273 | 18.8585 | 12.0324 | 8.6479 | 9.8633 | 19.1374 | 11.7543 | 8.448 | 9.6378 | 19.4858 | 11.4911 | 8.2589 | 9.545 | 19.8808 | 11.1538 | 8.0165 | 9.3979 | 20.2796 | 10.7539 | 7.7291 | 9.2641 | 20.6853 | 10.2712 | 7.3821 | 9.1983 | 21.1508 | 9.8785 | 7.0999 | 9.1442 | 21.6842 | 9.3897 | 6.7486 | 8.9803 | 22.2038 | 8.3677 | 6.014 | 8.7983 | 23.6791 | 8.8629 | 6.3699 | 7.5276 | 24.3997 | 8.5471 | 6.143 | 4.2472 | 24.8723 | 9.1307 | 6.5624 | 1.8668 | 25.1672 | 11.492 | 8.2595 | -0.08343 | 25.2245 | 13.0665 | 9.3912 | -1.3771 | 18.6686 | 12.2316 | 8.7911 | 10.273 | 18.6543 | 12.11 | 8.7037 | 10.2357 | 18.7642 | 11.8829 | 8.5405 | 10.1269 | 18.9457 | 11.6061 | 8.3415 | 10.074 | 19.2178 | 11.3097 | 8.1285 | 9.9513 | 19.6123 | 10.9997 | 7.9057 | 9.8036 | 20.0586 | 10.4727 | 7.5269 | 9.5828 | 20.4995 | 10.4179 | 7.4876 | 8.9795 | 20.996 | 10.0743 | 7.2406 | 8.2575 | 21.4955 | 9.9066 | 7.1201 | 7.514 | 23.0238 | 13.5882 | 9.7661 | 5.3795 | 24.1081 | 12.667 | 9.104 | 3.3622 | 24.5149 | 11.9889 | 8.6167 | 1.9007 | 24.7248 | 14.1651 | 10.1807 | 0.86512 | 24.601 | 13.4728 | 9.6832 | 0.78798 | 18.6825 | 12.2316 | 8.7911 | 10.273 | 18.8345 | 12.111 | 8.7044 | 9.9619 | 19.0112 | 11.9387 | 8.5806 | 9.7697 | 19.2213 | 11.7737 | 8.462 | 9.6885 | 19.4922 | 11.5242 | 8.2827 | 9.61 | 19.8968 | 11.1889 | 8.0417 | 9.4993 | 20.3918 | 10.7978 | 7.7606 | 9.3572 | 20.9088 | 10.5269 | 7.5659 | 9.1773 | 21.4545 | 10.2659 | 7.3783 | 8.8185 | 22.0097 | 10.0662 | 7.2348 | 8.455 | 23.4112 | 9.1803 | 6.5981 | 7.23 | 24.0883 | 9.5525 | 6.8656 | 5.9007 | 24.5471 | 11.1132 | 7.9873 | 5.0107 | 24.8711 | 13.7185 | 9.8597 | 3.655 | 24.9351 | 15.6658 | 11.2593 | 2.986 | 18.6825 | 12.2316 | 8.7911 | 10.273 | 18.7926 | 12.0575 | 8.666 | 10.0064 | 19.0808 | 11.8031 | 8.4831 | 9.7574 | 19.4665 | 11.5043 | 8.2684 | 9.5746 | 19.9067 | 11.1894 | 8.0421 | 9.3341 | 20.3543 | 10.8728 | 7.8145 | 9.1078 | 20.8484 | 10.4008 | 7.4753 | 8.7933 | 21.4316 | 10.2965 | 7.4003 | 8.0403 | 22.0461 | 10.01 | 7.1944 | 7.2191 | 22.5578 | 9.0771 | 6.5239 | 6.3828 | 23.6632 | 13.3622 | 9.6037 | 3.954 | 24.338 | 12.3599 | 8.8833 | 1.6611 | 24.7718 | 11.6842 | 8.3976 | -0.04315 | 24.9799 | 13.6709 | 9.8256 | -0.9937 | 24.864 | 13.2471 | 9.521 | -0.22605
THE HEIGHT | AGECROFT | KEARSLEY | 379792 | 400497 | 29.6073 | 9.8612 | 7.1936 | 16.8362 | 29.6699 | 9.668 | 7.0527 | 16.2324 | 29.7486 | 9.3928 | 6.8519 | 15.9316 | 29.8481 | 9.1627 | 6.6841 | 15.6885 | 29.9748 | 8.8726 | 6.4724 | 15.3413 | 30.1233 | 8.5954 | 6.2702 | 14.9638 | 30.4001 | 8.3803 | 6.1133 | 14.4954 | 30.6457 | 8.2425 | 6.0128 | 14.1129 | 30.9009 | 8.1025 | 5.9106 | 13.6973 | 31.1776 | 7.9611 | 5.8075 | 13.2157 | 32.1015 | 7.3955 | 5.3949 | 10.7783 | 32.896 | 6.8594 | 5.0038 | 7.6228 | 33.4107 | 6.5698 | 4.7926 | 5.3778 | 33.7966 | 6.3316 | 4.6188 | 3.4232 | 34.0213 | 6.0096 | 4.3839 | 2.1255 | 29.5889 | 9.8612 | 7.1936 | 16.8362 | 29.6566 | 9.7404 | 7.1055 | 16.6092 | 29.7215 | 9.5281 | 6.9506 | 16.4641 | 29.7989 | 9.296 | 6.7813 | 16.317 | 29.9027 | 9.0678 | 6.6149 | 16.1165 | 30.0263 | 8.8488 | 6.4551 | 15.9136 | 30.2532 | 8.4987 | 6.1997 | 15.555 | 30.417 | 8.3131 | 6.0643 | 15.1822 | 30.537 | 8.1542 | 5.9484 | 14.8824 | 30.6659 | 7.9985 | 5.8348 | 14.5647 | 31.1566 | 7.6242 | 5.5617 | 13.4899 | 31.7653 | 7.3444 | 5.3576 | 12.2103 | 32.3818 | 7.2075 | 5.2577 | 10.8854 | 32.9893 | 7.1659 | 5.2274 | 9.4938 | 33.3905 | 6.9639 | 5.08 | 8.5788 | 29.6114 | 9.8612 | 7.1936 | 16.8362 | 29.6884 | 9.6397 | 7.032 | 16.0934 | 29.7848 | 9.3455 | 6.8174 | 15.6987 | 29.9036 | 9.053 | 6.6041 | 15.3747 | 30.035 | 8.7441 | 6.3787 | 14.9449 | 30.1957 | 8.4253 | 6.1461 | 14.4843 | 30.4745 | 8.1781 | 5.9658 | 13.9535 | 30.7231 | 8.0056 | 5.84 | 13.4928 | 30.9674 | 7.8336 | 5.7145 | 13.0131 | 31.2361 | 7.6344 | 5.5692 | 12.3797 | 32.2207 | 7.0356 | 5.1323 | 9.5993 | 33.1728 | 6.3943 | 4.6646 | 6.2943 | 33.793 | 6.0516 | 4.4145 | 4.1039 | 34.2355 | 5.7951 | 4.2275 | 2.4374 | 33.9864 | 5.5129 | 4.0216 | 1.7322 | 29.6114 | 9.8612 | 7.1936 | 16.8362 | 29.6035 | 9.7202 | 7.0907 | 16.5021 | 29.6552 | 9.5605 | 6.9743 | 16.2086 | 29.8184 | 9.3254 | 6.8028 | 15.8235 | 29.9284 | 9.1052 | 6.6421 | 15.4019 | 30.0763 | 8.8193 | 6.4336 | 14.9287 | 30.2849 | 8.6021 | 6.2751 | 14.299 | 30.566 | 8.3097 | 6.0618 | 13.1762 | 30.86 | 7.9933 | 5.831 | 12.0606 | 31.1778 | 7.6963 | 5.6143 | 10.9369 | 32.1817 | 7.1211 | 5.1947 | 7.7078 | 32.9978 | 6.5406 | 4.7713 | 5.0044 | 33.496 | 6.0573 | 4.4187 | 3.3131 | 33.8201 | 5.6762 | 4.1407 | 2.5016 | 33.9226 | 5.5971 | 4.083 | 2.9586 | 29.6073 | 9.8612 | 7.1936 | 16.8362 | 29.6632 | 9.7171 | 7.0885 | 16.4949 | 29.722 | 9.4742 | 6.9113 | 16.2756 | 29.7888 | 9.2518 | 6.749 | 16.0956 | 29.8841 | 8.9794 | 6.5503 | 15.8711 | 30.0107 | 8.738 | 6.3743 | 15.6182 | 30.2659 | 8.5377 | 6.2282 | 15.2472 | 30.4721 | 8.4165 | 6.1397 | 14.9195 | 30.6817 | 8.2784 | 6.0389 | 14.5243 | 30.9149 | 8.1362 | 5.9352 | 14.0818 | 31.7368 | 7.7053 | 5.6209 | 12.3199 | 32.5183 | 7.4334 | 5.4225 | 10.4992 | 33.0286 | 7.3468 | 5.3594 | 9.2676 | 33.4049 | 7.302 | 5.3267 | 8.2246 | 33.5956 | 7.1043 | 5.1825 | 7.606 | 29.6073 | 9.8612 | 7.1936 | 16.8362 | 29.6208 | 9.6728 | 7.0561 | 16.2671 | 29.7024 | 9.492 | 6.9243 | 15.8683 | 29.8985 | 9.2211 | 6.7267 | 15.4087 | 30.0203 | 9.0021 | 6.5669 | 14.9213 | 30.1652 | 8.7105 | 6.3542 | 14.4077 | 30.3574 | 8.4756 | 6.1829 | 13.7278 | 30.63 | 8.169 | 5.9592 | 12.5419 | 30.9 | 7.8474 | 5.7246 | 11.389 | 31.1938 | 7.5418 | 5.5016 | 10.2122 | 32.1889 | 6.96 | 5.0772 | 6.7884 | 33.1092 | 6.2984 | 4.5946 | 3.8724 | 33.6887 | 5.7705 | 4.2095 | 1.9569 | 32.9846 | 5.3504 | 3.9031 | 0.93237 | 32.2411 | 5.2298 | 3.8151 | 1.1607
THORLEY LN | MOSS NOOK | SOUTH MANCHESTER | 381499 | 386063 | 38 | 7.3169 | 5.2588 | 37.5387 | 38 | 7.2803 | 5.2325 | 37.5387 | 38 | 7.2071 | 5.1799 | 37.4766 | 38 | 7.1568 | 5.1437 | 37.4144 | 38 | 7.1178 | 5.1157 | 37.3522 | 38 | 6.9745 | 5.0127 | 37.29 | 38 | 6.8688 | 4.9368 | 37.2279 | 38 | 6.7363 | 4.8415 | 37.1035 | 38 | 6.5951 | 4.7401 | 37.1035 | 38 | 6.4181 | 4.6128 | 37.1035 | 38 | 6.3207 | 4.5428 | 37.1035 | 37.4522 | 6.1662 | 4.4318 | 37.1035 | 36.2394 | 5.9665 | 4.2883 | 36.2394 | 37.3407 | 6.1479 | 4.4186 | 37.1035 | 37.0425 | 6.0988 | 4.3833 | 37.0425 | 38 | 7.3169 | 5.2588 | 37.5387 | 38 | 7.3147 | 5.2572 | 37.5387 | 38 | 7.2904 | 5.2397 | 37.5387 | 38 | 7.2424 | 5.2053 | 37.5387 | 38 | 7.1534 | 5.1413 | 37.5387 | 38 | 7.1666 | 5.1508 | 37.5387 | 38 | 6.9196 | 4.9733 | 37.5387 | 38 | 6.9157 | 4.9704 | 37.5387 | 38 | 6.8974 | 4.9573 | 37.5387 | 38 | 6.9029 | 4.9613 | 37.5387 | 38 | 6.9018 | 4.9605 | 37.5387 | 38 | 6.9538 | 4.9978 | 37.5387 | 38 | 6.9285 | 4.9797 | 37.5387 | 38 | 6.8898 | 4.9519 | 37.5387 | 38 | 6.8989 | 4.9584 | 37.5387 | 38 | 7.3169 | 5.2588 | 37.5387 | 38 | 7.2689 | 5.2243 | 37.5387 | 38 | 7.1883 | 5.1664 | 37.4766 | 38 | 7.1241 | 5.1203 | 37.4144 | 38 | 7.0867 | 5.0934 | 37.3522 | 38 | 6.9416 | 4.989 | 37.29 | 38 | 6.8089 | 4.8937 | 37.2279 | 38 | 6.6604 | 4.787 | 37.1035 | 38 | 6.5111 | 4.6797 | 37.1035 | 38 | 6.3843 | 4.5885 | 37.1035 | 37.8201 | 6.2268 | 4.4753 | 37.1035 | 36.9243 | 6.0793 | 4.3693 | 36.9243 | 36.8737 | 6.071 | 4.3633 | 36.8737 | 37.0489 | 6.0998 | 4.3841 | 37.0489 | 36.7301 | 6.0473 | 4.3463 | 36.7301 | 38 | 7.3169 | 5.2588 | 37.5387 | 38 | 7.2874 | 5.2376 | 37.5387 | 38 | 7.2308 | 5.1969 | 37.4766 | 38 | 7.1545 | 5.1421 | 37.4144 | 38 | 7.1655 | 5.15 | 37.3522 | 38 | 7.0704 | 5.0816 | 37.29 | 38 | 6.9916 | 5.025 | 37.2279 | 38 | 6.8954 | 4.9558 | 37.1035 | 38 | 6.822 | 4.9031 | 37.1035 | 38 | 6.6913 | 4.8092 | 37.1035 | 38 | 6.3971 | 4.5978 | 37.1035 | 37.2812 | 6.1381 | 4.4115 | 37.1035 | 37.4472 | 6.1654 | 4.4312 | 37.1035 | 37.4992 | 6.174 | 4.4373 | 37.1035 | 37.0937 | 6.1072 | 4.3894 | 37.0937 | 38 | 7.3169 | 5.2588 | 37.5387 | 38 | 7.3013 | 5.2476 | 37.5387 | 38 | 7.2333 | 5.1987 | 37.4766 | 38 | 7.189 | 5.1668 | 37.4144 | 38 | 7.1525 | 5.1407 | 37.3522 | 38 | 7.0277 | 5.0509 | 37.29 | 38 | 6.9162 | 4.9708 | 37.2279 | 38 | 6.7879 | 4.8786 | 37.1035 | 38 | 6.644 | 4.7752 | 37.1035 | 38 | 6.4575 | 4.6411 | 37.1035 | 38 | 6.377 | 4.5833 | 37.1035 | 37.9582 | 6.2495 | 4.4917 | 37.1035 | 37.0458 | 6.0993 | 4.3837 | 37.0458 | 38 | 6.3436 | 4.5593 | 37.1035 | 38 | 6.35 | 4.5639 | 37.1035 | 38 | 7.3169 | 5.2588 | 37.5387 | 38 | 7.264 | 5.2208 | 37.5387 | 38 | 7.2029 | 5.1768 | 37.4766 | 38 | 7.1219 | 5.1187 | 37.4144 | 38 | 7.1212 | 5.1182 | 37.3211 | 38 | 7.0186 | 5.0444 | 37.2279 | 38 | 6.935 | 4.9843 | 37.1346 | 38 | 6.8325 | 4.9107 | 36.9792 | 38 | 6.7587 | 4.8576 | 36.9792 | 38 | 6.6306 | 4.7656 | 36.9792 | 38 | 6.3315 | 4.5506 | 36.9792 | 37.0839 | 6.1056 | 4.3882 | 36.9792 | 37.01 | 6.0934 | 4.3795 | 36.9792 | 37.0321 | 6.0971 | 4.3821 | 36.9792 | 36.6576 | 6.0354 | 4.3378 | 36.6576
THORNTON | BISPHAM | PENWORTHAM WEST / STANAH | 334207 | 442111 | 23.3054 | 11.2391 | 8.0778 | 14.0337 | 23.3562 | 10.8431 | 7.7932 | 12.677 | 23.4211 | 10.5707 | 7.5973 | 12.3865 | 23.5011 | 10.7027 | 7.6923 | 12.3212 | 23.6122 | 10.9164 | 7.8459 | 12.1839 | 23.7457 | 11.0452 | 7.9384 | 12.0308 | 23.9053 | 10.9389 | 7.862 | 11.8741 | 24.1026 | 10.8605 | 7.8056 | 11.7116 | 24.2771 | 10.6937 | 7.6858 | 11.5059 | 28.8434 | 9.7909 | 7.0369 | 6.8968 | 29.4545 | 9.3841 | 6.7446 | 5.5091 | 30.4426 | 8.7886 | 6.3165 | 2.714 | 32.812 | 8.0635 | 5.7954 | -1.467 | 33.111 | 8.9422 | 6.4269 | -3.8755 | 33.3344 | 9.4701 | 6.8064 | -6.0486 | 23.2594 | 11.2391 | 8.0778 | 14.0337 | 23.3244 | 11.0653 | 7.9528 | 13.6911 | 23.3717 | 10.9522 | 7.8715 | 13.5704 | 23.4177 | 10.8232 | 7.7788 | 13.4783 | 23.4871 | 10.6992 | 7.6897 | 13.3251 | 23.575 | 10.7358 | 7.7161 | 13.1461 | 23.688 | 10.5446 | 7.5786 | 12.8987 | 23.8272 | 10.4925 | 7.5412 | 12.565 | 23.9273 | 10.4564 | 7.5152 | 12.2955 | 24.0324 | 10.4187 | 7.4881 | 12.0229 | 24.3785 | 10.2686 | 7.3802 | 11.1807 | 24.9812 | 10.1106 | 7.2667 | 10.0623 | 26.3489 | 9.8927 | 7.1101 | 8.0765 | 26.729 | 10.9317 | 7.8568 | 7.0683 | 26.997 | 11.7715 | 8.4604 | 6.4149 | 23.311 | 11.2391 | 8.0778 | 14.0337 | 23.3665 | 10.7764 | 7.7452 | 12.4886 | 23.4393 | 10.5635 | 7.5922 | 12.0972 | 23.5307 | 10.6909 | 7.6838 | 11.9816 | 23.6552 | 10.8633 | 7.8076 | 11.7994 | 23.8037 | 10.8477 | 7.7965 | 11.6096 | 23.9814 | 10.7521 | 7.7277 | 11.4407 | 24.1988 | 10.5053 | 7.5504 | 11.3611 | 24.3785 | 10.4137 | 7.4845 | 11.24 | 24.555 | 10.3051 | 7.4065 | 11.1321 | 26.2506 | 9.6219 | 6.9155 | 8.9102 | 32.4637 | 8.0889 | 5.8137 | 1.0352 | 32.7895 | 7.694 | 5.5298 | -0.9617 | 33.0608 | 8.5498 | 6.1449 | -3.1865 | 33.2377 | 9.1027 | 6.5423 | -5.1611 | 23.311 | 11.2391 | 8.0778 | 14.0337 | 23.2663 | 10.9136 | 7.8438 | 13.2288 | 23.2892 | 10.7519 | 7.7276 | 12.9951 | 23.334 | 10.9495 | 7.8696 | 12.8998 | 23.6859 | 11.0237 | 7.923 | 12.4384 | 23.806 | 10.9916 | 7.8999 | 12.2287 | 23.9861 | 10.8811 | 7.8204 | 11.8865 | 25.2909 | 10.4655 | 7.5217 | 10.1317 | 29.8797 | 9.485 | 6.8171 | 4.9951 | 31.0734 | 9.1023 | 6.542 | 3.2827 | 31.644 | 9.27 | 6.6625 | 1.0531 | 32.117 | 8.7232 | 6.2696 | -1.1728 | 32.4564 | 8.3749 | 6.0192 | -2.9802 | 32.7257 | 9.6091 | 6.9063 | -4.2867 | 32.6884 | 9.4449 | 6.7882 | -3.6784 | 23.3054 | 11.2391 | 8.0778 | 14.0337 | 23.347 | 10.9925 | 7.9005 | 13.5012 | 23.3877 | 10.7335 | 7.7144 | 13.3913 | 23.4293 | 10.8869 | 7.8246 | 13.3905 | 23.495 | 11.1238 | 7.9949 | 13.3499 | 23.6033 | 11.2764 | 8.1046 | 13.268 | 23.7489 | 11.1678 | 8.0265 | 13.1576 | 23.9142 | 11.128 | 7.9979 | 13.039 | 24.0631 | 10.9704 | 7.8846 | 12.8546 | 28.6097 | 10.0839 | 7.2475 | 8.2518 | 29.0786 | 9.8235 | 7.0604 | 7.6156 | 29.8144 | 9.5288 | 6.8485 | 6.3987 | 32.1762 | 9.0856 | 6.53 | 3.6831 | 32.5058 | 10.3271 | 7.4223 | 3.0211 | 32.7395 | 11.1996 | 8.0493 | 2.5819 | 23.3054 | 11.2391 | 8.0778 | 14.0337 | 23.2825 | 10.7876 | 7.7533 | 12.5441 | 23.3383 | 10.6081 | 7.6243 | 12.1197 | 23.4222 | 10.7831 | 7.75 | 11.9322 | 23.8055 | 10.8359 | 7.788 | 11.3875 | 23.9255 | 10.7992 | 7.7616 | 11.1217 | 24.0937 | 10.6562 | 7.6588 | 10.7079 | 25.4076 | 10.2178 | 7.3437 | 8.8593 | 30.0018 | 9.2216 | 6.6278 | 3.6552 | 31.1982 | 8.826 | 6.3434 | 1.8751 | 31.8064 | 8.9435 | 6.4279 | -0.56758 | 32.264 | 8.3609 | 6.0091 | -2.9805 | 32.5992 | 7.9757 | 5.7323 | -4.984 | 32.8795 | 9.1708 | 6.5913 | -6.484 | 32.8696 | 8.9517 | 6.4338 | -6.0843
TOWNLEY ST | CHADDERTON | WHITEGATE | 387242 | 405960 | 32.7932 | 14.2954 | 10.2744 | 23.979 | 32.8479 | 13.8701 | 9.9687 | 21.9807 | 32.8967 | 13.7087 | 9.8527 | 21.4746 | 32.9636 | 13.5724 | 9.7547 | 21.3783 | 33.0658 | 13.4352 | 9.6562 | 21.2718 | 33.1759 | 13.2617 | 9.5314 | 21.16 | 33.2841 | 13.1325 | 9.4386 | 21.0505 | 33.3958 | 13.0528 | 9.3813 | 20.9371 | 33.4921 | 12.9735 | 9.3243 | 20.7943 | 33.5812 | 12.9026 | 9.2733 | 20.664 | 34.191 | 12.6423 | 9.0862 | 19.9483 | 34.9201 | 12.3799 | 8.8977 | 18.7926 | 35.222 | 12.2815 | 8.827 | 17.8295 | 35.4627 | 12.2017 | 8.7696 | 16.828 | 35.5543 | 12.0079 | 8.6303 | 15.9315 | 32.7916 | 14.2954 | 10.2744 | 23.979 | 32.8343 | 14.2068 | 10.2107 | 23.7513 | 32.861 | 14.0909 | 10.1274 | 23.6146 | 32.8989 | 13.9936 | 10.0575 | 23.5276 | 32.9547 | 13.8805 | 9.9762 | 23.437 | 33.0161 | 13.7685 | 9.8957 | 23.3312 | 33.0908 | 13.5174 | 9.7153 | 22.9501 | 33.1779 | 13.4021 | 9.6324 | 22.5028 | 33.2477 | 13.3384 | 9.5865 | 22.3673 | 33.3194 | 13.2759 | 9.5416 | 22.2315 | 33.5374 | 13.0848 | 9.4043 | 21.8318 | 33.7528 | 12.9452 | 9.304 | 21.4665 | 33.9682 | 12.9358 | 9.2972 | 21.1514 | 34.2091 | 12.9684 | 9.3206 | 20.7984 | 34.4057 | 12.8165 | 9.2115 | 20.5988 | 32.7939 | 14.2954 | 10.2744 | 23.979 | 32.8505 | 13.8064 | 9.9229 | 21.6571 | 32.9006 | 13.6002 | 9.7747 | 21.0857 | 32.97 | 13.4354 | 9.6563 | 20.9894 | 33.0747 | 13.2576 | 9.5285 | 20.8838 | 33.1874 | 13.0902 | 9.4082 | 20.7734 | 33.2994 | 12.9331 | 9.2952 | 20.6645 | 33.4148 | 12.843 | 9.2305 | 20.5533 | 33.5139 | 12.7565 | 9.1684 | 20.4352 | 33.6045 | 12.6769 | 9.1111 | 20.3314 | 34.2197 | 12.3552 | 8.8799 | 19.6971 | 35.0261 | 12.0402 | 8.6535 | 18.6318 | 35.3346 | 11.8741 | 8.5342 | 17.7645 | 35.5411 | 11.8771 | 8.5363 | 16.8987 | 35.6013 | 11.6296 | 8.3584 | 16.1744 | 32.7939 | 14.2954 | 10.2744 | 23.979 | 32.7953 | 13.9446 | 10.0223 | 22.4003 | 32.8206 | 13.8694 | 9.9682 | 22.0071 | 32.8796 | 13.7628 | 9.8916 | 21.9424 | 32.9795 | 13.645 | 9.8069 | 21.8586 | 33.1028 | 13.5101 | 9.71 | 21.7477 | 33.2908 | 13.3643 | 9.6052 | 21.5728 | 33.666 | 13.2269 | 9.5064 | 21.216 | 34.0329 | 13.074 | 9.3966 | 20.8376 | 34.2474 | 12.8616 | 9.2438 | 20.4692 | 34.6349 | 13.0456 | 9.3761 | 19.4049 | 34.9654 | 12.6183 | 9.069 | 18.3612 | 35.1466 | 12.2364 | 8.7945 | 17.485 | 35.2703 | 11.9144 | 8.5631 | 16.943 | 35.2616 | 11.799 | 8.4802 | 17.3259 | 32.7932 | 14.2954 | 10.2744 | 23.979 | 32.8391 | 14.1533 | 10.1723 | 23.5954 | 32.8704 | 14.0549 | 10.1016 | 23.4412 | 32.9061 | 13.9339 | 10.0146 | 23.3878 | 32.9568 | 13.8136 | 9.9281 | 23.3425 | 33.0256 | 13.6583 | 9.8165 | 23.273 | 33.1103 | 13.5269 | 9.722 | 23.1838 | 33.2061 | 13.4541 | 9.6697 | 23.089 | 33.2978 | 13.378 | 9.615 | 22.9557 | 33.3912 | 13.3081 | 9.5648 | 22.8252 | 33.7187 | 13.1118 | 9.4237 | 22.3981 | 34.0979 | 13.0101 | 9.3506 | 21.9332 | 34.3824 | 13.054 | 9.3822 | 21.6037 | 34.6707 | 13.1747 | 9.4689 | 21.3079 | 34.8361 | 13.1598 | 9.4582 | 21.2103 | 32.7932 | 14.2954 | 10.2744 | 23.979 | 32.8098 | 13.7677 | 9.8951 | 21.4027 | 32.8584 | 13.6344 | 9.7993 | 20.7698 | 32.945 | 13.5133 | 9.7123 | 20.6557 | 33.0677 | 13.383 | 9.6186 | 20.5291 | 33.1958 | 13.2449 | 9.5194 | 20.4005 | 33.384 | 13.0993 | 9.4147 | 20.2126 | 33.7743 | 12.9555 | 9.3114 | 19.8202 | 34.1562 | 12.8003 | 9.1998 | 19.4161 | 34.3625 | 12.5841 | 9.0445 | 19.0248 | 34.756 | 12.7346 | 9.1526 | 17.9097 | 35.0951 | 12.3031 | 8.8425 | 16.8654 | 35.2618 | 11.9202 | 8.5673 | 16.0243 | 35.3641 | 11.5917 | 8.3312 | 15.4494 | 35.3529 | 11.4613 | 8.2374 | 15.7718
TRAFFORD | STRETFORD | SOUTH MANCHESTER | 380714 | 396551 | 22.046 | 7.9563 | 5.804 | 13.3274 | 22.0723 | 7.7975 | 5.6882 | 12.7716 | 22.1726 | 7.5478 | 5.506 | 11.6065 | 22.2841 | 7.3055 | 5.3293 | 10.4082 | 22.4248 | 7.0657 | 5.1543 | 9.2549 | 22.6345 | 6.7254 | 4.9061 | 8.0872 | 22.9395 | 6.3875 | 4.6596 | 7.055 | 23.3617 | 6.3171 | 4.6082 | 6.2863 | 23.8757 | 6.1255 | 4.4685 | 5.3375 | 24.4205 | 5.9224 | 4.3203 | 4.3642 | 26.0329 | 5.4026 | 3.9411 | 1.8283 | 27.3725 | 5.1443 | 3.7527 | 0.40835 | 28.0959 | 5.1046 | 3.7237 | -0.60623 | 28.6669 | 5.3079 | 3.8721 | -1.4701 | 28.803 | 5.3393 | 3.895 | -2.0559 | 22.0378 | 7.9563 | 5.804 | 13.3274 | 22.0558 | 7.8644 | 5.7369 | 13.1115 | 22.1302 | 7.8941 | 5.7586 | 12.797 | 22.1917 | 7.8418 | 5.7205 | 12.5331 | 22.252 | 7.7838 | 5.6782 | 12.3313 | 22.3347 | 7.6892 | 5.6092 | 12.1227 | 22.4432 | 7.4614 | 5.443 | 11.9582 | 22.5834 | 7.4155 | 5.4095 | 11.8889 | 22.7942 | 7.3362 | 5.3517 | 11.6301 | 23.0487 | 7.2596 | 5.2958 | 11.3547 | 24.0889 | 7.0173 | 5.119 | 10.451 | 25.3303 | 6.7931 | 4.9554 | 9.4226 | 26.383 | 6.6126 | 4.8238 | 7.9874 | 27.2763 | 6.6835 | 4.8755 | 6.4615 | 27.9055 | 6.6103 | 4.8221 | 5.4568 | 22.0494 | 7.9563 | 5.804 | 13.3274 | 22.0771 | 7.7845 | 5.6787 | 12.7392 | 22.1771 | 7.5007 | 5.4716 | 11.5691 | 22.2845 | 7.2173 | 5.2649 | 10.2217 | 22.4101 | 6.9411 | 5.0634 | 8.9261 | 22.59 | 6.5924 | 4.8091 | 7.774 | 22.8444 | 6.2111 | 4.5309 | 6.0122 | 23.1924 | 5.9573 | 4.3458 | 4.525 | 23.6051 | 5.6395 | 4.114 | 2.9243 | 24.0471 | 5.3103 | 3.8738 | 1.3051 | 25.6705 | 4.7753 | 3.4835 | -0.99219 | 27.0626 | 4.4874 | 3.2735 | -2.2818 | 27.4113 | 4.4464 | 3.2436 | -3.1591 | 28.3075 | 4.677 | 3.4118 | -3.7316 | 28.3597 | 4.7742 | 3.4827 | -3.8526 | 22.0494 | 7.9563 | 5.804 | 13.3274 | 22.069 | 7.8245 | 5.7078 | 12.8162 | 22.157 | 7.5564 | 5.5123 | 11.6784 | 22.2559 | 7.2432 | 5.2838 | 10.3432 | 22.3846 | 7.0972 | 5.1773 | 9.0537 | 22.5944 | 6.7978 | 4.9589 | 7.8872 | 22.9037 | 6.4615 | 4.7136 | 6.0519 | 23.3212 | 6.154 | 4.4892 | 4.3585 | 23.8241 | 5.7614 | 4.2029 | 2.5369 | 24.3467 | 5.558 | 4.0544 | 0.69761 | 26.0077 | 5.6664 | 4.1336 | -1.9208 | 27.3063 | 5.2633 | 3.8395 | -3.0985 | 28.0283 | 4.9826 | 3.6348 | -3.847 | 28.2591 | 4.9521 | 3.6125 | -4.1294 | 28.0772 | 4.9244 | 3.5923 | -3.6055 | 22.046 | 7.9563 | 5.804 | 13.3274 | 22.0667 | 7.8326 | 5.7138 | 12.8579 | 22.1527 | 7.6142 | 5.5545 | 11.7261 | 22.2369 | 7.3718 | 5.3776 | 10.5588 | 22.3399 | 7.137 | 5.2064 | 9.4542 | 22.5057 | 6.8079 | 4.9662 | 8.3276 | 22.7483 | 6.4488 | 4.7043 | 7.3235 | 23.0704 | 6.415 | 4.6797 | 6.5908 | 23.4917 | 6.2363 | 4.5493 | 5.6863 | 23.948 | 6.0396 | 4.4058 | 4.7538 | 25.4926 | 5.5794 | 4.0701 | 2.4559 | 26.5096 | 5.4259 | 3.9581 | 1.4239 | 27.1943 | 5.4814 | 3.9986 | 0.75045 | 27.6801 | 5.8173 | 4.2436 | 0.32395 | 27.8059 | 6.0101 | 4.3843 | 0.36409 | 22.046 | 7.9563 | 5.804 | 13.3274 | 22.0725 | 7.7758 | 5.6723 | 12.7089 | 22.1688 | 7.4863 | 5.4611 | 11.5296 | 22.2708 | 7.1836 | 5.2403 | 10.171 | 22.3894 | 7.0197 | 5.1208 | 8.8666 | 22.5608 | 6.731 | 4.9102 | 7.7075 | 22.805 | 6.389 | 4.6607 | 5.8915 | 23.1402 | 6.0829 | 4.4374 | 4.2153 | 23.5681 | 5.6959 | 4.1551 | 2.4233 | 24.0104 | 5.4944 | 4.0081 | 0.61278 | 25.6213 | 5.5883 | 4.0766 | -2.0051 | 27.1428 | 5.1633 | 3.7666 | -3.2927 | 28.1134 | 4.8567 | 3.5429 | -4.1601 | 28.5963 | 4.8089 | 3.508 | -4.5086 | 28.5696 | 4.7747 | 3.483 | -4.0016
TRAFFORD PARK NORTH | BARTON | CARRINGTON | 378738 | 397694 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 1.5327 | 2.6914 | 0.43658 | 0.31848 | -2.6444 | 2.6914 | 0.43658 | 0.31848 | -7.4649 | 2.6914 | 0.43658 | 0.31848 | -8.6549 | 2.6914 | 0.43658 | 0.31848 | -9.1118 | 2.6914 | 0.43658 | 0.31848 | -8.8975 | 31.5249 | 6.3885 | 4.6603 | -8.9749 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 23.698 | 5.4815 | 3.9987 | 2.2147 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 1.8571 | 2.6914 | 0.43658 | 0.31848 | -1.8567 | 2.6914 | 0.43658 | 0.31848 | -6.3093 | 2.6914 | 0.43658 | 0.31848 | -7.5548 | 2.6914 | 0.43658 | 0.31848 | -8.102 | 2.6914 | 0.43658 | 0.31848 | -7.9077 | 30.9537 | 6.4502 | 4.7053 | -7.8513 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 1.7759 | 2.6914 | 0.43658 | 0.31848 | -6.651 | 2.6914 | 0.43658 | 0.31848 | -6.0158 | 2.6914 | 0.43658 | 0.31848 | -5.4732 | 2.6914 | 0.43658 | 0.31848 | -4.9875 | 2.6914 | 0.43658 | 0.31848 | -5.0289 | 2.6914 | 0.43658 | 0.31848 | -5.1019 | 2.6914 | 0.43658 | 0.31848 | -6.3072 | 2.6914 | 0.43658 | 0.31848 | -7.689 | 2.6914 | 0.43658 | 0.31848 | -8.0202 | 31.3042 | 6.5388 | 4.77 | -7.725 | 30.8705 | 6.5005 | 4.742 | -7.6476 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 1.6502 | 2.6914 | 0.43658 | 0.31848 | -2.3566 | 2.6914 | 0.43658 | 0.31848 | -7.0506 | 2.6914 | 0.43658 | 0.31848 | -8.2988 | 2.6914 | 0.43658 | 0.31848 | -8.8686 | 2.6914 | 0.43658 | 0.31848 | -8.7334 | 31.213 | 6.5516 | 4.7793 | -8.8189 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 1.7547 | 2.6914 | 0.43658 | 0.31848 | -6.6755 | 2.6914 | 0.43658 | 0.31848 | -6.0335 | 2.6914 | 0.43658 | 0.31848 | -5.4775 | 2.6914 | 0.43658 | 0.31848 | -4.9737 | 2.6914 | 0.43658 | 0.31848 | -4.9959 | 2.6914 | 0.43658 | 0.31848 | -5.0505 | 2.6914 | 0.43658 | 0.31848 | -6.0853 | 2.6914 | 0.43658 | 0.31848 | -7.6189 | 2.6914 | 0.43658 | 0.31848 | -8.1199 | 31.4011 | 6.4521 | 4.7067 | -7.9266 | 30.9756 | 6.4052 | 4.6725 | -7.8709
TRIMPELL | - | HEYSHAM | 341861 | 458979 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 1.6795 | 0.44197 | 0.31765 | 1.6795
TRINITY | FREDERICK RD | KEARSLEY | 382649 | 398230 | -11.1725 | -1.8123 | -1.322 | -11.1725 | -16.3693 | -2.6553 | -1.937 | -16.3693 | -20.4217 | -3.3126 | -2.4165 | -20.4217 | -21.4574 | -3.4806 | -2.5391 | -21.4574 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.1334 | 0.43658 | 0.31848 | 2.1334 | 1.3017 | 0.43658 | 0.31848 | 1.3017 | -11.1725 | -1.8123 | -1.322 | -11.1725 | -13.1818 | -2.1382 | -1.5598 | -13.1818 | -14.0933 | -2.2861 | -1.6677 | -14.0933 | -14.8554 | -2.4097 | -1.7578 | -14.8554 | -15.7158 | -2.5493 | -1.8596 | -15.7158 | -16.6558 | -2.7017 | -1.9709 | -16.6558 | -18.4928 | -2.9997 | -2.1882 | -18.4928 | -19.0276 | -3.0865 | -2.2515 | -19.0276 | -19.7069 | -3.1966 | -2.3319 | -19.7069 | -20.4423 | -3.3159 | -2.4189 | -20.4423 | -22.9644 | -3.725 | -2.7174 | -22.9644 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | -11.1725 | -1.8123 | -1.322 | -11.1725 | -17.2248 | -2.794 | -2.0382 | -17.2248 | -20.5186 | -3.3283 | -2.428 | -20.5186 | -22.5405 | -3.6563 | -2.6672 | -22.5405 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.4801 | 0.43658 | 0.31848 | 2.4801 | 1.4205 | 0.43658 | 0.31848 | 1.4205 | 0.59401 | 0.22546 | 0.18422 | 0.59401 | -0.16761 | -0.063618 | -0.051982 | -0.16761 | -0.95404 | -0.36212 | -0.29589 | -0.95404 | -11.1725 | -1.8123 | -1.322 | -11.1725 | -15.6026 | -2.5309 | -1.8463 | -15.6026 | -18.1224 | -2.9396 | -2.1444 | -18.1224 | -20.1368 | -3.2664 | -2.3828 | -20.1368 | -22.2029 | -3.6015 | -2.6273 | -22.2029 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 1.7946 | 0.43658 | 0.31848 | 1.7946 | 0.89057 | 0.33803 | 0.2762 | 0.89057 | 0.15408 | 0.058481 | 0.047785 | 0.15408 | -0.57556 | -0.21846 | -0.1785 | -0.57556 | -11.1725 | -1.8123 | -1.322 | -11.1725 | -14.5502 | -2.3602 | -1.7217 | -14.5502 | -17.6913 | -2.8697 | -2.0934 | -17.6913 | -19.3238 | -3.1345 | -2.2866 | -19.3238 | -21.4989 | -3.4873 | -2.544 | -21.4989 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | -11.1725 | -1.8123 | -1.322 | -11.1725 | -17.8507 | -2.8956 | -2.1123 | -17.8507 | -20.7163 | -3.3604 | -2.4514 | -20.7163 | -22.8351 | -3.7041 | -2.7021 | -22.8351 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 2.6914 | 0.43658 | 0.31848 | 2.6914 | 1.7713 | 0.43658 | 0.31848 | 1.7713 | 0.52247 | 0.19831 | 0.16204 | 0.52247 | -0.43942 | -0.16679 | -0.13628 | -0.43942 | -1.2462 | -0.47303 | -0.38651 | -1.2462 | -2.0586 | -0.78138 | -0.63847 | -2.0586 | Switchgear to be replaced in RIIO-ED2
TULKETH | RIBBLE | PENWORTHAM EAST / ROCHDALE | 352393 | 431036 | 30.006 | 9.7997 | 7.1487 | 13.8089 | 30.0932 | 9.4809 | 6.9162 | 12.4479 | 30.2041 | 9.3464 | 6.8181 | 12.0873 | 30.3473 | 9.2481 | 6.7463 | 11.9271 | 30.5275 | 9.123 | 6.6551 | 11.6416 | 30.7364 | 8.8807 | 6.4783 | 11.3507 | 30.9787 | 8.7246 | 6.3645 | 11.1086 | 31.229 | 8.5836 | 6.2616 | 10.9074 | 31.3825 | 8.4428 | 6.1589 | 10.6702 | 31.5276 | 8.2956 | 6.0515 | 10.4731 | 32.0226 | 7.6176 | 5.5569 | 8.3237 | 32.5863 | 6.6904 | 4.8806 | 4.0964 | 33.0081 | 5.9873 | 4.3677 | 0.49945 | 31.186 | 5.0587 | 3.6902 | -3.3302 | 26.1101 | 4.2353 | 3.0896 | -6.6268 | 29.9813 | 9.7997 | 7.1487 | 13.8089 | 30.0407 | 9.6597 | 7.0466 | 13.3063 | 30.0977 | 9.4533 | 6.896 | 13.1012 | 30.1738 | 9.2571 | 6.7529 | 12.9376 | 30.2814 | 9.0878 | 6.6294 | 12.7103 | 30.4186 | 9.1163 | 6.6502 | 12.4712 | 30.5856 | 8.8574 | 6.4614 | 12.1592 | 30.7768 | 8.7622 | 6.3919 | 11.7708 | 30.9013 | 8.685 | 6.3356 | 11.4631 | 31.0323 | 8.5957 | 6.2704 | 11.154 | 31.4585 | 8.2844 | 6.0434 | 10.2421 | 31.8895 | 8.0589 | 5.8788 | 9.375 | 32.2599 | 7.7874 | 5.6808 | 8.517 | 32.6082 | 7.4684 | 5.4481 | 7.6646 | 32.7598 | 7.2048 | 5.2558 | 7.1472 | 30.0164 | 9.7997 | 7.1487 | 13.8089 | 30.1077 | 9.4299 | 6.879 | 12.2697 | 30.2303 | 9.2517 | 6.749 | 11.9052 | 30.3922 | 9.1306 | 6.6606 | 11.7958 | 30.5955 | 8.9477 | 6.5273 | 11.5651 | 30.8316 | 8.7346 | 6.3717 | 11.3384 | 31.095 | 8.5379 | 6.2283 | 11.185 | 31.3212 | 8.3838 | 6.1159 | 11.0803 | 31.4843 | 8.2425 | 6.0128 | 10.9497 | 31.6389 | 8.0743 | 5.8901 | 10.841 | 32.175 | 7.353 | 5.3639 | 8.9555 | 32.7839 | 6.5015 | 4.7427 | 4.9547 | 33.2388 | 5.6344 | 4.1102 | 1.5534 | 28.8699 | 4.683 | 3.4162 | -2.0519 | 23.6144 | 3.8305 | 2.7943 | -5.0996 | 30.0165 | 9.7997 | 7.1487 | 13.8089 | 30.0124 | 9.5821 | 6.99 | 12.9848 | 30.0665 | 9.4818 | 6.9168 | 12.7904 | 30.1502 | 9.3603 | 6.8282 | 12.7133 | 30.2841 | 9.218 | 6.7244 | 12.4797 | 30.4924 | 9.01 | 6.5726 | 12.211 | 30.7556 | 8.7906 | 6.4126 | 11.722 | 30.9823 | 8.4541 | 6.1671 | 10.3739 | 31.1759 | 8.0935 | 5.9041 | 8.9745 | 31.3652 | 7.6643 | 5.591 | 7.5937 | 31.9338 | 6.7421 | 4.9183 | 3.6222 | 32.5046 | 5.7107 | 4.1659 | -0.16626 | 30.5248 | 4.9514 | 3.612 | -3.2784 | 25.9212 | 4.2047 | 3.0673 | -5.2305 | 25.9514 | 4.2096 | 3.0708 | -3.6491 | 30.006 | 9.7997 | 7.1487 | 13.8089 | 30.0753 | 9.591 | 6.9965 | 12.982 | 30.1452 | 9.4927 | 6.9248 | 12.7679 | 30.2258 | 9.4102 | 6.8646 | 12.7132 | 30.3364 | 9.3325 | 6.8079 | 12.6311 | 30.5102 | 9.1273 | 6.6583 | 12.5234 | 30.741 | 8.9952 | 6.5619 | 12.3979 | 30.9976 | 8.87 | 6.4706 | 12.2617 | 31.1727 | 8.7265 | 6.3658 | 12.0388 | 31.3037 | 8.5771 | 6.2568 | 11.8227 | 31.7278 | 8.1454 | 5.942 | 11.0339 | 32.1718 | 7.761 | 5.6616 | 9.9951 | 32.4956 | 7.5939 | 5.5396 | 9.2463 | 32.7809 | 7.244 | 5.2844 | 8.5062 | 32.9176 | 6.8924 | 5.0279 | 8.2467 | 30.006 | 9.7997 | 7.1487 | 13.8089 | 30.0277 | 9.4444 | 6.8895 | 12.2949 | 30.1268 | 9.2907 | 6.7774 | 11.8873 | 30.2651 | 9.151 | 6.6755 | 11.6905 | 30.4419 | 8.9748 | 6.547 | 11.3498 | 30.6433 | 8.7595 | 6.3899 | 11.0129 | 30.8896 | 8.5234 | 6.2177 | 10.4418 | 31.2021 | 8.1663 | 5.9572 | 8.9729 | 31.4058 | 7.789 | 5.682 | 7.4832 | 31.6036 | 7.3454 | 5.3584 | 6.0113 | 32.1842 | 6.3615 | 4.6407 | 1.7578 | 32.7044 | 5.305 | 3.8699 | -2.2817 | 27.497 | 4.4603 | 3.2537 | -5.6579 | 22.4115 | 3.6354 | 2.652 | -7.9646 | 22.0748 | 3.5807 | 2.6121 | -6.7968
ULVERSTON | ULVERSTON | HARKER / HUTTON | 327495 | 477808 | 15.057 | 10.9945 | 7.9019 | 8.5903 | 15.1655 | 10.7905 | 7.7554 | 8.153 | 15.3153 | 10.6012 | 7.6193 | 7.8476 | 15.4617 | 10.4452 | 7.5072 | 7.6175 | 15.6345 | 10.2775 | 7.3867 | 7.2525 | 15.8223 | 10.1389 | 7.287 | 6.8874 | 16.0064 | 9.9972 | 7.1852 | 6.5644 | 16.201 | 9.8731 | 7.096 | 6.2655 | 16.3481 | 9.7333 | 6.9955 | 5.9355 | 16.4897 | 9.5892 | 6.8919 | 5.6262 | 16.942 | 8.9673 | 6.445 | 3.7753 | 17.4117 | 8.2641 | 5.9396 | 0.68698 | 17.7465 | 7.576 | 5.445 | -2.0018 | 18.0222 | 6.8736 | 4.9402 | -4.7446 | 18.1953 | 6.2598 | 4.499 | -7.1306 | 15.0615 | 10.9945 | 7.9019 | 8.5903 | 15.1891 | 10.9315 | 7.8567 | 8.3749 | 15.2756 | 10.8269 | 7.7815 | 8.1485 | 15.3381 | 10.7285 | 7.7108 | 7.9467 | 15.4184 | 10.5939 | 7.6141 | 7.7263 | 15.4992 | 10.4533 | 7.513 | 7.4986 | 15.6025 | 10.2145 | 7.3413 | 7.2204 | 15.7403 | 10.0413 | 7.2169 | 6.875 | 15.832 | 9.8922 | 7.1097 | 6.6286 | 15.9258 | 9.7662 | 7.0192 | 6.3843 | 16.2148 | 9.3957 | 6.7529 | 5.6714 | 16.509 | 9.1133 | 6.5499 | 4.9887 | 16.8289 | 8.8629 | 6.3699 | 4.3183 | 17.0721 | 8.6151 | 6.1919 | 3.5518 | 17.2191 | 8.4083 | 6.0432 | 2.9353 | 15.0555 | 10.9945 | 7.9019 | 8.5903 | 15.1635 | 10.7564 | 7.7308 | 8.1154 | 15.3112 | 10.5285 | 7.567 | 7.8153 | 15.4907 | 10.3692 | 7.4526 | 7.6144 | 15.6779 | 10.1965 | 7.3285 | 7.2761 | 15.8829 | 10.0355 | 7.2127 | 6.9415 | 16.0881 | 9.8781 | 7.0996 | 6.6612 | 16.31 | 9.7136 | 6.9814 | 6.4096 | 16.4787 | 9.5446 | 6.8599 | 6.1597 | 16.6363 | 9.2877 | 6.6753 | 5.91 | 17.1507 | 8.7986 | 6.3237 | 4.243 | 17.6705 | 7.9897 | 5.7423 | 1.3292 | 18.039 | 7.229 | 5.1957 | -1.1968 | 18.3113 | 6.4642 | 4.6459 | -3.7356 | 18.4556 | 5.8308 | 4.1907 | -5.8784 | 15.0555 | 10.9945 | 7.9019 | 8.5903 | 15.0691 | 10.8145 | 7.7726 | 8.3592 | 15.1257 | 10.6319 | 7.6414 | 8.129 | 15.2088 | 10.4711 | 7.5258 | 7.932 | 15.3271 | 10.3059 | 7.407 | 7.5928 | 15.5021 | 10.1306 | 7.2811 | 7.2415 | 15.7049 | 9.8271 | 7.0629 | 6.7648 | 15.9266 | 9.3543 | 6.7231 | 5.7733 | 16.1376 | 8.8947 | 6.3928 | 4.7554 | 16.3432 | 8.4133 | 6.0468 | 3.7395 | 16.9117 | 7.4254 | 5.3368 | 0.81258 | 17.4082 | 6.6443 | 4.7754 | -1.9862 | 17.7561 | 5.9148 | 4.2511 | -4.3339 | 18.0054 | 5.4341 | 3.9056 | -5.8633 | 18.0013 | 5.2959 | 3.8063 | -5.259 | 15.057 | 10.9945 | 7.9019 | 8.5903 | 15.1488 | 10.8499 | 7.798 | 8.3369 | 15.2508 | 10.6711 | 7.6695 | 8.0849 | 15.3691 | 10.5206 | 7.5614 | 7.9011 | 15.5018 | 10.3766 | 7.4579 | 7.6437 | 15.6272 | 10.2631 | 7.3763 | 7.3825 | 15.7758 | 10.1334 | 7.283 | 7.1172 | 15.9462 | 10.0163 | 7.1989 | 6.8377 | 16.0941 | 9.8749 | 7.0973 | 6.4959 | 16.2442 | 9.7238 | 6.9887 | 6.1563 | 16.7372 | 9.2608 | 6.6559 | 5.0458 | 17.1604 | 8.9501 | 6.4326 | 3.8352 | 17.4618 | 8.6231 | 6.1976 | 2.8611 | 17.7085 | 8.3187 | 5.9788 | 2.0107 | 17.8193 | 8.0949 | 5.818 | 1.4932 | 15.057 | 10.9945 | 7.9019 | 8.5903 | 15.1355 | 10.7557 | 7.7303 | 8.1485 | 15.2814 | 10.5559 | 7.5867 | 7.8269 | 15.4661 | 10.3823 | 7.4619 | 7.5581 | 15.6637 | 10.2023 | 7.3326 | 7.1507 | 15.8473 | 10.0156 | 7.1984 | 6.7484 | 16.004 | 9.6873 | 6.9624 | 6.2136 | 16.2189 | 9.2032 | 6.6145 | 5.1421 | 16.3947 | 8.7345 | 6.2776 | 4.0773 | 16.5638 | 8.2458 | 5.9264 | 3.0147 | 17.057 | 7.2217 | 5.1904 | -0.054744 | 17.513 | 6.4071 | 4.6049 | -2.9851 | 17.833 | 5.6451 | 4.0573 | -5.4737 | 18.0485 | 5.1223 | 3.6815 | -7.1943 | 18.0746 | 4.9377 | 3.5488 | -6.815
UNION RD | BOLTON | KEARSLEY | 372174 | 410598 | 31.1247 | 10.2812 | 7.5 | 12.3364 | 31.3461 | 10.1334 | 7.3922 | 12.0874 | 31.558 | 9.7724 | 7.1288 | 11.7818 | 31.8157 | 9.3976 | 6.8554 | 11.4826 | 32.1517 | 8.9902 | 6.5582 | 11.1002 | 32.539 | 8.5741 | 6.2547 | 10.6937 | 32.954 | 8.1679 | 5.9584 | 10.2916 | 33.911 | 7.8785 | 5.7472 | 9.3619 | 34.3267 | 7.6494 | 5.5801 | 8.923 | 34.7513 | 7.5188 | 5.4849 | 8.487 | 35.8361 | 6.9902 | 5.0993 | 6.0742 | 36.6955 | 6.1475 | 4.4845 | 2.3937 | 33.634 | 5.4558 | 3.9799 | -0.83925 | 29.5937 | 4.8004 | 3.5018 | -3.2221 | 25.9709 | 4.2127 | 3.0731 | -4.9285 | 31.0979 | 10.2812 | 7.5 | 12.3364 | 31.2467 | 10.1822 | 7.4278 | 12.1676 | 31.3573 | 10.1072 | 7.373 | 11.9676 | 31.4907 | 9.9908 | 7.2881 | 11.7837 | 31.6641 | 9.8508 | 7.1861 | 11.5685 | 31.8639 | 9.6974 | 7.0741 | 11.3309 | 32.1102 | 9.4297 | 6.8789 | 11.0297 | 32.4142 | 9.2714 | 6.7634 | 10.6458 | 32.6403 | 9.134 | 6.6631 | 10.3296 | 32.8973 | 8.9939 | 6.5609 | 9.9787 | 33.8429 | 8.5424 | 6.2316 | 8.6737 | 34.9577 | 8.0993 | 5.9083 | 7.0439 | 36.2292 | 7.5637 | 5.5176 | 5.0203 | 36.8573 | 7.1376 | 5.2067 | 3.4566 | 37.6855 | 6.6961 | 4.8847 | 1.8666 | 31.1326 | 10.2812 | 7.5 | 12.3364 | 31.3821 | 10.0848 | 7.3567 | 11.9824 | 31.6409 | 9.63 | 7.025 | 11.5636 | 31.952 | 9.1558 | 6.679 | 11.1374 | 32.3427 | 8.6842 | 6.335 | 10.6215 | 33.2274 | 8.0899 | 5.9015 | 9.4912 | 33.5727 | 7.5687 | 5.5213 | 8.9397 | 33.9886 | 7.4946 | 5.4672 | 8.3731 | 34.3985 | 7.3371 | 5.3523 | 7.7881 | 34.7513 | 7.1409 | 5.2092 | 7.1952 | 36.8444 | 6.2129 | 4.5322 | 3.6898 | 32.7911 | 5.319 | 3.8802 | 0.24003 | 28.0516 | 4.5502 | 3.3193 | -2.3971 | 23.2854 | 3.7771 | 2.7554 | -4.7196 | 19.2789 | 3.1272 | 2.2813 | -6.195 | 31.1328 | 10.2812 | 7.5 | 12.3364 | 31.2975 | 10.1549 | 7.4079 | 12.2454 | 31.5138 | 9.7631 | 7.122 | 11.928 | 33.0914 | 9.0824 | 6.6255 | 10.2684 | 33.9505 | 8.501 | 6.2013 | 9.2832 | 34.1652 | 7.9905 | 5.829 | 8.8329 | 34.478 | 7.7091 | 5.6237 | 8.22 | 34.8994 | 7.4231 | 5.415 | 7.1958 | 35.3756 | 7.1762 | 5.2349 | 6.122 | 35.8729 | 6.8858 | 5.0231 | 5.0712 | 36.8013 | 5.9954 | 4.3736 | 1.5798 | 31.4117 | 5.0953 | 3.7169 | -1.526 | 27.173 | 4.4077 | 3.2154 | -3.3879 | 23.3872 | 3.7936 | 2.7674 | -4.4605 | 21.2524 | 3.4474 | 2.5148 | -4.3318 | 31.1242 | 10.2812 | 7.5 | 12.3364 | 31.3094 | 10.1617 | 7.4128 | 12.1143 | 31.477 | 9.8237 | 7.1662 | 11.853 | 31.6627 | 9.4691 | 6.9076 | 11.6368 | 31.8923 | 9.094 | 6.634 | 11.4008 | 32.1798 | 8.704 | 6.3495 | 11.1207 | 32.5305 | 8.3174 | 6.0674 | 10.7955 | 33.4478 | 8.0441 | 5.868 | 9.9137 | 33.7764 | 7.8302 | 5.712 | 9.4962 | 34.1384 | 7.6087 | 5.5504 | 9.0412 | 35.2447 | 7.299 | 5.3245 | 7.5658 | 36.1564 | 6.7665 | 4.9361 | 5.6704 | 37.2402 | 6.3758 | 4.6511 | 3.5933 | 36.6136 | 5.9391 | 4.3325 | 2.1421 | 34.004 | 5.5158 | 4.0237 | 1.1397 | 31.1242 | 10.2812 | 7.5 | 12.3364 | 31.2948 | 10.1191 | 7.3817 | 12.1894 | 31.5353 | 9.7013 | 7.0769 | 11.793 | 33.141 | 9.0008 | 6.5659 | 10.0426 | 34.0201 | 8.405 | 6.1313 | 8.9903 | 34.2083 | 7.9165 | 5.775 | 8.5114 | 34.4717 | 7.6086 | 5.5504 | 7.8809 | 34.861 | 7.3076 | 5.3308 | 6.7968 | 35.2939 | 7.0453 | 5.1394 | 5.6789 | 35.7591 | 6.7427 | 4.9187 | 4.588 | 35.5844 | 5.7721 | 4.2107 | 0.7063 | 29.6408 | 4.808 | 3.5074 | -2.6856 | 25.0765 | 4.0677 | 2.9673 | -4.8325 | 20.9603 | 3.4 | 2.4802 | -6.207 | 18.5812 | 3.0141 | 2.1987 | -6.2729
UPHOLLAND | ORRELL | WASHWAY FARM / KIRKBY | 352531 | 404369 | 22.9865 | 11.7069 | 8.414 | 7.8154 | 23.0875 | 11.5837 | 8.3254 | 7.5305 | 23.235 | 11.4734 | 8.2461 | 7.3892 | 23.4254 | 11.3669 | 8.1696 | 7.2954 | 23.6072 | 11.1823 | 8.0369 | 7.118 | 23.8007 | 10.9886 | 7.8977 | 6.9353 | 24.0213 | 10.7904 | 7.7553 | 6.7756 | 24.2914 | 10.5873 | 7.6093 | 6.6262 | 24.5083 | 10.3933 | 7.4699 | 6.4118 | 24.7005 | 10.3174 | 7.4153 | 6.2293 | 25.2477 | 9.7675 | 7.0201 | 4.4856 | 25.8473 | 9.0402 | 6.4974 | 1.2585 | 26.3086 | 8.4553 | 6.077 | -1.4911 | 26.6792 | 8.0607 | 5.7934 | -4.512 | 26.9274 | 7.5439 | 5.4219 | -7.1604 | 22.9509 | 11.7069 | 8.414 | 7.8154 | 23.015 | 11.651 | 8.3738 | 7.6527 | 23.073 | 11.5835 | 8.3253 | 7.5372 | 23.1518 | 11.5074 | 8.2706 | 7.4204 | 23.2669 | 11.4086 | 8.1996 | 7.244 | 23.4169 | 11.3018 | 8.1228 | 7.0368 | 23.594 | 11.0106 | 7.9135 | 6.7593 | 23.7628 | 10.8903 | 7.8271 | 6.4045 | 23.8871 | 10.7855 | 7.7518 | 6.0956 | 24.0099 | 10.6813 | 7.6768 | 5.785 | 24.3867 | 10.3861 | 7.4647 | 4.8644 | 24.7503 | 10.1882 | 7.3225 | 3.8523 | 25.0785 | 9.9406 | 7.1445 | 2.8518 | 25.4134 | 9.8715 | 7.0949 | 1.8317 | 25.6591 | 9.8208 | 7.0584 | 1.1767 | 23.0016 | 11.7069 | 8.414 | 7.8154 | 23.1165 | 11.561 | 8.3091 | 7.5262 | 23.2872 | 11.4147 | 8.204 | 7.4115 | 23.494 | 11.2715 | 8.101 | 7.3702 | 23.6912 | 11.0772 | 7.9614 | 7.2504 | 23.9181 | 10.8664 | 7.8099 | 7.1352 | 24.1795 | 10.653 | 7.6566 | 7.0688 | 24.4995 | 10.4084 | 7.4807 | 7.0213 | 24.7005 | 10.2856 | 7.3924 | 6.9153 | 24.8662 | 10.1877 | 7.3221 | 6.8256 | 25.3821 | 9.4983 | 6.8266 | 5.1716 | 25.997 | 8.7372 | 6.2796 | 2.129 | 26.4606 | 8.1122 | 5.8304 | -0.40174 | 26.8827 | 7.7055 | 5.5381 | -3.0396 | 27.1705 | 7.2165 | 5.1867 | -5.2253 | 23.0016 | 11.7069 | 8.414 | 7.8154 | 23.0027 | 11.6337 | 8.3613 | 7.91 | 23.0811 | 11.524 | 8.2825 | 7.903 | 23.1952 | 11.4416 | 8.2233 | 7.8841 | 23.3677 | 11.1955 | 8.0464 | 7.7628 | 23.567 | 10.9117 | 7.8424 | 7.6131 | 23.83 | 10.487 | 7.5372 | 7.2951 | 24.1799 | 9.9037 | 7.118 | 6.3554 | 24.4656 | 9.3682 | 6.7331 | 5.3617 | 24.6493 | 8.9074 | 6.4019 | 4.3808 | 25.2073 | 8.2702 | 5.944 | 1.5415 | 25.7871 | 7.628 | 5.4824 | -1.274 | 26.2042 | 7.0039 | 5.0338 | -3.6052 | 26.5205 | 6.6236 | 4.7605 | -5.1557 | 26.5591 | 6.514 | 4.6817 | -4.1852 | 22.9865 | 11.7069 | 8.414 | 7.8154 | 23.0712 | 11.6237 | 8.3542 | 7.6438 | 23.167 | 11.5314 | 8.2878 | 7.5705 | 23.2772 | 11.4416 | 8.2233 | 7.557 | 23.4256 | 11.2846 | 8.1105 | 7.5164 | 23.5947 | 11.1114 | 7.986 | 7.4379 | 23.813 | 10.9188 | 7.8475 | 7.3176 | 24.0582 | 10.713 | 7.6996 | 7.147 | 24.2567 | 10.5065 | 7.5512 | 6.8744 | 24.4535 | 10.4204 | 7.4894 | 6.6057 | 25.0415 | 10.0094 | 7.194 | 5.6412 | 25.5333 | 9.5762 | 6.8826 | 4.1139 | 25.8843 | 9.2827 | 6.6716 | 2.9981 | 26.196 | 9.2778 | 6.6681 | 1.9795 | 26.3176 | 9.1748 | 6.5941 | 1.6038 | 22.9865 | 11.7069 | 8.414 | 7.8154 | 23.03 | 11.5895 | 8.3296 | 7.7483 | 23.1677 | 11.4568 | 8.2343 | 7.6194 | 23.3576 | 11.3519 | 8.1589 | 7.4822 | 23.5456 | 11.0891 | 7.97 | 7.2537 | 23.7414 | 10.7988 | 7.7613 | 7.0329 | 23.9859 | 10.3499 | 7.4386 | 6.6276 | 24.3533 | 9.7487 | 7.0066 | 5.5645 | 24.6622 | 9.1981 | 6.6108 | 4.4748 | 24.861 | 8.6999 | 6.2528 | 3.3994 | 25.4283 | 8.0261 | 5.7685 | 0.24105 | 25.9614 | 7.3363 | 5.2727 | -2.8244 | 26.3439 | 6.6718 | 4.7951 | -5.3714 | 26.6149 | 6.2476 | 4.4903 | -7.1769 | 26.651 | 6.0833 | 4.3722 | -6.4915
URMSTON | STRETFORD | SOUTH MANCHESTER | 377117 | 395709 | 29.3243 | 8.0642 | 5.8827 | 16.6833 | 29.3666 | 7.9635 | 5.8093 | 16.4238 | 29.4253 | 7.8639 | 5.7366 | 16.3809 | 29.4842 | 7.7765 | 5.6729 | 16.2976 | 29.5537 | 7.6869 | 5.6075 | 16.1437 | 29.6355 | 7.5332 | 5.4953 | 15.971 | 29.7332 | 7.3826 | 5.3855 | 15.797 | 29.8531 | 7.2526 | 5.2906 | 15.6278 | 29.9493 | 7.1035 | 5.1819 | 15.4378 | 30.0389 | 6.9672 | 5.0824 | 15.2742 | 30.3419 | 6.5294 | 4.7631 | 13.8641 | 30.6937 | 6.1297 | 4.4715 | 11.2075 | 30.9619 | 5.9167 | 4.3161 | 8.921 | 31.2164 | 6.339 | 4.6242 | 6.3843 | 31.4016 | 6.0587 | 4.4197 | 4.0881 | 29.3121 | 8.0642 | 5.8827 | 16.6833 | 29.3525 | 8.0248 | 5.854 | 16.4887 | 29.3966 | 7.9733 | 5.8164 | 16.4553 | 29.4498 | 7.8879 | 5.7541 | 16.3582 | 29.5234 | 7.7672 | 5.6661 | 16.211 | 29.6186 | 7.7032 | 5.6193 | 16.04 | 29.7346 | 7.4685 | 5.4482 | 15.8122 | 29.8621 | 7.3805 | 5.384 | 15.5247 | 29.9288 | 7.2959 | 5.3223 | 15.2904 | 29.9968 | 7.235 | 5.2778 | 15.0528 | 30.2025 | 7.0322 | 5.1299 | 14.3367 | 30.3982 | 6.8689 | 5.0107 | 13.624 | 30.5677 | 6.8212 | 4.9759 | 12.9138 | 30.7353 | 7.2436 | 5.2841 | 12.1156 | 30.8571 | 7.5076 | 5.4767 | 11.5076 | 29.3293 | 8.0642 | 5.8827 | 16.6833 | 29.3765 | 7.9434 | 5.7946 | 16.4215 | 29.4416 | 7.8202 | 5.7047 | 16.3931 | 29.5048 | 7.704 | 5.62 | 16.3387 | 29.5839 | 7.6155 | 5.5554 | 16.2151 | 29.6772 | 7.4294 | 5.4196 | 16.0772 | 29.7899 | 7.2806 | 5.3111 | 15.9559 | 29.9271 | 7.14 | 5.2085 | 15.8393 | 30.0312 | 6.977 | 5.0896 | 15.7112 | 30.1272 | 6.8034 | 4.963 | 15.5998 | 30.4491 | 6.4301 | 4.6907 | 14.3581 | 30.8136 | 5.9468 | 4.3381 | 11.8438 | 31.0861 | 5.672 | 4.1376 | 9.685 | 31.3357 | 6.1468 | 4.484 | 7.2993 | 31.5046 | 5.8448 | 4.2637 | 5.1733 | 29.3293 | 8.0642 | 5.8827 | 16.6833 | 29.2926 | 8.014 | 5.8461 | 16.7422 | 29.3095 | 7.9551 | 5.8031 | 16.8048 | 29.3317 | 7.8585 | 5.7327 | 16.7771 | 29.3717 | 7.8119 | 5.6987 | 16.6526 | 29.4447 | 7.6932 | 5.6121 | 16.4846 | 29.5467 | 7.547 | 5.5054 | 16.1709 | 29.6779 | 7.4058 | 5.4024 | 15.3701 | 29.7891 | 7.2433 | 5.2839 | 14.5429 | 29.8971 | 7.0994 | 5.1789 | 13.7222 | 30.2259 | 7.5815 | 5.5306 | 11.3192 | 30.5722 | 6.9578 | 5.0756 | 8.9258 | 30.827 | 6.359 | 4.6388 | 6.9442 | 31.0231 | 6.1741 | 4.5039 | 5.5615 | 31.0408 | 6.1159 | 4.4615 | 6.1459 | 29.3243 | 8.0642 | 5.8827 | 16.6833 | 29.3591 | 8.0061 | 5.8403 | 16.4884 | 29.3951 | 7.9233 | 5.7799 | 16.4982 | 29.4287 | 7.8514 | 5.7275 | 16.4879 | 29.468 | 7.7807 | 5.6759 | 16.4466 | 29.5391 | 7.6513 | 5.5815 | 16.3626 | 29.6383 | 7.5052 | 5.4749 | 16.2463 | 29.7465 | 7.3888 | 5.39 | 16.1196 | 29.8314 | 7.2409 | 5.2821 | 15.9438 | 29.9143 | 7.1018 | 5.1807 | 15.7752 | 30.1793 | 6.7997 | 4.9603 | 15.1392 | 30.4654 | 6.7297 | 4.9092 | 14.3379 | 30.6777 | 6.8228 | 4.9772 | 13.7497 | 30.8759 | 7.6197 | 5.5585 | 13.1315 | 30.9893 | 7.7013 | 5.618 | 12.7394 | 29.3243 | 8.0642 | 5.8827 | 16.6833 | 29.3111 | 7.9655 | 5.8107 | 16.6333 | 29.3623 | 7.8871 | 5.7535 | 16.6064 | 29.4182 | 7.7703 | 5.6683 | 16.4893 | 29.4897 | 7.7067 | 5.6219 | 16.2851 | 29.5714 | 7.5778 | 5.5279 | 16.0708 | 29.6752 | 7.4266 | 5.4176 | 15.7001 | 29.8274 | 7.2678 | 5.3018 | 14.8145 | 29.9519 | 7.0951 | 5.1758 | 13.9218 | 30.0707 | 6.941 | 5.0634 | 13.0367 | 30.411 | 7.3878 | 5.3893 | 10.4512 | 30.7355 | 6.7341 | 4.9124 | 7.9353 | 30.974 | 6.0994 | 4.4494 | 5.8329 | 31.1487 | 5.8898 | 4.2966 | 4.2983 | 31.1706 | 5.8015 | 4.2321 | 4.692
VICTORIA PARK | LONGSIGHT | BREDBURY | 385373 | 395948 | 26.5791 | 14.6052 | 10.6543 | 12.9879 | 26.5861 | 14.2084 | 10.3648 | 11.6335 | 26.6521 | 11.606 | 8.4664 | 11.1712 | 26.6872 | 9.0189 | 6.5792 | 11.078 | 26.6992 | 6.3929 | 4.6636 | 11.058 | 22.6177 | 3.6688 | 2.6763 | 11.0498 | 6.1158 | 0.99204 | 0.72368 | 6.1158 | 5.5716 | 0.90377 | 0.65928 | 5.5716 | 4.9904 | 0.80949 | 0.59051 | 4.9904 | 4.9944 | 0.81014 | 0.59099 | 4.9944 | 5.6729 | 0.9202 | 0.67127 | 5.6729 | 10.9821 | 1.7814 | 1.2995 | 10.2011 | 25.6123 | 4.1546 | 3.0307 | 9.833 | 27.0104 | 9.5125 | 6.9392 | 9.5288 | 26.9382 | 12.9927 | 9.478 | 9.3886 | 26.5766 | 14.6052 | 10.6543 | 12.9879 | 26.5831 | 14.4975 | 10.5757 | 12.5815 | 26.6459 | 11.8016 | 8.6091 | 12.2961 | 26.6777 | 9.2658 | 6.7593 | 12.1757 | 26.6882 | 6.6766 | 4.8705 | 12.1169 | 24.9708 | 4.0505 | 2.9548 | 12.0537 | 7.6858 | 1.2467 | 0.90945 | 7.6858 | 7.3764 | 1.1965 | 0.87285 | 7.3764 | 6.9979 | 1.1351 | 0.82807 | 6.9979 | 6.682 | 1.0839 | 0.79068 | 6.682 | 5.7824 | 0.93796 | 0.68423 | 5.7824 | 5.4 | 0.87593 | 0.63898 | 5.4 | 14.2506 | 2.3116 | 1.6863 | 10.4979 | 27.3169 | 6.4915 | 4.7354 | 10.2329 | 27.386 | 9.1255 | 6.6569 | 10.0495 | 26.5801 | 14.6052 | 10.6543 | 12.9879 | 26.591 | 14.1482 | 10.3209 | 11.4075 | 26.6591 | 11.5258 | 8.4079 | 10.7782 | 26.6995 | 8.892 | 6.4866 | 10.56 | 26.7153 | 6.2278 | 4.5431 | 10.4174 | 21.4616 | 3.4813 | 2.5395 | 10.2873 | 4.8255 | 0.78275 | 0.571 | 4.8255 | 4.2561 | 0.69038 | 0.50362 | 4.2561 | 3.7259 | 0.60438 | 0.44088 | 3.7259 | 3.7246 | 0.60416 | 0.44073 | 3.7246 | 4.4298 | 0.71856 | 0.52418 | 4.4298 | 9.8263 | 1.5939 | 1.1627 | 9.8263 | 24.5361 | 3.98 | 2.9034 | 9.7368 | 26.7265 | 9.3845 | 6.8459 | 9.7511 | 26.5262 | 12.9457 | 9.4437 | 10.0248 | 26.5801 | 14.6052 | 10.6543 | 12.9879 | 26.5813 | 14.2512 | 10.3961 | 11.877 | 26.6404 | 14.2565 | 10.3999 | 11.3619 | 26.6703 | 14.1828 | 10.3461 | 11.168 | 26.6763 | 14.0834 | 10.2736 | 11.0481 | 26.6839 | 13.9466 | 10.1739 | 10.9339 | 26.6928 | 13.8744 | 10.1212 | 10.8219 | 26.7005 | 13.7878 | 10.058 | 10.8226 | 26.7303 | 13.7038 | 9.9967 | 10.7459 | 26.7497 | 13.6182 | 9.9343 | 10.6609 | 26.7859 | 13.3818 | 9.7618 | 10.2625 | 26.7944 | 13.1852 | 9.6184 | 9.9637 | 26.7568 | 13.0669 | 9.5321 | 9.8349 | 26.6505 | 13.2448 | 9.6619 | 9.9817 | 26.4411 | 13.2583 | 9.6718 | 10.6332 | 26.5791 | 14.6052 | 10.6543 | 12.9879 | 26.5849 | 14.3788 | 10.4891 | 12.2367 | 26.6468 | 11.7554 | 8.5754 | 11.9042 | 26.6758 | 9.1876 | 6.7023 | 11.8224 | 26.6816 | 6.571 | 4.7934 | 11.8148 | 23.7448 | 3.8516 | 2.8097 | 11.812 | 7.2408 | 1.1745 | 0.8568 | 7.2408 | 6.6909 | 1.0853 | 0.79173 | 6.6909 | 6.1019 | 0.9898 | 0.72204 | 6.1019 | 6.1016 | 0.98974 | 0.722 | 6.1016 | 6.9001 | 1.1193 | 0.81648 | 6.9001 | 12.6646 | 2.0543 | 1.4986 | 11.2073 | 26.9964 | 4.5103 | 3.2902 | 11.1498 | 26.9938 | 9.9509 | 7.259 | 11.1407 | 26.9212 | 13.5158 | 9.8596 | 11.3411 | 26.5791 | 14.6052 | 10.6543 | 12.9879 | 26.5854 | 14.0835 | 10.2737 | 11.1914 | 26.6515 | 14.0744 | 10.2671 | 10.5172 | 26.6897 | 13.9846 | 10.2016 | 10.2977 | 26.7029 | 13.8732 | 10.1203 | 10.1541 | 26.7127 | 13.7345 | 10.0191 | 10.0237 | 26.7225 | 13.6601 | 9.9648 | 9.8958 | 26.735 | 13.5685 | 9.898 | 9.8723 | 26.7671 | 13.485 | 9.8371 | 9.7877 | 26.7883 | 13.4029 | 9.7772 | 9.7249 | 26.8253 | 13.1726 | 9.6093 | 9.3769 | 26.8268 | 12.9722 | 9.4631 | 9.0752 | 26.7837 | 12.8504 | 9.3742 | 8.944 | 26.6705 | 13.0258 | 9.5022 | 9.0904 | 26.4597 | 13.0321 | 9.5068 | 9.7337
WARBRECK | BISPHAM | PENWORTHAM WEST / STANAH | 331775 | 438420 | 23.3975 | 12.6671 | 9.2405 | 11.2168 | 23.4369 | 12.5114 | 9.1269 | 10.6324 | 23.4991 | 12.4447 | 9.0782 | 10.5363 | 23.586 | 12.3938 | 9.0411 | 10.5262 | 23.6954 | 12.2958 | 8.9696 | 10.4187 | 23.8203 | 12.203 | 8.9019 | 10.2835 | 23.9745 | 12.1233 | 8.8438 | 10.1455 | 24.1746 | 12.0302 | 8.7759 | 10.023 | 24.362 | 11.9594 | 8.7242 | 9.823 | 24.5414 | 11.8707 | 8.6595 | 9.599 | 25.0355 | 11.5445 | 8.4216 | 8.1761 | 25.5201 | 11.1382 | 8.1252 | 5.8446 | 25.8545 | 10.8809 | 7.9374 | 3.932 | 26.1256 | 11.1477 | 8.1321 | 1.9645 | 26.3051 | 10.8054 | 7.8824 | 0.016858 | 23.3822 | 12.6671 | 9.2405 | 11.2168 | 23.4112 | 12.6236 | 9.2087 | 11.1228 | 23.443 | 12.5921 | 9.1858 | 11.0861 | 23.4863 | 12.5521 | 9.1566 | 11.0502 | 23.5524 | 12.4992 | 9.118 | 10.971 | 23.6421 | 12.4424 | 9.0766 | 10.876 | 23.7564 | 12.2999 | 8.9726 | 10.7314 | 23.892 | 12.2263 | 8.9189 | 10.5414 | 23.9818 | 12.1643 | 8.8737 | 10.3884 | 24.0822 | 12.1016 | 8.8279 | 10.2258 | 24.4315 | 11.8983 | 8.6796 | 9.5961 | 24.8044 | 11.7217 | 8.5508 | 8.8575 | 25.189 | 11.6475 | 8.4967 | 8.1108 | 25.6015 | 11.8469 | 8.6421 | 7.3188 | 25.8375 | 12.005 | 8.7575 | 6.7931 | 23.404 | 12.6671 | 9.2405 | 11.2168 | 23.4494 | 12.4852 | 9.1078 | 10.5549 | 23.5215 | 12.4004 | 9.0459 | 10.4607 | 23.6217 | 12.3411 | 9.0026 | 10.4797 | 23.7327 | 12.253 | 8.9384 | 10.4046 | 23.859 | 12.1532 | 8.8656 | 10.3087 | 24.0204 | 12.0564 | 8.795 | 10.2301 | 24.2262 | 11.9708 | 8.7325 | 10.169 | 24.3866 | 11.8918 | 8.6749 | 10.0032 | 24.5327 | 11.8276 | 8.6281 | 9.8367 | 25.006 | 11.4682 | 8.3659 | 8.5507 | 25.5286 | 10.9433 | 7.983 | 6.2743 | 25.9002 | 10.8206 | 7.8935 | 4.3998 | 26.1837 | 11.0049 | 8.0279 | 2.5629 | 26.345 | 10.674 | 7.7865 | 0.88408 | 23.404 | 12.6671 | 9.2405 | 11.2168 | 23.3738 | 12.5713 | 9.1706 | 10.989 | 23.3977 | 12.5201 | 9.1333 | 10.986 | 23.4448 | 12.4451 | 9.0786 | 11.0066 | 23.5323 | 12.3807 | 9.0316 | 10.9097 | 23.6493 | 12.3117 | 8.9812 | 10.7741 | 23.8084 | 12.2035 | 8.9023 | 10.5116 | 24.0178 | 12.0645 | 8.8008 | 9.8072 | 24.2209 | 11.9226 | 8.6973 | 9.0598 | 24.4204 | 11.8036 | 8.6105 | 8.3065 | 24.9899 | 12.2051 | 8.9035 | 6.0839 | 25.4558 | 11.7325 | 8.5587 | 3.9423 | 25.766 | 11.3087 | 8.2495 | 2.21 | 25.958 | 10.9993 | 8.0238 | 1.1748 | 25.9455 | 10.9829 | 8.0119 | 1.846 | 23.3975 | 12.6671 | 9.2405 | 11.2168 | 23.4293 | 12.6064 | 9.1962 | 11.112 | 23.4666 | 12.5607 | 9.1629 | 11.1265 | 23.5124 | 12.5228 | 9.1352 | 11.1794 | 23.5858 | 12.4456 | 9.0789 | 11.1993 | 23.6988 | 12.3732 | 9.0261 | 11.1883 | 23.8477 | 12.3133 | 8.9824 | 11.1444 | 24.0156 | 12.2258 | 8.9186 | 11.0763 | 24.1679 | 12.1656 | 8.8746 | 10.9133 | 24.3268 | 12.0785 | 8.8111 | 10.7047 | 24.8045 | 11.8647 | 8.6551 | 9.9046 | 25.2167 | 11.7176 | 8.5478 | 8.9866 | 25.5003 | 11.72 | 8.5496 | 8.3371 | 25.7095 | 12.2737 | 8.9535 | 7.7782 | 25.7918 | 12.2687 | 8.9499 | 7.5342 | 23.3975 | 12.6671 | 9.2405 | 11.2168 | 23.3863 | 12.5047 | 9.122 | 10.6721 | 23.4408 | 12.4327 | 9.0695 | 10.5643 | 23.5242 | 12.347 | 9.0069 | 10.5216 | 23.6289 | 12.2702 | 8.9509 | 10.3685 | 23.7493 | 12.1951 | 8.8961 | 10.1979 | 23.8961 | 12.0775 | 8.8104 | 9.8916 | 24.1061 | 11.9274 | 8.7009 | 9.131 | 24.2972 | 11.7794 | 8.5929 | 8.3479 | 24.4847 | 11.6534 | 8.501 | 7.5577 | 25.0631 | 12.0032 | 8.7562 | 5.1917 | 25.5597 | 11.5068 | 8.3941 | 2.8987 | 25.9073 | 11.0546 | 8.0642 | 1.0136 | 26.117 | 10.7113 | 7.8138 | -0.1869 | 26.1169 | 10.665 | 7.78 | 0.31361
WARDLEWORTH | BELFIELD | ROCHDALE | 390339 | 414050 | 30.3801 | 8.8377 | 6.4469 | 16.2097 | 30.4746 | 8.6148 | 6.2844 | 15.2833 | 30.6138 | 8.4599 | 6.1714 | 14.9718 | 30.7852 | 8.2066 | 5.9866 | 14.8369 | 30.9246 | 8.0135 | 5.8457 | 14.6346 | 31.0313 | 7.9003 | 5.7632 | 14.418 | 31.159 | 7.8008 | 5.6906 | 14.2141 | 31.3151 | 7.6693 | 5.5947 | 14.0252 | 31.4505 | 7.5861 | 5.534 | 13.7759 | 31.5846 | 7.499 | 5.4704 | 13.5476 | 32.0185 | 7.1132 | 5.189 | 12.0531 | 32.4608 | 6.5615 | 4.7865 | 9.4633 | 32.7758 | 6.0787 | 4.4343 | 7.3321 | 33.0471 | 5.7473 | 4.1925 | 5.098 | 33.2376 | 5.4643 | 3.9861 | 3.0764 | 30.3476 | 8.8377 | 6.4469 | 16.2097 | 30.4257 | 8.7454 | 6.3796 | 15.8286 | 30.5084 | 8.6862 | 6.3365 | 15.6208 | 30.6078 | 8.615 | 6.2845 | 15.4727 | 30.7394 | 8.5198 | 6.2151 | 15.3014 | 30.902 | 8.4283 | 6.1483 | 15.123 | 31.0351 | 8.2164 | 5.9937 | 14.8901 | 31.2008 | 8.1093 | 5.9157 | 14.5711 | 31.3499 | 8.0069 | 5.8409 | 14.2729 | 31.4946 | 7.9017 | 5.7642 | 13.9711 | 31.8295 | 7.6357 | 5.5701 | 13.0523 | 32.1275 | 7.4043 | 5.4014 | 12.0696 | 32.4053 | 7.1596 | 5.2228 | 11.1484 | 32.698 | 6.9893 | 5.0986 | 10.1243 | 32.9168 | 6.7942 | 4.9563 | 9.3674 | 30.3914 | 8.8377 | 6.4469 | 16.2097 | 30.4972 | 8.5763 | 6.2563 | 15.156 | 30.6552 | 8.376 | 6.1101 | 14.8308 | 30.8541 | 8.0611 | 5.8805 | 14.7138 | 30.9552 | 7.908 | 5.7687 | 14.5366 | 31.0725 | 7.7636 | 5.6634 | 14.3509 | 31.2128 | 7.6764 | 5.5998 | 14.1821 | 31.3827 | 7.5427 | 5.5023 | 14.047 | 31.5185 | 7.4641 | 5.4449 | 13.884 | 31.6518 | 7.3854 | 5.3876 | 13.7414 | 32.0986 | 6.95 | 5.0699 | 12.4312 | 32.5695 | 6.3713 | 4.6477 | 10.1077 | 32.9051 | 5.8603 | 4.275 | 8.1542 | 33.1768 | 5.5107 | 4.02 | 6.1216 | 32.1572 | 5.2162 | 3.8052 | 4.3427 | 30.3914 | 8.8377 | 6.4469 | 16.2097 | 30.404 | 8.6652 | 6.3211 | 15.6413 | 30.4837 | 8.5024 | 6.2024 | 15.4321 | 30.5887 | 8.1937 | 5.9772 | 15.3377 | 30.742 | 8.0704 | 5.8873 | 15.1643 | 30.8393 | 7.9169 | 5.7753 | 14.9699 | 30.9642 | 7.7344 | 5.6421 | 14.6474 | 31.1223 | 7.4522 | 5.4363 | 13.8952 | 31.2674 | 7.1982 | 5.251 | 13.0926 | 31.414 | 6.9939 | 5.102 | 12.3065 | 31.8623 | 6.4375 | 4.6961 | 10.0384 | 32.2961 | 5.8859 | 4.2937 | 7.7565 | 32.5941 | 5.4485 | 3.9746 | 5.9585 | 32.8083 | 5.4343 | 3.9642 | 4.8088 | 32.8447 | 5.3529 | 3.9048 | 5.4037 | 30.3801 | 8.8377 | 6.4469 | 16.2097 | 30.4623 | 8.6838 | 6.3347 | 15.625 | 30.5615 | 8.5547 | 6.2405 | 15.4039 | 30.6697 | 8.3113 | 6.0629 | 15.3175 | 30.8081 | 8.1321 | 5.9322 | 15.2194 | 30.9371 | 8.0455 | 5.8691 | 15.1086 | 31.0603 | 7.9595 | 5.8064 | 14.9858 | 31.1989 | 7.8378 | 5.7175 | 14.8453 | 31.3166 | 7.7578 | 5.6592 | 14.6165 | 31.4369 | 7.6668 | 5.5928 | 14.3703 | 31.83 | 7.402 | 5.3997 | 13.5022 | 32.2317 | 7.125 | 5.1976 | 12.3865 | 32.5208 | 6.8919 | 5.0275 | 11.6094 | 32.7671 | 6.8405 | 4.9901 | 10.8886 | 32.9059 | 6.8527 | 4.999 | 10.4723 | 30.3801 | 8.8377 | 6.4469 | 16.2097 | 30.4249 | 8.5796 | 6.2587 | 15.2083 | 30.5564 | 8.3872 | 6.1183 | 14.8641 | 30.7251 | 8.0726 | 5.8888 | 14.7074 | 30.8642 | 7.9351 | 5.7886 | 14.4763 | 30.9668 | 7.7734 | 5.6706 | 14.2396 | 31.0939 | 7.5783 | 5.5283 | 13.8737 | 31.27 | 7.2846 | 5.314 | 13.0543 | 31.4182 | 7.0232 | 5.1233 | 12.2088 | 31.566 | 6.8074 | 4.9659 | 11.3548 | 32.0154 | 6.2076 | 4.5284 | 8.847 | 32.4417 | 5.6235 | 4.1023 | 6.4074 | 31.7788 | 5.1548 | 3.7604 | 4.4482 | 31.4663 | 5.1041 | 3.7234 | 3.0962 | 30.7056 | 4.9807 | 3.6334 | 3.4598
WARTON | PEEL | PENWORTHAM WEST / STANAH | 341290 | 428540 | 27.8284 | 13.7919 | 10.061 | 15.9975 | 27.9041 | 13.7724 | 10.0468 | 15.3077 | 28.02 | 13.8132 | 10.0765 | 14.9153 | 28.1197 | 13.7525 | 10.0322 | 14.669 | 28.2133 | 13.511 | 9.8561 | 14.3581 | 28.3807 | 13.1855 | 9.6186 | 13.9879 | 28.492 | 13.0585 | 9.526 | 13.7055 | 28.5758 | 12.9383 | 9.4383 | 13.4318 | 28.659 | 12.8456 | 9.3707 | 13.135 | 28.7372 | 12.7542 | 9.304 | 12.856 | 28.9727 | 12.505 | 9.1222 | 12.0452 | 29.2052 | 12.2249 | 8.9179 | 11.0249 | 29.3669 | 11.9726 | 8.7338 | 10.2879 | 29.5008 | 11.9844 | 8.7424 | 9.5803 | 29.576 | 11.9907 | 8.747 | 8.9439 | 27.815 | 13.7919 | 10.061 | 15.9975 | 27.8676 | 13.7942 | 10.0626 | 15.6804 | 27.941 | 13.7625 | 10.0396 | 15.442 | 27.9986 | 13.7576 | 10.036 | 15.2992 | 28.0506 | 13.7282 | 10.0145 | 15.1794 | 28.1043 | 13.6877 | 9.985 | 15.0755 | 28.1686 | 13.5742 | 9.9022 | 14.9441 | 28.2529 | 13.5214 | 9.8637 | 14.7484 | 28.3734 | 13.4503 | 9.8118 | 14.4571 | 28.4969 | 13.4187 | 9.7887 | 14.1705 | 28.8635 | 13.2692 | 9.6797 | 13.3383 | 29.169 | 13.0629 | 9.5292 | 12.4558 | 29.3668 | 12.8653 | 9.3851 | 11.7168 | 29.5669 | 12.7308 | 9.287 | 10.8819 | 31.0537 | 12.3589 | 9.0156 | 8.9367 | 27.8272 | 13.7919 | 10.061 | 15.9975 | 27.9061 | 13.7587 | 10.0367 | 15.2474 | 28.0239 | 13.7931 | 10.0619 | 14.855 | 28.199 | 13.6519 | 9.9588 | 14.5549 | 28.2936 | 13.3711 | 9.754 | 14.263 | 28.397 | 13.0998 | 9.5561 | 13.9837 | 28.5139 | 12.9703 | 9.4617 | 13.7216 | 28.5858 | 12.8555 | 9.3779 | 13.4765 | 28.6561 | 12.7691 | 9.3149 | 13.248 | 28.7197 | 12.6883 | 9.2559 | 13.0418 | 30.1509 | 12.2287 | 8.9207 | 11.2145 | 30.3807 | 11.8958 | 8.6778 | 10.3637 | 30.5144 | 11.8057 | 8.6121 | 9.8076 | 30.5832 | 11.792 | 8.6021 | 9.3544 | 30.5653 | 11.8351 | 8.6336 | 9.0392 | 27.8273 | 13.7919 | 10.061 | 15.9975 | 27.8774 | 13.813 | 10.0764 | 15.5141 | 28.0491 | 13.8688 | 10.1171 | 15.1082 | 28.1201 | 13.6877 | 9.985 | 14.8895 | 28.1916 | 13.3349 | 9.7276 | 14.6084 | 29.7527 | 12.8672 | 9.3864 | 12.8605 | 29.8007 | 12.6801 | 9.2499 | 12.6317 | 29.817 | 12.5144 | 9.1291 | 12.3084 | 29.8493 | 12.4203 | 9.0604 | 11.9748 | 29.8777 | 12.3181 | 8.9859 | 11.6595 | 30.0714 | 12.1014 | 8.8278 | 10.8393 | 30.2855 | 11.8869 | 8.6713 | 10.0481 | 30.4031 | 11.7489 | 8.5707 | 9.5472 | 30.4406 | 11.9288 | 8.7019 | 9.3183 | 30.3541 | 11.8909 | 8.6743 | 9.6193 | 27.8283 | 13.7919 | 10.061 | 15.9975 | 27.891 | 13.7901 | 10.0597 | 15.4109 | 27.9898 | 13.8395 | 10.0957 | 15.0469 | 28.0645 | 13.8011 | 10.0677 | 14.8252 | 28.1289 | 13.5696 | 9.8988 | 14.5552 | 28.2791 | 13.2493 | 9.6652 | 14.2227 | 28.3804 | 13.129 | 9.5774 | 13.9623 | 28.4918 | 13.0078 | 9.489 | 13.6835 | 28.5952 | 12.9035 | 9.4129 | 13.3545 | 28.6718 | 12.8076 | 9.343 | 13.032 | 28.9039 | 12.5631 | 9.1646 | 12.2312 | 29.1296 | 12.3118 | 8.9813 | 11.4349 | 29.2878 | 12.1768 | 8.8828 | 10.9071 | 29.418 | 12.2099 | 8.9069 | 10.4347 | 29.4588 | 12.3123 | 8.9816 | 10.2394 | 27.8283 | 13.7919 | 10.061 | 15.9975 | 27.8775 | 13.7601 | 10.0378 | 15.2479 | 28.0613 | 13.8076 | 10.0724 | 14.7684 | 28.1541 | 13.6033 | 9.9234 | 14.5224 | 28.2376 | 13.2525 | 9.6675 | 14.2122 | 29.791 | 12.781 | 9.3236 | 12.4458 | 29.8233 | 12.5976 | 9.1898 | 12.1982 | 29.8706 | 12.405 | 9.0493 | 11.8425 | 29.9067 | 12.3154 | 8.9839 | 11.4851 | 29.9388 | 12.2188 | 8.9135 | 11.1472 | 30.1416 | 11.9817 | 8.7405 | 10.2634 | 30.3562 | 11.7527 | 8.5734 | 9.3912 | 30.4761 | 11.6027 | 8.464 | 8.8298 | 30.5137 | 11.7708 | 8.5866 | 8.5377 | 30.4346 | 11.7118 | 8.5436 | 8.7603
WATERHEAD | GREENHILL | WHITEGATE | 394942 | 405940 | 28.8492 | 13.9756 | 10.195 | 20.1052 | 28.9047 | 13.8958 | 10.1368 | 19.9422 | 28.9603 | 13.6357 | 9.9471 | 19.7746 | 29.0308 | 13.4479 | 9.81 | 19.6022 | 29.1278 | 13.2528 | 9.6677 | 19.3592 | 29.2369 | 12.9971 | 9.4812 | 19.1062 | 29.3562 | 12.7542 | 9.304 | 18.8715 | 29.4912 | 12.6415 | 9.2218 | 18.6546 | 29.5977 | 12.5355 | 9.1445 | 18.4253 | 29.7012 | 12.4453 | 9.0787 | 18.208 | 30.132 | 12.0386 | 8.782 | 16.8242 | 30.6774 | 11.5289 | 8.4102 | 14.6098 | 30.9245 | 11.106 | 8.1017 | 12.9007 | 31.1448 | 10.7767 | 7.8615 | 11.2862 | 31.3009 | 10.4345 | 7.6118 | 10.1437 | 28.8285 | 13.9756 | 10.195 | 20.1052 | 28.8781 | 13.9429 | 10.1712 | 19.9972 | 28.9111 | 13.7011 | 9.9948 | 19.8932 | 28.9513 | 13.558 | 9.8904 | 19.7871 | 29.0079 | 13.3806 | 9.761 | 19.6494 | 29.0757 | 13.2271 | 9.649 | 19.5019 | 29.1599 | 12.8851 | 9.3995 | 19.3129 | 29.2613 | 12.7972 | 9.3354 | 19.0707 | 29.3148 | 12.7209 | 9.2797 | 18.8743 | 29.3719 | 12.6471 | 9.2259 | 18.6682 | 29.5536 | 12.421 | 9.0609 | 18.0411 | 29.7425 | 12.273 | 8.953 | 17.4029 | 29.9268 | 12.1325 | 8.8505 | 16.7688 | 30.1267 | 11.9241 | 8.6985 | 16.0614 | 30.2795 | 11.6248 | 8.4802 | 15.5226 | 28.8546 | 13.9756 | 10.195 | 20.1052 | 28.9273 | 13.8518 | 10.1047 | 19.8786 | 29.0052 | 13.585 | 9.91 | 19.6463 | 29.1027 | 13.3403 | 9.7316 | 19.409 | 29.2297 | 13.0872 | 9.5469 | 19.0359 | 29.372 | 12.7785 | 9.3217 | 18.6493 | 29.5292 | 12.4885 | 9.1102 | 18.2848 | 29.7067 | 12.3421 | 9.0034 | 17.9292 | 29.8512 | 12.1958 | 8.8967 | 17.5663 | 29.9935 | 12.0523 | 8.792 | 17.1976 | 30.5419 | 11.4779 | 8.3729 | 15.4065 | 31.0824 | 10.8342 | 7.9034 | 13.2454 | 31.38 | 10.5507 | 7.6966 | 11.7956 | 31.6408 | 10.2223 | 7.457 | 10.6632 | 31.8158 | 9.9351 | 7.2475 | 10.2659 | 28.8546 | 13.9756 | 10.195 | 20.1052 | 28.8677 | 13.9015 | 10.141 | 20.061 | 28.915 | 13.7418 | 10.0245 | 19.8826 | 28.9833 | 13.5816 | 9.9076 | 19.6626 | 29.085 | 13.3679 | 9.7517 | 19.2902 | 29.216 | 13.0267 | 9.5028 | 18.8886 | 29.3859 | 12.5542 | 9.1581 | 18.3779 | 29.629 | 12.3752 | 9.0276 | 17.4857 | 29.8427 | 12.1484 | 8.8621 | 16.6122 | 30.0235 | 11.887 | 8.6714 | 15.7674 | 30.4499 | 11.2353 | 8.196 | 13.4101 | 30.8646 | 10.6755 | 7.7877 | 11.6113 | 31.1441 | 10.2577 | 7.4828 | 10.5331 | 31.3611 | 9.9134 | 7.2317 | 10.1631 | 31.4669 | 9.7908 | 7.1423 | 10.8621 | 28.8492 | 13.9756 | 10.195 | 20.1052 | 28.8994 | 13.9194 | 10.154 | 19.959 | 28.941 | 13.6569 | 9.9625 | 19.8197 | 28.9875 | 13.4843 | 9.8366 | 19.6998 | 29.0509 | 13.3166 | 9.7143 | 19.5597 | 29.1376 | 13.0915 | 9.5501 | 19.3981 | 29.2451 | 12.8557 | 9.3781 | 19.2206 | 29.3643 | 12.7507 | 9.3014 | 19.03 | 29.4626 | 12.6449 | 9.2243 | 18.797 | 29.5631 | 12.5457 | 9.1519 | 18.5593 | 29.893 | 12.2523 | 8.9379 | 17.7531 | 30.2375 | 11.9966 | 8.7514 | 16.9017 | 30.4922 | 11.7326 | 8.5588 | 16.2991 | 30.7389 | 11.6685 | 8.512 | 15.6778 | 30.9152 | 11.4491 | 8.3519 | 15.2395 | 28.8492 | 13.9756 | 10.195 | 20.1052 | 28.8788 | 13.8724 | 10.1197 | 20.0218 | 28.947 | 13.6997 | 9.9937 | 19.7888 | 29.0405 | 13.526 | 9.867 | 19.5069 | 29.1636 | 13.2962 | 9.6994 | 19.0781 | 29.2985 | 12.9509 | 9.4475 | 18.6383 | 29.4664 | 12.4676 | 9.0949 | 18.0808 | 29.721 | 12.2745 | 8.9541 | 17.1233 | 29.9428 | 12.0389 | 8.7822 | 16.2012 | 30.1459 | 11.7703 | 8.5863 | 15.3075 | 30.5924 | 11.0896 | 8.0897 | 12.7993 | 30.9831 | 10.509 | 7.6661 | 10.8692 | 31.2471 | 10.058 | 7.3372 | 9.6608 | 31.4559 | 9.6838 | 7.0642 | 9.1298 | 31.5782 | 9.523 | 6.9469 | 9.6341
WATERSWALLOWS | BUXTON | STALYBRIDGE | 407734 | 375459 | 28.9418 | 13.2607 | 9.5307 | 17.8559 | 29.0276 | 13.131 | 9.4375 | 17.6284 | 29.1763 | 13.0692 | 9.3931 | 17.4429 | 29.3692 | 12.9805 | 9.3293 | 17.3404 | 29.6039 | 12.8675 | 9.2481 | 17.2559 | 29.7563 | 12.7511 | 9.1645 | 17.1585 | 29.9477 | 12.6378 | 9.0831 | 17.0475 | 30.1585 | 12.6275 | 9.0756 | 16.909 | 30.35 | 12.5608 | 9.0277 | 16.6692 | 30.5556 | 12.4998 | 8.9838 | 16.4211 | 31.2334 | 12.2133 | 8.7779 | 15.0334 | 31.8532 | 11.9242 | 8.5702 | 13.394 | 32.249 | 11.791 | 8.4745 | 12.3034 | 32.5974 | 12.9312 | 9.2939 | 11.4289 | 32.7352 | 12.7289 | 9.1485 | 11.0176 | 28.9423 | 13.2607 | 9.5307 | 17.8559 | 28.9957 | 13.1927 | 9.4818 | 17.7897 | 29.0648 | 13.1247 | 9.433 | 17.656 | 29.1645 | 13.0669 | 9.3914 | 17.5797 | 29.3062 | 13.0004 | 9.3436 | 17.5341 | 29.4842 | 12.9258 | 9.29 | 17.4856 | 29.6074 | 12.747 | 9.1615 | 17.4279 | 29.7071 | 12.6989 | 9.1269 | 17.2818 | 29.8331 | 12.6419 | 9.086 | 17.0484 | 29.9791 | 12.5881 | 9.0473 | 16.8003 | 30.5408 | 12.4085 | 8.9182 | 15.9831 | 31.2508 | 12.2758 | 8.8229 | 15.0541 | 31.9975 | 12.1009 | 8.6972 | 13.9032 | 32.7174 | 12.5274 | 9.0037 | 12.6223 | 33.0469 | 13.0473 | 9.3774 | 11.861 | 28.9421 | 13.2607 | 9.5307 | 17.8559 | 29.0275 | 13.1265 | 9.4343 | 17.5955 | 29.174 | 13.0353 | 9.3687 | 17.4038 | 29.3609 | 12.9163 | 9.2832 | 17.3017 | 29.586 | 12.7791 | 9.1846 | 17.2214 | 29.7431 | 12.5959 | 9.0529 | 17.1323 | 29.8728 | 12.5894 | 9.0482 | 17.0343 | 29.9684 | 12.5185 | 8.9973 | 16.9156 | 30.1054 | 12.4337 | 8.9364 | 16.7374 | 30.2579 | 12.3668 | 8.8883 | 16.5542 | 30.8371 | 12.0369 | 8.6512 | 15.2836 | 31.5053 | 11.6673 | 8.3855 | 13.3274 | 31.9039 | 11.4918 | 8.2594 | 12.0321 | 32.1468 | 12.5346 | 9.0088 | 11.1761 | 32.218 | 12.3201 | 8.8547 | 10.8507 | 28.9421 | 13.2607 | 9.5307 | 17.8559 | 28.9712 | 13.153 | 9.4533 | 17.7029 | 29.0582 | 13.0796 | 9.4006 | 17.5491 | 29.1857 | 12.9479 | 9.3059 | 17.4637 | 29.4552 | 12.7818 | 9.1866 | 17.3069 | 29.723 | 12.6981 | 9.1264 | 17.2168 | 29.8604 | 12.5387 | 9.0118 | 17.0746 | 30.0001 | 12.5277 | 9.0039 | 16.7763 | 30.1875 | 12.4885 | 8.9757 | 16.3571 | 30.3913 | 12.4589 | 8.9545 | 15.9304 | 31.0325 | 13.1862 | 9.4772 | 14.5134 | 31.5638 | 12.8413 | 9.2293 | 13.2967 | 31.8818 | 12.5047 | 8.9874 | 12.2925 | 32.0344 | 12.2102 | 8.7757 | 11.6524 | 31.9717 | 12.0538 | 8.6633 | 11.7262 | 28.9418 | 13.2607 | 9.5307 | 17.8559 | 29.0101 | 13.1498 | 9.451 | 17.7534 | 29.1116 | 13.1051 | 9.4189 | 17.6084 | 29.2343 | 13.0226 | 9.3596 | 17.5324 | 29.3943 | 12.9185 | 9.2848 | 17.4868 | 29.6328 | 12.8054 | 9.2035 | 17.4216 | 29.7881 | 12.7028 | 9.1298 | 17.3338 | 29.9868 | 12.6954 | 9.1244 | 17.2259 | 30.178 | 12.6327 | 9.0793 | 17.0175 | 30.3506 | 12.5759 | 9.0385 | 16.7961 | 30.9476 | 12.3617 | 8.8846 | 15.8894 | 31.5223 | 12.1063 | 8.701 | 14.524 | 31.9003 | 11.9924 | 8.6192 | 13.5227 | 32.213 | 13.2505 | 9.5234 | 12.6946 | 32.2686 | 13.0935 | 9.4106 | 12.4454 | 28.9418 | 13.2607 | 9.5307 | 17.8559 | 29.0096 | 13.13 | 9.4368 | 17.5936 | 29.1549 | 13.0454 | 9.376 | 17.3974 | 29.3471 | 12.9066 | 9.2762 | 17.2865 | 29.6622 | 12.7479 | 9.1622 | 17.1113 | 29.8098 | 12.6549 | 9.0953 | 17.024 | 30.0106 | 12.506 | 8.9883 | 16.8938 | 30.1961 | 12.4868 | 8.9745 | 16.6343 | 30.3895 | 12.4504 | 8.9483 | 16.2361 | 30.5989 | 12.4209 | 8.9272 | 15.8256 | 31.3064 | 13.1552 | 9.4549 | 14.4913 | 31.9697 | 12.7521 | 9.1652 | 12.9047 | 32.4118 | 12.3969 | 8.9099 | 11.7944 | 32.6552 | 12.1104 | 8.704 | 11.2268 | 32.6467 | 11.9813 | 8.6112 | 11.5013
WEASTE | FREDERICK RD | KEARSLEY | 378751 | 398897 | 28.1813 | 7.4464 | 5.432 | 12.8371 | 28.2275 | 7.2077 | 5.2579 | 12.5131 | 28.3228 | 7.0216 | 5.1221 | 12.221 | 28.4262 | 6.8143 | 4.971 | 12.0535 | 28.5505 | 6.6255 | 4.8332 | 11.9357 | 28.7156 | 6.3719 | 4.6482 | 11.8088 | 28.9364 | 6.1764 | 4.5056 | 11.3638 | 29.2279 | 6.0028 | 4.379 | 10.8905 | 29.5662 | 5.8091 | 4.2376 | 10.3112 | 29.9385 | 5.6082 | 4.0911 | 9.7294 | 30.624 | 4.9675 | 3.6237 | 7.8435 | 28.6185 | 4.6422 | 3.3864 | 5.3723 | 26.9978 | 4.3793 | 3.1946 | 4.16 | 33.0013 | 5.6571 | 4.1268 | 3.0272 | 33.2224 | 7.1033 | 5.1818 | 1.9954 | 28.1713 | 7.4464 | 5.432 | 12.8371 | 28.219 | 7.335 | 5.3508 | 12.6382 | 28.3023 | 7.2328 | 5.2762 | 12.345 | 28.3813 | 7.121 | 5.1947 | 12.133 | 28.4678 | 6.998 | 5.105 | 11.9547 | 28.5751 | 6.8615 | 5.0053 | 11.7487 | 28.7071 | 6.7231 | 4.9044 | 11.5104 | 28.8669 | 6.6181 | 4.8278 | 11.2384 | 29.0182 | 6.524 | 4.7591 | 10.9792 | 29.1914 | 6.4113 | 4.677 | 10.716 | 29.8509 | 6.1429 | 4.4812 | 9.902 | 30.6714 | 5.8897 | 4.2964 | 9.0834 | 31.5213 | 5.6445 | 4.1176 | 8.3383 | 32.3582 | 6.3905 | 4.6618 | 7.2067 | 32.9216 | 7.4833 | 5.459 | 6.3943 | 28.1851 | 7.4464 | 5.432 | 12.8371 | 28.2346 | 7.1773 | 5.2357 | 12.4731 | 28.3334 | 6.9157 | 5.0449 | 12.1735 | 28.4404 | 6.6577 | 4.8567 | 12.0057 | 28.5639 | 6.418 | 4.6818 | 11.8918 | 28.7219 | 6.1968 | 4.5205 | 11.7727 | 28.9272 | 5.9551 | 4.3442 | 11.3392 | 29.1933 | 5.6768 | 4.1411 | 10.8838 | 29.4813 | 5.4481 | 3.9743 | 10.3812 | 29.8023 | 5.4263 | 3.9584 | 9.8818 | 30.8596 | 5.0471 | 3.6818 | 8.167 | 27.6812 | 4.4902 | 3.2755 | 5.8378 | 25.1506 | 4.0797 | 2.9761 | 4.776 | 32.9967 | 5.5798 | 4.0704 | 3.9042 | 33.1513 | 7.0013 | 5.1073 | 3.3188 | 28.1851 | 7.4464 | 5.432 | 12.8371 | 28.1931 | 7.2337 | 5.2769 | 12.6347 | 28.2627 | 6.9976 | 5.1046 | 12.4061 | 28.3402 | 6.672 | 4.8671 | 12.2933 | 28.4418 | 6.4304 | 4.6909 | 12.2262 | 28.6008 | 6.014 | 4.3871 | 12.1344 | 28.8239 | 6.1091 | 4.4565 | 11.7126 | 29.1156 | 5.939 | 4.3324 | 11.0761 | 29.452 | 5.6663 | 4.1335 | 10.251 | 29.8212 | 5.3413 | 3.8964 | 9.4305 | 30.4302 | 4.9361 | 3.6008 | 7.0274 | 27.3421 | 4.4352 | 3.2354 | 4.7972 | 27.3069 | 4.4295 | 3.2312 | 3.8238 | 32.8043 | 7.1013 | 5.1803 | 3.2866 | 32.7682 | 7.0445 | 5.1389 | 3.8801 | 28.1813 | 7.4464 | 5.432 | 12.8371 | 28.2219 | 7.2848 | 5.3141 | 12.6139 | 28.3011 | 7.1144 | 5.1898 | 12.3614 | 28.3769 | 6.914 | 5.0437 | 12.2251 | 28.4669 | 6.7227 | 4.9041 | 12.1409 | 28.6028 | 6.4865 | 4.7318 | 12.0328 | 28.7909 | 6.2813 | 4.5821 | 11.5984 | 29.025 | 6.1171 | 4.4624 | 11.1516 | 29.2954 | 5.9295 | 4.3255 | 10.605 | 29.5998 | 5.7322 | 4.1816 | 10.0528 | 30.6238 | 5.1024 | 3.7221 | 8.3617 | 30.6048 | 4.9644 | 3.6215 | 6.7421 | 29.5133 | 4.7873 | 3.4923 | 6.2006 | 32.4655 | 6.2821 | 4.5827 | 5.7027 | 32.5936 | 7.8739 | 5.7439 | 5.5948 | 28.1813 | 7.4464 | 5.432 | 12.8371 | 28.2041 | 7.1691 | 5.2297 | 12.4829 | 28.2941 | 6.8981 | 5.0321 | 12.1821 | 28.3923 | 6.5625 | 4.7873 | 12.0152 | 28.5059 | 6.3157 | 4.6072 | 11.9001 | 28.6511 | 5.9018 | 4.3053 | 11.7816 | 28.8435 | 6 | 4.3769 | 11.3398 | 29.105 | 5.8394 | 4.2598 | 10.793 | 29.395 | 5.5701 | 4.0633 | 9.9683 | 29.7193 | 5.2559 | 3.8341 | 9.1493 | 29.6403 | 4.8079 | 3.5073 | 6.7163 | 26.4615 | 4.2923 | 3.1312 | 4.4109 | 25.7722 | 4.1805 | 3.0496 | 3.246 | 32.9891 | 6.8902 | 5.0263 | 2.5997 | 32.9896 | 6.8167 | 4.9727 | 3.0931
WERNETH | GREENHILL | WHITEGATE | 391273 | 403453 | 29.6622 | 13.4497 | 9.8114 | 18.7098 | 29.8066 | 13.3491 | 9.7379 | 18.3461 | 29.9481 | 13.1645 | 9.6033 | 18.1114 | 30.1212 | 12.9319 | 9.4337 | 17.8858 | 30.3349 | 12.5174 | 9.1312 | 17.5568 | 30.5495 | 12.4516 | 9.0833 | 17.1921 | 30.7395 | 12.2069 | 8.9048 | 16.8232 | 30.9604 | 12.0753 | 8.8087 | 16.4613 | 31.1647 | 11.9362 | 8.7073 | 16.0358 | 31.3721 | 11.799 | 8.6072 | 15.5779 | 32.0407 | 11.2784 | 8.2274 | 13.5396 | 32.6388 | 10.658 | 7.7748 | 10.7199 | 33.0167 | 10.1886 | 7.4325 | 8.5773 | 33.3449 | 9.6696 | 7.0539 | 6.6282 | 33.5752 | 9.2055 | 6.7153 | 5.1963 | 29.6469 | 13.4497 | 9.8114 | 18.7098 | 29.74 | 13.4019 | 9.7765 | 18.5197 | 29.8151 | 13.2173 | 9.6418 | 18.3764 | 29.9062 | 13.0673 | 9.5324 | 18.2263 | 30.0264 | 12.8945 | 9.4064 | 18.0261 | 30.174 | 12.6576 | 9.2335 | 17.8082 | 30.3502 | 12.2261 | 8.9188 | 17.5298 | 30.554 | 12.1329 | 8.8508 | 17.1597 | 30.7088 | 12.0508 | 8.7909 | 16.8718 | 30.881 | 11.9651 | 8.7284 | 16.5702 | 31.3277 | 11.6652 | 8.5096 | 15.5158 | 31.8253 | 11.4606 | 8.3603 | 14.2612 | 32.2704 | 11.2423 | 8.2011 | 13.044 | 32.7047 | 10.9564 | 7.9926 | 11.6418 | 33.0261 | 10.6176 | 7.7454 | 10.6612 | 29.6684 | 13.4497 | 9.8114 | 18.7098 | 29.823 | 13.3093 | 9.7089 | 18.263 | 29.986 | 13.082 | 9.5431 | 17.9581 | 30.1861 | 12.7982 | 9.3361 | 17.6653 | 30.4289 | 12.4824 | 9.1057 | 17.2067 | 30.6157 | 12.2135 | 8.9096 | 16.71 | 30.8204 | 11.9404 | 8.7104 | 16.2191 | 31.057 | 11.7607 | 8.5793 | 15.724 | 31.2692 | 11.5812 | 8.4483 | 15.1758 | 31.4894 | 11.3962 | 8.3134 | 14.5648 | 32.2379 | 10.7153 | 7.8167 | 12.2008 | 32.8937 | 10.007 | 7.3 | 9.3378 | 33.3159 | 9.4694 | 6.9078 | 7.2718 | 33.6712 | 8.9146 | 6.5031 | 5.5422 | 33.8899 | 8.5507 | 6.2376 | 4.564 | 29.6685 | 13.4497 | 9.8114 | 18.7098 | 29.758 | 13.378 | 9.7591 | 18.559 | 29.8773 | 13.2597 | 9.6728 | 18.3314 | 30.0285 | 13.0119 | 9.492 | 18.0641 | 30.2324 | 12.8238 | 9.3548 | 17.609 | 30.4516 | 12.567 | 9.1674 | 17.0905 | 30.6791 | 12.1994 | 8.8993 | 16.4459 | 30.9292 | 11.8277 | 8.6282 | 15.3914 | 31.1497 | 11.4378 | 8.3437 | 14.3493 | 31.3769 | 11.0645 | 8.0714 | 13.3353 | 32.075 | 10.4377 | 7.6141 | 10.6274 | 32.6991 | 9.7465 | 7.1099 | 8.1517 | 33.0506 | 9.2086 | 6.7175 | 6.498 | 33.3141 | 8.7483 | 6.3818 | 5.5387 | 33.4266 | 8.5007 | 6.2011 | 5.6144 | 29.6621 | 13.4497 | 9.8114 | 18.7098 | 29.7829 | 13.3855 | 9.7646 | 18.4745 | 29.8872 | 13.2159 | 9.6408 | 18.2933 | 30.0042 | 12.9983 | 9.4821 | 18.1296 | 30.153 | 12.6591 | 9.2346 | 17.9219 | 30.3577 | 12.5673 | 9.1677 | 17.6809 | 30.5497 | 12.3466 | 9.0067 | 17.4034 | 30.7286 | 12.2218 | 8.9156 | 17.087 | 30.9003 | 12.0943 | 8.8226 | 16.719 | 31.0827 | 11.961 | 8.7254 | 16.2975 | 31.7031 | 11.5472 | 8.4235 | 14.7712 | 32.3235 | 11.1736 | 8.151 | 13.1813 | 32.7135 | 10.89 | 7.9441 | 11.9548 | 33.0224 | 10.4854 | 7.649 | 10.7766 | 33.2238 | 10.1848 | 7.4296 | 9.9244 | 29.6621 | 13.4497 | 9.8114 | 18.7098 | 29.7569 | 13.3414 | 9.7323 | 18.4547 | 29.9003 | 13.2086 | 9.6355 | 18.1546 | 30.0809 | 12.9427 | 9.4415 | 17.8205 | 30.3026 | 12.7411 | 9.2945 | 17.3025 | 30.5162 | 12.4706 | 9.0971 | 16.7472 | 30.7277 | 12.097 | 8.8246 | 16.0568 | 30.9986 | 11.715 | 8.5459 | 14.9395 | 31.2082 | 11.3272 | 8.263 | 13.8546 | 31.4269 | 10.9673 | 8.0005 | 12.7939 | 32.1308 | 10.2715 | 7.4929 | 9.9082 | 32.7911 | 9.5477 | 6.9649 | 7.2737 | 33.2118 | 8.9686 | 6.5425 | 5.4182 | 33.501 | 8.466 | 6.1759 | 4.2389 | 33.6491 | 8.1718 | 5.9612 | 4.0666
WESLEY PLACE BACUP | ROSSENDALE | PADIHAM | 386475 | 422130 | 29.5652 | 15.3966 | 11.2316 | 17.3225 | 29.6381 | 15.3631 | 11.2072 | 17.1978 | 29.7319 | 15.2417 | 11.1186 | 16.8734 | 29.8478 | 14.5813 | 10.6369 | 16.5755 | 29.9915 | 14.4434 | 10.5363 | 16.28 | 30.1611 | 14.1398 | 10.3148 | 16.0532 | 30.3616 | 14.2608 | 10.403 | 15.8472 | 30.6106 | 14.316 | 10.4433 | 15.642 | 30.8222 | 14.1687 | 10.3358 | 15.3976 | 31.0356 | 14.0187 | 10.2264 | 15.1646 | 31.7206 | 13.4712 | 9.827 | 13.3657 | 32.3535 | 12.7014 | 9.2655 | 10.074 | 32.6944 | 11.9719 | 8.7333 | 7.3236 | 32.9732 | 11.1658 | 8.1453 | 4.3991 | 33.1538 | 10.495 | 7.656 | 1.8358 | 29.5439 | 15.3966 | 11.2316 | 17.3225 | 29.6105 | 15.3651 | 11.2087 | 17.201 | 29.6871 | 15.243 | 11.1195 | 16.9924 | 29.7802 | 15.1159 | 11.0269 | 16.8407 | 29.8911 | 15.0231 | 10.9591 | 16.7074 | 30.0281 | 14.9042 | 10.8724 | 16.5171 | 30.1931 | 14.595 | 10.6468 | 16.2624 | 30.3877 | 14.4864 | 10.5676 | 15.9005 | 30.4907 | 14.4104 | 10.5122 | 15.5995 | 30.6014 | 14.3231 | 10.4485 | 15.2946 | 30.9725 | 14.0787 | 10.2702 | 14.3628 | 31.3768 | 13.7953 | 10.0635 | 13.3671 | 31.766 | 13.5698 | 9.899 | 12.3987 | 32.1774 | 13.0762 | 9.5389 | 11.2786 | 32.4695 | 12.4165 | 9.0577 | 10.4691 | 29.5742 | 15.3966 | 11.2316 | 17.3225 | 29.6514 | 15.3674 | 11.2103 | 17.196 | 29.7553 | 15.1899 | 11.0808 | 16.8717 | 29.8859 | 14.4655 | 10.5524 | 16.5731 | 30.0471 | 14.3389 | 10.46 | 16.2788 | 30.2368 | 14.1772 | 10.3421 | 16.0544 | 30.4599 | 14.2752 | 10.4135 | 15.8506 | 30.7356 | 14.0739 | 10.2667 | 15.6506 | 30.9555 | 13.9501 | 10.1764 | 15.4416 | 31.1763 | 13.8343 | 10.0919 | 15.2473 | 31.8262 | 13.1784 | 9.6135 | 13.859 | 32.3547 | 12.3801 | 9.0311 | 10.8317 | 32.7438 | 11.6438 | 8.494 | 8.2337 | 33.0675 | 10.8786 | 7.9358 | 5.5135 | 33.2175 | 10.2005 | 7.4411 | 3.2066 | 29.5742 | 15.3966 | 11.2316 | 17.3225 | 29.5851 | 15.4005 | 11.2345 | 17.3309 | 29.6402 | 15.3466 | 11.1952 | 17.0559 | 29.7106 | 14.4836 | 10.5656 | 16.7792 | 29.8159 | 14.1724 | 10.3386 | 16.4992 | 29.9772 | 14.3059 | 10.4359 | 16.2741 | 30.188 | 14.5038 | 10.5803 | 15.9091 | 30.454 | 14.0884 | 10.2773 | 15.0699 | 30.6889 | 13.5554 | 9.8885 | 14.0525 | 30.9287 | 13.0369 | 9.5103 | 12.9839 | 31.6654 | 12.0941 | 8.8225 | 9.91 | 32.2453 | 11.3863 | 8.3061 | 6.9456 | 32.5647 | 10.716 | 7.8172 | 4.5633 | 32.7733 | 10.153 | 7.4065 | 2.9941 | 32.7688 | 10.0944 | 7.3637 | 3.7974 | 29.5652 | 15.3966 | 11.2316 | 17.3225 | 29.629 | 15.358 | 11.2034 | 17.2179 | 29.6991 | 15.2555 | 11.1287 | 16.9157 | 29.7757 | 14.6002 | 10.6506 | 16.6628 | 29.8742 | 14.4906 | 10.5707 | 16.4717 | 30.0213 | 14.2248 | 10.3768 | 16.3434 | 30.2139 | 14.3413 | 10.4618 | 16.1952 | 30.4338 | 14.4225 | 10.521 | 16.0163 | 30.6154 | 14.2735 | 10.4123 | 15.7642 | 30.8043 | 14.1294 | 10.3072 | 15.5074 | 31.4256 | 13.7586 | 10.0367 | 14.6518 | 32.0284 | 13.4123 | 9.7841 | 13.5428 | 32.2964 | 13.0578 | 9.5255 | 12.7846 | 32.5139 | 12.7183 | 9.2778 | 12.0572 | 32.6102 | 12.4497 | 9.0819 | 11.6587 | 29.5652 | 15.3966 | 11.2316 | 17.3225 | 29.6048 | 15.3954 | 11.2307 | 17.2999 | 29.6953 | 15.3287 | 11.1821 | 16.9833 | 29.8092 | 14.4717 | 10.5569 | 16.6591 | 29.951 | 14.1516 | 10.3234 | 16.3367 | 30.1154 | 14.2249 | 10.3769 | 16.0896 | 30.3162 | 14.434 | 10.5294 | 15.7072 | 30.5927 | 13.9934 | 10.208 | 14.7181 | 30.8258 | 13.4406 | 9.8048 | 13.607 | 31.0615 | 12.9122 | 9.4193 | 12.4959 | 31.7884 | 11.9394 | 8.7096 | 9.2706 | 32.3889 | 11.194 | 8.1659 | 6.1412 | 32.7257 | 10.4837 | 7.6477 | 3.5752 | 32.9381 | 9.8792 | 7.2067 | 1.7577 | 32.9446 | 9.763 | 7.122 | 2.2774
WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 383306 | 392514 | 29.1223 | 12.7391 | 9.293 | 15.2949 | 29.217 | 12.5266 | 9.1379 | 14.2109 | 29.3346 | 12.3758 | 9.0279 | 13.6928 | 29.4798 | 12.242 | 8.9304 | 13.3058 | 29.6555 | 12.0813 | 8.8131 | 12.8261 | 29.8538 | 11.7978 | 8.6063 | 12.3313 | 30.0775 | 11.5673 | 8.4382 | 11.8664 | 30.3432 | 11.3753 | 8.2981 | 11.4527 | 30.5364 | 11.2817 | 8.2298 | 11.0388 | 30.7199 | 11.2025 | 8.1721 | 10.6626 | 31.2796 | 10.8156 | 7.8898 | 8.9329 | 31.8515 | 10.4411 | 7.6167 | 6.5064 | 32.2611 | 10.3798 | 7.5719 | 4.8303 | 32.6181 | 10.6157 | 7.744 | 3.4702 | 32.8841 | 10.6631 | 7.7786 | 2.3953 | 29.0776 | 12.7391 | 9.293 | 15.2949 | 29.155 | 12.6773 | 9.2479 | 14.8976 | 29.2261 | 12.6182 | 9.2048 | 14.6384 | 29.3178 | 12.5387 | 9.1468 | 14.3914 | 29.4388 | 12.4438 | 9.0776 | 14.0832 | 29.5861 | 12.321 | 8.988 | 13.7964 | 29.7607 | 12.0942 | 8.8225 | 13.4495 | 29.9597 | 11.953 | 8.7196 | 13.0307 | 30.0731 | 11.8333 | 8.6323 | 12.6553 | 30.1913 | 11.7203 | 8.5498 | 12.2709 | 30.5467 | 11.427 | 8.3358 | 11.1661 | 30.8833 | 11.2585 | 8.2129 | 10.1498 | 31.1567 | 11.217 | 8.1827 | 9.2979 | 31.4132 | 11.3256 | 8.2619 | 8.4678 | 31.6192 | 11.3335 | 8.2677 | 7.9223 | 29.1366 | 12.7391 | 9.293 | 15.2949 | 29.2499 | 12.4802 | 9.1041 | 14.0126 | 29.3916 | 12.2729 | 8.9529 | 13.3984 | 29.5719 | 12.0941 | 8.8224 | 12.9483 | 29.7888 | 11.9017 | 8.6821 | 12.4017 | 30.0346 | 11.6129 | 8.4714 | 11.839 | 30.3142 | 11.3663 | 8.2916 | 11.3164 | 30.6459 | 11.1266 | 8.1167 | 10.8301 | 30.8888 | 11.0875 | 8.0881 | 10.356 | 31.1209 | 10.9569 | 7.9929 | 9.8921 | 31.8315 | 10.4703 | 7.6379 | 7.9276 | 32.5279 | 10.039 | 7.3233 | 5.5243 | 32.8627 | 9.9434 | 7.2535 | 4.0243 | 33.1311 | 10.1825 | 7.428 | 2.9558 | 33.2721 | 10.2817 | 7.5004 | 2.4842 | 29.1366 | 12.7391 | 9.293 | 15.2949 | 29.1513 | 12.5779 | 9.1754 | 14.5587 | 29.2206 | 12.4263 | 9.0648 | 14.1222 | 29.3179 | 12.246 | 8.9333 | 13.7667 | 29.4586 | 12.1239 | 8.8442 | 13.279 | 29.6636 | 11.9275 | 8.7009 | 12.7183 | 29.9121 | 11.7559 | 8.5758 | 12.0958 | 30.1913 | 11.5135 | 8.399 | 11.2006 | 30.4093 | 11.3236 | 8.2604 | 10.3067 | 30.6226 | 11.0812 | 8.0836 | 9.4359 | 31.2728 | 11.4574 | 8.358 | 6.9999 | 31.9361 | 10.9363 | 7.9779 | 4.9302 | 32.4042 | 10.6039 | 7.7354 | 3.7633 | 32.7824 | 10.7024 | 7.8073 | 3.3508 | 32.8169 | 10.6145 | 7.7431 | 3.8852 | 29.1223 | 12.7391 | 9.293 | 15.2949 | 29.2043 | 12.6074 | 9.1969 | 14.6341 | 29.2903 | 12.4894 | 9.1108 | 14.2637 | 29.3842 | 12.3837 | 9.0338 | 13.9966 | 29.5053 | 12.2621 | 8.945 | 13.7013 | 29.6805 | 12.0089 | 8.7603 | 13.3857 | 29.9021 | 11.8097 | 8.615 | 13.0664 | 30.1435 | 11.6245 | 8.4799 | 12.7432 | 30.3167 | 11.5255 | 8.4077 | 12.3555 | 30.4885 | 11.4535 | 8.3552 | 11.9712 | 31.0219 | 11.168 | 8.1469 | 10.7623 | 31.5769 | 11.0189 | 8.0381 | 9.5332 | 31.9907 | 11.1199 | 8.1118 | 8.7157 | 32.3677 | 11.4774 | 8.3726 | 7.9448 | 32.5292 | 11.6437 | 8.4939 | 7.4585 | 29.1223 | 12.7391 | 9.293 | 15.2949 | 29.1763 | 12.4866 | 9.1088 | 14.0675 | 29.2962 | 12.2935 | 8.9679 | 13.4318 | 29.4534 | 12.091 | 8.8202 | 12.9463 | 29.6449 | 11.9471 | 8.7152 | 12.3486 | 29.8582 | 11.7456 | 8.5683 | 11.7378 | 30.1019 | 11.5618 | 8.4341 | 11.0587 | 30.409 | 11.3058 | 8.2474 | 10.0592 | 30.6431 | 11.1096 | 8.1043 | 9.0773 | 30.8682 | 10.8501 | 7.915 | 8.1221 | 31.5175 | 11.1704 | 8.1487 | 5.4623 | 32.116 | 10.6211 | 7.7479 | 3.262 | 32.5358 | 10.2628 | 7.4866 | 1.9762 | 32.8852 | 10.3369 | 7.5406 | 1.4347 | 32.9792 | 10.2137 | 7.4508 | 1.776
WESTGATE | LANCASTER | HEYSHAM | 343077 | 463204 | 23.6018 | 10.25 | 7.4772 | 13.0704 | 23.8206 | 10.0822 | 7.3548 | 12.6946 | 24.0477 | 9.7564 | 7.1171 | 12.4458 | 24.3337 | 9.4014 | 6.8582 | 12.2069 | 24.6885 | 8.9146 | 6.5031 | 11.8348 | 25.0553 | 8.5915 | 6.2674 | 11.4372 | 25.4026 | 8.1469 | 5.9431 | 11.0629 | 25.821 | 7.845 | 5.7228 | 10.7016 | 26.1847 | 7.5715 | 5.5233 | 10.2956 | 26.5628 | 7.39 | 5.3909 | 9.916 | 27.7881 | 6.501 | 4.7424 | 7.0338 | 28.825 | 5.3826 | 3.9265 | 2.5312 | 26.9591 | 4.373 | 3.1901 | -1.2094 | 20.1365 | 3.2663 | 2.3827 | -5.0951 | 13.2993 | 2.1573 | 1.5737 | -8.4384 | 23.5685 | 10.25 | 7.4772 | 13.0704 | 23.7467 | 10.1376 | 7.3952 | 12.7551 | 23.9107 | 9.7613 | 7.1208 | 12.4798 | 24.1112 | 9.0885 | 6.6299 | 12.1905 | 24.3653 | 9.0982 | 6.637 | 11.8146 | 24.6754 | 8.7985 | 6.4184 | 11.4351 | 25.047 | 8.3949 | 6.124 | 10.9663 | 25.3478 | 8.1719 | 5.9613 | 10.3993 | 25.5636 | 7.994 | 5.8315 | 10.0126 | 25.7882 | 7.8113 | 5.6983 | 9.6152 | 26.4966 | 7.2757 | 5.3076 | 8.3642 | 27.2478 | 6.7775 | 4.9441 | 7.0094 | 28.0141 | 6.2304 | 4.545 | 5.3642 | 28.895 | 5.6831 | 4.1458 | 3.6582 | 29.3952 | 5.1563 | 3.7614 | 2.5966 | 23.6118 | 10.25 | 7.4772 | 13.0704 | 23.8084 | 10.0228 | 7.3115 | 12.7008 | 24.0297 | 9.5532 | 6.969 | 12.4812 | 24.3117 | 9.1229 | 6.655 | 12.3056 | 24.6583 | 8.5983 | 6.2723 | 11.998 | 25.0167 | 8.2917 | 6.0487 | 11.6787 | 25.3416 | 7.8385 | 5.7181 | 11.4139 | 25.7425 | 7.5188 | 5.4849 | 11.1752 | 26.0615 | 7.1966 | 5.2498 | 10.9145 | 26.4015 | 6.9787 | 5.0909 | 10.6544 | 27.641 | 5.8596 | 4.2745 | 8.0669 | 27.6051 | 4.4778 | 3.2665 | 2.8977 | 19.7296 | 3.2003 | 2.3346 | -1.1968 | 11.439 | 1.8555 | 1.3536 | -4.8423 | 4.2608 | 0.69114 | 0.50418 | -7.4129 | 23.6121 | 10.25 | 7.4772 | 13.0704 | 23.7365 | 10.1156 | 7.3792 | 13.0531 | 23.8917 | 9.7067 | 7.0809 | 12.938 | 24.0995 | 9.2633 | 6.7574 | 12.7844 | 24.3874 | 8.7356 | 6.3725 | 12.4857 | 24.7717 | 8.5992 | 6.273 | 12.1251 | 25.1187 | 8.0201 | 5.8505 | 11.5407 | 25.5597 | 7.3205 | 5.3402 | 10.1368 | 26.009 | 6.7445 | 4.92 | 8.6538 | 26.4803 | 6.1322 | 4.4734 | 7.1675 | 27.7986 | 4.7436 | 3.4604 | 2.8355 | 21.1217 | 3.4262 | 2.4993 | -1.3266 | 14.0402 | 2.2775 | 1.6614 | -4.5727 | 7.419 | 1.2034 | 0.87789 | -6.6037 | 4.9439 | 0.80195 | 0.58501 | -5.3365 | 23.6015 | 10.25 | 7.4772 | 13.0704 | 23.7745 | 10.1227 | 7.3843 | 12.7612 | 23.9374 | 9.821 | 7.1643 | 12.5699 | 24.1275 | 9.4761 | 6.9127 | 12.4339 | 24.3682 | 9.0005 | 6.5657 | 12.2534 | 24.7045 | 8.7574 | 6.3884 | 12.0504 | 25.0743 | 8.3323 | 6.0783 | 11.82 | 25.4175 | 8.0461 | 5.8695 | 11.5427 | 25.7494 | 7.773 | 5.6703 | 11.1706 | 26.071 | 7.5895 | 5.5364 | 10.7879 | 27.1374 | 6.9866 | 5.0966 | 9.3374 | 28.1525 | 6.2854 | 4.5851 | 7.192 | 28.7996 | 5.6832 | 4.1458 | 4.9638 | 29.2214 | 4.9634 | 3.6208 | 2.9007 | 26.7837 | 4.3446 | 3.1693 | 1.9165 | 23.6015 | 10.25 | 7.4772 | 13.0704 | 23.7383 | 10.0536 | 7.3339 | 12.9042 | 23.9364 | 9.6223 | 7.0193 | 12.6705 | 24.1939 | 9.1599 | 6.682 | 12.3979 | 24.5112 | 8.6755 | 6.3286 | 11.9741 | 24.8777 | 8.4431 | 6.1591 | 11.5413 | 25.1932 | 7.8555 | 5.7304 | 10.876 | 25.6145 | 7.1408 | 5.2091 | 9.3594 | 26.0199 | 6.5436 | 4.7735 | 7.8184 | 26.4556 | 5.919 | 4.3179 | 6.2689 | 27.6217 | 4.4805 | 3.2685 | 1.6938 | 19.1026 | 3.0986 | 2.2604 | -2.8036 | 11.3122 | 1.8349 | 1.3386 | -6.4111 | 4.2672 | 0.69218 | 0.50494 | -8.8632 | 1.2974 | 0.21046 | 0.15353 | -8.0075
WESTHOUGHTON | WESTHOUGHTON | KEARSLEY | 365831 | 407025 | 24.9797 | 11.534 | 8.2897 | 9.5456 | 25.1128 | 10.8519 | 7.7995 | 7.3358 | 25.3042 | 10.306 | 7.4072 | 6.4245 | 25.5658 | 9.7688 | 7.021 | 5.918 | 25.9066 | 9.4161 | 6.7675 | 5.2326 | 26.264 | 8.9764 | 6.4515 | 4.5209 | 26.5465 | 8.8705 | 6.3754 | 3.8336 | 26.9087 | 8.6974 | 6.251 | 3.1527 | 27.2425 | 8.5046 | 6.1124 | 2.3868 | 27.5898 | 8.323 | 5.9819 | 1.6361 | 28.7208 | 7.4902 | 5.3833 | -2.2331 | 29.8108 | 6.5099 | 4.6788 | -7.3469 | 30.5567 | 5.7568 | 4.1375 | -11.4166 | 31.1528 | 5.6703 | 4.0754 | -15.6867 | 29.1873 | 4.8055 | 3.4538 | -19.4872 | 24.9361 | 11.534 | 8.2897 | 9.5456 | 25.0285 | 11.1519 | 8.0151 | 8.8835 | 25.1179 | 10.7889 | 7.7542 | 8.6589 | 25.2425 | 10.3976 | 7.473 | 8.517 | 25.427 | 9.9445 | 7.1473 | 8.282 | 25.6676 | 9.6015 | 6.9008 | 8.0031 | 25.9385 | 9.3573 | 6.7253 | 7.6204 | 26.2519 | 9.2333 | 6.6361 | 7.1145 | 26.4957 | 9.1132 | 6.5499 | 6.6635 | 26.7634 | 8.9912 | 6.4622 | 6.1908 | 27.5966 | 8.6223 | 6.197 | 4.7145 | 28.3182 | 8.2807 | 5.9515 | 3.1464 | 29.0244 | 7.9649 | 5.7245 | 1.6477 | 29.7628 | 8.0932 | 5.8168 | -0.053718 | 30.259 | 8.2874 | 5.9563 | -1.1358 | 24.998 | 11.534 | 8.2897 | 9.5456 | 25.1484 | 10.773 | 7.7428 | 7.025 | 25.368 | 10.163 | 7.3044 | 6.0855 | 25.6699 | 9.5311 | 6.8502 | 5.6449 | 26.0415 | 9.2952 | 6.6806 | 5.0345 | 26.3355 | 8.9181 | 6.4096 | 4.4137 | 26.6347 | 8.732 | 6.2758 | 3.8576 | 27.0122 | 8.5557 | 6.1491 | 3.321 | 27.338 | 8.3646 | 6.0118 | 2.707 | 27.6774 | 8.1778 | 5.8775 | 2.0906 | 28.8284 | 7.3147 | 5.2572 | -1.4123 | 29.9692 | 6.2925 | 4.5225 | -6.2786 | 30.7884 | 5.5013 | 3.9539 | -10.1489 | 31.441 | 5.3679 | 3.858 | -14.1622 | 27.2934 | 4.4937 | 3.2297 | -17.654 | 24.998 | 11.534 | 8.2897 | 9.5456 | 24.9876 | 10.9858 | 7.8957 | 8.1819 | 25.0833 | 10.4571 | 7.5158 | 7.5193 | 25.2391 | 9.9034 | 7.1178 | 7.141 | 25.4973 | 9.6039 | 6.9025 | 6.5434 | 25.8983 | 9.2091 | 6.6188 | 5.8882 | 26.2097 | 8.9093 | 6.4033 | 4.9962 | 26.5894 | 8.5012 | 6.11 | 3.2028 | 26.9493 | 8.0882 | 5.8131 | 1.3205 | 27.3296 | 7.7392 | 5.5623 | -0.57095 | 28.5175 | 7.4575 | 5.3598 | -6.1277 | 29.6261 | 6.354 | 4.5667 | -10.7107 | 30.3754 | 5.4379 | 3.9083 | -14.2257 | 28.4119 | 4.6778 | 3.362 | -16.5331 | 27.8938 | 4.5925 | 3.3007 | -15.3422 | 24.9797 | 11.534 | 8.2897 | 9.5456 | 25.0917 | 11.0579 | 7.9475 | 8.435 | 25.2161 | 10.5669 | 7.5947 | 7.8103 | 25.3707 | 10.059 | 7.2296 | 7.4319 | 25.5934 | 9.7307 | 6.9936 | 6.9906 | 25.9438 | 9.3422 | 6.7144 | 6.4832 | 26.3167 | 9.2536 | 6.6507 | 5.9139 | 26.628 | 9.0956 | 6.5372 | 5.3021 | 26.9056 | 8.9098 | 6.4037 | 4.5566 | 27.2034 | 8.7269 | 6.2722 | 3.7946 | 28.2164 | 8.1371 | 5.8483 | 1.2693 | 29.2306 | 7.7357 | 5.5598 | -0.61983 | 29.8715 | 7.5128 | 5.3996 | -1.7657 | 30.371 | 8.0379 | 5.777 | -2.9334 | 30.6107 | 7.7607 | 5.5778 | -3.5756 | 24.9797 | 11.534 | 8.2897 | 9.5456 | 25.0187 | 10.7778 | 7.7462 | 7.068 | 25.1951 | 10.1874 | 7.3219 | 6.0676 | 25.4493 | 9.6288 | 6.9204 | 5.5428 | 25.7842 | 9.2906 | 6.6774 | 4.8149 | 26.1195 | 8.8781 | 6.3808 | 4.079 | 26.3913 | 8.5594 | 6.1518 | 3.0881 | 26.7803 | 8.1229 | 5.8381 | 1.1573 | 27.1305 | 7.6918 | 5.5282 | -0.82585 | 27.4983 | 7.3234 | 5.2635 | -2.8189 | 28.6798 | 6.9581 | 5.0009 | -8.7276 | 29.8114 | 5.7831 | 4.1564 | -13.6588 | 29.1402 | 4.7977 | 3.4482 | -17.5193 | 24.079 | 3.9644 | 2.8493 | -20.2196 | 23.1156 | 3.8058 | 2.7353 | -19.4468
WESTLINTON | CARLISLE | HARKER / HUTTON | 339551 | 564489 | 17.5873 | 17.5873 | 16.1861 | 10.2245 | 17.638 | 17.638 | 15.8428 | 7.9642 | 17.7366 | 17.7366 | 15.7309 | 7.4665 | 17.8606 | 17.8606 | 15.6657 | 7.3399 | 18.0285 | 18.0285 | 15.579 | 7.137 | 18.2852 | 18.2852 | 15.483 | 6.8641 | 18.6594 | 18.6594 | 15.3703 | 6.4008 | 19.1269 | 19.1269 | 15.2124 | 5.5574 | 19.5817 | 19.5817 | 15.0283 | 4.5202 | 20.0488 | 20.0488 | 14.8272 | 3.3472 | 21.5709 | 19.6827 | 14.1464 | -0.62527 | 22.8619 | 18.8364 | 13.5381 | -4.1539 | 23.6496 | 18.2214 | 13.0961 | -6.3573 | 24.1358 | 17.7436 | 12.7527 | -7.7583 | 24.4019 | 16.5033 | 11.8613 | -8.6434 | 17.5794 | 17.5794 | 16.1861 | 10.2245 | 17.6399 | 17.6399 | 16.0995 | 9.7408 | 17.7305 | 17.7305 | 16.0403 | 9.5481 | 17.8475 | 17.8475 | 15.9766 | 9.393 | 17.9609 | 17.9609 | 15.9011 | 9.2047 | 18.1072 | 18.1072 | 15.8258 | 9.0178 | 18.2971 | 18.2971 | 15.7513 | 8.7747 | 18.5386 | 18.5386 | 15.6711 | 8.4633 | 18.7565 | 18.7565 | 15.5995 | 8.1938 | 19.0273 | 19.0273 | 15.5007 | 7.7374 | 19.9541 | 19.9541 | 15.121 | 5.7481 | 21.0286 | 20.3885 | 14.6536 | 3.1038 | 22.129 | 19.7049 | 14.1623 | 0.22701 | 23.3304 | 19.0819 | 13.7146 | -3.0094 | 24.1128 | 18.5451 | 13.3287 | -5.1951 | 17.5906 | 17.5906 | 16.1861 | 10.2245 | 17.6408 | 17.6408 | 15.7796 | 7.6001 | 17.7377 | 17.7377 | 15.632 | 7.0427 | 17.8433 | 17.8433 | 15.5438 | 6.9256 | 17.9865 | 17.9865 | 15.4412 | 6.7416 | 18.2 | 18.2 | 15.3349 | 6.501 | 18.5048 | 18.5048 | 15.2306 | 6.2099 | 18.9188 | 18.9188 | 15.087 | 5.6101 | 19.3126 | 19.3126 | 14.9134 | 4.7925 | 19.7339 | 19.7339 | 14.721 | 3.8286 | 21.2058 | 19.4646 | 13.9896 | 0.025807 | 22.6764 | 18.4061 | 13.2288 | -3.9472 | 23.6618 | 17.5075 | 12.583 | -6.6432 | 24.2598 | 15.6743 | 11.2655 | -8.2953 | 24.5294 | 14.5977 | 10.4917 | -9.1302 | 17.5906 | 17.5906 | 16.1861 | 10.2245 | 17.6013 | 17.6013 | 15.8978 | 8.422 | 17.6713 | 17.6713 | 15.7908 | 8.015 | 17.7867 | 17.7867 | 15.6977 | 7.8664 | 17.9368 | 17.9368 | 15.5909 | 7.6694 | 18.1825 | 18.1825 | 15.4489 | 7.3957 | 18.5526 | 18.5526 | 15.2412 | 6.9024 | 19.0245 | 19.0245 | 14.9515 | 5.9176 | 19.4726 | 19.4726 | 14.4678 | 4.7197 | 19.963 | 19.8752 | 14.2847 | 3.3755 | 21.4898 | 17.6768 | 12.7047 | -0.85102 | 22.7284 | 16.4761 | 11.8417 | -4.2825 | 23.4657 | 15.3545 | 11.0356 | -6.3251 | 23.8845 | 14.6313 | 10.5158 | -7.3499 | 24.0033 | 14.3121 | 10.2864 | -7.3801 | 17.5873 | 17.5873 | 16.1861 | 10.2245 | 17.6303 | 17.6303 | 16.0377 | 9.339 | 17.7096 | 17.7096 | 15.9616 | 9.0894 | 17.8163 | 17.8163 | 15.9005 | 8.9848 | 17.9423 | 17.9423 | 15.8252 | 8.8493 | 18.1426 | 18.1426 | 15.7448 | 8.6744 | 18.4368 | 18.4368 | 15.6521 | 8.3472 | 18.8317 | 18.8317 | 15.5252 | 7.7209 | 19.204 | 19.204 | 15.3748 | 6.9229 | 19.6055 | 19.6055 | 15.2072 | 5.9872 | 20.9633 | 20.3197 | 14.6042 | 2.5181 | 22.2801 | 19.5156 | 14.0262 | -0.8864 | 23.1502 | 18.8185 | 13.5252 | -3.1133 | 23.6973 | 18.3163 | 13.1643 | -4.5182 | 23.9009 | 17.0644 | 12.2645 | -5.0517 | 17.5873 | 17.5873 | 16.1861 | 10.2245 | 17.6137 | 17.6137 | 15.7384 | 7.3049 | 17.7031 | 17.7031 | 15.5988 | 6.6779 | 17.8142 | 17.8142 | 15.5007 | 6.5004 | 17.9561 | 17.9561 | 15.3908 | 6.2876 | 18.1659 | 18.1659 | 15.2511 | 6.0302 | 18.4699 | 18.4699 | 15.0646 | 5.6828 | 18.898 | 18.898 | 14.8053 | 4.9537 | 19.3694 | 19.3694 | 14.4687 | 3.9406 | 19.8264 | 19.745 | 14.1911 | 2.7703 | 21.3611 | 17.4468 | 12.5393 | -1.3798 | 22.8235 | 16.2857 | 11.7049 | -5.3335 | 23.7765 | 15.058 | 10.8224 | -7.9511 | 24.3158 | 14.1764 | 10.1888 | -9.3375 | 24.4607 | 13.8456 | 9.9511 | -9.4764
WHALLEY | PADIHAM | PADIHAM | 373376 | 436176 | 25.6942 | 13.1598 | 9.4582 | 15.4451 | 25.8177 | 12.9881 | 9.3348 | 14.6796 | 25.9907 | 12.9106 | 9.2791 | 14.3399 | 26.2199 | 12.5171 | 8.9963 | 14.1117 | 26.4952 | 12.2413 | 8.7981 | 13.7919 | 26.7338 | 11.7456 | 8.4418 | 13.4695 | 27.0114 | 11.3121 | 8.1303 | 13.1773 | 27.3523 | 10.9344 | 7.8587 | 12.8905 | 27.6201 | 10.7918 | 7.7563 | 12.5564 | 27.8835 | 10.753 | 7.7284 | 12.2517 | 28.6869 | 10.3538 | 7.4415 | 10.6869 | 29.2822 | 9.8385 | 7.0711 | 8.2134 | 29.6848 | 9.4251 | 6.774 | 6.2675 | 30.0409 | 10.1252 | 7.2772 | 4.3112 | 30.3082 | 9.97 | 7.1656 | 2.5272 | 25.6516 | 13.1598 | 9.4582 | 15.4451 | 25.7515 | 13.0773 | 9.3989 | 15.0704 | 25.8539 | 12.9964 | 9.3408 | 14.8331 | 25.9949 | 12.8961 | 9.2687 | 14.6194 | 26.1881 | 12.7562 | 9.1681 | 14.3577 | 26.4279 | 12.6028 | 9.0579 | 14.0914 | 26.7132 | 12.293 | 8.8352 | 13.7369 | 27.0411 | 12.1257 | 8.715 | 13.2377 | 27.1977 | 12.0161 | 8.6362 | 12.8333 | 27.3387 | 11.9237 | 8.5698 | 12.4316 | 27.7937 | 11.5008 | 8.2658 | 11.2419 | 28.2636 | 11.0954 | 7.9745 | 10.0385 | 28.6997 | 10.8286 | 7.7827 | 8.9255 | 29.1524 | 11.2563 | 8.0901 | 7.6634 | 29.4841 | 11.6609 | 8.3809 | 6.7851 | 25.7129 | 13.1598 | 9.4582 | 15.4451 | 25.8507 | 12.9336 | 9.2957 | 14.6071 | 26.0475 | 12.8395 | 9.228 | 14.2754 | 26.3118 | 12.4018 | 8.9134 | 14.0268 | 26.5853 | 11.9583 | 8.5947 | 13.6886 | 26.8572 | 11.4939 | 8.2609 | 13.3556 | 27.1743 | 11.0728 | 7.9583 | 13.1369 | 27.5628 | 10.7818 | 7.7491 | 12.9294 | 27.8568 | 10.6849 | 7.6795 | 12.6921 | 28.1439 | 10.5733 | 7.5992 | 12.4677 | 28.7732 | 10.0386 | 7.215 | 11.1427 | 29.3491 | 9.4075 | 6.7613 | 8.8638 | 29.7631 | 8.8992 | 6.396 | 7.0871 | 30.1055 | 9.5649 | 6.8745 | 5.3373 | 30.3291 | 9.3321 | 6.7071 | 3.7909 | 25.7129 | 13.1598 | 9.4582 | 15.4451 | 25.7351 | 13.0356 | 9.3689 | 15.0704 | 25.8262 | 13.0051 | 9.347 | 14.86 | 25.965 | 12.4575 | 8.9535 | 14.6504 | 26.1732 | 12.2311 | 8.7907 | 14.3471 | 26.4539 | 11.9687 | 8.6022 | 14.0287 | 26.739 | 11.5941 | 8.3329 | 13.6907 | 27.071 | 10.8381 | 7.7896 | 12.9703 | 27.3428 | 10.7648 | 7.7369 | 12.2093 | 27.6149 | 10.4757 | 7.5291 | 11.4542 | 28.4527 | 10.6112 | 7.6265 | 9.2785 | 29.1435 | 10.0225 | 7.2034 | 7.1252 | 29.5598 | 9.4529 | 6.794 | 5.5271 | 29.8222 | 9.6532 | 6.9379 | 4.5093 | 29.8453 | 9.3783 | 6.7403 | 4.9748 | 25.6942 | 13.1598 | 9.4582 | 15.4451 | 25.7988 | 13.0469 | 9.3771 | 14.9194 | 25.9176 | 12.9964 | 9.3408 | 14.6482 | 26.0646 | 12.5813 | 9.0424 | 14.4712 | 26.2595 | 12.363 | 8.8855 | 14.2674 | 26.5365 | 11.8974 | 8.5509 | 14.0523 | 26.8126 | 11.4593 | 8.236 | 13.8129 | 27.1221 | 11.0824 | 7.9652 | 13.5303 | 27.3585 | 10.9111 | 7.842 | 13.1528 | 27.599 | 10.8718 | 7.8138 | 12.7826 | 28.3729 | 10.5613 | 7.5906 | 11.5751 | 29.0492 | 10.2578 | 7.3725 | 10.2252 | 29.406 | 10.0384 | 7.2148 | 9.3061 | 29.7065 | 10.9478 | 7.8684 | 8.4324 | 29.8456 | 11.0309 | 7.9281 | 7.943 | 25.6942 | 13.1598 | 9.4582 | 15.4451 | 25.7676 | 12.9449 | 9.3038 | 14.7236 | 25.9328 | 12.8851 | 9.2608 | 14.3781 | 26.1594 | 12.3212 | 8.8555 | 14.0724 | 26.4366 | 12.0676 | 8.6732 | 13.6812 | 26.6689 | 11.7975 | 8.4791 | 13.3017 | 26.9431 | 11.4234 | 8.2102 | 12.8892 | 27.2982 | 10.6665 | 7.6662 | 12.0684 | 27.5771 | 10.5667 | 7.5945 | 11.2414 | 27.8522 | 10.2653 | 7.3779 | 10.4205 | 28.6685 | 10.3689 | 7.4523 | 8.0381 | 29.2849 | 9.7424 | 7.002 | 5.7062 | 29.7125 | 9.0984 | 6.5392 | 3.9291 | 29.9746 | 9.298 | 6.6826 | 2.705 | 30.0107 | 8.9491 | 6.4319 | 2.9589
WHALLEY RANGE | WEST DIDSBURY | SOUTH MANCHESTER | 382923 | 394645 | 36.016 | 9.2033 | 6.7137 | 14.9476 | 36.1415 | 8.9867 | 6.5557 | 14.3095 | 36.2953 | 8.8331 | 6.4436 | 13.8244 | 36.483 | 8.6646 | 6.3207 | 13.3686 | 36.7094 | 8.4696 | 6.1784 | 12.7997 | 36.9661 | 8.1967 | 5.9794 | 12.2115 | 37.2574 | 7.9085 | 5.7692 | 11.6573 | 37.5858 | 7.6296 | 5.5657 | 11.1574 | 37.7563 | 7.336 | 5.3515 | 10.6501 | 37.9147 | 7.0494 | 5.1425 | 10.165 | 38.5815 | 6.3548 | 4.6358 | 7.5877 | 34.0217 | 5.5187 | 4.0258 | 3.7501 | 30.5513 | 4.9557 | 3.6151 | 1.0083 | 26.6883 | 4.3291 | 3.158 | -1.4368 | 23.6515 | 3.8365 | 2.7987 | -3.0639 | 35.9888 | 9.2033 | 6.7137 | 14.9476 | 36.1256 | 9.1247 | 6.6564 | 14.618 | 36.2717 | 9.0313 | 6.5882 | 14.3021 | 36.4542 | 8.8951 | 6.4889 | 13.9535 | 36.6905 | 8.7298 | 6.3683 | 13.5137 | 36.9767 | 8.5519 | 6.2385 | 13.1083 | 37.218 | 8.2128 | 5.9911 | 12.6077 | 37.4626 | 8.0093 | 5.8427 | 11.9963 | 37.5652 | 7.8374 | 5.7173 | 11.5718 | 37.672 | 7.6718 | 5.5965 | 11.1331 | 37.996 | 7.1752 | 5.2342 | 9.8521 | 38.3163 | 6.7852 | 4.9497 | 8.6361 | 38.6019 | 6.4357 | 4.6948 | 7.5714 | 37.5472 | 6.0905 | 4.443 | 6.4808 | 35.2768 | 5.7222 | 4.1743 | 5.7295 | 36.0275 | 9.2033 | 6.7137 | 14.9476 | 36.1839 | 8.9456 | 6.5257 | 14.1481 | 36.3772 | 8.7136 | 6.3565 | 13.5282 | 36.6149 | 8.4988 | 6.1998 | 12.9481 | 36.8999 | 8.2387 | 6.01 | 12.2461 | 37.2236 | 7.902 | 5.7644 | 11.5187 | 37.5837 | 7.5664 | 5.5196 | 10.837 | 37.8869 | 7.2061 | 5.2568 | 10.1258 | 38.1063 | 6.9108 | 5.0414 | 9.4437 | 38.3147 | 6.6031 | 4.8169 | 8.7685 | 34.7757 | 5.641 | 4.115 | 5.6769 | 29.8095 | 4.8354 | 3.5274 | 1.8024 | 25.5779 | 4.149 | 3.0266 | -0.67342 | 21.3968 | 3.4708 | 2.5319 | -2.5536 | 18.9593 | 3.0754 | 2.2435 | -3.159 | 36.0275 | 9.2033 | 6.7137 | 14.9476 | 36.0349 | 9.055 | 6.6055 | 14.64 | 36.1241 | 8.9222 | 6.5086 | 14.1904 | 36.2455 | 8.748 | 6.3816 | 13.7118 | 36.4216 | 8.5226 | 6.2171 | 13.0703 | 36.6766 | 8.2649 | 6.0291 | 12.3526 | 36.9919 | 7.9533 | 5.8018 | 11.4658 | 37.3593 | 7.5346 | 5.4964 | 9.9617 | 37.6468 | 7.1546 | 5.2191 | 8.4899 | 37.9287 | 6.6459 | 4.8481 | 7.0731 | 34.0071 | 5.5163 | 4.0241 | 3.1589 | 29.4704 | 4.7804 | 3.4872 | -0.091571 | 25.615 | 4.155 | 3.031 | -1.9671 | 22.7048 | 3.6829 | 2.6867 | -2.6547 | 21.9285 | 3.557 | 2.5948 | -1.5066 | 36.016 | 9.2033 | 6.7137 | 14.9476 | 36.1289 | 9.0524 | 6.6036 | 14.5203 | 36.2434 | 8.9135 | 6.5023 | 14.1406 | 36.3707 | 8.7613 | 6.3913 | 13.8015 | 36.5342 | 8.6139 | 6.2837 | 13.4142 | 36.7644 | 8.3909 | 6.1211 | 13.023 | 37.0546 | 8.1319 | 5.9321 | 12.6276 | 37.3346 | 7.8643 | 5.7369 | 12.2071 | 37.491 | 7.5666 | 5.5197 | 11.7196 | 37.6466 | 7.2515 | 5.2898 | 11.1938 | 38.1427 | 6.7466 | 4.9216 | 9.4983 | 38.6644 | 6.2987 | 4.5948 | 7.7915 | 37.2422 | 6.0411 | 4.4069 | 6.6412 | 35.0046 | 5.6781 | 4.1421 | 5.5549 | 33.1728 | 5.3809 | 3.9253 | 4.9547 | 36.016 | 9.2033 | 6.7137 | 14.9476 | 36.0783 | 9 | 6.5654 | 14.4074 | 36.2427 | 8.8319 | 6.4428 | 13.7869 | 36.4522 | 8.6196 | 6.2879 | 13.1459 | 36.7068 | 8.3641 | 6.1015 | 12.3599 | 36.9912 | 8.0875 | 5.8997 | 11.5536 | 37.3214 | 7.7576 | 5.659 | 10.5605 | 37.7448 | 7.3097 | 5.3323 | 8.9003 | 38.0521 | 6.909 | 5.04 | 7.3176 | 38.3486 | 6.348 | 4.6308 | 5.7908 | 31.8936 | 5.1734 | 3.774 | 1.5577 | 27.1513 | 4.4042 | 3.2128 | -1.8772 | 23.0445 | 3.738 | 2.7268 | -3.9338 | 19.8198 | 3.215 | 2.3453 | -4.8711 | 18.6684 | 3.0282 | 2.209 | -4.0793
WHASSET | KENDAL (PARKSIDE RD) | HARKER / HUTTON | 350648 | 481468 | 21.3411 | 21.3411 | 15.3533 | 7.2936 | 21.4141 | 21.1584 | 15.2069 | 6.461 | 21.5032 | 21.0443 | 15.125 | 6.1878 | 21.6233 | 20.9547 | 15.0606 | 6.0971 | 24.4222 | 20.3649 | 14.6366 | 3.2461 | 24.4647 | 20.2552 | 14.5578 | 3.2711 | 26.7209 | 19.754 | 14.1976 | 1.0474 | 26.6414 | 19.6828 | 14.1464 | 1.1998 | 26.7425 | 19.5662 | 14.0626 | 1.1025 | 26.8599 | 19.4141 | 13.9533 | 1.0122 | 27.5273 | 18.8581 | 13.5537 | 0.11701 | 28.0645 | 18.4573 | 13.2656 | -1.3901 | 28.2517 | 18.0383 | 12.9644 | -2.4578 | 28.1261 | 17.4791 | 12.5626 | -3.2307 | 28.1584 | 16.4085 | 11.7931 | -4.0883 | 21.3269 | 21.3269 | 15.3533 | 7.2936 | 21.4057 | 21.2638 | 15.2827 | 6.9072 | 21.4901 | 21.1898 | 15.2295 | 6.6735 | 21.5989 | 21.1126 | 15.174 | 6.524 | 21.7405 | 21.011 | 15.101 | 6.3779 | 21.8902 | 20.9059 | 15.0255 | 6.2308 | 21.9822 | 20.7811 | 14.9358 | 6.0451 | 22.0955 | 20.6619 | 14.8501 | 5.8186 | 22.1818 | 20.5549 | 14.7732 | 5.6148 | 22.2784 | 20.4451 | 14.6943 | 5.411 | 22.6355 | 20.1201 | 14.4607 | 4.7939 | 23.0615 | 19.8114 | 14.2389 | 4.1841 | 23.5005 | 19.5133 | 14.0246 | 3.6023 | 23.9916 | 19.1712 | 13.7787 | 2.9264 | 24.3404 | 18.7794 | 13.4972 | 2.4024 | 21.347 | 21.347 | 15.3533 | 7.2936 | 21.4201 | 21.1178 | 15.1778 | 6.3375 | 21.5139 | 20.9661 | 15.0687 | 6.0518 | 21.6411 | 20.8478 | 14.9837 | 5.9749 | 24.3357 | 20.2535 | 14.5566 | 3.2574 | 24.3787 | 20.1223 | 14.4623 | 3.292 | 26.4885 | 19.5463 | 14.0483 | 1.2046 | 26.3959 | 19.5196 | 14.0291 | 1.3935 | 26.465 | 19.2209 | 13.8144 | 1.3765 | 26.552 | 18.9987 | 13.6548 | 1.3702 | 29.0453 | 18.3949 | 13.2208 | -1.2149 | 29.6404 | 17.8052 | 12.7969 | -2.5449 | 29.8311 | 17.2176 | 12.3746 | -3.3879 | 29.5599 | 16.041 | 11.529 | -3.7853 | 29.5005 | 15.0388 | 10.8087 | -4.2505 | 21.347 | 21.347 | 15.3533 | 7.2936 | 21.3662 | 21.1979 | 15.2353 | 6.7344 | 21.4135 | 21.0863 | 15.1551 | 6.5361 | 23.956 | 20.5184 | 14.747 | 3.9095 | 26.4018 | 19.9554 | 14.3423 | 1.4123 | 26.2725 | 19.6523 | 14.1245 | 1.6135 | 26.2268 | 19.2932 | 13.8664 | 1.709 | 26.2335 | 18.6741 | 13.4214 | 1.5454 | 26.548 | 17.7151 | 12.7322 | 0.98994 | 26.6539 | 17.5825 | 12.6369 | 0.60141 | 27.4603 | 16.5202 | 11.8734 | -1.0073 | 27.8832 | 15.6806 | 11.27 | -2.1659 | 28.0429 | 15.3339 | 11.0208 | -2.9024 | 27.9019 | 14.7982 | 10.6357 | -2.9273 | 27.721 | 14.7754 | 10.6194 | -1.943 | 21.341 | 21.341 | 15.3533 | 7.2936 | 21.4024 | 21.2012 | 15.2378 | 6.6611 | 21.4672 | 21.0986 | 15.164 | 6.4333 | 21.5491 | 21.0162 | 15.1048 | 6.3642 | 24.3025 | 20.4446 | 14.6939 | 3.5856 | 24.3143 | 20.3535 | 14.6285 | 3.6935 | 26.5673 | 19.8622 | 14.2754 | 1.5196 | 26.474 | 19.794 | 14.2263 | 1.6786 | 26.5596 | 19.6748 | 14.1406 | 1.5612 | 26.6692 | 19.5169 | 14.0272 | 1.4325 | 27.2614 | 19.0075 | 13.661 | 0.77937 | 27.8272 | 18.72 | 13.4544 | 0.015489 | 28.0481 | 18.4316 | 13.2472 | -0.35689 | 27.951 | 17.8767 | 12.8483 | -0.43271 | 27.9412 | 16.8513 | 12.1114 | -0.37568 | 21.341 | 21.341 | 15.3533 | 7.2936 | 21.3832 | 21.1094 | 15.1718 | 6.3146 | 21.4649 | 20.9726 | 15.0734 | 6.0005 | 24.0468 | 20.392 | 14.6562 | 3.3182 | 26.5246 | 19.8177 | 14.2434 | 0.76862 | 26.3962 | 19.5504 | 14.0512 | 0.94503 | 26.3362 | 19.1614 | 13.7717 | 1.0089 | 26.3432 | 18.629 | 13.389 | 0.79499 | 26.6229 | 17.6018 | 12.6507 | 0.21856 | 26.7024 | 17.419 | 12.5194 | -0.18983 | 27.504 | 16.3684 | 11.7643 | -1.8724 | 27.966 | 15.685 | 11.2731 | -3.1251 | 28.1753 | 15.0786 | 10.8373 | -3.9591 | 28.0591 | 14.6038 | 10.496 | -4.0892 | 27.9068 | 14.4957 | 10.4184 | -3.2171
WHITTLE LE WOODS | LEYLAND | PENWORTHAM WEST / STANAH | 357874 | 421203 | 23.4293 | 15.6301 | 11.2337 | 11.035 | 23.4958 | 15.2091 | 10.9311 | 10.4296 | 23.5864 | 15.0157 | 10.7921 | 10.1557 | 23.6963 | 14.9726 | 10.7611 | 9.945 | 23.8303 | 14.8113 | 10.6452 | 9.6323 | 23.9821 | 14.5798 | 10.4788 | 9.3152 | 24.1563 | 14.3769 | 10.333 | 9.0264 | 24.3675 | 14.2369 | 10.2324 | 8.7601 | 24.54 | 14.1156 | 10.1452 | 8.4635 | 24.7056 | 13.9969 | 10.0599 | 8.1775 | 25.2261 | 13.4855 | 9.6923 | 6.488 | 25.7534 | 12.8466 | 9.2331 | 3.6659 | 26.1127 | 12.3198 | 8.8545 | 1.3858 | 26.4507 | 11.7454 | 8.4416 | -0.98466 | 26.7187 | 11.1992 | 8.0491 | -3.2236 | 23.3951 | 15.6301 | 11.2337 | 11.035 | 23.4645 | 15.4262 | 11.0871 | 10.8389 | 23.5223 | 15.2835 | 10.9846 | 10.687 | 23.5901 | 15.1493 | 10.8881 | 10.5294 | 23.6807 | 14.9553 | 10.7487 | 10.3235 | 23.7931 | 14.7141 | 10.5753 | 10.1057 | 23.9286 | 14.6639 | 10.5392 | 9.8117 | 24.0853 | 14.4865 | 10.4117 | 9.3902 | 24.1855 | 14.318 | 10.2907 | 9.0286 | 24.289 | 14.1176 | 10.1466 | 8.6666 | 24.6099 | 13.9215 | 10.0056 | 7.5273 | 24.9292 | 13.6992 | 9.8459 | 6.346 | 25.2163 | 13.4106 | 9.6384 | 5.2535 | 25.5121 | 13.1264 | 9.4342 | 4.0587 | 25.7329 | 12.8201 | 9.2141 | 3.2721 | 23.4368 | 15.6301 | 11.2337 | 11.035 | 23.5097 | 15.1115 | 10.8609 | 10.3764 | 23.6107 | 15.0177 | 10.7935 | 10.1136 | 23.736 | 14.863 | 10.6824 | 9.94 | 23.8888 | 14.6857 | 10.5549 | 9.668 | 24.0627 | 14.4346 | 10.3744 | 9.3984 | 24.2638 | 14.2521 | 10.2433 | 9.1766 | 24.5073 | 14.1088 | 10.1402 | 8.9826 | 24.6967 | 13.9843 | 10.0508 | 8.7637 | 24.8774 | 13.8619 | 9.9628 | 8.5613 | 25.3554 | 13.3128 | 9.5682 | 7.0416 | 25.8458 | 12.6258 | 9.0744 | 4.3875 | 26.2088 | 12.0509 | 8.6612 | 2.2869 | 26.5345 | 11.4582 | 8.2352 | 0.16303 | 26.7738 | 10.8783 | 7.8184 | -1.9259 | 23.4368 | 15.6301 | 11.2337 | 11.035 | 23.4312 | 15.2263 | 10.9435 | 10.771 | 23.4769 | 15.21 | 10.9317 | 10.6144 | 23.5397 | 15.1102 | 10.86 | 10.4798 | 23.6364 | 14.9503 | 10.7451 | 10.222 | 23.7839 | 14.7663 | 10.6128 | 9.9408 | 23.9708 | 14.5634 | 10.467 | 9.5551 | 24.1933 | 14.2936 | 10.2731 | 8.7232 | 24.3775 | 14.0393 | 10.0903 | 7.8527 | 24.5586 | 13.7752 | 9.9005 | 6.9914 | 25.1105 | 13.0715 | 9.3948 | 4.4889 | 25.6782 | 12.4157 | 8.9234 | 1.9842 | 26.0472 | 11.848 | 8.5154 | 0.019053 | 26.2984 | 11.3603 | 8.1648 | -1.3093 | 26.3335 | 11.2028 | 8.0516 | -0.90288 | 23.4293 | 15.6301 | 11.2337 | 11.035 | 23.486 | 15.3065 | 11.0011 | 10.819 | 23.5488 | 15.119 | 10.8664 | 10.6478 | 23.6162 | 15.1038 | 10.8554 | 10.5099 | 23.7039 | 14.9795 | 10.766 | 10.3419 | 23.8371 | 14.7806 | 10.6231 | 10.1483 | 24.0112 | 14.5831 | 10.4812 | 9.9388 | 24.2017 | 14.4538 | 10.3882 | 9.7207 | 24.3543 | 14.3336 | 10.3019 | 9.4248 | 24.5063 | 14.2157 | 10.2171 | 9.1373 | 24.9882 | 13.8365 | 9.9446 | 8.1227 | 25.4713 | 13.4813 | 9.6893 | 6.8413 | 25.7506 | 13.2001 | 9.4872 | 5.9257 | 26.0031 | 12.9114 | 9.2796 | 5.0736 | 26.1453 | 12.6643 | 9.1021 | 4.511 | 23.4293 | 15.6301 | 11.2337 | 11.035 | 23.4492 | 15.1094 | 10.8594 | 10.5016 | 23.5327 | 15.1039 | 10.8554 | 10.2288 | 23.6407 | 14.9746 | 10.7626 | 10.0049 | 23.7745 | 14.7868 | 10.6276 | 9.6664 | 23.9237 | 14.5928 | 10.4881 | 9.3317 | 24.1007 | 14.3768 | 10.3329 | 8.8801 | 24.3385 | 14.0865 | 10.1242 | 7.9562 | 24.5339 | 13.8226 | 9.9346 | 7.0176 | 24.7231 | 13.5469 | 9.7364 | 6.0889 | 25.2762 | 12.8166 | 9.2116 | 3.3653 | 25.8022 | 12.1271 | 8.716 | 0.67593 | 26.1794 | 11.5206 | 8.2801 | -1.4476 | 26.4066 | 11.0032 | 7.9082 | -2.9543 | 26.4583 | 10.8089 | 7.7685 | -2.7598
WHITWORTH | ROCHDALE CENTRAL | ROCHDALE | 388779 | 419157 | 9.9575 | 4.5398 | 3.3118 | 6.5725 | 9.9956 | 4.5587 | 3.3255 | 6.5164 | 10.0533 | 4.4553 | 3.25 | 6.4411 | 10.1287 | 4.1227 | 3.0074 | 6.366 | 10.2127 | 4.0974 | 2.989 | 6.2741 | 10.304 | 4.3776 | 3.1934 | 6.1826 | 10.3816 | 4.3937 | 3.2052 | 6.1014 | 10.4358 | 4.4306 | 3.2321 | 6.0234 | 10.4818 | 4.3601 | 3.1806 | 5.9232 | 10.5233 | 4.3635 | 3.1831 | 5.826 | 10.658 | 4.07 | 2.969 | 5.2361 | 10.8098 | 3.7368 | 2.7259 | 4.3215 | 10.9226 | 3.5478 | 2.5881 | 3.5988 | 11.0263 | 3.3042 | 2.4104 | 2.8606 | 11.1025 | 3.0731 | 2.2418 | 2.2641 | 9.9452 | 4.5398 | 3.3118 | 6.5725 | 9.9719 | 4.4923 | 3.277 | 6.5246 | 10.0001 | 4.5579 | 3.3249 | 6.4696 | 10.038 | 4.539 | 3.3111 | 6.4107 | 10.0897 | 4.5468 | 3.3168 | 6.3363 | 10.1544 | 4.5025 | 3.2845 | 6.2521 | 10.2301 | 4.5341 | 3.3075 | 6.1476 | 10.314 | 4.4454 | 3.2428 | 6.0105 | 10.3611 | 4.4502 | 3.2463 | 5.8825 | 10.4045 | 4.3942 | 3.2055 | 5.753 | 10.518 | 4.1281 | 3.0114 | 5.3544 | 10.6124 | 4.0528 | 2.9565 | 4.9385 | 10.6859 | 3.8248 | 2.7901 | 4.5667 | 10.758 | 3.6195 | 2.6404 | 4.1856 | 10.8104 | 3.8339 | 2.7968 | 3.9488 | 9.9627 | 4.5398 | 3.3118 | 6.5725 | 10.0055 | 4.552 | 3.3206 | 6.5229 | 10.071 | 4.3891 | 3.2018 | 6.4575 | 10.1582 | 3.8044 | 2.7753 | 6.3992 | 10.2528 | 4.2812 | 3.1231 | 6.3258 | 10.351 | 4.4214 | 3.2254 | 6.2562 | 10.4055 | 4.4642 | 3.2566 | 6.2035 | 10.4626 | 4.4024 | 3.2115 | 6.131 | 10.5088 | 4.308 | 3.1426 | 6.0494 | 10.5519 | 4.1929 | 3.0587 | 5.9706 | 10.6923 | 3.8562 | 2.813 | 5.134 | 10.8482 | 3.5981 | 2.6247 | 4.1174 | 10.962 | 3.3371 | 2.4344 | 3.3429 | 11.0632 | 3.0749 | 2.2431 | 2.6162 | 11.1326 | 2.8711 | 2.0945 | 2.0594 | 9.9627 | 4.5398 | 3.3118 | 6.5725 | 9.9781 | 4.5435 | 3.3144 | 6.5834 | 10.0124 | 4.3126 | 3.146 | 6.5447 | 10.0604 | 4.0891 | 2.983 | 6.4998 | 10.1283 | 4.407 | 3.2149 | 6.4306 | 10.2202 | 4.4482 | 3.2449 | 6.3517 | 10.3323 | 4.2762 | 3.1194 | 6.2382 | 10.3946 | 4.1296 | 3.0125 | 5.9833 | 10.4457 | 3.9843 | 2.9065 | 5.7095 | 10.4947 | 3.7747 | 2.7536 | 5.4388 | 10.6409 | 3.4264 | 2.4995 | 4.6633 | 10.791 | 3.2122 | 2.3433 | 3.9056 | 10.8998 | 2.9877 | 2.1795 | 3.2692 | 10.9827 | 2.7758 | 2.0249 | 2.6994 | 10.9946 | 2.7662 | 2.0179 | 2.6298 | 9.9575 | 4.5398 | 3.3118 | 6.5725 | 9.9902 | 4.5573 | 3.3245 | 6.5288 | 10.0305 | 4.4505 | 3.2466 | 6.4718 | 10.0789 | 4.1209 | 3.0061 | 6.4238 | 10.1406 | 4.1376 | 3.0183 | 6.3713 | 10.2247 | 4.4163 | 3.2216 | 6.3067 | 10.3292 | 4.4503 | 3.2464 | 6.2389 | 10.392 | 4.4592 | 3.2529 | 6.171 | 10.4341 | 4.4066 | 3.2146 | 6.0719 | 10.4757 | 4.4012 | 3.2107 | 5.9744 | 10.6027 | 4.1486 | 3.0263 | 5.6132 | 10.7303 | 3.9337 | 2.8696 | 5.1432 | 10.823 | 3.8038 | 2.7748 | 4.6784 | 10.9052 | 3.6161 | 2.6379 | 4.2418 | 10.9487 | 3.4386 | 2.5084 | 3.9827 | 9.9575 | 4.5398 | 3.3118 | 6.5725 | 9.9867 | 4.5428 | 3.3139 | 6.5576 | 10.043 | 4.319 | 3.1506 | 6.486 | 10.1185 | 4.0287 | 2.9389 | 6.4041 | 10.2028 | 4.3591 | 3.1799 | 6.3012 | 10.2941 | 4.423 | 3.2265 | 6.2001 | 10.3754 | 4.221 | 3.0792 | 6.0609 | 10.4438 | 4.0771 | 2.9742 | 5.7666 | 10.5014 | 3.9369 | 2.8719 | 5.4609 | 10.5553 | 3.6842 | 2.6876 | 5.1592 | 10.7082 | 3.3652 | 2.4549 | 4.2953 | 10.8512 | 3.1387 | 2.2896 | 3.4621 | 10.9546 | 2.9158 | 2.127 | 2.7519 | 11.0301 | 2.6956 | 1.9664 | 2.2459 | 11.0441 | 2.6811 | 1.9558 | 2.3161
WIGTON | CARLISLE | HARKER / HUTTON | 325814 | 549933 | 4.9809 | 4.9809 | 4.9809 | 4.9809 | 5.136 | 5.136 | 5.136 | 5.136 | 5.2983 | 5.2983 | 5.2983 | 5.2983 | 5.4914 | 5.4914 | 5.4914 | 5.4914 | 5.7809 | 5.7809 | 5.7809 | 5.7809 | 6.0866 | 6.0866 | 6.0866 | 6.0336 | 6.3687 | 6.3687 | 6.3687 | 5.6229 | 8.7204 | 8.7204 | 8.7204 | 2.7911 | 8.8848 | 8.8848 | 8.8848 | 2.219 | 9.033 | 9.033 | 9.033 | 1.6454 | 9.8686 | 9.8686 | 9.8686 | -0.1759 | 10.5894 | 10.5894 | 10.5894 | -1.8416 | 11.9857 | 11.9857 | 11.9857 | -4.7872 | 12.408 | 12.408 | 12.408 | -6.21 | 12.732 | 12.732 | 12.732 | -7.2946 | 4.9845 | 4.9845 | 4.9845 | 4.9845 | 5.1418 | 5.1418 | 5.1418 | 5.1418 | 5.2943 | 5.2943 | 5.2943 | 5.2943 | 5.4869 | 5.4869 | 5.4869 | 5.4869 | 5.7257 | 5.7257 | 5.7257 | 5.7257 | 5.9479 | 5.9479 | 5.9479 | 5.9479 | 6.2135 | 6.2135 | 6.2135 | 5.7065 | 6.5415 | 6.5415 | 6.5415 | 5.1005 | 6.718 | 6.718 | 6.718 | 4.7014 | 6.8958 | 6.8958 | 6.8958 | 4.1495 | 7.427 | 7.427 | 7.427 | 2.3515 | 7.9427 | 7.9427 | 7.9427 | 0.55955 | 8.4787 | 8.4787 | 8.4787 | -0.91721 | 9.2081 | 9.2081 | 9.2081 | -2.19 | 9.4788 | 9.4788 | 9.4788 | -2.8001 | 4.9792 | 4.9792 | 4.9792 | 4.9792 | 5.1346 | 5.1346 | 5.1346 | 5.1346 | 5.2941 | 5.2941 | 5.2941 | 5.2941 | 5.4847 | 5.4847 | 5.4847 | 5.4847 | 5.7679 | 5.7679 | 5.7679 | 5.7679 | 6.0647 | 6.0647 | 6.0647 | 6.0647 | 6.3363 | 6.3363 | 6.3363 | 5.9397 | 8.6058 | 8.6058 | 8.6058 | 3.3049 | 8.7556 | 8.7556 | 8.7556 | 2.9019 | 8.8844 | 8.8844 | 8.8844 | 2.4817 | 9.7191 | 9.7191 | 9.7191 | 0.91397 | 10.4134 | 10.4134 | 10.4134 | -1.4376 | 11.7845 | 11.7845 | 11.7845 | -4.7669 | 12.1667 | 12.1667 | 12.1667 | -6.4407 | 12.4333 | 12.4333 | 12.4333 | -7.4375 | 4.9792 | 4.9792 | 4.9792 | 4.9792 | 5.0686 | 5.0686 | 5.0686 | 5.0686 | 5.1949 | 5.1949 | 5.1949 | 5.1949 | 5.4239 | 5.4239 | 5.4239 | 5.4239 | 5.6965 | 5.6965 | 5.6965 | 5.6965 | 8.1821 | 8.1821 | 8.1821 | 3.8303 | 8.4507 | 8.4507 | 8.4507 | 3.6129 | 9.7667 | 9.7667 | 9.7667 | 1.8874 | 9.9116 | 9.9116 | 9.9116 | 1.2487 | 10.0574 | 10.0574 | 10.0574 | 0.56212 | 10.6214 | 10.6214 | 10.6214 | -1.6555 | 11.1964 | 11.1964 | 11.1964 | -3.6955 | 11.621 | 11.621 | 11.621 | -5.0963 | 11.8995 | 11.8995 | 11.8995 | -6.18 | 11.8632 | 11.8632 | 11.8632 | -5.8688 | 4.9809 | 4.9809 | 4.9809 | 4.9809 | 5.1187 | 5.1187 | 5.1187 | 5.1187 | 5.2696 | 5.2696 | 5.2696 | 5.2696 | 5.4425 | 5.4425 | 5.4425 | 5.4425 | 5.6485 | 5.6485 | 5.6485 | 5.6485 | 5.8436 | 5.8436 | 5.8436 | 5.8436 | 6.0462 | 6.0462 | 6.0462 | 6.0462 | 8.3653 | 8.3653 | 8.3653 | 3.5598 | 8.5461 | 8.5461 | 8.5461 | 3.1085 | 8.7398 | 8.7398 | 8.7398 | 2.6251 | 9.6037 | 9.6037 | 9.6037 | 0.89256 | 10.1997 | 10.1997 | 10.1997 | -0.86751 | 11.47 | 11.47 | 11.47 | -3.0602 | 11.7688 | 11.7688 | 11.7688 | -4.0263 | 11.8742 | 11.8742 | 11.8742 | -4.715 | 4.9809 | 4.9809 | 4.9809 | 4.9809 | 5.1102 | 5.1102 | 5.1102 | 5.1102 | 5.2929 | 5.2929 | 5.2929 | 5.2929 | 5.5874 | 5.5874 | 5.5874 | 5.5874 | 5.9191 | 5.9191 | 5.9191 | 5.9191 | 8.437 | 8.437 | 8.437 | 3.3126 | 8.7338 | 8.7338 | 8.7338 | 3.0259 | 10.1923 | 10.1923 | 10.1923 | 1.2037 | 10.3667 | 10.3667 | 10.3667 | 0.51536 | 10.5386 | 10.5386 | 10.5386 | -0.21477 | 11.1626 | 11.1626 | 11.1626 | -2.623 | 11.76 | 11.76 | 11.76 | -4.873 | 12.2009 | 12.2009 | 12.2009 | -6.4208 | 12.4778 | 12.4778 | 12.4778 | -7.079 | 12.4546 | 12.4546 | 12.4546 | -6.4309
WILLOW HEY | SKELMERSDALE | WASHWAY FARM / KIRKBY | 347779 | 406066 | 27.849 | 9.688 | 6.9629 | 17.8092 | 27.9066 | 9.473 | 6.8084 | 16.8461 | 27.9763 | 9.2917 | 6.6781 | 16.2418 | 28.0739 | 9.1538 | 6.579 | 15.9424 | 28.2111 | 8.9408 | 6.4259 | 15.699 | 28.3872 | 8.7293 | 6.2739 | 15.4301 | 28.6103 | 8.6447 | 6.2131 | 15.1519 | 28.8922 | 8.5219 | 6.1249 | 14.8626 | 29.1722 | 8.3862 | 6.0273 | 14.547 | 29.4622 | 8.2756 | 5.9478 | 14.239 | 30.3795 | 7.8088 | 5.6124 | 12.8502 | 31.3023 | 7.4238 | 5.3356 | 11.0171 | 31.7675 | 7.5063 | 5.3949 | 9.6751 | 32.077 | 8.6303 | 6.2028 | 8.5382 | 32.2329 | 8.7119 | 6.2614 | 7.7703 | 27.8354 | 9.688 | 6.9629 | 17.8092 | 27.8847 | 9.6302 | 6.9214 | 17.6284 | 27.9296 | 9.5391 | 6.8559 | 17.3973 | 27.9919 | 9.4444 | 6.7879 | 17.238 | 28.0807 | 9.3351 | 6.7093 | 17.1046 | 28.1939 | 9.2192 | 6.626 | 16.9488 | 28.3356 | 9.0555 | 6.5084 | 16.7522 | 28.5053 | 8.9479 | 6.4311 | 16.5204 | 28.6147 | 8.8518 | 6.362 | 16.3403 | 28.7424 | 8.7501 | 6.2889 | 16.1521 | 29.2336 | 8.4574 | 6.0785 | 15.5631 | 29.8411 | 8.1689 | 5.8712 | 14.9561 | 30.3898 | 8.1791 | 5.8785 | 14.3326 | 30.9607 | 9.0384 | 6.4961 | 13.6443 | 31.3415 | 9.5521 | 6.8653 | 13.1561 | 27.8529 | 9.688 | 6.9629 | 17.8092 | 27.9249 | 9.405 | 6.7596 | 16.6597 | 28.0121 | 9.117 | 6.5526 | 15.9059 | 28.1288 | 8.8691 | 6.3744 | 15.4206 | 28.285 | 8.5452 | 6.1416 | 15.0165 | 28.4779 | 8.3778 | 6.0213 | 14.5851 | 28.7147 | 8.1962 | 5.8908 | 14.2174 | 29.0066 | 8.0001 | 5.7498 | 13.8347 | 29.2841 | 7.7867 | 5.5965 | 13.4483 | 29.5552 | 7.6015 | 5.4633 | 13.0631 | 30.5353 | 6.878 | 4.9433 | 11.4232 | 31.5776 | 6.3297 | 4.5493 | 9.5263 | 32.1846 | 6.1835 | 4.4442 | 8.2751 | 32.5938 | 7.1338 | 5.1272 | 7.3891 | 32.6989 | 7.1817 | 5.1616 | 7.1357 | 27.8529 | 9.688 | 6.9629 | 17.8092 | 27.8599 | 9.4858 | 6.8176 | 17.1154 | 27.9096 | 9.2558 | 6.6523 | 16.4661 | 27.9897 | 10.285 | 7.392 | 16.0126 | 28.117 | 10.0188 | 7.2007 | 15.6344 | 28.3047 | 9.86 | 7.0866 | 15.1991 | 28.5556 | 9.6535 | 6.9381 | 14.7388 | 28.8793 | 9.4808 | 6.814 | 14.0311 | 29.2074 | 9.215 | 6.623 | 13.3174 | 29.5595 | 8.9548 | 6.436 | 12.6209 | 30.5989 | 8.7232 | 6.2695 | 10.6355 | 31.3732 | 8.0374 | 5.7766 | 9.0182 | 31.856 | 7.4758 | 5.373 | 8.0555 | 32.1777 | 7.5273 | 5.41 | 7.6974 | 32.2421 | 7.0817 | 5.0898 | 8.1955 | 27.849 | 9.688 | 6.9629 | 17.8092 | 27.8983 | 9.5913 | 6.8935 | 17.5268 | 27.9471 | 9.439 | 6.784 | 17.0792 | 28.0094 | 9.3142 | 6.6943 | 16.8444 | 28.1017 | 9.1217 | 6.5559 | 16.7178 | 28.2427 | 8.925 | 6.4146 | 16.5426 | 28.4344 | 8.8563 | 6.3652 | 16.3247 | 28.6652 | 8.7437 | 6.2843 | 16.0807 | 28.8901 | 8.6136 | 6.1907 | 15.7917 | 29.1402 | 8.5052 | 6.1129 | 15.4935 | 29.9311 | 8.1126 | 5.8307 | 14.5069 | 30.6748 | 7.908 | 5.6836 | 13.5249 | 31.1825 | 8.1113 | 5.8298 | 12.8555 | 31.5597 | 9.3746 | 6.7377 | 12.2867 | 31.729 | 9.5798 | 6.8852 | 12.0383 | 27.849 | 9.688 | 6.9629 | 17.8092 | 27.873 | 9.402 | 6.7574 | 16.6522 | 27.9486 | 9.1498 | 6.5761 | 15.8766 | 28.0573 | 10.1593 | 7.3017 | 15.3616 | 28.2048 | 9.8863 | 7.1055 | 14.9302 | 28.3846 | 9.7187 | 6.985 | 14.4798 | 28.6122 | 9.5071 | 6.8329 | 14.0154 | 28.9215 | 9.3258 | 6.7026 | 13.2744 | 29.2225 | 9.0539 | 6.5072 | 12.538 | 29.5484 | 8.787 | 6.3154 | 11.8218 | 30.6086 | 8.543 | 6.1401 | 9.7705 | 31.4506 | 7.8382 | 5.6334 | 8.0858 | 32.0147 | 7.262 | 5.2193 | 7.049 | 32.3801 | 7.281 | 5.233 | 6.6289 | 32.5133 | 6.8261 | 4.9061 | 7.0376
WILLOWBANK | GREENHILL | WHITEGATE | 391885 | 406064 | 25.3861 | 14.0839 | 10.274 | 8.3532 | 25.4732 | 13.9255 | 10.1585 | 7.703 | 25.6075 | 13.7114 | 10.0023 | 7.3104 | 25.7537 | 13.4426 | 9.8062 | 6.9086 | 25.9269 | 13.158 | 9.5986 | 6.4754 | 26.1248 | 12.9149 | 9.4212 | 6.0193 | 26.3783 | 12.6752 | 9.2464 | 5.5519 | 26.6959 | 12.5233 | 9.1356 | 5.0571 | 27.0127 | 12.372 | 9.0252 | 4.5231 | 27.3242 | 12.2515 | 8.9373 | 4.1444 | 28.2652 | 11.7985 | 8.6068 | 2.4649 | 29.0344 | 11.2878 | 8.2343 | 0.24753 | 29.5345 | 10.9178 | 7.9644 | -1.4148 | 29.9005 | 10.4849 | 7.6486 | -3.1833 | 30.098 | 10.222 | 7.4568 | -4.4471 | 25.3734 | 14.0839 | 10.274 | 8.3532 | 25.4341 | 13.9965 | 10.2102 | 8.0086 | 25.5242 | 13.8541 | 10.1064 | 7.9272 | 25.6112 | 13.6745 | 9.9754 | 7.791 | 25.7112 | 13.4666 | 9.8237 | 7.5623 | 25.8378 | 13.1238 | 9.5736 | 7.265 | 25.9935 | 12.8402 | 9.3667 | 6.9099 | 26.1793 | 12.7133 | 9.2741 | 6.4938 | 26.3514 | 12.615 | 9.2024 | 6.2747 | 26.547 | 12.5355 | 9.1445 | 6.0494 | 27.2099 | 12.3411 | 9.0027 | 5.3464 | 27.9342 | 12.1824 | 8.8869 | 4.6299 | 28.674 | 11.9787 | 8.7383 | 3.6204 | 29.4704 | 11.8032 | 8.6103 | 2.2818 | 29.9257 | 11.5279 | 8.4095 | 1.2715 | 25.3914 | 14.0839 | 10.274 | 8.3532 | 25.4979 | 13.893 | 10.1348 | 7.5795 | 25.6554 | 13.6229 | 9.9377 | 7.1122 | 25.8207 | 13.2217 | 9.645 | 6.6392 | 25.9931 | 13.0118 | 9.4919 | 6.1325 | 26.2042 | 12.7084 | 9.2706 | 5.5722 | 26.4663 | 12.4149 | 9.0565 | 4.9978 | 26.7588 | 12.2268 | 8.9193 | 4.4007 | 27.0421 | 12.0432 | 8.7854 | 3.8052 | 27.3232 | 11.8857 | 8.6704 | 3.3606 | 28.2718 | 11.297 | 8.241 | 1.4632 | 29.1091 | 10.698 | 7.804 | -0.77588 | 29.6598 | 10.2625 | 7.4863 | -2.2836 | 30.0106 | 9.9305 | 7.2442 | -3.4426 | 30.1081 | 9.6989 | 7.0752 | -3.9322 | 25.3915 | 14.0839 | 10.274 | 8.3532 | 25.4331 | 13.9566 | 10.1811 | 7.8772 | 25.5477 | 13.7903 | 10.0598 | 7.4966 | 25.661 | 13.5494 | 9.8841 | 7.0581 | 25.795 | 13.3416 | 9.7325 | 6.5411 | 25.9945 | 13.0765 | 9.5391 | 5.9746 | 26.2624 | 12.7015 | 9.2656 | 5.2889 | 26.5979 | 12.3221 | 8.9888 | 4.2948 | 26.926 | 11.9598 | 8.7245 | 3.3162 | 27.2532 | 11.7673 | 8.5841 | 2.5138 | 28.2547 | 11.1245 | 8.1152 | 0.22021 | 28.9935 | 10.533 | 7.6837 | -1.6972 | 29.4231 | 10.0906 | 7.361 | -2.8728 | 29.6564 | 9.8543 | 7.1886 | -3.4181 | 29.6488 | 9.6479 | 7.038 | -3.0253 | 25.3861 | 14.0839 | 10.274 | 8.3532 | 25.4617 | 13.9604 | 10.1839 | 7.8663 | 25.5697 | 13.7578 | 10.0361 | 7.5321 | 25.6732 | 13.515 | 9.859 | 7.1812 | 25.7965 | 13.2467 | 9.6633 | 6.8346 | 25.9766 | 13.0236 | 9.5005 | 6.4509 | 26.1996 | 12.7936 | 9.3327 | 6.0283 | 26.4675 | 12.6501 | 9.2281 | 5.575 | 26.7432 | 12.5029 | 9.1207 | 5.0671 | 27.0278 | 12.3828 | 9.0331 | 4.6903 | 27.9232 | 12.0232 | 8.7707 | 3.4502 | 28.6667 | 11.7118 | 8.5436 | 2.2023 | 29.1637 | 11.4968 | 8.3868 | 1.3271 | 29.5181 | 11.2417 | 8.2006 | 0.53815 | 29.6692 | 11.1599 | 8.141 | 0.050365 | 25.3861 | 14.0839 | 10.274 | 8.3532 | 25.4432 | 13.9095 | 10.1468 | 7.6658 | 25.5849 | 13.7162 | 10.0058 | 7.2018 | 25.7404 | 13.4629 | 9.821 | 6.7136 | 25.8984 | 13.2479 | 9.6641 | 6.1673 | 26.0906 | 12.9756 | 9.4655 | 5.5906 | 26.3333 | 12.6006 | 9.192 | 4.9036 | 26.6437 | 12.2254 | 8.9183 | 3.8877 | 26.936 | 11.8296 | 8.6296 | 2.8971 | 27.2433 | 11.6599 | 8.5057 | 2.0841 | 28.2306 | 10.991 | 8.0178 | -0.26587 | 29.0905 | 10.3861 | 7.5765 | -2.2679 | 29.6047 | 9.874 | 7.203 | -3.8279 | 29.8895 | 9.5876 | 6.994 | -4.6562 | 29.9114 | 9.347 | 6.8185 | -4.4425
WILLOWHOLME | CARLISLE | HARKER / HUTTON | 338653 | 556688 | 28.7749 | 7.0375 | 5.058 | 14.0959 | 28.8816 | 6.5207 | 4.6866 | 11.5898 | 28.9834 | 6.2198 | 4.4703 | 11.3223 | 29.1099 | 5.9615 | 4.2846 | 11.2546 | 29.2767 | 5.7051 | 4.1004 | 11.1126 | 29.4781 | 5.454 | 3.9199 | 10.952 | 29.718 | 5.2187 | 3.7508 | 10.8041 | 30.0089 | 5.1242 | 3.6829 | 10.658 | 30.2841 | 5.0162 | 3.6053 | 10.4558 | 29.8877 | 4.9208 | 3.5367 | 10.2754 | 26.8066 | 4.4135 | 3.1721 | 8.496 | 23.1845 | 3.8172 | 2.7435 | 5.6683 | 21.363 | 3.5173 | 2.5279 | 3.3898 | 23.7617 | 3.9122 | 2.8118 | 1.0696 | 25.5959 | 4.2142 | 3.0288 | -0.98023 | 28.7648 | 7.0375 | 5.058 | 14.0959 | 28.8425 | 6.8162 | 4.8989 | 13.0217 | 28.9086 | 6.5798 | 4.729 | 12.9903 | 28.9898 | 6.331 | 4.5502 | 12.8969 | 29.0983 | 6.0742 | 4.3656 | 12.7687 | 29.2331 | 5.8183 | 4.1817 | 12.6205 | 29.4006 | 5.5075 | 3.9584 | 12.4086 | 29.6012 | 5.386 | 3.871 | 12.1255 | 29.7431 | 5.281 | 3.7956 | 11.8802 | 29.8999 | 5.1911 | 3.7309 | 11.6322 | 29.7536 | 4.8987 | 3.5208 | 10.7861 | 27.9116 | 4.5954 | 3.3028 | 9.7117 | 26.8308 | 4.4175 | 3.1749 | 8.7554 | 29.5782 | 4.8698 | 3.5 | 7.8463 | 32.5063 | 5.3709 | 3.8602 | 7.3439 | 28.7789 | 7.0375 | 5.058 | 14.0959 | 28.8749 | 6.4377 | 4.6269 | 11.2478 | 28.9737 | 6.0879 | 4.3755 | 10.9392 | 29.0981 | 5.8109 | 4.1764 | 10.9094 | 29.2614 | 5.5339 | 3.9774 | 10.8053 | 29.4563 | 5.2591 | 3.7798 | 10.6893 | 29.687 | 5.0046 | 3.5969 | 10.609 | 29.6164 | 4.8761 | 3.5046 | 10.5317 | 28.8939 | 4.7572 | 3.4191 | 10.4248 | 28.2173 | 4.6458 | 3.339 | 10.3203 | 24.7443 | 4.074 | 2.928 | 8.8852 | 21.178 | 3.4868 | 2.506 | 6.1683 | 18.2751 | 3.0089 | 2.1625 | 3.9773 | 19.7488 | 3.2515 | 2.3369 | 1.7804 | 21.1836 | 3.4877 | 2.5067 | -0.033322 | 28.7791 | 7.0375 | 5.058 | 14.0959 | 28.8057 | 6.6334 | 4.7676 | 12.2764 | 28.8673 | 6.5067 | 4.6765 | 12.171 | 28.9573 | 6.3949 | 4.5962 | 12.156 | 29.095 | 6.2018 | 4.4574 | 12.0455 | 29.2924 | 5.8914 | 4.2343 | 11.9016 | 29.5598 | 5.7621 | 4.1413 | 11.6105 | 29.9322 | 5.4573 | 3.9222 | 10.7745 | 30.2925 | 5.1273 | 3.6851 | 9.8957 | 29.1473 | 4.7989 | 3.4491 | 9.0146 | 24.3775 | 4.0136 | 2.8846 | 6.4728 | 19.9989 | 3.2927 | 2.3665 | 3.9946 | 16.9523 | 2.7911 | 2.006 | 1.9962 | 22.8594 | 3.7636 | 2.705 | 0.76982 | 22.3632 | 3.6819 | 2.6463 | 1.7638 | 28.7748 | 7.0375 | 5.058 | 14.0959 | 28.8574 | 6.6744 | 4.797 | 12.3025 | 28.9263 | 6.4044 | 4.603 | 12.1909 | 29.0027 | 6.1579 | 4.4258 | 12.1865 | 29.1053 | 5.9239 | 4.2576 | 12.1655 | 29.2547 | 5.6931 | 4.0918 | 12.1124 | 29.4497 | 5.4684 | 3.9302 | 12.0289 | 29.6755 | 5.3821 | 3.8682 | 11.9232 | 29.8911 | 5.2759 | 3.7919 | 11.7308 | 30.1227 | 5.1798 | 3.7228 | 11.5401 | 29.2922 | 4.8227 | 3.4662 | 10.6281 | 27.4115 | 4.5131 | 3.2436 | 9.4771 | 27.3416 | 4.5016 | 3.2354 | 8.7138 | 31.7429 | 5.2262 | 3.7562 | 8.0968 | 32.4244 | 5.8793 | 4.2255 | 7.9553 | 28.7748 | 7.0375 | 5.058 | 14.0959 | 28.8077 | 6.4148 | 4.6105 | 11.134 | 28.8923 | 6.238 | 4.4834 | 10.7689 | 29.0098 | 6.1113 | 4.3923 | 10.6748 | 29.1652 | 5.9057 | 4.2446 | 10.4931 | 29.3466 | 5.598 | 4.0234 | 10.3056 | 29.5813 | 5.4499 | 3.917 | 9.9603 | 29.9376 | 5.1324 | 3.6888 | 9.05 | 29.1297 | 4.796 | 3.447 | 8.1212 | 27.0891 | 4.46 | 3.2055 | 7.1874 | 22.1106 | 3.6403 | 2.6164 | 4.4634 | 17.5346 | 2.8869 | 2.0749 | 1.8328 | 14.2901 | 2.3528 | 1.691 | -0.33622 | 19.85 | 3.2681 | 2.3489 | -1.765 | 19.192 | 3.1598 | 2.271 | -0.99237
WILMSLOW | MOSS NOOK | SOUTH MANCHESTER | 384710 | 381286 | 24.9294 | 10.8618 | 7.8066 | 8.4089 | 24.9894 | 10.708 | 7.696 | 8.1714 | 25.0839 | 10.7075 | 7.6957 | 7.893 | 25.1795 | 10.5562 | 7.5869 | 7.5319 | 25.277 | 10.4083 | 7.4806 | 7.1978 | 25.3764 | 10.4027 | 7.4766 | 6.8554 | 25.4899 | 10.3047 | 7.4062 | 6.5146 | 25.6259 | 10.1766 | 7.3141 | 6.1753 | 25.7244 | 9.9958 | 7.1842 | 5.8059 | 25.8091 | 9.8328 | 7.067 | 5.4557 | 26.0763 | 9.3519 | 6.7214 | 3.9203 | 26.367 | 8.8096 | 6.3316 | 1.7907 | 26.5827 | 8.3418 | 5.9954 | 0.1214 | 26.7797 | 7.8938 | 5.6734 | -1.7229 | 26.9017 | 7.4465 | 5.3519 | -3.3431 | 24.902 | 10.8618 | 7.8066 | 8.4089 | 24.9889 | 10.6984 | 7.6891 | 8.259 | 25.0859 | 10.645 | 7.6508 | 8.0566 | 25.1745 | 10.7269 | 7.7096 | 7.8878 | 25.2775 | 10.7201 | 7.7048 | 7.7176 | 25.397 | 10.5865 | 7.6087 | 7.5022 | 25.5392 | 10.374 | 7.456 | 7.2282 | 25.7026 | 10.222 | 7.3468 | 6.8827 | 25.7791 | 10.1206 | 7.2738 | 6.6588 | 25.8557 | 10.0184 | 7.2004 | 6.4378 | 26.0825 | 9.6909 | 6.965 | 5.7897 | 26.2976 | 9.3585 | 6.7261 | 5.1389 | 26.4866 | 9.2389 | 6.6402 | 4.513 | 26.6839 | 9.2879 | 6.6754 | 3.7976 | 26.8431 | 9.1897 | 6.6048 | 3.2377 | 24.9372 | 10.8618 | 7.8066 | 8.4089 | 25.0029 | 10.7114 | 7.6985 | 8.1484 | 25.1056 | 10.6774 | 7.6741 | 7.8656 | 25.2138 | 10.5016 | 7.5477 | 7.5023 | 25.326 | 10.3634 | 7.4484 | 7.1675 | 25.4427 | 10.2577 | 7.3724 | 6.8248 | 25.5769 | 10.1358 | 7.2848 | 6.4811 | 25.7209 | 9.9592 | 7.1578 | 6.1412 | 25.8166 | 9.7588 | 7.0138 | 5.8036 | 25.9026 | 9.5905 | 6.8928 | 5.49 | 26.1714 | 9.037 | 6.4951 | 4.077 | 26.4573 | 8.4477 | 6.0715 | 2.1425 | 26.6584 | 7.956 | 5.7181 | 0.8283 | 26.8232 | 7.509 | 5.3968 | -0.68838 | 26.8612 | 7.1149 | 5.1136 | -2.064 | 24.9372 | 10.8618 | 7.8066 | 8.4089 | 24.9191 | 10.794 | 7.7578 | 8.372 | 24.9634 | 10.8171 | 7.7745 | 8.1624 | 25.0087 | 10.7003 | 7.6905 | 7.8293 | 25.0673 | 10.5276 | 7.5664 | 7.5014 | 25.1594 | 10.4314 | 7.4973 | 7.1525 | 25.2765 | 10.2387 | 7.3587 | 6.7072 | 25.3985 | 10.0781 | 7.2433 | 5.9663 | 25.4936 | 9.8789 | 7.1001 | 5.1911 | 25.5831 | 9.6364 | 6.9259 | 4.4339 | 25.8475 | 8.9739 | 6.4497 | 2.2765 | 26.1198 | 8.3368 | 5.9919 | 0.393 | 26.3073 | 7.8247 | 5.6238 | -0.98304 | 26.4358 | 7.4802 | 5.3762 | -1.8707 | 26.402 | 7.4069 | 5.3235 | -1.2564 | 24.9294 | 10.8618 | 7.8066 | 8.4089 | 24.9823 | 10.7354 | 7.7158 | 8.2834 | 25.0562 | 10.7482 | 7.725 | 8.0483 | 25.1221 | 10.6038 | 7.6212 | 7.725 | 25.1904 | 10.4653 | 7.5216 | 7.4514 | 25.2804 | 10.4851 | 7.5359 | 7.1613 | 25.3966 | 10.4002 | 7.4749 | 6.8561 | 25.5204 | 10.2828 | 7.3905 | 6.545 | 25.617 | 10.1062 | 7.2635 | 6.183 | 25.7061 | 9.9378 | 7.1425 | 5.8283 | 25.9491 | 9.5513 | 6.8647 | 4.766 | 26.2021 | 9.2483 | 6.6469 | 3.8634 | 26.3878 | 9.0044 | 6.4716 | 3.4358 | 26.5574 | 8.8272 | 6.3443 | 3.0201 | 26.6446 | 8.6974 | 6.251 | 2.8192 | 24.9294 | 10.8618 | 7.8066 | 8.4089 | 24.9473 | 10.7668 | 7.7383 | 8.2732 | 25.0358 | 10.7679 | 7.7391 | 8.0009 | 25.1309 | 10.6425 | 7.649 | 7.6188 | 25.2273 | 10.4596 | 7.5175 | 7.258 | 25.3263 | 10.3568 | 7.4437 | 6.8955 | 25.4438 | 10.1734 | 7.3119 | 6.4371 | 25.6024 | 9.9884 | 7.1789 | 5.658 | 25.7129 | 9.7822 | 7.0307 | 4.8602 | 25.8085 | 9.5322 | 6.8509 | 4.0826 | 26.0741 | 8.8248 | 6.3425 | 1.6887 | 26.3196 | 8.1478 | 5.856 | -0.44738 | 26.4875 | 7.6037 | 5.465 | -1.923 | 26.593 | 7.257 | 5.2158 | -2.9457 | 26.56 | 7.1169 | 5.1151 | -2.4949
WINDERMERE | KENDAL (PARKSIDE RD) | HARKER / HUTTON | 341657 | 498418 | 30.3442 | 21.9331 | 15.7637 | 12.6772 | 30.5146 | 21.7254 | 15.6145 | 12.0241 | 30.7245 | 21.4304 | 15.4025 | 11.6602 | 30.9965 | 20.986 | 15.083 | 11.3485 | 31.2397 | 20.8304 | 14.9712 | 10.968 | 31.441 | 20.9554 | 15.0611 | 10.5758 | 31.6743 | 20.8215 | 14.9648 | 10.3582 | 31.9533 | 20.6396 | 14.8341 | 10.1378 | 32.1493 | 20.3746 | 14.6436 | 9.8872 | 32.3384 | 20.1603 | 14.4896 | 9.6667 | 32.9219 | 19.4864 | 14.0052 | 8.2961 | 33.494 | 18.8782 | 13.5681 | 5.958 | 33.8972 | 18.1415 | 13.0386 | 4.0102 | 34.2121 | 17.331 | 12.4562 | 2.0173 | 34.3881 | 16.6544 | 11.9699 | -0.080545 | 30.331 | 21.9331 | 15.7637 | 12.6772 | 30.4488 | 21.8227 | 15.6844 | 12.3024 | 30.5606 | 21.7377 | 15.6233 | 12.1096 | 30.7247 | 21.6147 | 15.5349 | 11.883 | 30.9569 | 21.3802 | 15.3664 | 11.6312 | 31.2385 | 21.0934 | 15.1602 | 11.3578 | 31.5694 | 21.0264 | 15.1121 | 11.0115 | 31.8669 | 20.7209 | 14.8925 | 10.5997 | 31.9909 | 20.395 | 14.6583 | 10.363 | 32.1223 | 19.8099 | 14.2378 | 10.1296 | 32.5623 | 19.9248 | 14.3203 | 9.4513 | 33.016 | 19.7959 | 14.2277 | 8.8098 | 33.4021 | 19.3723 | 13.9233 | 8.2317 | 33.7603 | 19.054 | 13.6945 | 7.4801 | 33.9923 | 18.632 | 13.3912 | 6.7743 | 30.3512 | 21.9331 | 15.7637 | 12.6772 | 30.5159 | 21.6642 | 15.5705 | 11.9464 | 30.7276 | 21.1861 | 15.2269 | 11.569 | 31.0056 | 20.2107 | 14.5258 | 11.2556 | 31.2775 | 20.8965 | 15.0187 | 10.8746 | 31.4947 | 20.7085 | 14.8836 | 10.482 | 31.748 | 20.5423 | 14.7642 | 10.2619 | 32.0523 | 20.0751 | 14.4284 | 10.041 | 32.2582 | 19.8211 | 14.2458 | 9.8287 | 32.4581 | 19.5944 | 14.0829 | 9.6501 | 33.0997 | 19.0706 | 13.7064 | 8.4133 | 33.7435 | 18.1907 | 13.074 | 6.2375 | 34.1999 | 17.3157 | 12.4451 | 4.4663 | 34.3886 | 16.5355 | 11.8844 | 2.7614 | 34.4349 | 16.1235 | 11.5882 | 1.3668 | 30.3513 | 21.9331 | 15.7637 | 12.6772 | 30.3945 | 21.7064 | 15.6008 | 12.2989 | 30.5071 | 21.1403 | 15.194 | 12.0247 | 30.6847 | 21.1986 | 15.2359 | 11.7359 | 30.9364 | 21.1621 | 15.2096 | 11.3979 | 31.0973 | 20.4048 | 14.6653 | 11.0272 | 31.3045 | 20.2447 | 14.5503 | 10.6773 | 31.5512 | 19.5991 | 14.0863 | 9.9133 | 31.7549 | 19.0249 | 13.6736 | 9.1232 | 31.9553 | 18.8959 | 13.5808 | 8.3578 | 32.5621 | 18.0671 | 12.9852 | 6.1714 | 33.1584 | 17.3621 | 12.4785 | 4.0918 | 33.5696 | 16.7496 | 12.0382 | 2.4846 | 33.8572 | 16.464 | 11.833 | 1.5645 | 33.7684 | 16.298 | 11.7137 | 2.3795 | 30.3441 | 21.9331 | 15.7637 | 12.6772 | 30.4782 | 21.7547 | 15.6356 | 12.1843 | 30.6157 | 21.4688 | 15.4301 | 11.8732 | 30.7832 | 21.0307 | 15.1152 | 11.6092 | 31.0008 | 20.9308 | 15.0434 | 11.3432 | 31.2739 | 21.0551 | 15.1327 | 11.0621 | 31.4951 | 20.9122 | 15.03 | 10.892 | 31.7439 | 20.7935 | 14.9447 | 10.6707 | 31.9125 | 20.5178 | 14.7465 | 10.3839 | 32.0838 | 20.2387 | 14.546 | 10.0991 | 32.6432 | 19.7153 | 14.1698 | 9.1343 | 33.2158 | 19.3132 | 13.8808 | 8.0431 | 33.6317 | 18.7656 | 13.4872 | 7.2719 | 33.9792 | 18.2121 | 13.0894 | 6.5311 | 34.1262 | 18.0121 | 12.9457 | 6.3256 | 30.3441 | 21.9331 | 15.7637 | 12.6772 | 30.4382 | 21.6553 | 15.5641 | 12.0224 | 30.6352 | 21.0968 | 15.1627 | 11.6368 | 30.9134 | 21.0732 | 15.1458 | 11.2643 | 31.1609 | 21.0482 | 15.1278 | 10.8514 | 31.3519 | 20.3799 | 14.6474 | 10.4426 | 31.5782 | 20.1228 | 14.4626 | 10.0617 | 31.8709 | 19.4589 | 13.9855 | 9.2296 | 32.0774 | 18.8347 | 13.5369 | 8.3976 | 32.2808 | 18.7058 | 13.4443 | 7.5944 | 32.893 | 17.8618 | 12.8376 | 5.3228 | 33.463 | 17.1336 | 12.3142 | 3.1986 | 33.8627 | 16.4396 | 11.8155 | 1.1649 | 34.1384 | 16.0815 | 11.5581 | -0.14275 | 34.0869 | 15.8835 | 11.4158 | 0.50645
WINIFRED RD | ADSWOOD | BREDBURY | 389971 | 388470 | 16.7387 | 15.9791 | 11.6565 | 8.0741 | 16.9157 | 15.8101 | 11.5333 | 7.6015 | 17.125 | 15.6308 | 11.4024 | 7.2381 | 17.3777 | 15.4182 | 11.2474 | 6.9165 | 17.7008 | 15.1557 | 11.0559 | 6.5074 | 18.0495 | 14.8612 | 10.841 | 6.0909 | 18.3826 | 14.75 | 10.7599 | 5.7038 | 18.7143 | 14.5566 | 10.6188 | 5.3475 | 18.8496 | 14.3434 | 10.4633 | 4.9613 | 18.981 | 14.146 | 10.3193 | 4.5929 | 19.4293 | 13.5424 | 9.879 | 2.5215 | 19.9213 | 12.8145 | 9.348 | -0.65504 | 20.2783 | 12.2031 | 8.902 | -3.0441 | 20.5937 | 11.5366 | 8.4158 | -5.2783 | 20.7993 | 10.9611 | 7.996 | -6.8775 | 16.7213 | 15.9791 | 11.6565 | 8.0741 | 16.8137 | 15.8849 | 11.5878 | 7.8538 | 16.901 | 15.771 | 11.5047 | 7.6171 | 17.007 | 15.6073 | 11.3853 | 7.383 | 17.1431 | 15.4083 | 11.2401 | 7.1064 | 17.2803 | 15.1743 | 11.0695 | 6.8309 | 17.4507 | 14.8336 | 10.8209 | 6.4795 | 17.6692 | 14.6327 | 10.6743 | 6.0168 | 17.8222 | 14.5177 | 10.5905 | 5.6917 | 17.9779 | 14.416 | 10.5163 | 5.3387 | 18.4814 | 14.0406 | 10.2424 | 4.2687 | 19.0263 | 13.695 | 9.9903 | 3.1753 | 19.5654 | 13.3698 | 9.7531 | 2.1389 | 20.0982 | 13.1319 | 9.5795 | 0.98936 | 20.3365 | 12.7717 | 9.3168 | 0.13771 | 16.746 | 15.9791 | 11.6565 | 8.0741 | 16.99 | 15.7589 | 11.4959 | 7.4869 | 17.2795 | 15.5037 | 11.3097 | 7.0255 | 17.6257 | 15.1917 | 11.0821 | 6.6176 | 18.0521 | 14.8493 | 10.8324 | 6.1132 | 18.4877 | 14.623 | 10.6673 | 5.5968 | 18.6757 | 14.4125 | 10.5137 | 5.1163 | 18.868 | 14.1586 | 10.3285 | 4.6543 | 19.022 | 13.8973 | 10.1379 | 4.1871 | 19.1726 | 13.6591 | 9.9641 | 3.7016 | 19.692 | 12.8659 | 9.3855 | 1.3275 | 20.2295 | 12.0284 | 8.7746 | -1.7596 | 20.6008 | 11.3219 | 8.2591 | -3.8562 | 20.9025 | 10.5758 | 7.7149 | -5.5535 | 21.0505 | 9.9997 | 7.2947 | -6.3309 | 16.746 | 15.9791 | 11.6565 | 8.0741 | 16.9103 | 15.8268 | 11.5454 | 7.7904 | 17.1487 | 15.6252 | 11.3983 | 7.4295 | 17.4462 | 15.2904 | 11.1541 | 7.0692 | 17.8304 | 15.0266 | 10.9617 | 6.5903 | 18.1819 | 14.7647 | 10.7707 | 6.0743 | 18.3989 | 14.6319 | 10.6738 | 5.4154 | 18.6098 | 14.3197 | 10.446 | 4.246 | 18.7913 | 14.0104 | 10.2204 | 3.0869 | 18.969 | 13.6895 | 9.9863 | 1.9567 | 19.4953 | 12.7557 | 9.3051 | -1.1797 | 19.9776 | 11.9589 | 8.7238 | -3.7746 | 20.2952 | 11.3158 | 8.2547 | -5.3267 | 20.5124 | 10.7608 | 7.8499 | -5.9255 | 20.5389 | 10.4395 | 7.6155 | -5.2085 | 16.7386 | 15.9791 | 11.6565 | 8.0741 | 16.8957 | 15.8687 | 11.576 | 7.8012 | 17.0726 | 15.7023 | 11.4546 | 7.5146 | 17.2679 | 15.5178 | 11.32 | 7.269 | 17.4987 | 15.2773 | 11.1446 | 7.0051 | 17.7674 | 14.996 | 10.9394 | 6.7282 | 18.0599 | 14.9197 | 10.8837 | 6.4387 | 18.3631 | 14.7408 | 10.7532 | 6.1277 | 18.6438 | 14.5244 | 10.5954 | 5.7345 | 18.8274 | 14.3189 | 10.4454 | 5.3316 | 19.223 | 13.8508 | 10.104 | 4.0169 | 19.6231 | 13.4438 | 9.807 | 2.6231 | 19.9154 | 13.0639 | 9.5299 | 1.5307 | 20.1822 | 12.6209 | 9.2068 | 0.48506 | 20.3348 | 12.2161 | 8.9115 | -0.20855 | 16.7386 | 15.9791 | 11.6565 | 8.0741 | 16.922 | 15.7763 | 11.5086 | 7.624 | 17.1954 | 15.5487 | 11.3426 | 7.1544 | 17.5355 | 15.1973 | 11.0862 | 6.6953 | 17.9531 | 14.9184 | 10.8827 | 6.1258 | 18.3699 | 14.6488 | 10.6861 | 5.5466 | 18.5843 | 14.4933 | 10.5727 | 4.8131 | 18.8099 | 14.1593 | 10.329 | 3.5403 | 18.999 | 13.8365 | 10.0935 | 2.3155 | 19.1834 | 13.5025 | 9.8499 | 1.1183 | 19.7243 | 12.533 | 9.1426 | -2.23 | 20.2044 | 11.695 | 8.5313 | -5.0132 | 20.5264 | 11.0127 | 8.0336 | -6.7527 | 20.7462 | 10.4163 | 7.5985 | -7.5834 | 20.7991 | 10.0624 | 7.3404 | -7.0508
WITHINGTON | WEST DIDSBURY | SOUTH MANCHESTER | 384841 | 392774 | 24.0726 | 10.563 | 7.7055 | 6.7616 | 24.221 | 10.3653 | 7.5613 | 6.091 | 24.4315 | 10.2137 | 7.4508 | 5.7146 | 24.6802 | 10.0461 | 7.3285 | 5.406 | 24.8243 | 9.895 | 7.2182 | 4.9873 | 24.9592 | 9.6714 | 7.0551 | 4.5206 | 25.1 | 9.4335 | 6.8816 | 4.0841 | 25.2449 | 9.2146 | 6.7219 | 3.7102 | 25.3445 | 8.9847 | 6.5542 | 3.3616 | 25.4347 | 8.7448 | 6.3792 | 3.0505 | 25.9092 | 8.1312 | 5.9316 | 1.1294 | 26.3387 | 7.4598 | 5.4418 | -1.8836 | 26.6362 | 6.9031 | 5.0357 | -4.0583 | 26.8914 | 6.6456 | 4.8479 | -5.8989 | 27.0485 | 6.4353 | 4.6944 | -7.0974 | 24.0409 | 10.563 | 7.7055 | 6.7616 | 24.1542 | 10.4955 | 7.6563 | 6.5301 | 24.2675 | 10.3698 | 7.5646 | 6.2874 | 24.4302 | 10.2668 | 7.4895 | 6.0302 | 24.6622 | 10.1088 | 7.3742 | 5.71 | 24.9404 | 9.9728 | 7.275 | 5.4205 | 25.0642 | 9.679 | 7.0607 | 5.0636 | 25.1961 | 9.525 | 6.9483 | 4.6474 | 25.2627 | 9.394 | 6.8528 | 4.3848 | 25.3315 | 9.2812 | 6.7705 | 4.1144 | 25.538 | 8.9211 | 6.5078 | 3.3323 | 25.7374 | 8.6293 | 6.295 | 2.606 | 25.9077 | 8.3411 | 6.0847 | 1.9458 | 26.0762 | 8.2313 | 6.0046 | 1.2952 | 26.2015 | 8.0942 | 5.9046 | 0.84332 | 24.0813 | 10.563 | 7.7055 | 6.7616 | 24.2509 | 10.3197 | 7.528 | 5.9405 | 24.4832 | 10.1073 | 7.3731 | 5.4621 | 24.7695 | 9.8948 | 7.2181 | 5.0419 | 24.917 | 9.6833 | 7.0638 | 4.4674 | 25.08 | 9.4045 | 6.8605 | 3.8709 | 25.2534 | 9.1268 | 6.6579 | 3.3159 | 25.4354 | 8.8473 | 6.454 | 2.8021 | 25.5645 | 8.5603 | 6.2446 | 2.3377 | 25.6846 | 8.3276 | 6.0749 | 1.8767 | 26.2253 | 7.5644 | 5.5181 | -0.43089 | 26.8999 | 6.7291 | 4.9088 | -3.3975 | 27.3009 | 6.2919 | 4.5899 | -5.26 | 27.6019 | 5.9451 | 4.3369 | -6.5156 | 27.6368 | 5.8306 | 4.2533 | -6.6642 | 24.0813 | 10.563 | 7.7055 | 6.7616 | 24.0831 | 10.4158 | 7.5982 | 6.3922 | 24.1758 | 10.2737 | 7.4945 | 6.0576 | 24.3152 | 10.0983 | 7.3666 | 5.7263 | 24.5247 | 9.9354 | 7.2478 | 5.2 | 24.8244 | 9.6949 | 7.0723 | 4.6058 | 25.0108 | 9.4588 | 6.9001 | 3.8848 | 25.2401 | 9.1022 | 6.64 | 2.6864 | 25.4122 | 8.7891 | 6.4115 | 1.5251 | 25.5798 | 8.4252 | 6.1461 | 0.40356 | 26.0885 | 7.4669 | 5.447 | -2.6879 | 26.5677 | 6.7432 | 4.919 | -5.1444 | 26.8862 | 6.3255 | 4.6144 | -6.49 | 27.1239 | 6.2944 | 4.5917 | -6.7087 | 27.1234 | 6.2363 | 4.5493 | -5.3239 | 24.0726 | 10.563 | 7.7055 | 6.7616 | 24.196 | 10.4492 | 7.6225 | 6.4741 | 24.3269 | 10.3237 | 7.531 | 6.2245 | 24.4773 | 10.1789 | 7.4253 | 6.0204 | 24.6735 | 10.0633 | 7.341 | 5.7882 | 24.8052 | 9.8926 | 7.2165 | 5.5354 | 24.9158 | 9.6808 | 7.062 | 5.2541 | 25.0401 | 9.4767 | 6.9131 | 4.9629 | 25.1346 | 9.2475 | 6.7459 | 4.6319 | 25.2294 | 9.0026 | 6.5673 | 4.302 | 25.5418 | 8.5344 | 6.2257 | 3.2148 | 25.8686 | 8.2112 | 5.9899 | 2.1227 | 26.0984 | 7.9433 | 5.7945 | 1.3916 | 26.3104 | 7.9068 | 5.7679 | 0.72145 | 26.3989 | 7.876 | 5.7455 | 0.43034 | 24.0726 | 10.563 | 7.7055 | 6.7616 | 24.1561 | 10.3476 | 7.5484 | 6.0947 | 24.3657 | 10.1728 | 7.4209 | 5.6035 | 24.6395 | 9.9742 | 7.2761 | 5.137 | 24.8259 | 9.7818 | 7.1357 | 4.4943 | 24.9841 | 9.53 | 6.952 | 3.8357 | 25.1829 | 9.2764 | 6.767 | 3.0417 | 25.4763 | 8.8996 | 6.4921 | 1.7265 | 25.6615 | 8.5693 | 6.2512 | 0.48413 | 25.8396 | 8.1946 | 5.9778 | -0.71651 | 26.3593 | 7.1965 | 5.2497 | -4.0271 | 26.8163 | 6.419 | 4.6826 | -6.6291 | 27.1219 | 5.9737 | 4.3577 | -8.1229 | 27.348 | 5.906 | 4.3084 | -8.5263 | 27.398 | 5.8028 | 4.2331 | -7.4039
WITHYFOLD DRIVE | MACCLESFIELD | MACCLESFIELD | 392132 | 374352 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844
WOODBINE ST | CASTLETON | ROCHDALE | 390519 | 412388 | 23.9292 | 15.2063 | 11.0928 | 9.8198 | 24.0283 | 15.1458 | 11.0487 | 9.3403 | 24.1816 | 15.0828 | 11.0027 | 9.0728 | 24.3722 | 15.0335 | 10.9667 | 8.8734 | 24.5351 | 14.8279 | 10.8168 | 8.5944 | 24.6985 | 14.5494 | 10.6136 | 8.2932 | 24.8973 | 14.3759 | 10.487 | 8.0001 | 25.1451 | 14.2955 | 10.4284 | 7.7214 | 25.3799 | 14.1916 | 10.3526 | 7.3877 | 25.6224 | 14.0796 | 10.2709 | 7.0689 | 26.3809 | 13.6329 | 9.945 | 5.3903 | 27.0135 | 13.0693 | 9.5339 | 2.7344 | 27.4413 | 12.6189 | 9.2053 | 0.60266 | 27.7797 | 12.1203 | 8.8416 | -1.5743 | 28.0112 | 11.5924 | 8.4565 | -3.6395 | 23.9064 | 15.2063 | 11.0928 | 9.8198 | 23.9691 | 15.1837 | 11.0763 | 9.5737 | 24.0412 | 15.0657 | 10.9902 | 9.3722 | 24.1227 | 14.9454 | 10.9024 | 9.1976 | 24.228 | 14.8417 | 10.8268 | 8.9962 | 24.3546 | 14.7423 | 10.7543 | 8.78 | 24.5114 | 14.4475 | 10.5393 | 8.4986 | 24.7089 | 14.3736 | 10.4853 | 8.1057 | 24.8965 | 14.2966 | 10.4292 | 7.7418 | 25.0973 | 14.2189 | 10.3725 | 7.3718 | 25.6554 | 13.9423 | 10.1707 | 6.2295 | 26.1803 | 13.6558 | 9.9617 | 4.9955 | 26.6944 | 13.282 | 9.6891 | 3.8112 | 27.2471 | 13.2711 | 9.6811 | 2.4573 | 27.6469 | 13.083 | 9.5439 | 1.4529 | 23.9388 | 15.2063 | 11.0928 | 9.8198 | 24.0481 | 15.1041 | 11.0182 | 9.307 | 24.2171 | 15.0535 | 10.9813 | 9.049 | 24.4268 | 14.9489 | 10.905 | 8.8849 | 24.5737 | 14.7176 | 10.7363 | 8.6414 | 24.7479 | 14.3812 | 10.4909 | 8.382 | 24.9577 | 14.2975 | 10.4298 | 8.1308 | 25.2159 | 14.1903 | 10.3516 | 7.848 | 25.4421 | 14.0619 | 10.258 | 7.559 | 25.6751 | 13.9346 | 10.1651 | 7.2851 | 26.3543 | 13.4696 | 9.8259 | 5.9265 | 27.0203 | 12.878 | 9.3943 | 3.4842 | 27.4911 | 12.3855 | 9.0351 | 1.4915 | 27.848 | 11.8622 | 8.6533 | -0.49574 | 28.0683 | 11.3203 | 8.258 | -2.3204 | 23.9388 | 15.2063 | 11.0928 | 9.8198 | 23.9668 | 15.1682 | 11.065 | 9.6306 | 24.0723 | 15.2444 | 11.1206 | 9.4622 | 24.2145 | 15.1781 | 11.0722 | 9.3297 | 24.3492 | 15.0058 | 10.9465 | 9.0958 | 24.5007 | 14.7993 | 10.7959 | 8.8267 | 24.7006 | 14.6597 | 10.694 | 8.4562 | 24.9473 | 14.4238 | 10.5219 | 7.6967 | 25.1862 | 14.1968 | 10.3564 | 6.8851 | 25.4357 | 13.9391 | 10.1684 | 6.0662 | 26.1952 | 13.2749 | 9.6838 | 3.6799 | 26.8131 | 12.6776 | 9.2481 | 1.3224 | 27.2172 | 12.1561 | 8.8677 | -0.49034 | 27.493 | 11.7432 | 8.5665 | -1.6756 | 27.5682 | 11.6308 | 8.4845 | -1.3828 | 23.9292 | 15.2063 | 11.0928 | 9.8198 | 24.0137 | 15.2076 | 11.0937 | 9.5262 | 24.1303 | 15.138 | 11.043 | 9.322 | 24.2577 | 15.1157 | 11.0267 | 9.1842 | 24.4183 | 14.9247 | 10.8873 | 9.0301 | 24.5684 | 14.6861 | 10.7133 | 8.8483 | 24.7547 | 14.5167 | 10.5897 | 8.6485 | 24.9689 | 14.4516 | 10.5422 | 8.4266 | 25.1669 | 14.3466 | 10.4656 | 8.1009 | 25.3768 | 14.2364 | 10.3853 | 7.772 | 26.0778 | 13.9019 | 10.1412 | 6.6685 | 26.6913 | 13.6015 | 9.9221 | 5.427 | 27.0913 | 13.3892 | 9.7673 | 4.5715 | 27.4108 | 13.1383 | 9.5842 | 3.7393 | 27.5858 | 12.7896 | 9.3298 | 3.1406 | 23.9292 | 15.2063 | 11.0928 | 9.8198 | 23.981 | 15.1035 | 11.0178 | 9.4308 | 24.1276 | 15.173 | 11.0685 | 9.1675 | 24.3199 | 15.0898 | 11.0078 | 8.9638 | 24.4752 | 14.9001 | 10.8694 | 8.6654 | 24.6292 | 14.688 | 10.7147 | 8.3529 | 24.8185 | 14.5361 | 10.6039 | 7.9297 | 25.071 | 14.2844 | 10.4203 | 7.101 | 25.3007 | 14.0505 | 10.2496 | 6.2459 | 25.5394 | 13.7863 | 10.0569 | 5.3826 | 26.2944 | 13.099 | 9.5556 | 2.8369 | 26.9348 | 12.4716 | 9.0979 | 0.31802 | 27.3734 | 11.927 | 8.7006 | -1.6588 | 27.6586 | 11.458 | 8.3584 | -3.0346 | 27.7429 | 11.2917 | 8.2371 | -2.951
WOODFIELD RD | WRIGHTINGTON | PENWORTHAM WEST / STANAH | 358258 | 418014 | 30.3499 | 15.8849 | 11.4168 | 13.4038 | 30.4407 | 15.1986 | 10.9235 | 12.6897 | 30.5907 | 14.8795 | 10.6942 | 12.315 | 30.8052 | 14.6377 | 10.5204 | 12.0194 | 31.1007 | 14.2967 | 10.2753 | 11.521 | 31.3967 | 13.9298 | 10.0116 | 10.8963 | 31.8056 | 13.575 | 9.7566 | 10.2784 | 32.3512 | 13.2116 | 9.4954 | 9.4817 | 32.968 | 12.8199 | 9.2139 | 8.504 | 33.6584 | 12.5328 | 9.0076 | 7.4269 | 35.684 | 11.2468 | 8.0833 | 3.1963 | 37.5169 | 9.7342 | 6.9962 | -1.8578 | 38.4945 | 8.5028 | 6.1111 | -5.4533 | 39.2014 | 7.376 | 5.3013 | -8.5954 | 38.9311 | 6.4097 | 4.6068 | -10.9618 | 30.3057 | 15.8849 | 11.4168 | 13.4038 | 30.3861 | 15.6945 | 11.28 | 13.1134 | 30.4832 | 15.533 | 11.1639 | 12.8894 | 30.6048 | 15.3463 | 11.0297 | 12.6846 | 30.772 | 15.1282 | 10.8729 | 12.4287 | 30.9934 | 14.8906 | 10.7022 | 12.1097 | 31.2746 | 14.5254 | 10.4397 | 11.6925 | 31.618 | 14.2347 | 10.2308 | 11.1645 | 31.9249 | 13.97 | 10.0405 | 10.6769 | 32.2376 | 13.6927 | 9.8412 | 10.1243 | 33.396 | 12.8013 | 9.2006 | 8.0409 | 34.912 | 11.9301 | 8.5744 | 5.4304 | 36.313 | 11.0478 | 7.9403 | 2.5832 | 37.6584 | 10.1792 | 7.316 | -0.77983 | 38.5485 | 9.4458 | 6.7889 | -3.0293 | 30.359 | 15.8849 | 11.4168 | 13.4038 | 30.4603 | 15.0709 | 10.8317 | 12.5982 | 30.6214 | 14.6169 | 10.5055 | 12.2135 | 30.8461 | 14.2598 | 10.2488 | 11.933 | 31.0967 | 13.8503 | 9.9545 | 11.4734 | 31.3677 | 13.4255 | 9.6492 | 10.9084 | 31.7325 | 12.9888 | 9.3353 | 10.3821 | 32.2103 | 12.6709 | 9.1068 | 9.7201 | 32.7287 | 12.3579 | 8.8819 | 8.936 | 33.3253 | 12.0096 | 8.6315 | 8.0453 | 35.3557 | 10.568 | 7.5954 | 4.0317 | 37.3434 | 8.8287 | 6.3454 | -1.2589 | 38.4561 | 7.3754 | 5.3008 | -5.2356 | 36.7748 | 6.0547 | 4.3516 | -8.4983 | 30.4215 | 5.0087 | 3.5998 | -10.6651 | 30.359 | 15.8849 | 11.4168 | 13.4038 | 30.3528 | 15.3459 | 11.0294 | 13.0407 | 30.4409 | 15.0234 | 10.7976 | 12.7767 | 30.5905 | 14.6993 | 10.5647 | 12.5336 | 30.8404 | 14.3271 | 10.2972 | 12.0828 | 31.1753 | 13.9478 | 10.0246 | 11.4659 | 31.6117 | 13.4884 | 9.6944 | 10.6974 | 32.255 | 12.8979 | 9.27 | 9.3069 | 32.9783 | 12.407 | 8.9171 | 7.7357 | 33.7778 | 11.85 | 8.5168 | 6.0603 | 35.908 | 10.1542 | 7.298 | 0.88426 | 37.3397 | 8.4903 | 6.1022 | -3.9338 | 38.232 | 7.1841 | 5.1633 | -7.2367 | 38.6837 | 6.369 | 4.5775 | -9.2824 | 35.7645 | 5.8883 | 4.2321 | -8.9803 | 30.3499 | 15.8849 | 11.4168 | 13.4038 | 30.4253 | 15.5909 | 11.2055 | 13.0321 | 30.5304 | 15.3564 | 11.037 | 12.7593 | 30.6695 | 15.1441 | 10.8843 | 12.5473 | 30.8803 | 14.8528 | 10.675 | 12.1957 | 31.1822 | 14.5309 | 10.4436 | 11.714 | 31.5162 | 14.2064 | 10.2104 | 11.2322 | 31.9451 | 13.8664 | 9.9661 | 10.6059 | 32.4284 | 13.4867 | 9.6932 | 9.8126 | 32.9843 | 13.2181 | 9.5001 | 8.9125 | 34.8863 | 12.1515 | 8.7335 | 5.6634 | 36.44 | 11.0918 | 7.9719 | 2.1739 | 37.4948 | 10.2395 | 7.3594 | -0.24509 | 38.2333 | 9.5302 | 6.8496 | -1.8942 | 38.5361 | 9.1006 | 6.5408 | -2.5347 | 30.3499 | 15.8849 | 11.4168 | 13.4038 | 30.3731 | 15.0425 | 10.8113 | 12.7132 | 30.5082 | 14.6383 | 10.5208 | 12.3313 | 30.7064 | 14.2809 | 10.264 | 12.0172 | 30.9811 | 13.8817 | 9.9771 | 11.526 | 31.2485 | 13.4836 | 9.6909 | 10.9345 | 31.6256 | 13.018 | 9.3563 | 10.2302 | 32.2051 | 12.3996 | 8.9118 | 8.905 | 32.833 | 11.9041 | 8.5557 | 7.4541 | 33.5413 | 11.3484 | 8.1563 | 5.8933 | 35.843 | 9.5964 | 6.8971 | 0.77666 | 37.5123 | 7.7921 | 5.6003 | -4.4426 | 38.596 | 6.3567 | 4.5687 | -8.3221 | 32.9593 | 5.4265 | 3.9001 | -10.7718 | 29.6941 | 4.8889 | 3.5138 | -10.6734
WOODHILL LANE | LANCASTER | HEYSHAM | 343294 | 463785 | 11.5017 | 9.6416 | 7.0334 | 4.0785 | 11.5344 | 9.5708 | 6.9817 | 3.9729 | 11.5596 | 9.3913 | 6.8508 | 3.298 | 11.5903 | 9.1788 | 6.6958 | 2.468 | 11.6335 | 8.9456 | 6.5257 | 1.585 | 11.6829 | 8.6925 | 6.3411 | 0.6915 | 11.7387 | 8.333 | 6.0788 | -0.7911 | 11.8024 | 8.2298 | 6.0035 | -0.89171 | 11.8452 | 8.1363 | 5.9353 | -0.96405 | 11.8842 | 8.0724 | 5.8887 | -1.0198 | 12.0585 | 7.7716 | 5.6692 | -1.7628 | 12.3102 | 7.3775 | 5.3818 | -3.2757 | 12.5085 | 7.0039 | 5.1092 | -4.5188 | 12.7087 | 6.5587 | 4.7845 | -5.8379 | 12.8699 | 6.0924 | 4.4443 | -7.014 | 11.5006 | 9.6416 | 7.0334 | 4.0785 | 11.5484 | 9.5931 | 6.998 | 3.9382 | 11.5918 | 9.4479 | 6.8921 | 3.6041 | 11.6464 | 9.2989 | 6.7835 | 3.2518 | 11.7193 | 9.1486 | 6.6738 | 2.8605 | 11.8067 | 8.9941 | 6.561 | 2.4758 | 11.9126 | 8.7661 | 6.3948 | 1.8473 | 12.0358 | 8.6631 | 6.3196 | 1.5689 | 12.0695 | 8.5938 | 6.269 | 1.4796 | 12.1036 | 8.5187 | 6.2143 | 1.3844 | 12.2051 | 8.2975 | 6.0529 | 1.1086 | 12.3018 | 8.1517 | 5.9465 | 0.83898 | 12.3795 | 7.9927 | 5.8306 | 0.60385 | 12.4504 | 7.8421 | 5.7207 | 0.36045 | 12.4976 | 7.6358 | 5.5702 | 0.18172 | 11.5022 | 9.6416 | 7.0334 | 4.0785 | 11.5363 | 9.5404 | 6.9596 | 3.9776 | 11.5626 | 9.3085 | 6.7904 | 3.3112 | 11.5951 | 9.0457 | 6.5987 | 2.4947 | 11.6402 | 8.7856 | 6.409 | 1.6255 | 11.6918 | 8.5151 | 6.2117 | 0.74779 | 11.7508 | 8.1417 | 5.9393 | -0.70968 | 11.8178 | 8.0128 | 5.8452 | -0.78612 | 11.8628 | 7.8904 | 5.7559 | -0.82852 | 11.9032 | 7.7928 | 5.6847 | -0.85896 | 12.0814 | 7.3754 | 5.3803 | -1.5191 | 12.3333 | 6.864 | 5.0072 | -2.9582 | 12.5295 | 6.3796 | 4.6538 | -4.1309 | 12.7243 | 5.7889 | 4.2229 | -5.3619 | 12.876 | 5.2158 | 3.8048 | -6.4335 | 11.5022 | 9.6416 | 7.0334 | 4.0785 | 11.4794 | 9.5779 | 6.9869 | 4.1386 | 11.4776 | 9.3869 | 6.8476 | 3.5263 | 11.4829 | 9.1296 | 6.6599 | 2.7415 | 11.5043 | 8.8931 | 6.4874 | 1.8944 | 11.5395 | 8.6597 | 6.3171 | 1.0328 | 11.5926 | 8.249 | 6.0175 | -0.50996 | 11.6798 | 7.9959 | 5.8329 | -1.0095 | 11.7608 | 7.779 | 5.6747 | -1.5183 | 11.8403 | 7.5864 | 5.5342 | -2.0184 | 12.0781 | 7.0434 | 5.1381 | -3.4444 | 12.3164 | 6.5269 | 4.7613 | -4.8014 | 12.4981 | 6.0352 | 4.4026 | -5.8658 | 12.6275 | 5.5286 | 4.0331 | -6.488 | 12.6017 | 5.2455 | 3.8265 | -5.8987 | 11.5017 | 9.6416 | 7.0334 | 4.0785 | 11.5306 | 9.5839 | 6.9913 | 3.9863 | 11.5467 | 9.4098 | 6.8643 | 3.3254 | 11.5633 | 9.2006 | 6.7117 | 2.5231 | 11.5904 | 8.9782 | 6.5495 | 1.6986 | 11.6303 | 8.7397 | 6.3755 | 0.88806 | 11.6844 | 8.3929 | 6.1225 | -0.52797 | 11.7456 | 8.2948 | 6.051 | -0.60336 | 11.7873 | 8.2005 | 5.9821 | -0.6783 | 11.8287 | 8.1337 | 5.9334 | -0.75037 | 11.9659 | 7.9182 | 5.7762 | -1.0176 | 12.1138 | 7.7342 | 5.642 | -1.3326 | 12.222 | 7.5513 | 5.5086 | -1.5429 | 12.3248 | 7.3041 | 5.3282 | -1.7581 | 12.3646 | 7.0451 | 5.1393 | -1.8046 | 11.5017 | 9.6416 | 7.0334 | 4.0785 | 11.4956 | 9.56 | 6.9739 | 4.1003 | 11.5156 | 9.3581 | 6.8266 | 3.4401 | 11.5461 | 9.092 | 6.6325 | 2.6018 | 11.5908 | 8.8447 | 6.4521 | 1.7025 | 11.6401 | 8.6015 | 6.2746 | 0.7973 | 11.7056 | 8.1814 | 5.9682 | -0.79746 | 11.8146 | 7.9263 | 5.7821 | -1.3598 | 11.904 | 7.7021 | 5.6186 | -1.8967 | 11.9907 | 7.4956 | 5.4679 | -2.4258 | 12.2419 | 6.9328 | 5.0574 | -3.9433 | 12.4808 | 6.3957 | 4.6656 | -5.3782 | 12.6647 | 5.8834 | 4.2918 | -6.5302 | 12.7969 | 5.3552 | 3.9066 | -7.2792 | 12.7852 | 5.0452 | 3.6804 | -6.8491
WOODHOUSE PARK | MOSS NOOK | SOUTH MANCHESTER | 382132 | 386340 | 24.6162 | 11.3812 | 8.1799 | 9.0397 | 24.6485 | 11.1614 | 8.0219 | 8.6248 | 24.69 | 11.22 | 8.0641 | 8.4751 | 24.7335 | 11.0377 | 7.933 | 8.4262 | 24.7943 | 10.8707 | 7.813 | 8.3388 | 24.8701 | 11.0392 | 7.9341 | 8.2324 | 24.9623 | 10.8803 | 7.8199 | 8.1353 | 25.0721 | 10.6949 | 7.6866 | 8.0646 | 25.1699 | 10.3682 | 7.4518 | 7.9314 | 25.2617 | 10.5538 | 7.5852 | 7.8336 | 25.5689 | 10.202 | 7.3324 | 6.6859 | 25.9128 | 9.7368 | 6.998 | 4.3492 | 26.1643 | 9.3005 | 6.6845 | 2.3957 | 26.3701 | 8.9622 | 6.4413 | 0.63673 | 26.5213 | 8.5835 | 6.1692 | -1.4049 | 24.6075 | 11.3812 | 8.1799 | 9.0397 | 24.6352 | 11.3802 | 8.1791 | 8.8783 | 24.667 | 11.5762 | 8.32 | 8.7572 | 24.696 | 11.6659 | 8.3845 | 8.69 | 24.7336 | 11.6614 | 8.3813 | 8.6385 | 24.7842 | 11.5744 | 8.3188 | 8.5791 | 24.851 | 11.4434 | 8.2246 | 8.4853 | 24.9319 | 11.3478 | 8.1559 | 8.3521 | 24.9962 | 11.2546 | 8.0889 | 8.1903 | 25.0624 | 11.1617 | 8.0222 | 8.0307 | 25.2727 | 10.8785 | 7.8186 | 7.5687 | 25.4872 | 10.6455 | 7.6511 | 7.1202 | 25.6688 | 10.4777 | 7.5305 | 6.7355 | 25.843 | 10.6295 | 7.6396 | 6.3458 | 25.961 | 10.5548 | 7.586 | 5.993 | 24.6193 | 11.3812 | 8.1799 | 9.0397 | 24.6537 | 11.1459 | 8.0108 | 8.5773 | 24.6995 | 11.2666 | 8.0975 | 8.428 | 24.7502 | 11.15 | 8.0137 | 8.4054 | 24.8196 | 11.0301 | 7.9276 | 8.3393 | 24.9054 | 10.9861 | 7.896 | 8.2561 | 25.0107 | 10.7986 | 7.7612 | 8.1966 | 25.1357 | 10.5804 | 7.6043 | 8.1589 | 25.236 | 10.4904 | 7.5397 | 8.0765 | 25.33 | 10.4936 | 7.5419 | 8.0199 | 25.6527 | 10.142 | 7.2893 | 7.0055 | 26.0133 | 9.6281 | 6.9199 | 4.7716 | 26.2722 | 9.164 | 6.5863 | 2.9142 | 26.4725 | 8.8241 | 6.342 | 1.2758 | 26.5268 | 8.4283 | 6.0576 | -0.62145 | 24.6193 | 11.3812 | 8.1799 | 9.0397 | 24.5773 | 11.2698 | 8.0998 | 8.9084 | 24.5904 | 11.4432 | 8.2244 | 8.836 | 24.608 | 11.3941 | 8.1892 | 8.8374 | 24.6495 | 11.1458 | 8.0107 | 8.7789 | 24.7217 | 11.1561 | 8.0181 | 8.6942 | 24.8215 | 11.0031 | 7.9082 | 8.5741 | 24.9498 | 10.8246 | 7.7798 | 7.8619 | 25.0646 | 10.6356 | 7.644 | 7.1044 | 25.1769 | 10.3206 | 7.4176 | 6.3558 | 25.5121 | 9.8134 | 7.0531 | 4.2046 | 25.8438 | 9.2979 | 6.6826 | 2.094 | 26.0743 | 8.8372 | 6.3515 | 0.39927 | 26.2116 | 8.7145 | 6.2633 | -0.35368 | 26.1797 | 8.6586 | 6.2231 | 0.31515 | 24.6162 | 11.3812 | 8.1799 | 9.0397 | 24.6417 | 11.2248 | 8.0675 | 8.7929 | 24.6677 | 11.2549 | 8.0891 | 8.6936 | 24.6848 | 11.0693 | 7.9557 | 8.6941 | 24.7111 | 10.9226 | 7.8503 | 8.7168 | 24.7634 | 11.1434 | 8.009 | 8.724 | 24.842 | 11.0115 | 7.9142 | 8.7159 | 24.9334 | 10.8298 | 7.7836 | 8.6907 | 25.0179 | 10.4907 | 7.5399 | 8.5805 | 25.1023 | 10.6882 | 7.6818 | 8.4743 | 25.3758 | 10.4752 | 7.5287 | 8.0981 | 25.66 | 10.3651 | 7.4496 | 7.6774 | 25.8633 | 10.2088 | 7.3373 | 7.2956 | 26.0282 | 10.1095 | 7.2659 | 6.8552 | 26.1018 | 10.0437 | 7.2186 | 6.6654 | 24.6162 | 11.3812 | 8.1799 | 9.0397 | 24.5841 | 11.2407 | 8.0789 | 8.6899 | 24.6152 | 11.375 | 8.1754 | 8.54 | 24.6548 | 11.3183 | 8.1347 | 8.4977 | 24.7144 | 11.0701 | 7.9563 | 8.3991 | 24.7859 | 11.0687 | 7.9553 | 8.2871 | 24.8775 | 10.8915 | 7.828 | 8.1305 | 25.0113 | 10.7162 | 7.7019 | 7.3663 | 25.1292 | 10.5201 | 7.561 | 6.5739 | 25.244 | 10.1997 | 7.3307 | 5.7881 | 25.5803 | 9.6636 | 6.9454 | 3.5163 | 25.896 | 9.1305 | 6.5623 | 1.3176 | 26.1183 | 8.6534 | 6.2194 | -0.47251 | 26.2452 | 8.5069 | 6.1141 | -1.3495 | 26.2225 | 8.4077 | 6.0428 | -0.83928
WOODLEY | VERNON PARK | BREDBURY | 393116 | 392019 | 13.0148 | 2.1428 | 1.5401 | 13.0148 | 11.161 | 1.8376 | 1.3207 | 11.161 | 9.4857 | 1.5617 | 1.1225 | 9.4857 | 7.662 | 1.2615 | 0.90666 | 7.662 | 5.418 | 0.89204 | 0.64112 | 5.418 | 3.8406 | 0.63233 | 0.45447 | 3.8406 | 2.8196 | 0.46422 | 0.33365 | 2.8196 | 1.4842 | 0.24436 | 0.17562 | 1.4842 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 1.5878 | 13.0148 | 2.1428 | 1.5401 | 13.0148 | 11.9372 | 1.9654 | 1.4125 | 11.9372 | 10.9395 | 1.8011 | 1.2945 | 10.9395 | 9.5621 | 1.5743 | 1.1315 | 9.5621 | 8.0005 | 1.3172 | 0.94671 | 8.0005 | 5.9585 | 0.98102 | 0.70508 | 5.9585 | 4.1761 | 0.68757 | 0.49417 | 4.1761 | 3.3961 | 0.55913 | 0.40186 | 3.3961 | 2.5836 | 0.42537 | 0.30572 | 2.5836 | 1.6824 | 0.277 | 0.19909 | 1.6824 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 13.0148 | 2.1428 | 1.5401 | 13.0148 | 10.8748 | 1.7904 | 1.2868 | 10.8748 | 8.7898 | 1.4472 | 1.0401 | 8.7898 | 6.2391 | 1.0272 | 0.73828 | 6.2391 | 3.8868 | 0.63993 | 0.45993 | 3.8868 | 2.4684 | 0.4064 | 0.29209 | 2.4684 | 0.84312 | 0.13881 | 0.099768 | 0.84312 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 1.6495 | 2.6844 | 0.44197 | 0.31765 | 0.75187 | 13.0148 | 2.1428 | 1.5401 | 13.0148 | 11.3723 | 1.8724 | 1.3457 | 11.3723 | 9.6704 | 1.5922 | 1.1443 | 9.6704 | 6.6592 | 1.0964 | 0.78799 | 6.6592 | 4.474 | 0.73661 | 0.52942 | 4.474 | 3.8334 | 0.63114 | 0.45361 | 3.8334 | 2.8217 | 0.46458 | 0.3339 | 2.8217 | 1.1431 | 0.1882 | 0.13526 | 1.1431 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.5677 | 2.6844 | 0.44197 | 0.31765 | 1.8969 | 2.6844 | 0.44197 | 0.31765 | 2.1403 | 13.0148 | 2.1428 | 1.5401 | 13.0148 | 11.7343 | 1.932 | 1.3885 | 11.7343 | 10.285 | 1.6933 | 1.217 | 10.285 | 8.5853 | 1.4135 | 1.0159 | 8.5853 | 6.5796 | 1.0833 | 0.77857 | 6.5796 | 5.0737 | 0.83534 | 0.60038 | 5.0737 | 4.2787 | 0.70446 | 0.50631 | 4.2787 | 3.0793 | 0.50698 | 0.36438 | 3.0793 | 1.4792 | 0.24354 | 0.17504 | 1.4792 | 0.21596 | 0.035555 | 0.025554 | 0.21596 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 13.0148 | 2.1428 | 1.5401 | 13.0148 | 10.9195 | 1.7978 | 1.2921 | 10.9195 | 9.0337 | 1.4873 | 1.069 | 9.0337 | 5.936 | 0.97731 | 0.70241 | 5.936 | 3.7034 | 0.60974 | 0.43823 | 3.7034 | 3.022 | 0.49755 | 0.3576 | 3.022 | 1.9727 | 0.32479 | 0.23343 | 1.9727 | 0.26496 | 0.043624 | 0.031353 | 0.26496 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 2.6844 | 0.44197 | 0.31765 | 1.9663 | 2.6844 | 0.44197 | 0.31765 | 0.96317 | 2.6844 | 0.44197 | 0.31765 | 0.68308
WOOLFOLD | BURY | KEARSLEY | 378874 | 411666 | 29.0367 | 14.5468 | 10.4551 | 16.14 | 29.1024 | 14.4336 | 10.3737 | 15.8777 | 29.2018 | 13.9242 | 10.0076 | 15.6917 | 29.3274 | 13.55 | 9.7387 | 15.5543 | 29.4811 | 13.0907 | 9.4085 | 15.3698 | 29.652 | 12.6517 | 9.093 | 15.1877 | 29.8419 | 12.2045 | 8.7716 | 15.0359 | 30.0705 | 12.1213 | 8.7118 | 14.9005 | 30.2483 | 12.0345 | 8.6495 | 14.697 | 30.4151 | 11.9575 | 8.5941 | 14.5175 | 31.0206 | 11.5554 | 8.3051 | 12.8863 | 31.7388 | 11.0024 | 7.9077 | 9.7719 | 32.1006 | 10.6564 | 7.6589 | 7.093 | 32.4369 | 10.2521 | 7.3684 | 4.1217 | 32.6781 | 9.8082 | 7.0493 | 1.5594 | 29.0029 | 14.5468 | 10.4551 | 16.14 | 29.0543 | 14.4912 | 10.4151 | 16.0208 | 29.1035 | 14.4254 | 10.3678 | 15.8819 | 29.1632 | 14.364 | 10.3237 | 15.746 | 29.2472 | 14.2476 | 10.24 | 15.5754 | 29.3524 | 14.1361 | 10.1599 | 15.3838 | 29.4785 | 13.9247 | 10.008 | 15.1381 | 29.6231 | 13.915 | 10.001 | 14.827 | 29.7222 | 13.8336 | 9.9425 | 14.5407 | 29.8243 | 13.7741 | 9.8997 | 14.2521 | 30.1346 | 13.5181 | 9.7157 | 13.3898 | 30.4323 | 13.2988 | 9.5581 | 12.5399 | 30.7032 | 13.2384 | 9.5147 | 11.7057 | 30.9869 | 13.2203 | 9.5017 | 10.7252 | 31.2075 | 13.025 | 9.3613 | 10.0633 | 29.0457 | 14.5468 | 10.4551 | 16.14 | 29.1201 | 14.4051 | 10.3532 | 15.875 | 29.2329 | 13.9105 | 9.9977 | 15.7119 | 29.3788 | 13.5017 | 9.7039 | 15.6221 | 29.5571 | 12.9844 | 9.3321 | 15.0297 | 29.7571 | 12.4455 | 8.9448 | 14.447 | 29.9824 | 11.9097 | 8.5597 | 13.9136 | 30.2543 | 11.755 | 8.4485 | 13.4058 | 30.4594 | 11.621 | 8.3522 | 12.9986 | 30.6501 | 11.4929 | 8.2602 | 12.5961 | 31.3241 | 11.0057 | 7.91 | 10.914 | 31.9631 | 10.4216 | 7.4902 | 8.0384 | 32.3405 | 9.9868 | 7.1777 | 5.5722 | 32.6797 | 9.7222 | 6.9875 | 2.8585 | 32.8811 | 9.2421 | 6.6425 | 0.59431 | 29.0457 | 14.5468 | 10.4551 | 16.14 | 29.0447 | 14.4704 | 10.4001 | 16.1397 | 29.0971 | 14.0199 | 10.0764 | 16.0626 | 29.1752 | 13.5986 | 9.7736 | 15.9973 | 29.293 | 13.1092 | 9.4218 | 15.4017 | 29.4694 | 12.5596 | 9.0268 | 14.7836 | 29.7013 | 11.9668 | 8.6008 | 14.0079 | 30.0163 | 11.6857 | 8.3988 | 12.635 | 30.2784 | 11.4297 | 8.2147 | 11.3583 | 30.5319 | 11.1862 | 8.0398 | 10.084 | 31.1702 | 11.1578 | 8.0194 | 6.9613 | 31.659 | 10.4951 | 7.5431 | 4.2143 | 32.0205 | 9.8985 | 7.1142 | 1.9339 | 32.3086 | 9.3925 | 6.7506 | 0.36566 | 32.361 | 9.3646 | 6.7305 | 1.3181 | 29.0367 | 14.5468 | 10.4551 | 16.14 | 29.0908 | 14.4816 | 10.4082 | 16.0373 | 29.1565 | 14.0143 | 10.0723 | 15.9262 | 29.2305 | 13.6096 | 9.7815 | 15.8618 | 29.3269 | 13.1898 | 9.4798 | 15.794 | 29.4741 | 12.768 | 9.1766 | 15.6966 | 29.6625 | 12.3328 | 8.8638 | 15.5882 | 29.866 | 12.2562 | 8.8088 | 15.4861 | 30.0237 | 12.1723 | 8.7485 | 15.2939 | 30.1786 | 12.0945 | 8.6925 | 15.1084 | 30.669 | 11.864 | 8.5269 | 14.4483 | 31.1989 | 11.7005 | 8.4094 | 13.5187 | 31.5971 | 11.6932 | 8.4042 | 12.7058 | 31.9738 | 11.7185 | 8.4224 | 11.9499 | 32.1831 | 11.6739 | 8.3903 | 11.5188 | 29.0367 | 14.5468 | 10.4551 | 16.14 | 29.0631 | 14.428 | 10.3697 | 15.9941 | 29.1582 | 13.9751 | 10.0442 | 15.8116 | 29.2879 | 13.5271 | 9.7222 | 15.6469 | 29.4472 | 13.0099 | 9.3505 | 14.9622 | 29.6219 | 12.4428 | 8.9429 | 14.2849 | 29.8388 | 11.8425 | 8.5115 | 13.4382 | 30.17 | 11.5467 | 8.2988 | 11.9617 | 30.4493 | 11.275 | 8.1036 | 10.6058 | 30.7161 | 11.0193 | 7.9198 | 9.2538 | 31.3893 | 10.9313 | 7.8566 | 5.9033 | 31.8353 | 10.2309 | 7.3532 | 2.957 | 32.1645 | 9.5964 | 6.8971 | 0.47735 | 32.4136 | 9.0414 | 6.4982 | -1.3507 | 32.4644 | 8.9618 | 6.441 | -0.6957
WORDSWORTH ST | BOLTON | KEARSLEY | 370709 | 410873 | 30.691 | 9.8489 | 7.1846 | 14.9351 | 30.7862 | 9.7459 | 7.1095 | 14.7254 | 30.9005 | 9.647 | 7.0373 | 14.5832 | 31.0472 | 9.5053 | 6.934 | 14.4241 | 31.235 | 9.2018 | 6.7126 | 14.1239 | 31.4514 | 9.2036 | 6.7139 | 13.8048 | 31.6955 | 9.0645 | 6.6124 | 13.508 | 31.9229 | 8.9673 | 6.5415 | 13.2355 | 32.1014 | 8.8587 | 6.4623 | 12.9634 | 32.2721 | 8.7506 | 6.3834 | 12.7073 | 32.7248 | 8.2061 | 5.9862 | 10.6698 | 33.249 | 7.4463 | 5.432 | 7.1871 | 33.6385 | 6.829 | 4.9817 | 4.4692 | 33.9942 | 6.5138 | 4.7517 | 1.8963 | 34.2197 | 6.0861 | 4.4397 | 0.22156 | 30.6546 | 9.8489 | 7.1846 | 14.9351 | 30.7115 | 9.7916 | 7.1429 | 14.803 | 30.7517 | 9.7249 | 7.0942 | 14.7325 | 30.803 | 9.6206 | 7.0181 | 14.6431 | 30.8869 | 9.5252 | 6.9485 | 14.4809 | 30.9989 | 9.4311 | 6.8798 | 14.2939 | 31.1374 | 9.2415 | 6.7415 | 14.0372 | 31.2942 | 9.1153 | 6.6495 | 13.7123 | 31.4026 | 9.0035 | 6.568 | 13.4841 | 31.5173 | 8.8986 | 6.4914 | 13.2398 | 31.8698 | 8.6131 | 6.2832 | 12.4987 | 32.2036 | 8.2534 | 6.0207 | 11.7365 | 32.4587 | 8.1908 | 5.9751 | 10.9894 | 32.7196 | 8.2433 | 6.0134 | 10.1281 | 32.9206 | 8.2374 | 6.0091 | 9.5486 | 30.7047 | 9.8489 | 7.1846 | 14.9351 | 30.8331 | 9.7048 | 7.0795 | 14.6198 | 30.9934 | 9.5443 | 6.9625 | 14.3655 | 31.1982 | 9.2834 | 6.7721 | 14.091 | 31.4539 | 9.1785 | 6.6956 | 13.6709 | 31.7482 | 8.9933 | 6.5605 | 13.2267 | 32.0139 | 8.8308 | 6.442 | 12.8139 | 32.3213 | 8.6707 | 6.3252 | 12.4068 | 32.4869 | 8.511 | 6.2087 | 11.9924 | 32.648 | 8.3539 | 6.0941 | 11.5749 | 33.2182 | 7.6387 | 5.5723 | 9.1561 | 33.822 | 6.8104 | 4.9681 | 5.8014 | 34.2325 | 6.1793 | 4.5077 | 3.541 | 34.5207 | 6.0607 | 4.4212 | 1.6919 | 34.644 | 5.7094 | 4.1649 | 1.058 | 30.7047 | 9.8489 | 7.1846 | 14.9351 | 30.7091 | 9.7917 | 7.1429 | 15.007 | 30.7922 | 9.6857 | 7.0656 | 14.8516 | 30.9087 | 9.4351 | 6.8828 | 14.6133 | 31.0847 | 9.3067 | 6.7891 | 14.198 | 31.3418 | 9.2027 | 6.7132 | 13.738 | 31.6643 | 8.9688 | 6.5426 | 13.0789 | 32.0297 | 8.6075 | 6.279 | 11.7358 | 32.2529 | 8.2904 | 6.0477 | 10.4425 | 32.4723 | 7.9977 | 5.8342 | 9.2072 | 33.0633 | 7.4681 | 5.4479 | 5.8276 | 33.583 | 6.8353 | 4.9862 | 3.1068 | 33.8846 | 6.3047 | 4.5992 | 1.4883 | 34.0824 | 5.945 | 4.3368 | 1.0814 | 34.0694 | 5.9327 | 4.3278 | 2.3602 | 30.691 | 9.8489 | 7.1846 | 14.9351 | 30.7744 | 9.7666 | 7.1246 | 14.7515 | 30.8495 | 9.688 | 7.0672 | 14.6535 | 30.9351 | 9.5618 | 6.9752 | 14.5764 | 31.0569 | 9.3754 | 6.8392 | 14.4417 | 31.2476 | 9.3118 | 6.7928 | 14.2684 | 31.5007 | 9.1956 | 6.7081 | 14.0486 | 31.7216 | 9.1103 | 6.6458 | 13.7953 | 31.8856 | 9.0013 | 6.5663 | 13.5 | 32.0503 | 8.8896 | 6.4848 | 13.194 | 32.5393 | 8.5307 | 6.223 | 12.128 | 32.9282 | 8.1988 | 5.9809 | 10.8923 | 33.2127 | 7.9086 | 5.7692 | 9.9163 | 33.4803 | 7.8239 | 5.7074 | 8.9876 | 33.6215 | 7.7408 | 5.6468 | 8.4742 | 30.691 | 9.8489 | 7.1846 | 14.9351 | 30.7266 | 9.7579 | 7.1183 | 14.943 | 30.8571 | 9.6301 | 7.025 | 14.7011 | 31.0325 | 9.3851 | 6.8463 | 14.3655 | 31.2564 | 9.2236 | 6.7285 | 13.8609 | 31.509 | 9.0917 | 6.6323 | 13.3393 | 31.8086 | 8.8413 | 6.4496 | 12.5996 | 32.1993 | 8.4567 | 6.169 | 11.1501 | 32.4391 | 8.1294 | 5.9303 | 9.7758 | 32.6539 | 7.8196 | 5.7043 | 8.4575 | 33.258 | 7.2663 | 5.3006 | 4.8203 | 33.7808 | 6.5559 | 4.7824 | 1.8856 | 34.0728 | 5.9841 | 4.3653 | 0.051019 | 34.2609 | 5.5715 | 4.0643 | -0.64443 | 33.9495 | 5.5069 | 4.0172 | 0.35088
WORSLEY MESNES | WIGAN | WASHWAY FARM / KIRKBY | 357435 | 403977 | 25.912 | 14.4455 | 10.5378 | 18.7902 | 25.9534 | 14.0867 | 10.276 | 17.2588 | 26.0132 | 13.9113 | 10.1481 | 16.898 | 26.0827 | 13.7826 | 10.0542 | 16.8186 | 26.1706 | 13.5463 | 9.8818 | 16.5866 | 26.2612 | 13.349 | 9.7379 | 16.3405 | 26.3637 | 13.1384 | 9.5843 | 16.1037 | 26.4914 | 12.9577 | 9.4524 | 15.8602 | 26.6021 | 12.7749 | 9.3191 | 15.5681 | 26.7097 | 12.6738 | 9.2454 | 15.2967 | 27.0683 | 12.1165 | 8.8388 | 13.776 | 27.4547 | 11.4335 | 8.3406 | 11.2593 | 27.7356 | 11.0721 | 8.0769 | 9.087 | 27.9819 | 10.6532 | 7.7713 | 6.6559 | 28.1527 | 10.1152 | 7.3789 | 4.4181 | 25.9028 | 14.4455 | 10.5378 | 18.7902 | 25.9429 | 14.3183 | 10.445 | 18.272 | 25.9889 | 14.2373 | 10.3859 | 18.1305 | 26.0401 | 14.1653 | 10.3334 | 18.0651 | 26.1086 | 14.0721 | 10.2654 | 17.9516 | 26.1887 | 13.971 | 10.1917 | 17.8116 | 26.2829 | 13.6532 | 9.9598 | 17.6125 | 26.3986 | 13.5474 | 9.8827 | 17.3365 | 26.4839 | 13.4526 | 9.8134 | 17.0716 | 26.5723 | 13.3616 | 9.7471 | 16.799 | 26.8316 | 13.1111 | 9.5644 | 15.9775 | 27.0645 | 12.9553 | 9.4507 | 15.1569 | 27.2752 | 12.8264 | 9.3567 | 14.3845 | 27.4865 | 12.6672 | 9.2405 | 13.5728 | 27.6319 | 12.4786 | 9.103 | 13.0445 | 25.9159 | 14.4455 | 10.5378 | 18.7902 | 25.962 | 14.0278 | 10.2331 | 17.033 | 26.029 | 13.8199 | 10.0814 | 16.6414 | 26.1092 | 13.679 | 9.9786 | 16.589 | 26.2056 | 13.4268 | 9.7947 | 16.388 | 26.3001 | 13.2218 | 9.6451 | 16.1791 | 26.4161 | 13.0122 | 9.4922 | 15.9975 | 26.559 | 12.8243 | 9.3551 | 15.8135 | 26.6735 | 12.6489 | 9.2272 | 15.5796 | 26.7839 | 12.5412 | 9.1486 | 15.3592 | 27.1592 | 11.9499 | 8.7173 | 13.9907 | 27.5684 | 11.282 | 8.2301 | 11.5898 | 27.8638 | 10.9131 | 7.961 | 9.5263 | 28.1095 | 10.4227 | 7.6032 | 7.213 | 28.2614 | 9.8904 | 7.2149 | 5.1044 | 25.9159 | 14.4455 | 10.5378 | 18.7902 | 25.8878 | 14.1731 | 10.3391 | 17.771 | 25.9108 | 14.0306 | 10.2351 | 17.5472 | 25.9424 | 13.9002 | 10.14 | 17.519 | 25.9996 | 13.7105 | 10.0016 | 17.3175 | 26.0875 | 13.5115 | 9.8565 | 17.0861 | 26.193 | 12.9338 | 9.435 | 16.7192 | 26.3315 | 12.5262 | 9.1377 | 15.8667 | 26.4555 | 12.0943 | 8.8226 | 14.9873 | 26.5795 | 11.7505 | 8.5718 | 14.1191 | 26.96 | 11.1943 | 8.1661 | 11.6712 | 27.3407 | 10.7011 | 7.8063 | 9.3148 | 27.6084 | 10.1512 | 7.4052 | 7.3574 | 27.7993 | 9.6748 | 7.0577 | 5.9952 | 27.8102 | 9.6052 | 7.0069 | 6.4973 | 25.912 | 14.4455 | 10.5378 | 18.7902 | 25.947 | 14.2204 | 10.3736 | 17.8685 | 25.9871 | 14.0775 | 10.2694 | 17.6613 | 26.0252 | 13.9616 | 10.1848 | 17.6466 | 26.0781 | 13.7514 | 10.0315 | 17.5371 | 26.168 | 13.5758 | 9.9034 | 17.3922 | 26.2705 | 13.3764 | 9.7579 | 17.2142 | 26.3844 | 13.201 | 9.6299 | 17.0017 | 26.4811 | 13.017 | 9.4957 | 16.7131 | 26.5789 | 12.9129 | 9.4198 | 16.4272 | 26.8987 | 12.4796 | 9.1037 | 15.5452 | 27.2319 | 12.0841 | 8.8152 | 14.6132 | 27.4709 | 12.0538 | 8.7931 | 13.9538 | 27.6727 | 11.9961 | 8.751 | 13.3318 | 27.7694 | 11.8244 | 8.6257 | 12.9896 | 25.912 | 14.4455 | 10.5378 | 18.7902 | 25.9029 | 14.0188 | 10.2265 | 17.0127 | 25.9553 | 13.8364 | 10.0935 | 16.5798 | 26.0229 | 13.6919 | 9.9881 | 16.4781 | 26.111 | 13.4911 | 9.8416 | 16.2099 | 26.1961 | 13.2833 | 9.69 | 15.9365 | 26.3013 | 12.7199 | 9.279 | 15.5168 | 26.4555 | 12.2745 | 8.9541 | 14.5906 | 26.5867 | 11.8388 | 8.6362 | 13.6536 | 26.7159 | 11.4773 | 8.3725 | 12.7278 | 27.1019 | 10.8823 | 7.9385 | 10.1048 | 27.4687 | 10.3586 | 7.5564 | 7.6096 | 27.7297 | 9.7801 | 7.1344 | 5.5153 | 27.9053 | 9.2722 | 6.764 | 3.9855 | 27.9203 | 9.1656 | 6.6862 | 4.2915
WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM WEST / STANAH | 353466 | 413290 | 30.0588 | 15.8849 | 11.4168 | 16.0688 | 30.1357 | 15.1986 | 10.9235 | 13.0993 | 30.2459 | 14.8795 | 10.6942 | 12.4049 | 30.3839 | 14.6377 | 10.5204 | 12.2159 | 30.5613 | 14.2967 | 10.2753 | 11.936 | 30.7606 | 13.9298 | 10.0116 | 11.6147 | 30.9808 | 13.575 | 9.7566 | 11.3334 | 31.242 | 13.2116 | 9.4954 | 11.0624 | 31.455 | 12.8199 | 9.2139 | 10.7046 | 31.6572 | 12.5328 | 9.0076 | 10.3841 | 32.3666 | 11.2468 | 8.0833 | 8.734 | 32.9988 | 9.7342 | 6.9962 | 6.119 | 33.4063 | 8.5028 | 6.1111 | 4.0363 | 33.7618 | 7.376 | 5.3013 | 1.9841 | 34.0169 | 6.4097 | 4.6068 | 0.1773 | 30.012 | 15.8849 | 11.4168 | 16.0688 | 30.0869 | 15.6945 | 11.28 | 15.5013 | 30.1591 | 15.533 | 11.1639 | 15.2352 | 30.2479 | 15.3463 | 11.0297 | 15.0236 | 30.3646 | 15.1282 | 10.8729 | 14.76 | 30.4991 | 14.8906 | 10.7022 | 14.4722 | 30.6627 | 14.5254 | 10.4397 | 14.1144 | 30.8579 | 14.2347 | 10.2308 | 13.6327 | 30.9858 | 13.97 | 10.0405 | 13.1819 | 31.1174 | 13.6927 | 9.8412 | 12.7286 | 31.5207 | 12.8013 | 9.2006 | 11.4018 | 31.9152 | 11.9301 | 8.5744 | 10.1477 | 32.2748 | 11.0478 | 7.9403 | 9.0214 | 32.6618 | 10.1792 | 7.316 | 7.7803 | 32.9505 | 9.4458 | 6.7889 | 6.9069 | 30.0667 | 15.8849 | 11.4168 | 16.0688 | 30.1505 | 15.0709 | 10.8317 | 12.6563 | 30.2717 | 14.6169 | 10.5055 | 11.6717 | 30.4263 | 14.2598 | 10.2488 | 11.2973 | 30.6242 | 13.8503 | 9.9545 | 10.868 | 30.8482 | 13.4255 | 9.6492 | 10.4017 | 31.0986 | 12.9888 | 9.3353 | 9.9887 | 31.3964 | 12.6709 | 9.1068 | 9.8415 | 31.6299 | 12.3579 | 8.8819 | 9.6196 | 31.8504 | 12.0096 | 8.6315 | 9.4122 | 32.5877 | 10.568 | 7.5954 | 8.104 | 33.1743 | 8.8287 | 6.3454 | 5.8044 | 33.5953 | 7.3754 | 5.3008 | 3.9913 | 33.9457 | 6.0547 | 4.3516 | 2.2423 | 30.4215 | 5.0087 | 3.5998 | 0.76244 | 30.0667 | 15.8849 | 11.4168 | 16.0688 | 30.0636 | 15.3459 | 11.0294 | 13.8311 | 30.1228 | 15.0234 | 10.7976 | 13.1035 | 30.2134 | 14.6993 | 10.5647 | 12.7684 | 30.3484 | 14.3271 | 10.2972 | 12.3397 | 30.5432 | 13.9478 | 10.0246 | 11.893 | 30.7954 | 13.4884 | 9.6944 | 11.318 | 31.1332 | 12.8979 | 9.27 | 10.5914 | 31.4237 | 12.407 | 8.9171 | 9.7957 | 31.7074 | 11.85 | 8.5168 | 9.009 | 32.287 | 10.1542 | 7.298 | 6.7588 | 32.8475 | 8.4903 | 6.1022 | 4.5593 | 33.2435 | 7.1841 | 5.1633 | 2.9178 | 33.5376 | 6.369 | 4.5775 | 1.9344 | 33.5835 | 5.8883 | 4.2321 | 2.657 | 30.0588 | 15.8849 | 11.4168 | 16.0688 | 30.1231 | 15.5909 | 11.2055 | 15.1316 | 30.2023 | 15.3564 | 11.037 | 14.8329 | 30.2927 | 15.1441 | 10.8843 | 14.7096 | 30.4103 | 14.8528 | 10.675 | 14.554 | 30.576 | 14.5309 | 10.4436 | 14.3432 | 30.7865 | 14.2064 | 10.2104 | 14.0962 | 31.0301 | 13.8664 | 9.9661 | 13.7942 | 31.2402 | 13.4867 | 9.6932 | 13.3616 | 31.451 | 13.2181 | 9.5001 | 12.9311 | 32.1274 | 12.1515 | 8.7335 | 11.5146 | 32.7777 | 11.0918 | 7.9719 | 9.9435 | 33.1583 | 10.2395 | 7.3594 | 8.828 | 33.4901 | 9.5302 | 6.8496 | 7.626 | 33.6437 | 9.1006 | 6.5408 | 7.1513 | 30.0588 | 15.8849 | 11.4168 | 16.0688 | 30.0872 | 15.0425 | 10.8113 | 12.3376 | 30.1929 | 14.6383 | 10.5208 | 11.2544 | 30.3392 | 14.2809 | 10.264 | 10.7978 | 30.5203 | 13.8817 | 9.9771 | 10.2536 | 30.7194 | 13.4836 | 9.6909 | 9.6856 | 30.9625 | 13.018 | 9.3563 | 9.0155 | 31.3224 | 12.3996 | 8.9118 | 8.1434 | 31.6308 | 11.9041 | 8.5557 | 7.2321 | 31.9284 | 11.3484 | 8.1563 | 6.3342 | 32.5485 | 9.5964 | 6.8971 | 3.7701 | 33.0792 | 7.7921 | 5.6003 | 1.3169 | 33.4538 | 6.3567 | 4.5687 | -0.54422 | 32.9593 | 5.4265 | 3.9001 | -1.7631 | 29.6941 | 4.8889 | 3.5138 | -1.2937
YEALAND | KENDAL (PARKSIDE RD) | HARKER / HUTTON | 351537 | 475934 | 12.6429 | 12.6429 | 12.6429 | 8.6231 | 12.6726 | 12.6726 | 12.6726 | 7.1348 | 12.7268 | 12.7268 | 12.7268 | 6.8218 | 12.8054 | 12.8054 | 12.8054 | 6.7582 | 12.9144 | 12.9144 | 12.9144 | 6.6653 | 13.063 | 13.063 | 13.063 | 6.5511 | 13.2633 | 13.2633 | 13.2633 | 6.3743 | 13.4939 | 13.4939 | 13.4939 | 6.1264 | 13.7288 | 13.7288 | 13.7288 | 5.7074 | 13.9853 | 13.9853 | 13.9853 | 5.1633 | 14.6598 | 14.6598 | 14.6598 | 3.3102 | 15.257 | 15.257 | 15.257 | 1.6243 | 15.6372 | 15.6372 | 15.6372 | 0.53845 | 15.9005 | 15.9005 | 15.9005 | -0.22991 | 16.0551 | 16.0551 | 16.0551 | -0.71325 | 12.6302 | 12.6302 | 12.6302 | 8.6231 | 12.6586 | 12.6586 | 12.6586 | 7.9807 | 12.6935 | 12.6935 | 12.6935 | 7.8161 | 12.7387 | 12.7387 | 12.7387 | 7.7538 | 12.7998 | 12.7998 | 12.7998 | 7.6778 | 12.8797 | 12.8797 | 12.8797 | 7.5895 | 12.9797 | 12.9797 | 12.9797 | 7.4794 | 13.1019 | 13.1019 | 13.1019 | 7.3476 | 13.2097 | 13.2097 | 13.2097 | 7.2105 | 13.3388 | 13.3388 | 13.3388 | 7.0599 | 13.8147 | 13.8147 | 13.8147 | 6.2531 | 14.358 | 14.358 | 14.358 | 5.0245 | 14.8238 | 14.8238 | 14.8238 | 3.7296 | 15.3219 | 15.3219 | 15.3219 | 2.3216 | 15.6416 | 15.6416 | 15.6416 | 1.4082 | 12.6463 | 12.6463 | 12.6463 | 8.6231 | 12.6778 | 12.6778 | 12.6778 | 6.9011 | 12.7349 | 12.7349 | 12.7349 | 6.555 | 12.8154 | 12.8154 | 12.8154 | 6.5087 | 12.9237 | 12.9237 | 12.9237 | 6.4364 | 13.0663 | 13.0663 | 13.0663 | 6.3275 | 13.2528 | 13.2528 | 13.2528 | 6.166 | 13.435 | 13.435 | 13.435 | 5.9618 | 13.6313 | 13.6313 | 13.6313 | 5.7132 | 13.8585 | 13.8585 | 13.8585 | 5.2956 | 14.5228 | 14.5228 | 14.5228 | 3.5241 | 15.1888 | 15.1888 | 15.1888 | 1.6535 | 15.6209 | 15.6209 | 15.6209 | 0.36327 | 15.8975 | 15.8975 | 15.8975 | -0.49916 | 16.0343 | 16.0343 | 16.0343 | -0.93962 | 12.6463 | 12.6463 | 12.6463 | 8.6231 | 12.6568 | 12.6568 | 12.6568 | 7.4377 | 12.6931 | 12.6931 | 12.6931 | 7.1968 | 12.7513 | 12.7513 | 12.7513 | 7.1575 | 12.8429 | 12.8429 | 12.8429 | 7.0882 | 12.9892 | 12.9892 | 12.9892 | 6.9524 | 13.1935 | 13.1935 | 13.1935 | 6.7358 | 13.4378 | 13.4378 | 13.4378 | 6.3843 | 13.6704 | 13.6704 | 13.6704 | 5.857 | 13.9328 | 13.9328 | 13.9328 | 5.2233 | 14.6829 | 14.6829 | 14.6829 | 3.2437 | 15.261 | 15.261 | 15.261 | 1.6122 | 15.5948 | 15.5948 | 15.5948 | 0.59191 | 15.7963 | 15.7963 | 15.7963 | 0.016594 | 15.8218 | 15.8218 | 15.8218 | 0.0027058 | 12.6429 | 12.6429 | 12.6429 | 8.6231 | 12.6677 | 12.6677 | 12.6677 | 7.396 | 12.7079 | 12.7079 | 12.7079 | 7.1412 | 12.7623 | 12.7623 | 12.7623 | 7.1004 | 12.841 | 12.841 | 12.841 | 7.0488 | 12.964 | 12.964 | 12.964 | 6.9733 | 13.1361 | 13.1361 | 13.1361 | 6.8379 | 13.3525 | 13.3525 | 13.3525 | 6.6343 | 13.5409 | 13.5409 | 13.5409 | 6.3649 | 13.7528 | 13.7528 | 13.7528 | 5.9166 | 14.4026 | 14.4026 | 14.4026 | 4.3037 | 14.9825 | 14.9825 | 14.9825 | 2.7525 | 15.3717 | 15.3717 | 15.3717 | 1.7214 | 15.6165 | 15.6165 | 15.6165 | 1.069 | 15.6937 | 15.6937 | 15.6937 | 0.86391 | 12.6429 | 12.6429 | 12.6429 | 8.6231 | 12.6633 | 12.6633 | 12.6633 | 6.6952 | 12.7142 | 12.7142 | 12.7142 | 6.3034 | 12.7872 | 12.7872 | 12.7872 | 6.2372 | 12.8858 | 12.8858 | 12.8858 | 6.1471 | 13.016 | 13.016 | 13.016 | 6.0439 | 13.1886 | 13.1886 | 13.1886 | 5.873 | 13.3972 | 13.3972 | 13.3972 | 5.5418 | 13.5928 | 13.5928 | 13.5928 | 5.1657 | 13.8198 | 13.8198 | 13.8198 | 4.7107 | 14.6271 | 14.6271 | 14.6271 | 2.753 | 15.2896 | 15.2896 | 15.2896 | 0.89321 | 15.7279 | 15.7279 | 15.7279 | -0.37842 | 15.9655 | 15.9655 | 15.9655 | -1.1106 | 16.003 | 16.003 | 16.003 | -1.1753

## Gen BSP Headroom
Click the scenario name to move directly to the associated results | Best View
Counterfactual
Electric Engagement
Holistic Transition
Hydrogen Evolution
Accelerated Decarbonisation
|  |  |  | Best View | [44 empty] | Counterfactual | [44 empty] | Electric Engagement | [44 empty] | Holistic Transition | [44 empty] | Hydrogen Evolution | [44 empty] | Accelerated Decarbonisation
BSP Headroom |  |  |  | 2024 |  |  | 2025 |  |  | 2026 |  |  | 2027 |  |  | 2028 |  |  | 2029 |  |  | 2030 |  |  | 2031 |  |  | 2032 |  |  | 2033 |  |  | 2036 |  |  | 2039 |  |  | 2042 |  |  | 2046 |  |  | 2051 |  |  | 2024 |  |  | 2025 |  |  | 2026 |  |  | 2027 |  |  | 2028 |  |  | 2029 |  |  | 2030 |  |  | 2031 |  |  | 2032 |  |  | 2033 |  |  | 2036 |  |  | 2039 |  |  | 2042 |  |  | 2046 |  |  | 2051 |  |  | 2024 |  |  | 2025 |  |  | 2026 |  |  | 2027 |  |  | 2028 |  |  | 2029 |  |  | 2030 |  |  | 2031 |  |  | 2032 |  |  | 2033 |  |  | 2036 |  |  | 2039 |  |  | 2042 |  |  | 2046 |  |  | 2051 |  |  | 2024 |  |  | 2025 |  |  | 2026 |  |  | 2027 |  |  | 2028 |  |  | 2029 |  |  | 2030 |  |  | 2031 |  |  | 2032 |  |  | 2033 |  |  | 2036 |  |  | 2039 |  |  | 2042 |  |  | 2046 |  |  | 2051 |  |  | 2024 |  |  | 2025 |  |  | 2026 |  |  | 2027 |  |  | 2028 |  |  | 2029 |  |  | 2030 |  |  | 2031 |  |  | 2032 |  |  | 2033 |  |  | 2036 |  |  | 2039 |  |  | 2042 |  |  | 2046 |  |  | 2051 |  |  | 2024 |  |  | 2025 |  |  | 2026 |  |  | 2027 |  |  | 2028 |  |  | 2029 |  |  | 2030 |  |  | 2031 |  |  | 2032 |  |  | 2033 |  |  | 2036 |  |  | 2039 |  |  | 2042 |  |  | 2046 |  |  | 2051
BSP | GSP Group | BSP Coordinates |  | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW) | Generation Headroom (MW) |  | Battery Headroom (MW)
| GSP Group | Easting | Northing | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Inverter Based (PV, Wind etc.) | Synchronous (Gas, Diesel etc.) |  | Comments (Based on Best View Headroom)
ADSWOOD | BREDBURY | 389188 | 388310 | 141.8535 | 53.7394 | 85.4473 | 142.1713 | 51.8802 | 79.6324 | 142.5595 | 50.5709 | 77.4393 | 142.9862 | 49.3674 | 75.8297 | 143.5085 | 48.0621 | 73.5188 | 144.1129 | 45.5006 | 71.0236 | 144.8147 | 43.2441 | 69.3419 | 145.6451 | 41.4504 | 67.6735 | 146.4254 | 39.5513 | 65.5879 | 147.2012 | 37.6772 | 63.7481 | 149.8825 | 34.8715 | 56.2972 | 151.9855 | 31.7138 | 45.9781 | 153.4687 | 29.053 | 38.0403 | 145.5425 | 26.4037 | 30.397 | 132.2656 | 23.9951 | 24.9457 | 141.7356 | 53.7394 | 85.4473 | 142.0639 | 52.7665 | 83.0586 | 142.355 | 51.4717 | 82.0806 | 142.6666 | 50.3942 | 81.0257 | 143.0523 | 49.1839 | 79.8101 | 143.517 | 47.7892 | 78.5294 | 144.0912 | 41.5849 | 77.0135 | 144.7728 | 40.9794 | 75.2573 | 145.2216 | 40.4454 | 73.6912 | 145.7054 | 40.1148 | 72.0895 | 147.3677 | 39.5224 | 68.3733 | 149.1932 | 40.9057 | 64.122 | 150.8067 | 41.1053 | 60.1652 | 152.3616 | 40.1314 | 56.1368 | 153.4751 | 39.0143 | 53.3914 | 141.8753 | 53.7394 | 85.4473 | 142.2143 | 51.5839 | 78.8028 | 142.6481 | 50.1524 | 76.2903 | 143.1338 | 48.7663 | 74.5331 | 143.716 | 47.2869 | 72.0553 | 144.3802 | 44.5653 | 69.4765 | 145.1434 | 42.1467 | 67.6526 | 146.0422 | 40.1535 | 65.65 | 146.8327 | 38.1238 | 63.4687 | 147.6319 | 36.113 | 61.396 | 150.3194 | 32.9661 | 53.2647 | 152.566 | 29.4936 | 43.1384 | 146.5494 | 26.5864 | 35.8698 | 131.4322 | 23.8439 | 29.7665 | 117.9763 | 21.4028 | 26.7545 | 141.8755 | 53.7394 | 85.4473 | 141.9169 | 52.0051 | 81.1305 | 142.1836 | 51.0963 | 79.2037 | 142.5073 | 49.9463 | 77.5842 | 142.959 | 48.8572 | 75.1422 | 143.5848 | 47.4999 | 72.4479 | 144.419 | 46.3791 | 69.9547 | 145.4787 | 45.1597 | 65.6181 | 146.3009 | 43.971 | 61.1671 | 147.1314 | 42.446 | 56.9336 | 149.6552 | 38.2953 | 46.4017 | 151.7819 | 34.5655 | 37.8215 | 153.0575 | 31.4539 | 32.4092 | 153.8324 | 28.5916 | 30.0922 | 146.7501 | 26.6228 | 32.3614 | 141.8528 | 53.7394 | 85.4473 | 142.1117 | 52.4751 | 82.2434 | 142.3965 | 51.3117 | 80.7384 | 142.6647 | 50.1796 | 79.4187 | 142.9905 | 48.9817 | 77.5768 | 143.4536 | 46.5133 | 75.5495 | 144.0496 | 44.3242 | 74.127 | 144.7206 | 42.5705 | 72.6472 | 145.3647 | 40.6884 | 70.6543 | 146.0382 | 38.8111 | 68.8201 | 148.2983 | 36.4941 | 63.8189 | 150.592 | 34.394 | 58.8267 | 151.9656 | 32.498 | 55.3798 | 153.0585 | 30.7755 | 51.9434 | 153.546 | 29.1021 | 49.9598 | 141.8528 | 53.7394 | 85.4473 | 141.9652 | 51.4866 | 78.899 | 142.3468 | 50.4043 | 76.2516 | 142.8032 | 49.1588 | 74.2849 | 143.3568 | 47.9917 | 71.5369 | 143.9746 | 46.5807 | 68.6102 | 144.7572 | 45.4121 | 65.9035 | 145.9334 | 44.1304 | 61.2461 | 146.7579 | 42.8957 | 56.5752 | 147.5711 | 41.3317 | 52.1106 | 150.1294 | 37.1656 | 40.7646 | 152.3626 | 33.3748 | 31.4026 | 153.7331 | 30.1166 | 25.2348 | 149.5651 | 27.1335 | 22.0663 | 138.1481 | 25.0623 | 24.1119
AGECROFT | KEARSLEY | 380345 | 401831 | 90.209 | 28.0058 | 27.0099 | 90.5004 | 22.9133 | 24.5195 | 81.1801 | 14.7274 | 22.9053 | 36.5295 | 6.627 | 21.603 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 2.0354 | 10.6707 | 1.9358 | -10.5208 | 10.6707 | 1.9358 | -19.8263 | 29.7095 | 5.3898 | -28.4177 | 38.2661 | 6.9421 | -34.6845 | 90.1377 | 28.0058 | 27.0099 | 90.4538 | 23.5439 | 25.8461 | 85.7227 | 15.5515 | 24.8466 | 42.0098 | 7.6212 | 23.9299 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.617 | 10.6707 | 1.9358 | 5.7965 | 10.6707 | 1.9358 | 1.2963 | 10.6707 | 1.9358 | -3.4232 | 10.6707 | 1.9358 | -6.7017 | 90.2331 | 28.0058 | 27.0099 | 90.5791 | 22.702 | 24.073 | 78.8607 | 14.3066 | 22.1575 | 33.6668 | 6.1077 | 20.6374 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 9.6181 | 10.6707 | 1.9358 | 7.4555 | 10.6707 | 1.9358 | -2.3011 | 10.6707 | 1.9358 | -14.843 | 10.6707 | 1.9358 | -23.3626 | 15.3203 | 2.7793 | -30.1309 | 24.9006 | 4.5174 | -33.0971 | 90.2331 | 28.0058 | 27.0099 | 90.204 | 23.2009 | 25.7614 | 90.439 | 18.6246 | 24.3179 | 76.2671 | 13.8361 | 22.8676 | 48.649 | 8.8257 | 21.0661 | 20.8782 | 3.7876 | 18.7466 | 9.51 | 1.7253 | 9.51 | 3.0356 | 0.5507 | 3.0356 | 10.6707 | 1.9358 | 5.7184 | 10.6707 | 1.9358 | 1.0036 | 44.6744 | 8.1047 | -11.7389 | 21.236 | 3.8526 | -22.1557 | 2.105 | 0.38188 | -28.4832 | 10.6707 | 1.9358 | -31.0069 | 10.6707 | 1.9358 | -27.6996 | 90.209 | 28.0058 | 27.0099 | 90.4633 | 23.2149 | 25.2485 | 83.4039 | 15.1308 | 23.9495 | 39.2169 | 7.1146 | 22.974 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 8.2966 | 10.6707 | 1.9358 | 2.3964 | 10.6707 | 1.9358 | -1.8414 | 58.4965 | 10.6122 | -5.573 | 72.163 | 13.0915 | -7.5439 | 90.209 | 28.0058 | 27.0099 | 90.2958 | 22.8507 | 24.8506 | 90.6952 | 18.1091 | 22.9048 | 73.0403 | 13.2507 | 21.0432 | 44.9698 | 8.1582 | 18.8772 | 16.6424 | 3.0192 | 16.3276 | 5.1617 | 0.93641 | 5.1617 | 10.6707 | 1.9358 | 7.7291 | 10.6707 | 1.9358 | 2.3954 | 10.6707 | 1.9358 | -2.5694 | 38.6656 | 7.0146 | -16.2124 | 14.4505 | 2.6215 | -27.5319 | 10.6707 | 1.9358 | -34.758 | 10.6707 | 1.9358 | -38.1415 | 10.6707 | 1.9358 | -35.4805
ALTRINCHAM | CARRINGTON | 376380 | 389012 | 150.7162 | 49.9637 | 78.8777 | 151.0668 | 48.9455 | 74.6142 | 151.6222 | 48.3265 | 73.1285 | 152.2153 | 47.8715 | 72.41 | 152.8944 | 47.2683 | 71.3982 | 153.6689 | 46.7595 | 70.3291 | 154.5155 | 46.2277 | 69.3206 | 155.4127 | 45.756 | 68.3634 | 156.1723 | 45.2732 | 67.2398 | 156.9014 | 44.7607 | 66.2083 | 159.2147 | 42.5419 | 59.2425 | 161.2632 | 39.6813 | 47.3666 | 162.7351 | 37.289 | 37.7814 | 164.0167 | 35.0589 | 27.792 | 164.8464 | 32.7172 | 19.4368 | 150.5598 | 49.9637 | 78.8777 | 150.8613 | 49.6375 | 77.4111 | 151.2562 | 49.2599 | 76.4975 | 151.7159 | 48.8274 | 75.6941 | 152.2945 | 48.3614 | 74.6801 | 152.9929 | 47.8497 | 73.597 | 153.8054 | 42.3743 | 72.2157 | 154.6287 | 41.87 | 70.4661 | 155.1231 | 41.4304 | 69.2004 | 155.6416 | 41.2331 | 67.9057 | 157.1921 | 40.6945 | 63.9752 | 158.6928 | 41.9934 | 59.9357 | 160.0594 | 42.3719 | 56.1105 | 161.4901 | 41.9154 | 51.6953 | 162.5721 | 41.2625 | 48.4358 | 150.7768 | 49.9637 | 78.8777 | 151.1944 | 48.7617 | 73.9922 | 151.8186 | 48.0087 | 72.3523 | 152.5272 | 47.366 | 71.6556 | 153.3419 | 46.7015 | 70.5143 | 154.2597 | 46.0903 | 69.329 | 155.1342 | 45.4494 | 67.8659 | 156.1824 | 44.8066 | 66.4492 | 156.8875 | 44.1203 | 64.9447 | 157.5633 | 43.3978 | 63.3277 | 160.0897 | 40.71 | 55.8049 | 162.3129 | 37.7493 | 44.8375 | 163.8783 | 35.246 | 36.3281 | 165.1536 | 32.7453 | 27.9763 | 165.8382 | 30.3351 | 21.883 | 150.7768 | 49.9637 | 78.8777 | 150.7688 | 49.151 | 76.4268 | 151.093 | 48.6253 | 75.4332 | 151.4515 | 48.1461 | 74.9487 | 151.9517 | 47.3518 | 73.9011 | 152.7239 | 46.6968 | 72.7074 | 153.6987 | 45.7662 | 70.5423 | 154.6666 | 44.4451 | 66.3 | 155.4863 | 43.149 | 61.9128 | 156.2995 | 41.809 | 57.5573 | 158.7728 | 38.4326 | 45.7889 | 160.8424 | 35.0542 | 35.7805 | 162.2557 | 32.1082 | 28.4677 | 163.2984 | 29.8578 | 24.1818 | 154.9697 | 28.114 | 27.3699 | 150.7162 | 49.9637 | 78.8777 | 151.0085 | 49.3768 | 76.7843 | 151.4215 | 48.8823 | 75.9013 | 151.7974 | 48.4886 | 75.4748 | 152.2526 | 47.98 | 74.9539 | 152.9452 | 47.5595 | 74.3144 | 153.8434 | 47.0632 | 73.5935 | 154.7062 | 46.626 | 72.8188 | 155.3721 | 46.1579 | 71.7367 | 156.0015 | 45.6452 | 70.6617 | 157.8998 | 43.9844 | 66.9721 | 159.8928 | 42.4216 | 62.1777 | 161.3359 | 41.1209 | 58.4779 | 162.6454 | 39.9879 | 54.9419 | 163.2729 | 38.6163 | 52.6908 | 150.7162 | 49.9637 | 78.8777 | 150.8856 | 48.7376 | 74.3416 | 151.4281 | 48.072 | 72.5982 | 152.0418 | 47.493 | 71.6887 | 152.7511 | 46.6362 | 70.2565 | 153.5465 | 45.929 | 68.7939 | 154.4195 | 44.9641 | 66.2962 | 155.4586 | 43.5877 | 61.6137 | 156.3144 | 42.2631 | 56.9519 | 157.1503 | 40.88 | 52.3205 | 159.6161 | 37.3796 | 39.688 | 161.6032 | 33.8869 | 28.9417 | 162.9777 | 30.8363 | 20.9033 | 157.0555 | 28.4924 | 15.6739 | 146.9301 | 26.6555 | 17.6835
ATHERTON | KEARSLEY | 366150 | 402088 | 125.2258 | 29.3588 | 26.9483 | 125.6664 | 26.5176 | 21.0293 | 126.3961 | 24.065 | 18.8952 | 120.1686 | 21.8005 | 17.7362 | 106.1375 | 19.255 | 15.5628 | 92.0544 | 16.7001 | 13.2877 | 85.8949 | 15.5827 | 11.0993 | 81.4342 | 14.7735 | 9.0015 | 76.6848 | 13.9118 | 6.5302 | 71.9959 | 13.0612 | 4.1718 | 52.8607 | 9.5898 | -9.1077 | 28.8382 | 5.2317 | -30.3801 | 7.7218 | 1.4009 | -48.2081 | 10.6707 | 1.9358 | -65.6457 | 10.6707 | 1.9358 | -80.2112 | 125.1245 | 29.3588 | 26.9483 | 125.4894 | 27.3054 | 24.6617 | 125.9976 | 25.3575 | 23.4823 | 126.5187 | 23.3518 | 22.536 | 117.0604 | 21.2366 | 21.2462 | 105.0995 | 19.0667 | 19.7711 | 70.089 | 12.7153 | 17.8101 | 65.5059 | 11.8838 | 15.2292 | 61.7179 | 11.1966 | 13.0261 | 58.8144 | 10.6699 | 10.7652 | 51.2052 | 9.2894 | 3.7992 | 55.6651 | 10.0985 | -3.4432 | 55.0601 | 9.9888 | -10.4389 | 56.0178 | 10.1625 | -18.1008 | 56.1235 | 10.1817 | -23.0175 | 125.2686 | 29.3588 | 26.9483 | 125.7753 | 26.266 | 20.1963 | 126.602 | 23.6361 | 17.8773 | 116.7146 | 21.1739 | 16.7893 | 101.2763 | 18.3731 | 13.8822 | 85.6002 | 15.5292 | 10.9179 | 77.7396 | 14.1032 | 8.0654 | 71.7628 | 13.0189 | 5.3299 | 65.6345 | 11.9072 | 2.3218 | 59.5348 | 10.8006 | -0.53669 | 36.816 | 6.679 | -13.8866 | 10.6053 | 1.924 | -34.0995 | 10.6707 | 1.9358 | -50.5528 | 10.6707 | 1.9358 | -65.8924 | 10.6707 | 1.9358 | -77.5268 | 125.2687 | 29.3588 | 26.9483 | 125.188 | 26.9845 | 23.7221 | 125.6191 | 24.816 | 22.3315 | 123.9988 | 22.4954 | 21.5192 | 108.8802 | 19.7526 | 18.6941 | 93.0649 | 16.8835 | 15.6084 | 83.7818 | 15.1993 | 11.3581 | 72.4921 | 13.1512 | 3.3868 | 61.6958 | 11.1926 | -4.8566 | 49.6277 | 9.0032 | -12.8859 | 21.7224 | 3.9408 | -34.6323 | 10.6707 | 1.9358 | -53.085 | 10.6707 | 1.9358 | -66.926 | 10.6707 | 1.9358 | -75.0097 | 10.6707 | 1.9358 | -69.4142 | 125.2257 | 29.3588 | 26.9483 | 125.5952 | 27.0315 | 23.4482 | 126.1254 | 24.7471 | 22.0724 | 124.4916 | 22.5848 | 21.4643 | 111.5785 | 20.2421 | 20.3215 | 98.4283 | 17.8565 | 18.9257 | 92.8173 | 16.8385 | 17.2631 | 88.6724 | 16.0866 | 15.4549 | 84.1281 | 15.2622 | 13.0316 | 79.4948 | 14.4216 | 10.5796 | 65.2633 | 11.8398 | 2.8798 | 52.4474 | 9.5148 | -6.2438 | 41.0276 | 7.4431 | -13.5646 | 38.5589 | 6.9952 | -19.4624 | 25.3764 | 4.6037 | -22.5717 | 125.2257 | 29.3588 | 26.9483 | 125.3121 | 26.4052 | 20.901 | 126.01 | 24.0193 | 18.4276 | 118.9101 | 21.5722 | 16.9442 | 103.2084 | 18.7236 | 13.5147 | 87.009 | 15.7848 | 10.0393 | 77.4061 | 14.0427 | 5.3202 | 65.6285 | 11.9061 | -3.3044 | 54.4612 | 9.8801 | -12.0101 | 41.9253 | 7.6059 | -20.5051 | 12.3363 | 2.238 | -43.8086 | 10.6707 | 1.9358 | -63.7547 | 10.6707 | 1.9358 | -79.0743 | 10.6707 | 1.9358 | -88.8771 | 10.6707 | 1.9358 | -85.1693
BARROW & SANDGATE | HARKER / HUTTON | 319709 | 470489 | 159.1463 | 29.9465 | 92.2962 | 159.4913 | 29.351 | 90.5277 | 154.918 | 28.1046 | 88.9006 | 148.88 | 27.0092 | 72.5647 | 140.9802 | 25.576 | 55.8205 | 132.8113 | 24.0941 | 53.3535 | 125.2075 | 22.7146 | 48.804 | 120.3127 | 21.8266 | 47.2399 | 116.1256 | 21.067 | 45.7341 | 111.5374 | 20.2347 | 44.2803 | 95.2024 | 17.2712 | 36.7614 | 76.0112 | 13.7896 | 15.9642 | 57.4518 | 10.4227 | 8.4793 | 42.9966 | 7.8003 | 2.8176 | 30.9601 | 5.6167 | -1.5646 | 159.0783 | 29.9465 | 92.2962 | 146.9277 | 26.655 | 91.3945 | 128.0077 | 23.2226 | 90.3224 | 108.991 | 19.7727 | 74.3192 | 89.3127 | 16.2027 | 58.2295 | 69.4179 | 12.5935 | 57.4745 | 34.1057 | 6.1873 | 34.1057 | 30.6224 | 5.5554 | 30.6224 | 27.8711 | 5.0563 | 27.8711 | 26.2387 | 4.7601 | 26.2387 | 22.5724 | 4.095 | 22.5724 | 30.744 | 5.5775 | 30.744 | 31.2325 | 5.6661 | 31.2325 | 28.2569 | 5.1263 | 28.2569 | 18.0921 | 3.2822 | 18.0921 | 159.1747 | 29.9465 | 92.2962 | 159.5257 | 29.2321 | 90.3619 | 153.2978 | 27.8107 | 88.7717 | 146.2002 | 26.523 | 72.4835 | 137.6729 | 24.9761 | 55.8806 | 129.7005 | 23.5297 | 53.593 | 122.0907 | 22.1492 | 49.199 | 116.7318 | 21.177 | 47.8366 | 111.1881 | 20.1713 | 46.5738 | 106.668 | 19.3513 | 45.3633 | 78.6363 | 14.2659 | 26.1133 | 57.9068 | 10.5052 | 7.725 | 38.3916 | 6.9648 | 1.4258 | 31.0367 | 5.6305 | -3.0038 | 17.5433 | 3.1826 | -5.6007 | 159.175 | 29.9465 | 92.2962 | 159.213 | 29.3496 | 91.8745 | 153.7295 | 27.889 | 90.0722 | 146.0569 | 26.497 | 74.0249 | 129.7954 | 23.5469 | 48.7745 | 119.2739 | 21.6382 | 46.8302 | 81.7374 | 14.8285 | 42.2158 | 52.2558 | 9.48 | 39.0992 | 24.6969 | 4.4804 | 22.8229 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 3.7952 | 10.6707 | 1.9358 | -1.7906 | 10.6707 | 1.9358 | -3.7485 | 10.6707 | 1.9358 | 2.3819 | 159.1461 | 29.9465 | 92.2962 | 159.4221 | 29.4654 | 91.0517 | 155.9293 | 28.2881 | 89.6102 | 149.9872 | 27.2101 | 73.4767 | 142.6054 | 25.8709 | 57.1842 | 134.8376 | 24.4617 | 55.2761 | 127.3769 | 23.1082 | 50.9261 | 122.6129 | 22.2439 | 49.5289 | 118.2216 | 21.4473 | 48.1314 | 113.5553 | 20.6007 | 46.6931 | 99.6288 | 18.0742 | 41.5045 | 87.0162 | 15.7861 | 26.1855 | 73.8572 | 13.3989 | 23.542 | 71.083 | 12.8956 | 23.0895 | 66.0821 | 11.9884 | 24.5257 | 159.1461 | 29.9465 | 92.2962 | 159.2662 | 29.1637 | 90.9236 | 152.1824 | 27.6083 | 88.7345 | 144.3421 | 26.186 | 72.401 | 127.8551 | 23.195 | 46.8848 | 117.2024 | 21.2624 | 44.9498 | 79.6546 | 14.4506 | 40.2605 | 49.1059 | 8.9086 | 36.891 | 21.5904 | 3.9168 | 20.4282 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 8.2022 | 10.6707 | 1.9358 | -0.038721 | 10.6707 | 1.9358 | -6.7372 | 10.6707 | 1.9358 | -9.6319 | 10.6707 | 1.9358 | -3.8663
BARTON | CARRINGTON | 376758 | 397174 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 4.9328 | 1.9358 | 4.9328 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | -17.5818 | 6.7308 | 1.9358 | -27.912 | 6.7308 | 1.9358 | -38.3427 | 6.7308 | 1.9358 | -46.4916 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 6.2358 | 1.9358 | 6.2358 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 7.6777 | 1.9358 | 7.6777 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 2.5729 | 1.0568 | 2.5729 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | -6.8437 | 6.7308 | 1.9358 | -97.9895 | 6.7308 | 1.9358 | -138.1249 | 6.7308 | 1.9358 | -148.1962 | 6.7308 | 1.9358 | -156.7357 | 6.7308 | 1.9358 | -159.6604 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 8.7616 | 1.9358 | 8.7616 | 4.9714 | 1.9358 | 4.9714 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 1.4557 | 6.7308 | 1.9358 | -16.0345 | 6.7308 | 1.9358 | -68.9625 | 6.7308 | 1.9358 | -107.4024 | 6.7308 | 1.9358 | -116.2136 | 6.7308 | 1.9358 | -121.9933 | 6.7308 | 1.9358 | -123.2663 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 8.9327 | 1.9358 | 8.9327 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | -1.085 | 6.7308 | 1.9358 | -7.5956 | 6.7308 | 1.9358 | -14.4416 | 6.7308 | 1.9358 | -19.3476 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 7.2392 | 1.9358 | -0.69095 | 4.1596 | 1.7085 | -23.5162 | 0.24925 | 0.10238 | -27.5386 | 6.7308 | 1.9358 | -57.59 | 6.7308 | 1.9358 | -63.736 | 6.7308 | 1.9358 | -89.0844 | 6.7308 | 1.9358 | -118.2184 | 6.7308 | 1.9358 | -157.8633 | 6.7308 | 1.9358 | -167.9048 | 6.7308 | 1.9358 | -174.6222 | 6.7308 | 1.9358 | -176.6589
BELFIELD | ROCHDALE | 391033 | 413945 | 57.5863 | 34.2327 | 39.8326 | 57.7637 | 33.3101 | 37.4448 | 58.0949 | 32.5178 | 30.4001 | 58.4503 | 30.7569 | 23.8462 | 58.8604 | 28.8777 | 17.1031 | 59.3531 | 27.0046 | 10.3089 | 59.9509 | 25.2093 | 3.7059 | 60.6296 | 23.5565 | -2.8798 | 61.1965 | 23.0636 | -9.6996 | 61.7731 | 22.6007 | -16.4768 | 63.9293 | 20.6467 | -39.6363 | 65.7319 | 18.1118 | -66.4569 | 66.8989 | 15.9401 | -79.717 | 67.8101 | 13.8479 | -87.3612 | 61.7295 | 11.1987 | -93.941 | 57.5393 | 34.2327 | 39.8326 | 57.6995 | 33.8805 | 38.86 | 57.9517 | 33.509 | 38.2514 | 58.1965 | 33.2145 | 37.8206 | 58.4788 | 32.789 | 37.3253 | 58.834 | 32.4282 | 36.7873 | 59.2654 | 28.5153 | 36.0773 | 59.7702 | 28.1427 | 35.1365 | 60.161 | 27.7852 | 34.2359 | 60.5786 | 27.5596 | 33.3177 | 61.9603 | 26.9279 | 30.4767 | 63.4127 | 27.664 | 27.4709 | 64.7557 | 27.6766 | 24.4592 | 66.2127 | 27.4555 | 21.0806 | 67.255 | 26.864 | 18.6029 | 57.6062 | 34.2327 | 39.8326 | 57.8053 | 33.1615 | 37.171 | 58.1679 | 32.2484 | 30.1235 | 58.569 | 30.3674 | 23.4218 | 59.0304 | 28.4031 | 16.527 | 59.5785 | 26.3814 | 9.6002 | 60.2205 | 24.5106 | 2.9881 | 60.793 | 22.8236 | -3.384 | 61.3214 | 22.3307 | -9.881 | 61.8526 | 21.8555 | -16.4047 | 63.9723 | 19.7746 | -38.8498 | 65.8333 | 17.1497 | -65.1247 | 67.0494 | 14.8784 | -77.8888 | 67.8886 | 12.3835 | -84.8515 | 57.7864 | 10.4834 | -90.5609 | 57.6062 | 34.2327 | 39.8326 | 57.5854 | 33.4818 | 38.5653 | 57.7886 | 32.8007 | 31.8609 | 58.0095 | 31.4137 | 25.2267 | 58.3091 | 28.5021 | 18.3309 | 58.7853 | 25.5273 | 11.3452 | 59.423 | 22.4109 | 4.1444 | 60.2289 | 18.9479 | -4.4414 | 60.9948 | 16.6356 | -13.1997 | 61.7241 | 15.4108 | -21.9892 | 63.5059 | 13.2316 | -48.0812 | 60.439 | 10.9646 | -73.8613 | 50.7175 | 9.201 | -85.9791 | 48.1296 | 8.7315 | -89.8538 | 47.5602 | 8.6282 | -87.3987 | 57.5863 | 34.2327 | 39.8326 | 57.7386 | 33.6415 | 38.4144 | 57.9918 | 32.9485 | 31.6504 | 58.2219 | 31.2396 | 25.269 | 58.4907 | 29.4556 | 18.8659 | 58.9109 | 27.663 | 12.3828 | 59.4772 | 25.9232 | 5.9801 | 60.0873 | 24.2995 | -0.48525 | 60.5697 | 23.8167 | -7.2731 | 61.0754 | 23.3503 | -14.0709 | 62.7706 | 21.9173 | -34.8627 | 64.4931 | 20.5656 | -56.0002 | 65.6877 | 19.4148 | -64.1212 | 66.6287 | 18.2545 | -66.0512 | 67.0014 | 17.3074 | -67.0628 | 57.5863 | 34.2327 | 39.8326 | 57.6362 | 33.1229 | 37.4103 | 57.9474 | 32.3062 | 30.3028 | 58.2966 | 30.8693 | 23.4478 | 58.6994 | 27.8963 | 16.3512 | 59.1711 | 24.8838 | 9.2293 | 59.7596 | 21.7382 | 1.863 | 60.5771 | 18.2421 | -6.9396 | 61.3262 | 15.9195 | -15.8336 | 62.077 | 14.6941 | -24.7627 | 63.8501 | 12.3884 | -51.3676 | 55.192 | 10.0127 | -77.6911 | 44.6209 | 8.0949 | -90.3805 | 40.6978 | 7.3832 | -94.9548 | 39.5613 | 7.1771 | -93.2637
BISPHAM | PENWORTHAM WEST / STANAH | 332328 | 439711 | 39.422 | 7.1518 | 39.422 | 34.0036 | 6.1688 | 34.0036 | 30.427 | 5.5199 | 30.427 | 27.3582 | 4.9632 | 27.3582 | 20.8841 | 3.7887 | 20.8841 | 11.6159 | 2.1073 | 11.6159 | 4.137 | 0.75051 | 4.137 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | -1.6444 | 31.0969 | 5.6415 | -16.8602 | 97.9627 | 27.9704 | -31.1345 | 98.9919 | 28.9453 | -43.7523 | 39.422 | 7.1518 | 39.422 | 37.4553 | 6.795 | 37.4553 | 35.8396 | 6.5019 | 35.8396 | 33.888 | 6.1478 | 33.888 | 31.2797 | 5.6746 | 31.2797 | 28.5624 | 5.1817 | 28.5624 | 6.2562 | 1.135 | 6.2562 | 3.0727 | 0.55744 | 3.0727 | 0.79104 | 0.14351 | 0.79104 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 24.381 | 4.4231 | 12.6974 | 86.9306 | 20.2647 | 7.7254 | 88.3602 | 30.7771 | 4.2257 | 39.422 | 7.1518 | 39.422 | 33.0508 | 5.9959 | 33.0508 | 28.5434 | 5.1782 | 28.5434 | 24.722 | 4.485 | 24.722 | 17.734 | 3.2172 | 17.734 | 8.1225 | 1.4735 | 8.1225 | 0.88041 | 0.15972 | 0.88041 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 0.9554 | 23.413 | 4.2475 | -11.2776 | 98.9711 | 26.3004 | -24.4086 | 99.9117 | 27.1921 | -36.1713 | 39.422 | 7.1518 | 39.422 | 35.7199 | 6.4802 | 35.7199 | 32.5596 | 5.9068 | 32.5596 | 28.7396 | 5.2138 | 28.7396 | 23.7073 | 4.3009 | 23.7073 | 21.2615 | 3.8572 | 21.2615 | 17.2276 | 3.1254 | 17.2276 | 22.1768 | 4.0232 | 22.1768 | 24.6398 | 4.4701 | 18.118 | 35.35 | 6.4131 | 12.2465 | 90.4495 | 38.9053 | -2.0869 | 93.2038 | 36.1415 | -15.9879 | 95.0971 | 33.5328 | -27.0506 | 96.4786 | 32.0246 | -34.1822 | 96.5412 | 30.6312 | -29.7199 | 39.422 | 7.1518 | 39.422 | 36.6726 | 6.653 | 36.6726 | 33.7561 | 6.1239 | 33.7561 | 31.0671 | 5.6361 | 31.0671 | 25.1831 | 4.5686 | 25.1831 | 16.3738 | 2.9705 | 16.3738 | 9.2549 | 1.679 | 9.2549 | 3.61 | 0.65492 | 3.61 | 0.25749 | 0.046712 | 0.25749 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 9.0036 | 1.6334 | 9.0036 | 56.4996 | 10.2499 | 13.5999 | 94.5717 | 34.1567 | 9.7343 | 95.5757 | 36.7535 | 7.6855 | 39.422 | 7.1518 | 39.422 | 33.5337 | 6.0836 | 33.5337 | 29.6204 | 5.3736 | 29.6204 | 25.3309 | 4.5954 | 25.3309 | 19.961 | 3.6213 | 19.961 | 17.1553 | 3.1122 | 17.1553 | 12.7377 | 2.3108 | 12.7377 | 17.2464 | 3.1288 | 17.2464 | 19.4524 | 3.529 | 12.4499 | 29.8789 | 5.4205 | 6.1773 | 91.5691 | 37.7345 | -9.4051 | 94.2539 | 34.8797 | -24.392 | 96.1362 | 32.1456 | -36.4714 | 97.4237 | 30.5066 | -44.7263 | 97.5043 | 28.9454 | -41.3602
BLACKBURN | PENWORTHAM EAST / ROCHDALE | 370584 | 429294 | 73.1149 | 54.0735 | 46.4952 | 73.5212 | 52.1117 | 41.1861 | 74.0134 | 48.6283 | 39.0914 | 74.4698 | 45.3572 | 37.8537 | 74.977 | 41.8655 | 36.3301 | 75.5953 | 36.9366 | 34.7467 | 76.3419 | 33.2938 | 33.0726 | 77.2076 | 31.6901 | 31.4985 | 77.9731 | 29.9536 | 29.7274 | 78.7682 | 28.2775 | 27.9449 | 81.3631 | 25.6888 | 20.2888 | 83.8593 | 23.6333 | 9.8912 | 85.6201 | 22.8308 | 0.2511 | 87.0823 | 21.5465 | -9.8972 | 88.0192 | 18.035 | -18.4828 | 73.0561 | 54.0735 | 46.4952 | 73.4486 | 53.3322 | 44.558 | 73.8886 | 51.1754 | 43.5889 | 74.3467 | 48.9046 | 42.9129 | 74.7611 | 46.0513 | 42.1348 | 75.2765 | 43.2476 | 41.2425 | 75.9181 | 38.0876 | 40.1061 | 76.6918 | 37.5054 | 38.7056 | 77.1428 | 36.9821 | 37.6182 | 77.6154 | 36.5796 | 36.4999 | 79.2517 | 35.5957 | 33.2214 | 81.1429 | 36.0184 | 30.0286 | 82.8543 | 36.2886 | 26.9805 | 84.6098 | 36.7474 | 23.7452 | 85.7819 | 36.5156 | 21.4634 | 73.1391 | 54.0735 | 46.4952 | 73.5284 | 51.852 | 40.4297 | 74.0313 | 48.0764 | 38.092 | 74.4842 | 44.5322 | 36.7605 | 74.9928 | 40.7714 | 35.0828 | 75.6019 | 35.5663 | 33.2649 | 76.3279 | 32.2042 | 31.4072 | 77.1435 | 30.3584 | 29.756 | 77.8205 | 28.3397 | 28.0587 | 78.5335 | 26.4728 | 26.3613 | 81.1019 | 23.099 | 18.845 | 83.7314 | 20.0288 | 8.541 | 85.618 | 18.5773 | 0.21336 | 87.0916 | 16.6955 | -8.4854 | 76.3888 | 13.8581 | -16.0382 | 73.1394 | 54.0735 | 46.4952 | 73.2454 | 52.1987 | 42.8148 | 73.5264 | 50.5039 | 41.0215 | 73.8894 | 44.0966 | 39.7996 | 74.2854 | 41.5024 | 38.2513 | 74.8622 | 38.5257 | 36.4889 | 75.688 | 36.7206 | 34.0478 | 76.6915 | 34.5013 | 30.0122 | 77.5955 | 32.2422 | 25.5208 | 78.5396 | 29.2528 | 21.0695 | 81.1625 | 23.7406 | 8.9588 | 83.5312 | 19.3006 | -1.412 | 85.1384 | 15.9728 | -9.788 | 69.0933 | 12.5346 | -14.9016 | 55.808 | 10.1245 | -11.112 | 73.1145 | 54.0735 | 46.4952 | 73.4438 | 52.4835 | 43.0227 | 73.8 | 49.088 | 41.3644 | 74.1721 | 45.8657 | 40.377 | 74.4747 | 42.4582 | 39.3713 | 74.9319 | 37.5504 | 38.2641 | 75.5494 | 34.1942 | 36.784 | 76.2827 | 32.6005 | 35.3704 | 76.9991 | 30.8626 | 33.6879 | 77.7372 | 29.2007 | 31.9278 | 80.1757 | 27.085 | 26.7116 | 82.2698 | 26.0079 | 21.9827 | 83.7267 | 26.0479 | 18.653 | 84.8305 | 25.5013 | 15.8307 | 85.2012 | 24.627 | 14.8264 | 73.1145 | 54.0735 | 46.4952 | 73.308 | 51.7369 | 40.431 | 73.7446 | 49.9352 | 37.9799 | 74.1978 | 43.5024 | 36.4466 | 74.6829 | 40.6999 | 34.6163 | 75.2527 | 37.5954 | 32.7729 | 76.0217 | 35.8008 | 30.2666 | 77.1451 | 33.5824 | 25.7177 | 78.0002 | 31.3148 | 21.0798 | 78.9007 | 28.3684 | 16.4841 | 81.6977 | 22.4838 | 3.8138 | 84.2163 | 17.9126 | -7.3133 | 79.17 | 14.3627 | -16.5011 | 60.5802 | 10.9902 | -22.5964 | 46.6934 | 8.4709 | -19.8265
BLACKPOOL | PENWORTHAM WEST / STANAH | 330835 | 435308 | 126.4077 | 42.5442 | 47.5796 | 126.9291 | 40.5132 | 35.5863 | 127.5621 | 39.7401 | 24.8466 | 128.2941 | 39.0493 | 20.7945 | 129.1717 | 37.5644 | 15.6949 | 129.9611 | 35.3922 | 3.1046 | 130.8978 | 33.8209 | -6.3425 | 132.036 | 32.2771 | -9.2445 | 133.0381 | 31.4362 | -12.2349 | 134.0373 | 30.8268 | -14.3875 | 137.3025 | 28.0586 | -25.434 | 136.6034 | 24.782 | -41.9805 | 126.2826 | 22.9097 | -55.7967 | 118.7114 | 21.5361 | -70.6986 | 104.2302 | 18.909 | -83.6082 | 126.3161 | 42.5442 | 47.5796 | 126.9947 | 41.8001 | 43.5547 | 127.7722 | 41.2749 | 36.4212 | 128.4916 | 40.5759 | 34.779 | 129.1299 | 39.7199 | 32.6302 | 129.9165 | 38.7769 | 27.9501 | 130.8956 | 32.8839 | 23.8688 | 132.065 | 31.689 | 21.3931 | 132.6202 | 31.0856 | 20.027 | 133.224 | 30.7704 | 18.8664 | 135.3482 | 29.7548 | 15.205 | 137.705 | 30.6749 | 11.3021 | 139.8042 | 31.5826 | 7.5476 | 141.7071 | 32.4095 | 3.4357 | 142.9518 | 32.0694 | 0.26427 | 126.4393 | 42.5442 | 47.5796 | 126.9449 | 40.1823 | 34.2226 | 127.597 | 39.1831 | -4.0403 | 128.3674 | 38.3103 | -35.2797 | 129.2757 | 36.6091 | -40.6843 | 130.085 | 34.4123 | -53.5503 | 131.0568 | 32.6426 | -63.1631 | 132.2367 | 30.9448 | -66.3019 | 133.1874 | 29.9671 | -69.3889 | 134.0706 | 29.1942 | -71.7353 | 137.3224 | 26.1705 | -81.8809 | 124.6829 | 22.6195 | -97.6871 | 113.0124 | 20.5022 | -110.8068 | 104.4134 | 18.9422 | -124.7848 | 90.582 | 16.433 | -136.1525 | 126.4398 | 42.5442 | 47.5796 | 126.4522 | 41.0187 | 38.7072 | 126.7353 | 40.4873 | 1.4193 | 127.1012 | 39.7064 | -29.685 | 127.6467 | 38.6924 | -35.0608 | 128.508 | 37.6987 | -47.9806 | 129.6545 | 36.1548 | -58.7368 | 131.0684 | 34.4928 | -66.4067 | 132.1904 | 33.0654 | -74.31 | 133.2165 | 31.2614 | -81.4917 | 135.8478 | 32.1598 | -99.4432 | 138.2988 | 28.7343 | -114.3116 | 139.8971 | 25.5322 | -126.1455 | 125.9738 | 22.8537 | -133.5018 | 118.1672 | 21.4374 | -127.7889 | 126.4073 | 42.5442 | 47.5796 | 126.8351 | 41.2422 | 39.3271 | 127.2995 | 40.6318 | 29.3885 | 127.7782 | 40.0149 | 25.6531 | 128.3742 | 38.6594 | 21.1625 | 129.0873 | 36.6048 | 9.2382 | 129.8869 | 35.1009 | 0.27158 | 130.8051 | 33.5921 | -2.3866 | 131.609 | 32.7609 | -5.3332 | 132.4562 | 32.139 | -7.564 | 135.079 | 30.1866 | -13.5956 | 137.6093 | 28.9358 | -18.0062 | 139.4032 | 28.6633 | -21.06 | 140.866 | 29.1126 | -24.0887 | 141.4737 | 28.5515 | -25.2795 | 126.4073 | 42.5442 | 47.5796 | 126.6041 | 40.1397 | 33.9387 | 127.1644 | 39.3625 | -4.5723 | 127.8494 | 38.4671 | -36.1849 | 128.6754 | 37.3613 | -42.0434 | 129.4818 | 36.2933 | -55.3356 | 130.4422 | 34.6847 | -66.5368 | 131.9139 | 32.9192 | -74.7598 | 133.21 | 31.4573 | -82.9313 | 134.4186 | 29.6106 | -90.3933 | 137.1393 | 30.2342 | -109.289 | 139.6583 | 26.6757 | -125.0184 | 128.4206 | 23.2975 | -137.761 | 112.6408 | 20.4348 | -146.3011 | 103.6265 | 18.7995 | -141.9529
BLOOM ST | SOUTH MANCHESTER | 384221 | 397717 | 149.543 | 48.7035 | 78.8849 | 149.7103 | 47.2133 | 69.4301 | 150.0432 | 43.1453 | 66.3951 | 150.3156 | 43.1398 | 65.2699 | 150.5349 | 43.1622 | 64.2991 | 150.7623 | 41.8219 | 63.3405 | 151.0005 | 40.4974 | 62.7871 | 151.2709 | 39.6413 | 62.2142 | 151.58 | 38.619 | 61.2949 | 151.8769 | 37.5712 | 60.4123 | 152.6949 | 36.1999 | 57.3688 | 153.4344 | 34.7667 | 53.7628 | 153.9388 | 33.5973 | 51.123 | 154.3798 | 33.5132 | 48.556 | 154.655 | 33.2343 | 46.47 | 149.5261 | 48.7035 | 78.8849 | 149.7285 | 48.6161 | 75.8556 | 150.0895 | 48.774 | 74.4293 | 150.4079 | 48.954 | 73.6541 | 150.6993 | 49.0912 | 73.0293 | 151.0288 | 48.6518 | 72.3822 | 151.3989 | 43.182 | 71.6815 | 151.8238 | 42.7972 | 70.8479 | 152.1262 | 42.4038 | 69.8218 | 152.4285 | 42.2166 | 68.7985 | 153.2715 | 41.797 | 65.9605 | 154.0369 | 43.3608 | 63.3413 | 154.6572 | 44.0843 | 61.2393 | 155.3132 | 44.3357 | 58.9966 | 155.9358 | 45.1565 | 56.8619 | 149.5502 | 48.7035 | 78.8849 | 149.7433 | 46.8622 | 67.934 | 150.103 | 42.7323 | 60.7605 | 150.4193 | 42.6274 | 55.7652 | 150.6834 | 42.5678 | 54.7009 | 150.9586 | 41.1427 | 53.6415 | 151.2545 | 40.0124 | 52.9698 | 151.5887 | 39.0819 | 52.2737 | 151.9063 | 38.0335 | 51.3971 | 152.2002 | 36.9436 | 50.5729 | 153.0281 | 35.4538 | 47.6932 | 153.681 | 33.9101 | 44.4734 | 154.0498 | 32.6348 | 42.3804 | 154.2801 | 32.4639 | 40.6581 | 154.2743 | 32.258 | 39.7654 | 149.5502 | 48.7035 | 78.8849 | 149.6278 | 47.414 | 71.0334 | 149.9002 | 43.4397 | 64.5767 | 150.1196 | 43.2518 | 59.7022 | 150.2986 | 43.9611 | 58.7429 | 150.5191 | 43.5095 | 57.7513 | 150.7605 | 42.4977 | 57.0195 | 151.014 | 41.5643 | 55.9262 | 151.3054 | 40.5279 | 54.5897 | 151.5789 | 38.7172 | 53.3084 | 152.3173 | 35.7118 | 49.8104 | 152.9209 | 33.6016 | 46.8278 | 153.2645 | 31.9492 | 44.9864 | 153.4601 | 32.3744 | 44.014 | 153.3756 | 30.7676 | 44.6199 | 149.543 | 48.7035 | 78.8849 | 149.7016 | 47.9315 | 73.0816 | 150.0065 | 44.0229 | 70.8346 | 150.2422 | 44.0358 | 69.7916 | 150.4266 | 44.091 | 68.9455 | 150.6422 | 42.7848 | 68.0798 | 150.8837 | 41.4738 | 67.5735 | 151.1388 | 40.6398 | 67.0311 | 151.4339 | 39.6255 | 66.1094 | 151.7229 | 38.578 | 65.1977 | 152.5307 | 37.3696 | 62.6348 | 153.272 | 36.3459 | 60.2789 | 153.7873 | 35.5459 | 58.7114 | 154.2549 | 35.9215 | 57.2362 | 154.5327 | 36.1493 | 56.3603 | 149.543 | 48.7035 | 78.8849 | 149.6727 | 46.5705 | 66.6997 | 150.0123 | 42.4048 | 59.2624 | 150.3084 | 42.1786 | 54.2556 | 150.558 | 42.8513 | 53.1763 | 150.8129 | 42.3858 | 52.1134 | 151.0798 | 41.3093 | 51.3203 | 151.3921 | 40.336 | 50.1142 | 151.697 | 39.2799 | 48.7306 | 151.9804 | 37.4486 | 47.4087 | 152.7537 | 34.3761 | 43.8316 | 153.3519 | 32.2297 | 40.8118 | 153.6697 | 30.5439 | 38.9229 | 153.8378 | 30.8947 | 37.8837 | 153.7723 | 29.2282 | 38.3319
BOLTON | KEARSLEY | 372255 | 410566 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 7.6856 | 10.6707 | 1.9358 | -19.284 | 4.9225 | 1.9358 | -40.8794 | -6.3395 | -2.6039 | -60.9325 | -20.4875 | -8.4151 | -76.5059 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 7.3166 | 10.6707 | 1.9358 | -1.0666 | 10.6707 | 1.9358 | -7.0685 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 3.5699 | 5.0611 | 1.9358 | -22.3335 | -9.2101 | -3.783 | -41.2026 | -21.4941 | -8.8285 | -57.7286 | -35.2006 | -14.4584 | -68.013 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 5.7471 | 10.6707 | 1.9358 | -20.1944 | -4.8942 | -2.0103 | -43.2489 | -21.8976 | -8.9943 | -59.1081 | -36.0887 | -14.8232 | -66.6919 | -44.3872 | -18.2317 | -58.5318 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 9.0848 | 10.6707 | 1.9358 | -0.076161 | 10.6707 | 1.9358 | -7.4268 | 10.6707 | 1.9358 | -11.0524 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 6.8228 | 10.6707 | 1.9358 | -3.0744 | 9.2338 | 1.9358 | -31.593 | -12.4203 | -5.1015 | -57.1711 | -30.1885 | -12.3997 | -74.765 | -45.1869 | -18.5602 | -84.4096 | -54.2311 | -22.275 | -78.571
BURNLEY | ROCHDALE | 385569 | 434469 | 79.8907 | 45.9186 | 66.5986 | 80.3584 | 45.0211 | 62.3039 | 80.8285 | 44.4526 | 60.8983 | 81.3259 | 43.9088 | 60.21 | 81.8464 | 43.2472 | 59.2585 | 82.4557 | 42.4592 | 58.262 | 83.1722 | 41.7458 | 57.3814 | 84.0215 | 41.2718 | 56.7682 | 84.6213 | 40.7518 | 55.9803 | 85.1555 | 40.5131 | 55.2766 | 87.097 | 39.2962 | 49.1638 | 89.3009 | 38.6978 | 37.6476 | 90.7314 | 41.0307 | 27.8939 | 91.9051 | 61.2752 | 17.5952 | 92.5589 | 59.8728 | 9.2009 | 79.8237 | 45.9186 | 66.5986 | 80.2068 | 45.6028 | 64.7687 | 80.593 | 45.339 | 63.8721 | 81.0016 | 45.0537 | 63.218 | 81.49 | 44.7244 | 62.4512 | 82.0167 | 44.3317 | 61.5983 | 82.6495 | 40.9464 | 60.5262 | 83.3875 | 40.5607 | 59.2395 | 83.8281 | 40.2116 | 58.2577 | 84.3004 | 39.9972 | 57.2743 | 85.9425 | 39.2128 | 54.2831 | 87.3525 | 39.6585 | 51.15 | 88.5068 | 41.0434 | 48.2516 | 89.6094 | 53.9142 | 44.9649 | 90.3412 | 65.6542 | 42.8722 | 79.918 | 45.9186 | 66.5986 | 80.3589 | 44.8561 | 61.7538 | 80.8374 | 44.1295 | 60.3213 | 81.3522 | 43.4133 | 59.7733 | 81.8909 | 42.6694 | 58.9617 | 82.517 | 41.7972 | 58.1269 | 83.2519 | 41.1781 | 57.4783 | 84.0754 | 40.6498 | 57.0539 | 84.6118 | 40.1641 | 56.3255 | 85.1094 | 39.8881 | 55.6862 | 87.0385 | 38.3866 | 50.8064 | 89.3579 | 37.5021 | 40.0637 | 91.0716 | 39.6312 | 30.8939 | 92.3234 | 59.5313 | 21.3407 | 92.9283 | 58.0307 | 13.8669 | 79.9185 | 45.9186 | 66.5986 | 80.1096 | 45.1488 | 63.8997 | 80.3989 | 44.5243 | 62.9659 | 80.7522 | 44.1605 | 62.5482 | 81.1329 | 42.8988 | 61.7874 | 81.6978 | 41.9432 | 60.928 | 82.4332 | 38.8617 | 59.4683 | 83.3408 | 36.2047 | 55.9083 | 84.0414 | 33.8587 | 52.2073 | 84.7408 | 33.2755 | 48.535 | 86.8395 | 52.8772 | 38.0074 | 88.7963 | 50.524 | 27.7757 | 90.1442 | 48.4333 | 19.4498 | 91.0507 | 47.109 | 14.2214 | 90.9887 | 46.4456 | 18.3025 | 79.8901 | 45.9186 | 66.5986 | 80.2773 | 45.2687 | 63.6869 | 80.615 | 44.7575 | 62.6359 | 80.9647 | 44.272 | 62.1787 | 81.3209 | 43.6919 | 61.6938 | 81.8127 | 42.9613 | 61.1191 | 82.4539 | 42.3235 | 60.4727 | 83.1785 | 41.8914 | 59.9619 | 83.8188 | 41.4375 | 59.1535 | 84.3804 | 41.2031 | 58.3502 | 86.0615 | 40.4335 | 55.512 | 87.7109 | 40.8431 | 52.3222 | 88.8976 | 44.0613 | 49.7008 | 89.9039 | 65.2153 | 47.1016 | 90.2783 | 64.5789 | 46.149 | 79.8901 | 45.9186 | 66.5986 | 80.1421 | 44.8109 | 61.8222 | 80.5554 | 44.0759 | 60.2921 | 81.0384 | 43.6695 | 59.5717 | 81.5209 | 42.3361 | 58.5326 | 82.0725 | 41.3564 | 57.4798 | 82.7463 | 38.2385 | 55.7877 | 83.6783 | 35.5667 | 51.9118 | 84.4043 | 33.2256 | 48.0114 | 85.0941 | 32.6516 | 44.1315 | 87.2335 | 52.2583 | 32.9081 | 89.2396 | 49.799 | 21.9429 | 90.6772 | 47.6254 | 12.853 | 91.6589 | 46.1304 | 6.5838 | 91.7127 | 45.3461 | 9.4473
BURY | KEARSLEY | 380272 | 411184 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | -8.4568 | 10.6707 | 1.9358 | -24.7879 | 64.0842 | 11.6259 | -42.0707 | 70.6835 | 12.8231 | -57.0549 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 30.4959 | 5.5324 | 4.3004 | 43.1439 | 7.827 | -1.0166 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 6.982 | 10.6707 | 1.9358 | -11.7272 | 10.6707 | 1.9358 | -27.1184 | 46.4761 | 8.4315 | -43.1288 | 54.466 | 9.881 | -56.5723 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 7.8278 | 100.8952 | 22.623 | -11.5702 | 98.6028 | 17.8881 | -30.0775 | 78.1465 | 14.177 | -44.168 | 61.4336 | 11.145 | -53.7915 | 53.7861 | 9.7577 | -49.9059 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 19.2925 | 3.5 | 7.9074 | 99.2979 | 18.0142 | 2.1138 | 106.1846 | 20.6236 | -1.0163 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 8.3212 | 10.6707 | 1.9358 | 1.2409 | 101.5297 | 21.3462 | -19.2361 | 89.4966 | 16.2361 | -39.1049 | 68.5693 | 12.4396 | -54.5757 | 50.0673 | 9.083 | -65.7482 | 41.6566 | 7.5572 | -63.4879
BUXTON | STALYBRIDGE | 407769 | 375476 | 85.2666 | 62.092 | 12.5387 | 85.3905 | 61.1684 | 11.9194 | 85.6484 | 60.2531 | 11.04 | 85.8334 | 59.323 | 10.5869 | 85.9908 | 58.2132 | 10.2711 | 86.1661 | 57.0599 | 9.942 | 86.37 | 56.5922 | 9.6747 | 89.1461 | 56.1671 | 6.7768 | 94.9028 | 55.9009 | 0.32223 | 95.1514 | 55.8914 | -0.27977 | 101.2062 | 55.5322 | -8.7159 | 102.4126 | 55.6571 | -13.143 | 104.029 | 57.7628 | -17.1071 | 104.5869 | 81.0831 | -19.5641 | 104.7452 | 80.1717 | -20.6455 | 85.2657 | 62.092 | 12.5387 | 85.3644 | 61.3519 | 12.2158 | 85.5889 | 60.555 | 11.3832 | 85.7411 | 59.724 | 10.9028 | 85.863 | 58.8317 | 10.6266 | 86.0119 | 57.968 | 10.4081 | 86.1896 | 54.4242 | 10.125 | 88.9219 | 54.2636 | 7.0759 | 89.1751 | 54.086 | 6.265 | 89.4387 | 54.037 | 5.4468 | 90.5402 | 53.8861 | 2.7314 | 91.5397 | 55.1154 | 0.18636 | 92.4469 | 56.0076 | -2.1866 | 103.033 | 69.5651 | -14.9391 | 103.4425 | 83.5816 | -16.5215 | 85.267 | 62.092 | 12.5387 | 85.4359 | 61.0993 | 11.8515 | 85.7323 | 60.1094 | -26.7895 | 85.9703 | 59.0981 | -64.914 | 86.1717 | 57.8716 | -65.2757 | 86.3894 | 56.6887 | -65.6577 | 86.6384 | 56.1128 | -65.937 | 89.0424 | 55.7346 | -68.4201 | 93.7225 | 55.4221 | -73.4021 | 93.7299 | 55.2987 | -73.6331 | 98.5977 | 54.6969 | -80.3846 | 102.1172 | 54.621 | -86.5171 | 103.5728 | 56.6184 | -89.3672 | 103.8471 | 79.8525 | -90.0875 | 103.5981 | 78.7126 | -88.735 | 85.267 | 62.092 | 12.5387 | 85.2775 | 61.2155 | 12.3594 | 85.5041 | 60.2781 | -26.1411 | 85.6811 | 59.1543 | -64.2253 | 85.9234 | 57.8114 | -64.6639 | 86.1199 | 56.9198 | -65.0507 | 86.3894 | 55.6589 | -65.568 | 88.7019 | 54.717 | -68.7848 | 93.2327 | 54.3618 | -74.4441 | 96.7318 | 55.0553 | -79.1611 | 99.0859 | 75.7525 | -84.2953 | 99.7415 | 74.4543 | -86.9014 | 100.2423 | 72.5948 | -88.2064 | 100.2832 | 71.6148 | -87.4961 | 99.6504 | 70.6053 | -83.8227 | 85.2666 | 62.092 | 12.5387 | 85.3758 | 61.2563 | 12.1856 | 85.6003 | 60.3545 | 11.3979 | 85.734 | 59.4454 | 11.0307 | 85.8298 | 58.3693 | 10.8901 | 85.9689 | 57.2542 | 10.7561 | 86.1609 | 56.8094 | 10.6461 | 88.9089 | 56.4147 | 7.8442 | 94.6281 | 56.1434 | 1.4288 | 94.8465 | 56.1295 | 0.83529 | 100.7303 | 55.9749 | -6.5175 | 101.6764 | 56.4571 | -8.5646 | 103.1017 | 58.8714 | -10.6341 | 103.4631 | 82.4087 | -11.2968 | 103.3783 | 81.4809 | -10.854 | 85.2666 | 62.092 | 12.5387 | 85.3149 | 61.1337 | 12.0939 | 85.5945 | 60.1659 | -26.5527 | 85.8311 | 59.0282 | -64.7574 | 86.1226 | 57.6667 | -65.3059 | 86.3322 | 56.7629 | -65.768 | 86.6024 | 55.4984 | -66.3716 | 88.9378 | 54.5594 | -69.6943 | 93.4723 | 54.2169 | -75.3925 | 96.9732 | 54.8735 | -80.1525 | 99.3672 | 75.5901 | -85.5177 | 100.1027 | 74.241 | -88.435 | 100.6917 | 72.3992 | -90.0582 | 100.7927 | 71.2018 | -89.6685 | 100.2304 | 70.2035 | -86.3084
CARLISLE | HARKER / HUTTON | 338655 | 556583 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | -11.5675 | 6.7308 | 1.9358 | -42.8641 | 6.7308 | 1.9358 | -68.4782 | 6.7308 | 1.9358 | -87.0518 | 6.7308 | 1.9358 | -102.748 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | -5.0444 | 6.7308 | 1.9358 | -20.621 | 6.7308 | 1.9358 | -33.6985 | 6.7308 | 1.9358 | -40.1649 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | -17.5527 | 6.7308 | 1.9358 | -49.4105 | 6.7308 | 1.9358 | -75.8522 | 6.7308 | 1.9358 | -94.336 | 6.7308 | 1.9358 | -107.6799 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | -2.154 | 6.7308 | 1.9358 | -12.0951 | 6.7308 | 1.9358 | -42.5469 | 6.7308 | 1.9358 | -71.3667 | 6.7308 | 1.9358 | -94.6356 | 6.7308 | 1.9358 | -104.5461 | -299.3551 | -122.9578 | -299.3551 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 5.9742 | 6.7308 | 1.9358 | -11.9673 | 6.7308 | 1.9358 | -25.441 | 6.7308 | 1.9358 | -31.3828 | 6.7308 | 1.9358 | -32.8383 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | -3.0133 | 6.7308 | 1.9358 | -12.9131 | 6.7308 | 1.9358 | -23.0987 | 6.7308 | 1.9358 | -54.9663 | 6.7308 | 1.9358 | -85.6783 | 6.7308 | 1.9358 | -110.8671 | 5.2427 | 1.9358 | -122.7079 | -308.1452 | -126.5683 | -308.1452
CARRINGTON BSP | CARRINGTON | 373110 | 393020 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 26.3316 | 4.777 | 14.4765 | 50.3599 | 23.7118 | 10.4409 | 50.662 | 28.5906 | 6.6539 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 40.8945 | 7.4189 | 21.4262 | 48.0195 | 8.7115 | 5.5084 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 14.1358 | 2.5645 | 6.3809 | 54.5795 | 21.2535 | 1.0889 | 54.7293 | 26.1252 | -2.3722 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 51.7291 | 30.9291 | 12.7107 | 52.5021 | 28.843 | 7.1644 | 53.1501 | 26.9177 | 2.4087 | 53.4126 | 25.1007 | -1.0726 | 53.142 | 24.0067 | 0.12233 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 36.8403 | 6.6834 | 22.7093 | 49.1953 | 26.1476 | 21.491 | 49.1953 | 31.5557 | 21.1256 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 51.7006 | 30.572 | 11.514 | 52.6635 | 28.4064 | 5.474 | 53.5225 | 26.3947 | 0.19871 | 53.9088 | 24.544 | -3.735 | 53.6872 | 23.5159 | -2.8811
CASTLETON | ROCHDALE | 388461 | 411290 | 100.663 | 54.342 | 45.287 | 101.0863 | 51.5724 | 39.2071 | 101.5839 | 47.5626 | 36.0227 | 102.2028 | 43.8931 | 32.7435 | 102.9955 | 40.1842 | 29.2051 | 103.997 | 36.5238 | 25.5501 | 105.7852 | 34.1822 | 21.3512 | 107.3851 | 33.5708 | 20.061 | 109.0075 | 32.9892 | 18.4742 | 110.1557 | 32.5084 | 16.8994 | 113.7691 | 30.4942 | 9.0197 | 117.4902 | 28.592 | -2.8032 | 120.5531 | 28.2771 | -12.7417 | 122.6848 | 28.797 | -22.6494 | 124.2003 | 26.8393 | -33.7635 | 100.5708 | 54.342 | 45.287 | 100.9671 | 53.9001 | 43.4109 | 101.4397 | 51.6452 | 42.4014 | 101.962 | 49.4398 | 41.7196 | 102.5837 | 47.3672 | 41.0284 | 103.3583 | 45.35 | 40.2806 | 104.1303 | 39.7555 | 39.3103 | 105.0357 | 39.3069 | 37.9809 | 105.7473 | 38.8716 | 36.5976 | 106.548 | 38.6098 | 35.1783 | 109.5092 | 37.7971 | 30.6918 | 112.9585 | 38.4488 | 25.7745 | 115.9177 | 39.6244 | 20.4939 | 118.5362 | 40.995 | 14.3652 | 120.3616 | 40.7454 | 9.1897 | 100.702 | 54.342 | 45.287 | 101.1284 | 51.3228 | 38.2998 | 101.6555 | 47.2002 | 34.9351 | 102.3102 | 43.366 | 31.1932 | 103.1313 | 39.5311 | 27.2266 | 104.1432 | 35.7255 | 23.1584 | 105.8899 | 33.2657 | 18.4653 | 107.4474 | 32.6213 | 17.2502 | 108.8342 | 32.0406 | 15.9085 | 109.7424 | 31.5208 | 14.5887 | 113.6956 | 29.3572 | 6.815 | 117.6157 | 27.2945 | -4.6285 | 120.3979 | 26.8527 | -13.6721 | 122.4386 | 26.8611 | -22.4202 | 123.6541 | 25.5506 | -30.7917 | 100.7021 | 54.342 | 45.287 | 100.8225 | 51.821 | 40.8474 | 101.1224 | 49.7518 | 38.1184 | 102.1161 | 47.9951 | 33.9286 | 103.2818 | 45.7909 | 29.4824 | 104.6675 | 43.5114 | 24.941 | 105.8538 | 42.3279 | 20.2042 | 107.4056 | 40.8652 | 16.6464 | 109.0656 | 39.4054 | 12.7957 | 110.8632 | 37.916 | 8.9553 | 114.8669 | 35.7928 | -2.3639 | 118.3954 | 33.1334 | -13.128 | 120.6023 | 31.0677 | -22.3204 | 121.9145 | 29.9546 | -28.876 | 121.9172 | 29.5218 | -26.4362 | 100.6629 | 54.342 | 45.287 | 101.0411 | 52.1929 | 42.2479 | 101.4232 | 48.3204 | 39.7898 | 101.8504 | 44.6847 | 36.7682 | 102.4122 | 41.0566 | 33.7413 | 103.2508 | 37.4691 | 30.5647 | 104.8972 | 35.1766 | 26.7119 | 106.2226 | 34.6063 | 25.6632 | 107.4862 | 34.0353 | 24.1683 | 108.8363 | 33.5587 | 22.615 | 112.3899 | 32.0409 | 17.3857 | 115.5448 | 31.2715 | 11.7619 | 118.1936 | 32.0063 | 7.4217 | 119.7708 | 33.5392 | 4.0273 | 120.4705 | 33.4291 | 2.1178 | 100.6629 | 54.342 | 45.287 | 100.904 | 51.2207 | 38.0113 | 101.3628 | 48.9867 | 34.5231 | 102.5337 | 47.1839 | 30.0929 | 103.8304 | 44.9195 | 25.4451 | 105.1842 | 42.6161 | 20.8346 | 106.25 | 41.4145 | 16.0736 | 107.7309 | 39.9369 | 12.3981 | 109.2199 | 38.4947 | 8.5133 | 110.8505 | 37.0464 | 4.6444 | 115.189 | 34.6055 | -6.8974 | 118.9934 | 31.837 | -18.0779 | 121.6072 | 29.6771 | -28.5503 | 123.0822 | 28.5086 | -36.6688 | 123.1995 | 27.8547 | -35.6738
CHADDERTON | WHITEGATE | 389137 | 403821 | 103.5019 | 26.4929 | 34.2862 | 104.2087 | 24.4924 | 26.0303 | 105.1828 | 20.7406 | 23.375 | 95.918 | 17.401 | 21.9179 | 77.8804 | 14.1287 | 20.0181 | 63.0319 | 11.435 | 17.6088 | 48.5774 | 8.8127 | 14.8637 | 44.9444 | 8.1536 | 12.1292 | 41.6826 | 7.5619 | 9.0299 | 40.5984 | 7.3652 | 6.0469 | 32.7371 | 5.939 | -8.1734 | 37.5248 | 6.8076 | -28.4738 | 82.2407 | 14.9198 | -44.1508 | 130.6363 | 25.226 | -58.8714 | 132.5007 | 26.3067 | -70.8757 | 103.3356 | 26.4929 | 34.2862 | 103.8658 | 25.8546 | 31.8984 | 104.4541 | 22.6957 | 30.7937 | 105.1026 | 19.6949 | 29.8539 | 92.8114 | 16.8375 | 28.8426 | 77.8015 | 14.1144 | 27.7701 | 43.8521 | 7.9555 | 26.3897 | 40.0493 | 7.2656 | 23.856 | 36.9265 | 6.6991 | 21.222 | 34.4839 | 6.2559 | 18.4824 | 27.6344 | 5.0133 | 10.0472 | 28.2012 | 5.1161 | 1.5148 | 57.628 | 10.4546 | -6.5831 | 103.7096 | 18.8146 | -15.1422 | 111.6245 | 20.2505 | -21.0448 | 103.5591 | 26.4929 | 34.2862 | 104.3416 | 24.0972 | 24.6142 | 105.444 | 20.0037 | 16.5173 | 90.3153 | 16.3846 | 9.8115 | 72.8661 | 13.2191 | 7.4889 | 56.9268 | 10.3274 | 5.1016 | 41.4455 | 7.5189 | 2.7075 | 37.7665 | 6.8515 | -0.18006 | 33.6767 | 6.1095 | -3.355 | 31.6538 | 5.7425 | -6.6129 | 22.3473 | 4.0542 | -21.5475 | 26.5029 | 4.8081 | -41.8264 | 68.53 | 12.4324 | -56.7265 | 124.2406 | 22.5392 | -69.7812 | 130.6941 | 23.71 | -78.7803 | 103.5594 | 26.4929 | 34.2862 | 103.8342 | 24.9085 | 28.2312 | 104.5286 | 23.7051 | 21.065 | 105.3777 | 22.6471 | 14.5965 | 106.5293 | 21.8139 | 12.4098 | 108.2062 | 20.9894 | 9.9873 | 110.3248 | 20.1926 | 6.7162 | 112.857 | 20.6037 | 0.066174 | 112.6017 | 20.4277 | -7.0101 | 114.8473 | 20.8351 | -14.0708 | 121.3825 | 34.9827 | -34.201 | 125.6859 | 30.3074 | -52.3712 | 128.5383 | 26.5128 | -64.9611 | 130.0215 | 23.588 | -72.0939 | 121.4583 | 22.0345 | -69.1732 | 103.5016 | 26.4929 | 34.2862 | 104.0962 | 25.4318 | 30.4495 | 104.8174 | 21.9016 | 28.8933 | 102.7487 | 18.6403 | 27.8955 | 85.5877 | 15.527 | 26.8602 | 71.5993 | 12.9893 | 25.68 | 57.5871 | 10.4472 | 23.8541 | 54.1886 | 9.8307 | 21.6013 | 51.1561 | 9.2805 | 18.742 | 49.9895 | 9.0689 | 15.8249 | 45.9915 | 8.3436 | 6.0315 | 60.1262 | 10.9078 | -4.3191 | 112.3587 | 20.3837 | -11.5968 | 126.8001 | 32.3306 | -18.2383 | 127.8086 | 34.8767 | -22.3519 | 103.5016 | 26.4929 | 34.2862 | 103.9205 | 24.1106 | 24.5735 | 104.8827 | 22.6875 | 16.342 | 106.0559 | 21.527 | 9.4417 | 107.4526 | 20.6189 | 6.8833 | 108.6847 | 19.7171 | 4.231 | 103.8666 | 18.8431 | -0.15751 | 105.7415 | 19.1832 | -7.57 | 104.0667 | 18.8794 | -15.0467 | 106.0519 | 19.2395 | -22.5028 | 122.0493 | 33.2322 | -43.9334 | 126.4722 | 28.4705 | -63.2224 | 129.5039 | 24.5565 | -76.9245 | 118.5471 | 21.5063 | -85.199 | 108.7919 | 19.7366 | -83.6322
DROYLSDEN | STALYBRIDGE | 390140 | 398146 | 35.7659 | 6.4885 | 35.7659 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 6.3099 | 10.6707 | 1.9358 | -6.2735 | 10.6707 | 1.9358 | -18.2781 | 10.6707 | 1.9358 | -27.6956 | 35.7659 | 6.4885 | 35.7659 | 4.0691 | 0.73821 | 4.0691 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 35.7659 | 6.4885 | 35.7659 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 3.6538 | 10.6707 | 1.9358 | -7.5394 | 10.6707 | 1.9358 | -17.0554 | 10.6707 | 1.9358 | -22.6161 | 35.7659 | 6.4885 | 35.7659 | 0.66727 | 0.12105 | 0.66727 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 6.023 | 10.6707 | 1.9358 | -7.6965 | 10.6707 | 1.9358 | -16.7087 | 10.6707 | 1.9358 | -20.7605 | 10.6707 | 1.9358 | -16.138 | 35.7659 | 6.4885 | 35.7659 | 2.2171 | 0.40221 | 2.2171 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 35.7659 | 6.4885 | 35.7659 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | -0.74907 | 10.6707 | 1.9358 | -15.4639 | 10.6707 | 1.9358 | -25.4605 | 10.6707 | 1.9358 | -30.646 | 10.6707 | 1.9358 | -27.3081
EGREMONT | HARKER / HUTTON | 301070 | 513074 | 19.8673 | 19.8673 | 19.8673 | 20.1993 | 20.1993 | 20.1993 | 20.6545 | 20.6545 | 20.6545 | 21.1873 | 21.1873 | 21.1873 | 21.7254 | 21.7254 | 21.7254 | 22.3561 | 22.3561 | 22.3561 | 23.0954 | 23.0954 | 23.0954 | 24.0061 | 24.0061 | 24.0061 | 24.6533 | 24.6533 | 24.6533 | 25.0551 | 25.0551 | 25.0551 | 26.3133 | 26.3133 | 22.1204 | 27.7424 | 27.7424 | 13.6529 | 28.7471 | 28.7471 | 6.6991 | 29.5262 | 29.5262 | 0.011063 | 29.8666 | 29.8666 | -5.3761 | 19.8025 | 19.8025 | 19.8025 | 20.1123 | 20.1123 | 20.1123 | 20.4842 | 20.4842 | 20.4842 | 20.9052 | 20.9052 | 20.9052 | 21.3854 | 21.3854 | 21.3854 | 21.8668 | 21.8668 | 21.8668 | 22.4531 | 22.4531 | 22.4531 | 23.135 | 23.135 | 23.135 | 23.5826 | 23.5826 | 23.5826 | 24.0589 | 24.0589 | 24.0589 | 25.4761 | 25.4761 | 23.907 | 26.6722 | 26.6722 | 21.6243 | 27.6901 | 27.6901 | 19.5894 | 28.3281 | 28.3281 | 17.5491 | 28.5822 | 28.5822 | 16.4114 | 19.8942 | 19.8942 | 19.8942 | 20.2276 | 20.2276 | 20.2276 | 20.7137 | 20.7137 | 20.7137 | 21.289 | 21.289 | 11.7016 | 21.8772 | 21.8772 | 11.2119 | 22.5702 | 22.5702 | 10.7155 | 23.3848 | 23.3848 | 10.4439 | 24.3573 | 24.3573 | 10.348 | 24.8063 | 24.8063 | 10.1294 | 25.141 | 25.141 | 9.9416 | 26.3653 | 26.3653 | 6.3248 | 27.7863 | 27.7863 | -1.3918 | 28.7569 | 28.7569 | -7.6831 | 29.4315 | 29.4315 | -13.5759 | 29.5731 | 29.5731 | -18.0424 | 19.8944 | 19.8944 | 19.8944 | 19.9302 | 19.9302 | 19.9302 | 20.1738 | 20.1738 | 20.1738 | 20.4777 | 20.4777 | 13.2955 | 20.8607 | 20.8607 | 12.8428 | 21.4258 | 21.4258 | 12.2875 | 22.1625 | 22.1625 | 11.3566 | 23.0534 | 23.0534 | 8.8394 | 23.8197 | 23.8197 | 6.1354 | 24.5641 | 24.0666 | 3.4556 | 25.9147 | 19.407 | -4.1471 | 27.2153 | 16.4191 | -11.3475 | 28.0601 | 13.5912 | -16.8686 | 28.4395 | 9.8588 | -19.3997 | 27.8719 | 7.3975 | -14.8905 | 19.867 | 19.867 | 19.867 | 20.1337 | 20.1337 | 20.1337 | 20.4548 | 20.4548 | 20.4548 | 20.781 | 20.781 | 20.781 | 21.1726 | 21.1726 | 21.1726 | 21.6906 | 21.6906 | 21.6906 | 22.38 | 22.38 | 22.38 | 23.1631 | 23.1631 | 23.1631 | 23.7862 | 23.7862 | 23.7862 | 24.3766 | 24.3766 | 24.3766 | 25.5912 | 25.5912 | 25.5912 | 26.7314 | 26.7314 | 23.6719 | 27.4976 | 27.4976 | 21.7392 | 28.051 | 28.051 | 20.1699 | 28.0118 | 28.0118 | 20.4743 | 19.867 | 19.867 | 19.867 | 19.999 | 19.999 | 19.999 | 20.4124 | 20.4124 | 20.4124 | 20.9228 | 20.9228 | 11.4495 | 21.4494 | 21.4494 | 10.487 | 22.0426 | 22.0426 | 9.5387 | 22.7561 | 22.7561 | 8.1805 | 23.7195 | 23.7195 | 5.177 | 24.4787 | 24.4787 | 2.0936 | 25.1009 | 23.3849 | -0.96702 | 26.6009 | 18.65 | -9.3373 | 27.8898 | 15.5726 | -17.1953 | 28.7442 | 12.5994 | -23.3511 | 29.1142 | 8.9525 | -26.6366 | 28.5972 | 6.459 | -22.9579
FREDERICK RD | KEARSLEY | 381795 | 399250 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 3.1326 | 6.7308 | 1.9358 | -5.1344 | 6.7308 | 1.9358 | -13.6427 | 6.7308 | 1.9358 | -21.1689 | 6.7308 | 1.9358 | -29.0818 | 6.7308 | 1.9358 | -34.0503 | 6.7308 | 1.9358 | -51.7692 | 6.7308 | 1.9358 | -70.6407 | 6.7308 | 1.9358 | -83.537 | 6.7308 | 1.9358 | -96.422 | 6.7308 | 1.9358 | -108.1781 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 1.2933 | 6.7308 | 1.9358 | -9.3481 | 6.7308 | 1.9358 | -18.9617 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.281 | 6.7308 | 1.9358 | -2.226 | 6.7308 | 1.9358 | -10.7966 | 6.7308 | 1.9358 | -22.053 | 6.7308 | 1.9358 | -32.9335 | 6.7308 | 1.9358 | -43.936 | 6.7308 | 1.9358 | -49.714 | 6.7308 | 1.9358 | -67.2827 | 6.7308 | 1.9358 | -85.8709 | 6.7308 | 1.9358 | -98.0367 | 6.7308 | 1.9358 | -109.3543 | 6.7308 | 1.9358 | -118.4634 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | -0.17307 | 6.7308 | 1.9358 | -11.9208 | 6.7308 | 1.9358 | -25.1254 | 6.7308 | 1.9358 | -38.6208 | 6.7308 | 1.9358 | -46.807 | 6.7308 | 1.9358 | -67.5615 | 6.7308 | 1.9358 | -84.7291 | 6.7308 | 1.9358 | -95.153 | 6.7308 | 1.9358 | -102.4723 | 6.7308 | 1.9358 | -104.6078 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 0.49618 | 6.7308 | 1.9358 | -6.794 | 6.7308 | 1.9358 | -14.7739 | 6.7308 | 1.9358 | -19.9961 | 6.7308 | 1.9358 | -35.4031 | 6.7308 | 1.9358 | -48.1569 | 6.7308 | 1.9358 | -55.9497 | 6.7308 | 1.9358 | -63.8789 | 6.7308 | 1.9358 | -70.4495 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 3.0121 | 6.7308 | 1.9358 | -5.6649 | 6.7308 | 1.9358 | -14.3698 | 6.7308 | 1.9358 | -26.3621 | 6.7308 | 1.9358 | -39.9263 | 6.7308 | 1.9358 | -54.0671 | 6.7308 | 1.9358 | -62.891 | 6.7308 | 1.9358 | -86.1261 | 6.7308 | 1.9358 | -105.5575 | 6.7308 | 1.9358 | -118.254 | 6.7308 | 1.9358 | -128.4224 | 6.7308 | 1.9358 | -134.0748
GOLBORNE | BOLD | 360607 | 397690 | 84.1593 | 42.1133 | 69.0817 | 84.6216 | 36.7357 | 65.2062 | 85.3755 | 29.2091 | 63.586 | 86.2506 | 21.8612 | 62.5145 | 79.7049 | 14.4597 | 61.0651 | 39.6391 | 7.1912 | 39.6391 | 26.8411 | 4.8694 | 26.8411 | 24.3256 | 4.4131 | 24.3256 | 21.5072 | 3.9017 | 21.5072 | 22.3121 | 4.0478 | 22.3121 | 23.2903 | 4.2252 | 23.2903 | 52.2022 | 9.4703 | 24.3215 | 108.1081 | 25.8804 | 11.9068 | 110.2247 | 48.6899 | -0.37254 | 111.4142 | 53.1418 | -11.0275 | 84.0596 | 42.1133 | 69.0817 | 84.3251 | 37.0933 | 67.7187 | 84.6698 | 30.2787 | 66.7404 | 85.0143 | 23.5693 | 66.018 | 85.4475 | 16.858 | 65.1584 | 56.5179 | 10.2533 | 56.5179 | 31.102 | 5.6424 | 31.102 | 28.5592 | 5.1811 | 28.5592 | 26.1488 | 4.7438 | 26.1488 | 24.2944 | 4.4074 | 24.2944 | 18.941 | 3.4362 | 18.941 | 20.0022 | 3.6287 | 20.0022 | 77.215 | 14.008 | 33.7467 | 106.4543 | 31.2232 | 25.5391 | 108.6992 | 36.7097 | 20.2968 | 84.2009 | 42.1133 | 69.0817 | 84.6791 | 36.6286 | 64.8114 | 85.4716 | 29.0068 | 63.2288 | 86.349 | 21.5972 | 62.4257 | 77.3741 | 14.0369 | 60.8255 | 36.8224 | 6.6802 | 36.8224 | 23.2192 | 4.2123 | 23.2192 | 19.9427 | 3.6179 | 19.9427 | 16.4995 | 2.9933 | 16.4995 | 16.866 | 3.0598 | 16.866 | 15.7314 | 2.8539 | 15.7314 | 42.866 | 7.7766 | 27.6171 | 107.8336 | 23.7872 | 15.7096 | 109.8673 | 46.141 | 4.7309 | 110.6039 | 50.373 | -4.3177 | 84.2009 | 42.1133 | 69.0817 | 84.2348 | 41.686 | 67.166 | 84.8008 | 40.8315 | 66.2067 | 85.5975 | 39.8989 | 65.5656 | 86.7695 | 38.6839 | 63.983 | 88.2721 | 37.5269 | 62.1648 | 90.4583 | 36.2274 | 59.6365 | 92.5068 | 37.0433 | 54.8021 | 94.1881 | 37.3221 | 49.4733 | 95.7175 | 38.6264 | 44.242 | 100.421 | 60.9656 | 29.299 | 104.3366 | 57.3513 | 15.1971 | 106.7811 | 54.2327 | 4.4958 | 108.1385 | 51.4197 | -2.0743 | 107.8315 | 49.5064 | 1.5598 | 84.1592 | 42.1133 | 69.0817 | 84.522 | 37.0032 | 67.124 | 85.1217 | 29.5634 | 66.0885 | 85.7412 | 22.2703 | 65.4175 | 82.4882 | 14.9647 | 64.6974 | 42.7679 | 7.7588 | 42.7679 | 30.1555 | 5.4707 | 30.1555 | 27.8085 | 5.0449 | 27.8085 | 25.1576 | 4.564 | 25.1576 | 26.0208 | 4.7206 | 26.0208 | 29.2178 | 5.3006 | 29.2178 | 62.7098 | 11.3766 | 40.5422 | 105.588 | 28.533 | 34.6997 | 107.4844 | 52.6299 | 30.0523 | 108.09 | 58.334 | 28.0244 | 84.1592 | 42.1133 | 69.0817 | 84.2884 | 41.4306 | 65.2642 | 85.0059 | 40.4663 | 63.5667 | 85.9328 | 39.4622 | 62.472 | 87.1993 | 38.1926 | 60.499 | 88.6197 | 37.0118 | 58.467 | 90.6276 | 35.6964 | 55.7039 | 92.7573 | 36.4959 | 50.536 | 94.2945 | 36.6805 | 45.0222 | 95.9221 | 37.985 | 39.5981 | 100.6345 | 60.0704 | 23.6728 | 104.9626 | 56.3041 | 8.2343 | 107.7872 | 53.0284 | -3.8172 | 109.3354 | 50.1509 | -11.6765 | 109.1268 | 48.2547 | -9.2358
GREENHILL | WHITEGATE | 393262 | 404755 | 85.2298 | 55.7664 | 33.3465 | 86.187 | 54.7333 | 29.3862 | 87.1975 | 50.7363 | 26.2317 | 88.371 | 46.8797 | 23.795 | 89.7679 | 43.0561 | 21.0229 | 91.4142 | 39.237 | 18.1389 | 93.2487 | 35.5476 | 15.3156 | 95.3777 | 34.7486 | 12.5803 | 97.2098 | 33.9849 | 9.8552 | 98.9985 | 33.42 | 7.8763 | 104.0048 | 31.0181 | -2.5073 | 108.604 | 28.7378 | -18.285 | 111.0294 | 28.5889 | -30.6262 | 113.0587 | 28.3758 | -42.1067 | 114.3256 | 26.0819 | -50.6392 | 85.1401 | 55.7664 | 33.3465 | 85.8977 | 55.3026 | 31.575 | 86.6638 | 51.8529 | 30.1784 | 87.53 | 48.4054 | 29.007 | 88.5878 | 45.0233 | 27.7285 | 89.8776 | 41.6852 | 26.3475 | 91.4151 | 33.3732 | 24.6375 | 93.2101 | 32.6807 | 22.4561 | 94.2892 | 32.1859 | 20.6157 | 95.4944 | 31.8617 | 18.781 | 99.5266 | 30.9472 | 12.8576 | 103.4742 | 31.937 | 6.2054 | 106.2617 | 33.2851 | -0.29176 | 109.1909 | 33.9405 | -7.5253 | 111.3048 | 32.7689 | -13.1835 | 85.2658 | 55.7664 | 33.3465 | 86.2301 | 54.4569 | 28.547 | 87.3074 | 50.1375 | 24.9185 | 88.5726 | 45.9808 | 22.0559 | 90.0573 | 41.9028 | 18.7013 | 91.7782 | 37.8761 | 15.2256 | 93.724 | 33.9991 | 11.784 | 95.9325 | 32.9539 | 8.4255 | 97.7691 | 31.9557 | 5.1666 | 99.5794 | 31.1346 | 2.615 | 104.5519 | 28.0638 | -9.0035 | 109.3786 | 25.4079 | -24.7175 | 111.7942 | 24.8624 | -35.6999 | 113.549 | 24.271 | -44.6661 | 114.1268 | 21.8781 | -49.0267 | 85.2667 | 55.7664 | 33.3465 | 85.8679 | 54.9219 | 30.7219 | 86.6509 | 52.7249 | 27.6505 | 87.5857 | 50.3501 | 24.9317 | 88.7967 | 47.9391 | 21.6197 | 90.4531 | 44.4669 | 18.1135 | 92.446 | 40.8277 | 13.8329 | 94.6574 | 38.1962 | 7.1931 | 96.6549 | 35.6342 | 0.72546 | 98.5992 | 32.7926 | -4.8167 | 104.3923 | 27.5474 | -20.034 | 108.5383 | 22.8038 | -33.489 | 104.1451 | 18.8936 | -41.9995 | 87.9941 | 15.9635 | -45.8235 | 76.8925 | 13.9495 | -42.8174 | 85.2289 | 55.7664 | 33.3465 | 86.0241 | 55.093 | 30.8245 | 86.7976 | 51.2005 | 28.0971 | 87.6161 | 47.4144 | 25.9887 | 88.597 | 43.7199 | 23.915 | 89.9305 | 40.0176 | 21.7123 | 91.6191 | 36.3907 | 19.3693 | 93.4501 | 35.6258 | 16.8553 | 95.0456 | 34.8737 | 14.0937 | 96.7512 | 34.3018 | 11.9617 | 101.8743 | 32.5354 | 4.9542 | 105.4521 | 31.5209 | -2.5353 | 107.9631 | 32.2855 | -8.2372 | 110.0424 | 32.7825 | -13.8565 | 111.0607 | 30.733 | -18.137 | 85.2289 | 55.7664 | 33.3465 | 85.8976 | 54.559 | 29.2493 | 86.8696 | 52.218 | 25.5911 | 88.0257 | 49.7573 | 22.4939 | 89.3876 | 47.2715 | 18.8348 | 90.9504 | 43.7593 | 15.0883 | 92.8035 | 40.078 | 10.5706 | 94.9449 | 37.383 | 3.5585 | 96.9006 | 34.7848 | -3.111 | 98.7412 | 31.9115 | -8.8535 | 104.653 | 26.6153 | -24.9821 | 109.2983 | 21.8773 | -39.422 | 97.5124 | 17.6903 | -48.9751 | 79.5502 | 14.4317 | -54.0401 | 66.8459 | 12.1269 | -52.4122
HAZEL GROVE | BREDBURY | 391313 | 386877 | 133.5804 | 45.7947 | 70.2018 | 133.9636 | 44.4776 | 67.6775 | 136.1479 | 40.1991 | 64.9511 | 138.3934 | 35.9198 | 62.8216 | 139.0375 | 32.1701 | 61.9314 | 139.8304 | 26.9905 | 61.1869 | 129.0655 | 23.4145 | 60.4941 | 121.4409 | 22.0313 | 59.6711 | 112.9144 | 20.4845 | 58.5173 | 104.1421 | 18.893 | 57.4722 | 89.4813 | 16.2333 | 49.4673 | 70.2804 | 12.75 | 33.2304 | 54.1694 | 9.8272 | 20.8369 | 62.1753 | 11.2796 | 7.7757 | 77.0197 | 13.9726 | -4.0288 | 133.4279 | 45.7947 | 70.2018 | 133.7951 | 45.1093 | 69.2862 | 134.2108 | 41.2226 | 68.6878 | 134.706 | 37.6597 | 68.0616 | 135.3073 | 34.103 | 67.1475 | 135.929 | 30.6428 | 66.0979 | 126.7868 | 23.0011 | 64.7399 | 123.218 | 22.3537 | 62.9145 | 120.4819 | 21.8573 | 61.4077 | 118.8685 | 21.5646 | 59.8663 | 114.4586 | 20.7646 | 55.1838 | 120.7268 | 21.9018 | 50.4828 | 120.4273 | 21.8474 | 45.5309 | 135.5109 | 24.5838 | 40.4916 | 147.6287 | 28.3954 | 35.9351 | 133.6342 | 45.7947 | 70.2018 | 134.06 | 44.3598 | 67.4949 | 136.2636 | 39.7933 | 64.9026 | 138.5498 | 35.5276 | 63.0758 | 139.3133 | 31.5667 | 62.44 | 140.1805 | 26.6108 | 61.9879 | 126.3378 | 22.9197 | 61.613 | 118.0568 | 21.4174 | 61.1669 | 108.8909 | 19.7546 | 60.4648 | 99.3967 | 18.0321 | 59.7337 | 80.96 | 14.6874 | 48.2943 | 60.9363 | 11.0548 | 34.8431 | 41.8794 | 7.5976 | 23.5062 | 44.3757 | 8.0505 | 11.2152 | 53.5741 | 9.7192 | 0.49499 | 133.6342 | 45.7947 | 70.2018 | 133.5512 | 44.7199 | 69.597 | 133.8156 | 42.8171 | 69.1746 | 138.7651 | 40.8034 | 64.3278 | 143.192 | 38.4471 | 59.5285 | 143.637 | 35.8793 | 59.1971 | 144.406 | 33.7275 | 58.0254 | 145.3981 | 31.571 | 54.2259 | 146.3502 | 29.3028 | 49.9061 | 147.0138 | 26.6706 | 45.5389 | 124.0731 | 22.5088 | 32.3518 | 100.2047 | 18.1787 | 19.558 | 78.2488 | 14.1956 | 9.0905 | 64.7944 | 11.7547 | 2.1467 | 50.8113 | 9.218 | 5.9275 | 133.5803 | 45.7947 | 70.2018 | 133.8995 | 44.8149 | 69.0234 | 135.899 | 40.6473 | 66.7925 | 137.865 | 36.4356 | 65.0401 | 138.22 | 32.7994 | 64.7002 | 138.9004 | 27.7126 | 64.3551 | 133.3221 | 24.1868 | 63.9042 | 125.9926 | 22.8571 | 63.2985 | 117.6478 | 21.3432 | 62.2744 | 108.9523 | 19.7657 | 61.2732 | 98.4115 | 17.8534 | 57.4928 | 87.8609 | 15.9394 | 50.7413 | 79.6167 | 14.4437 | 46.8157 | 97.5404 | 17.6954 | 43.608 | 123.4477 | 22.3954 | 41.4918 | 133.5803 | 45.7947 | 70.2018 | 133.6756 | 44.4058 | 68.3422 | 134.2028 | 42.3663 | 67.2687 | 139.4622 | 40.2618 | 61.9055 | 144.1441 | 37.802 | 56.6485 | 144.6091 | 35.1176 | 56.0271 | 145.2355 | 32.8888 | 54.481 | 146.0649 | 30.6293 | 50.1971 | 146.9885 | 28.2967 | 45.5143 | 141.1464 | 25.6062 | 40.7861 | 117.1063 | 21.2449 | 26.4832 | 92.3136 | 16.7472 | 12.736 | 69.4874 | 12.6061 | 1.3407 | 55.6048 | 10.0876 | -6.7156 | 40.9292 | 7.4252 | -4.1766
HARTSHEAD-HEYROD | STALYBRIDGE | 397322 | 399942 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 0.93401 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 4.2792 | 6.7308 | 1.9358 | -3.5006 | 6.7308 | 1.9358 | 1.0867
HUNCOAT | PADIHAM | 377997 | 431083 | 65.5769 | 40.2602 | 65.5769 | 66.4164 | 38.9764 | 65.6774 | 67.5042 | 35.2946 | 62.7542 | 68.6022 | 31.3649 | 60.8831 | 69.5163 | 27.7832 | 59.0663 | 70.5808 | 24.2862 | 57.1587 | 71.7579 | 20.8436 | 55.587 | 73.1255 | 19.4654 | 53.9615 | 74.4357 | 18.8668 | 52.6156 | 75.64 | 18.6611 | 51.3072 | 78.9327 | 17.2587 | 40.8158 | 82.656 | 18.4387 | 22.6804 | 85.4303 | 26.4386 | 7.9915 | 87.7835 | 37.2107 | -7.3105 | 89.3137 | 38.6404 | -19.2666 | 65.4032 | 40.2602 | 65.4032 | 65.9234 | 39.7887 | 65.9234 | 66.4339 | 37.1144 | 66.4339 | 67.0261 | 34.7249 | 67.0261 | 67.8296 | 32.5113 | 66.3211 | 68.8295 | 30.4689 | 65.2639 | 69.5607 | 25.9619 | 64.0362 | 70.4999 | 25.3771 | 62.5168 | 71.2703 | 24.8986 | 61.3424 | 72.0916 | 24.5057 | 60.1369 | 74.6701 | 23.2877 | 55.1938 | 77.6676 | 23.051 | 49.335 | 80.7561 | 28.8471 | 43.7221 | 82.9036 | 38.1221 | 38.0165 | 84.19 | 39.6295 | 34.3344 | 65.6582 | 40.2602 | 65.6582 | 66.5454 | 38.6905 | 64.5933 | 67.7595 | 34.7113 | 61.3615 | 68.9141 | 30.6646 | 59.3245 | 69.9453 | 26.9447 | 57.3406 | 71.1249 | 23.3352 | 55.2609 | 72.415 | 19.8096 | 53.5025 | 73.9696 | 18.2954 | 51.618 | 74.9454 | 17.5946 | 50.2533 | 75.77 | 17.2411 | 48.9235 | 79.0709 | 15.3696 | 40.1967 | 82.9444 | 16.2053 | 23.66 | 85.7362 | 23.4459 | 9.7954 | 87.9982 | 33.6357 | -3.3 | 89.2099 | 34.2456 | -12.6176 | 65.6587 | 40.2602 | 65.6587 | 66.0946 | 39.2308 | 66.0946 | 66.8457 | 38.1181 | 64.91 | 67.9511 | 36.9417 | 63.0137 | 69.1799 | 35.8768 | 61.1999 | 70.3513 | 34.7919 | 59.163 | 72.0847 | 33.4109 | 56.5146 | 73.4845 | 32.4585 | 51.1238 | 74.721 | 31.3382 | 46.0987 | 75.9871 | 31.753 | 40.548 | 79.8454 | 50.684 | 23.0784 | 83.3401 | 47.4782 | 6.7116 | 85.7319 | 43.434 | -5.7685 | 87.2293 | 39.4945 | -12.9392 | 86.8047 | 37.4451 | -6.5294 | 65.5764 | 40.2602 | 65.5764 | 66.2648 | 39.5008 | 66.2648 | 67.0241 | 35.9103 | 66.1203 | 67.9133 | 32.0372 | 64.558 | 68.7534 | 28.5674 | 63.3532 | 69.4964 | 25.1563 | 61.9701 | 70.4587 | 21.7429 | 60.6577 | 71.611 | 20.383 | 59.1755 | 72.7556 | 19.784 | 57.8579 | 74.0047 | 19.5679 | 56.4901 | 77.5204 | 18.8878 | 51.8327 | 80.321 | 21.7499 | 44.9254 | 82.3521 | 31.2265 | 39.6841 | 83.8559 | 44.2913 | 35.5007 | 84.3232 | 47.2955 | 33.9317 | 65.5764 | 40.2602 | 65.5764 | 66.1436 | 38.6734 | 64.4189 | 67.1814 | 37.4223 | 61.0963 | 68.6371 | 36.1554 | 58.8527 | 69.6726 | 35.0248 | 56.7328 | 70.8275 | 33.9026 | 54.5525 | 72.4789 | 32.4907 | 51.8013 | 74.2209 | 31.5138 | 46.1631 | 75.4642 | 30.2504 | 40.9619 | 76.7328 | 30.6429 | 34.6725 | 80.693 | 49.3942 | 15.9062 | 84.378 | 46.0097 | -1.8679 | 87.001 | 41.7947 | -15.7504 | 88.6604 | 37.6585 | -24.5945 | 88.4156 | 35.3452 | -19.9514
HYDE | STALYBRIDGE | 395522 | 395647 | 46.8854 | 8.5058 | 45.7804 | 33.0783 | 6.0009 | 33.0783 | 20.4998 | 3.719 | 20.4998 | 7.8412 | 1.4225 | 7.8412 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | -3.7778 | 39.1159 | 7.0962 | -19.9935 | 78.7775 | 22.4647 | -35.7571 | 79.85 | 25.4925 | -49.2401 | 46.8854 | 8.5058 | 45.7804 | 44.4349 | 8.0612 | 44.0656 | 42.2067 | 7.657 | 42.2067 | 39.9609 | 7.2495 | 39.9609 | 36.7931 | 6.6748 | 36.7931 | 33.4169 | 6.0624 | 33.4169 | 15.4518 | 2.8032 | 15.4518 | 12.3837 | 2.2466 | 12.3837 | 9.5256 | 1.7281 | 9.5256 | 7.3291 | 1.3296 | 7.3291 | 0.79367 | 0.14399 | 0.79367 | 0.060576 | 0.010989 | 0.060576 | 35.332 | 6.4098 | 7.889 | 75.1282 | 17.541 | 1.2928 | 76.556 | 19.7979 | -2.96 | 46.8854 | 8.5058 | 45.7804 | 32.2924 | 5.8584 | 32.2924 | 18.8476 | 3.4193 | 18.8476 | 4.4933 | 0.81516 | 4.4933 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | -3.817 | 34.1188 | 6.1897 | -18.9826 | 79.7101 | 21.3581 | -33.4231 | 80.661 | 24.5343 | -45.3299 | 46.8854 | 8.5058 | 45.7804 | 34.0584 | 6.1787 | 34.0584 | 21.4816 | 3.8971 | 21.4816 | 7.6449 | 1.3869 | 7.6449 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 4.3189 | 0.78352 | 4.3189 | 71.8072 | 33.5251 | -5.1878 | 74.5595 | 30.1552 | -22.4397 | 76.4544 | 26.9605 | -36.518 | 77.7948 | 24.5799 | -45.0139 | 77.9561 | 23.6657 | -40.4149 | 46.8854 | 8.5058 | 45.7804 | 34.6253 | 6.2816 | 34.6253 | 22.508 | 4.0833 | 22.508 | 10.1556 | 1.8424 | 10.1556 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 59.8835 | 10.8638 | 9.6766 | 76.8414 | 28.0511 | 4.9026 | 77.4503 | 32.7542 | 2.78 | 46.8854 | 8.5058 | 45.7804 | 32.3669 | 5.8719 | 32.3669 | 19.2164 | 3.4862 | 19.2164 | 5.0464 | 0.91549 | 5.0464 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 0.024787 | 0.0044968 | 0.024787 | 72.7424 | 32.4139 | -12.1049 | 75.4266 | 28.9332 | -30.4769 | 77.3097 | 25.622 | -45.6899 | 78.5648 | 23.0695 | -55.5769 | 78.7488 | 21.9826 | -52.54
KEARSLEY LOCAL | KEARSLEY | 376355 | 404783 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 0.79043 | 6.7308 | 1.9358 | -22.9327 | 6.7308 | 1.9358 | -44.9114 | 6.7308 | 1.9358 | -62.7373 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 5.8467 | 6.7308 | 1.9358 | -3.1702 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.2925 | 6.7308 | 1.9358 | -17.3986 | 6.7308 | 1.9358 | -38.6033 | 6.7308 | 1.9358 | -54.5768 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | -16.3998 | 6.7308 | 1.9358 | -37.0591 | 6.7308 | 1.9358 | -49.5365 | 6.7308 | 1.9358 | -44.375 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 5.6221 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 4.1685 | 6.7308 | 1.9358 | -25.418 | 6.7308 | 1.9358 | -48.6618 | 6.7308 | 1.9358 | -63.5134 | 6.7308 | 1.9358 | -60.5531
KENDAL (PARKSIDE RD) | HARKER / HUTTON | 351915 | 491858 | 99.1778 | 33.2336 | 36.393 | 100.075 | 31.8871 | 29.3214 | 101.2884 | 31.3389 | 26.8427 | 102.7343 | 30.7995 | 25.3721 | 106.9081 | 29.3273 | 20.5512 | 108.5933 | 28.151 | 18.3478 | 113.1748 | 26.5744 | 13.8798 | 115.3804 | 25.5643 | 12.1108 | 117.3987 | 24.4413 | 9.8529 | 119.7653 | 23.2883 | 7.5224 | 105.1418 | 19.0744 | -4.7075 | 78.2365 | 14.1933 | -28.032 | 54.6561 | 9.9155 | -44.4076 | 41.7245 | 7.5695 | -63.1099 | 31.1719 | 5.6551 | -76.6331 | 98.9875 | 33.2336 | 36.393 | 99.9204 | 32.528 | 32.7796 | 101.0209 | 32.0379 | 30.81 | 102.3421 | 31.4211 | 28.9754 | 103.9733 | 30.312 | 26.8222 | 105.1491 | 29.3584 | 24.5794 | 106.5751 | 25.7681 | 21.8026 | 108.2366 | 24.5576 | 18.4061 | 109.3789 | 23.5152 | 16.1903 | 110.6034 | 22.5292 | 13.9644 | 111.7173 | 20.2673 | 7.1445 | 105.9467 | 19.2204 | -0.0010926 | 96.838 | 17.568 | -6.5973 | 88.6726 | 16.0866 | -17.5449 | 81.3386 | 14.7561 | -23.3685 | 99.2579 | 33.2336 | 36.393 | 100.1705 | 31.6881 | 28.5293 | 101.4583 | 31.0279 | 26.0423 | 102.9677 | 30.3189 | 24.8631 | 107.1364 | 28.6622 | 20.4485 | 108.9273 | 27.3217 | 18.6031 | 113.5001 | 25.6382 | 14.7782 | 115.6956 | 24.4748 | 13.5831 | 117.9105 | 23.2158 | 11.8697 | 119.8884 | 21.9592 | 10.5134 | 88.7268 | 16.0964 | -13.016 | 60.256 | 10.9314 | -30.822 | 34.9698 | 6.3441 | -45.3469 | 20.5772 | 3.733 | -58.3168 | 5.6286 | 1.0211 | -69.4849 | 99.2583 | 33.2336 | 36.393 | 99.5125 | 32.249 | 32.1347 | 100.2047 | 31.9178 | 30.5314 | 108.3993 | 30.4132 | 22.0633 | 111.5664 | 28.6316 | 18.3068 | 113.0024 | 25.0968 | 16.5275 | 108.757 | 19.7302 | 14.0239 | 86.3288 | 15.6614 | 8.388 | 60.6564 | 11.004 | 1.5098 | 34.5404 | 6.2662 | -5.118 | 10.6707 | 1.9358 | -24.4709 | 10.6707 | 1.9358 | -41.5547 | 10.6707 | 1.9358 | -54.4277 | 10.6707 | 1.9358 | -61.2627 | 10.6707 | 1.9358 | -54.512 | 99.1774 | 33.2336 | 36.393 | 99.9302 | 32.2056 | 31.3681 | 100.8339 | 31.778 | 29.4113 | 101.8631 | 31.297 | 28.2765 | 105.7156 | 29.954 | 24.3297 | 107.128 | 28.8999 | 23.0621 | 111.5396 | 27.3897 | 19.1565 | 113.6036 | 26.4109 | 17.6068 | 115.2662 | 25.2971 | 15.306 | 117.3313 | 24.1229 | 12.7405 | 112.6692 | 20.44 | 4.7052 | 92.0468 | 16.6988 | -7.6565 | 72.978 | 13.2394 | -13.9354 | 70.0161 | 12.702 | -22.0914 | 68.2961 | 12.39 | -23.5518 | 99.1774 | 33.2336 | 36.393 | 99.7243 | 31.7 | 28.7996 | 100.857 | 31.213 | 26.0793 | 109.5335 | 29.6293 | 16.9143 | 113.0276 | 27.7753 | 12.5055 | 114.5477 | 24.2152 | 10.2523 | 104.1523 | 18.8949 | 7.2087 | 80.4676 | 14.5981 | 0.87036 | 54.7816 | 9.9382 | -6.3443 | 28.6856 | 5.204 | -13.3173 | 10.6707 | 1.9358 | -33.9692 | 10.6707 | 1.9358 | -52.4304 | 10.6707 | 1.9358 | -66.6704 | 10.6707 | 1.9358 | -75.001 | 10.6707 | 1.9358 | -69.7901
LANCASTER | HEYSHAM | 348644 | 463628 | 53.3672 | 21.0102 | 22.9917 | 54.1289 | 19.5195 | 15.0245 | 56.7852 | 17.5362 | 8.1318 | 57.8111 | 14.9669 | 4.2949 | 59.0807 | 10.8999 | -0.29264 | 24.6502 | 4.4719 | -5.0966 | 10.6707 | 1.9358 | -10.4328 | 10.6707 | 1.9358 | -16.2747 | 10.6707 | 1.9358 | -20.3696 | 10.6707 | 1.9358 | -23.0741 | 10.6707 | 1.9358 | -38.9511 | 10.6707 | 1.9358 | -105.8158 | 10.6707 | 1.9358 | -123.1728 | 10.6707 | 1.9358 | -143.2502 | 10.6707 | 1.9358 | -157.6164 | 53.2171 | 21.0102 | 22.9917 | 53.7841 | 20.2417 | 18.9588 | 54.514 | 17.0009 | 16.7984 | 55.2964 | 13.6406 | 14.7125 | 55.7329 | 10.1108 | 12.2608 | 36.1077 | 6.5505 | 9.7771 | 10.6707 | 1.9358 | 6.5685 | 10.6707 | 1.9358 | 3.064 | 10.6707 | 1.9358 | 0.079666 | 10.6707 | 1.9358 | -2.6747 | 10.6707 | 1.9358 | -11.2624 | 10.6707 | 1.9358 | -21.4344 | 10.6707 | 1.9358 | -30.168 | 10.6707 | 1.9358 | -40.0858 | 10.6707 | 1.9358 | -48.4897 | 53.4297 | 21.0102 | 22.9917 | 54.1847 | 19.1879 | 14.1542 | 56.8208 | 16.7968 | 7.3241 | 57.8987 | 13.8677 | 3.8266 | 52.9903 | 9.6133 | -0.40291 | 17.1031 | 3.1028 | -4.7713 | 10.6707 | 1.9358 | -10.608 | 10.6707 | 1.9358 | -15.6688 | 10.6707 | 1.9358 | -18.6912 | 10.6707 | 1.9358 | -20.5837 | 10.6707 | 1.9358 | -36.8157 | 10.6707 | 1.9358 | -101.5876 | 10.6707 | 1.9358 | -118.0556 | 10.6707 | 1.9358 | -136.1244 | 1.8124 | 0.74444 | -148.4253 | 53.4302 | 21.0102 | 22.9917 | 53.5818 | 19.8568 | 18.2941 | 54.2859 | 18.0361 | 14.0316 | 58.5563 | 14.6509 | 7.0131 | 61.9029 | 11.2302 | -0.017809 | 41.4485 | 7.5194 | -5.4175 | 10.6707 | 1.9358 | -11.4329 | 10.6707 | 1.9358 | -19.9504 | 10.6707 | 1.9358 | -29.2388 | 10.6707 | 1.9358 | -37.4356 | 6.7308 | 1.9358 | -103.1058 | 6.7308 | 1.9358 | -124.2333 | 6.7308 | 1.9358 | -138.7437 | 6.7308 | 1.9358 | -148.2584 | 6.7308 | 1.9358 | -137.9159 | 53.3667 | 21.0102 | 22.9917 | 53.9824 | 19.8828 | 17.107 | 56.3611 | 18.0087 | 10.823 | 57.0594 | 15.5258 | 7.4882 | 57.8803 | 11.6192 | 3.9214 | 29.5183 | 5.3551 | 0.19455 | 10.6707 | 1.9358 | -4.3633 | 10.6707 | 1.9358 | -9.7876 | 10.6707 | 1.9358 | -13.7629 | 10.6707 | 1.9358 | -16.5421 | 10.6707 | 1.9358 | -26.4033 | 10.6707 | 1.9358 | -78.6852 | 10.6707 | 1.9358 | -83.0422 | 10.6707 | 1.9358 | -88.8131 | 10.6707 | 1.9358 | -87.6118 | 53.3667 | 21.0102 | 22.9917 | 53.648 | 19.2659 | 14.7096 | 54.6076 | 17.2542 | 7.2151 | 59.1418 | 13.7571 | -2.5544 | 56.5172 | 10.2531 | -12.2594 | 35.7865 | 6.4922 | -20.1032 | 10.6707 | 1.9358 | -28.6143 | 10.6707 | 1.9358 | -39.7628 | 10.6707 | 1.9358 | -52.4248 | 10.1582 | 1.9358 | -64.0211 | 6.7308 | 1.9358 | -138.362 | 6.7308 | 1.9358 | -161.278 | 6.7308 | 1.9358 | -177.6436 | 6.7308 | 1.9358 | -189.161 | 6.7308 | 1.9358 | -180.8159
LEYLAND | PENWORTHAM WEST / STANAH | 354121 | 423373 | 128.9035 | 43.6226 | 48.0513 | 129.455 | 40.9757 | 35.5327 | 130.3124 | 38.1907 | 29.5913 | 131.3001 | 35.8992 | 25.7985 | 132.5219 | 32.9688 | 21.6199 | 134.0321 | 29.5624 | 17.785 | 135.9171 | 26.8072 | 15.8181 | 138.3046 | 25.3217 | 13.7388 | 134.1817 | 24.3427 | 10.817 | 129.4148 | 23.4779 | 7.8914 | 109.9765 | 19.9515 | -7.6902 | 91.4964 | 16.5989 | -27.1692 | 80.2364 | 14.5562 | -42.2938 | 75.2301 | 13.6479 | -57.0578 | 63.4032 | 11.5024 | -69.2389 | 128.74 | 43.6226 | 48.0513 | 129.1905 | 42.4949 | 42.9955 | 129.7351 | 40.6597 | 40.2512 | 130.2966 | 39.0266 | 38.3413 | 130.9725 | 37.3613 | 36.2683 | 131.8162 | 35.7404 | 34.2068 | 132.8642 | 30.02 | 32.22 | 134.1248 | 29.27 | 29.6515 | 135.3408 | 28.5593 | 26.923 | 136.6964 | 27.9867 | 24.0888 | 141.6227 | 26.3014 | 15.0892 | 144.6811 | 26.2475 | 5.5012 | 143.5956 | 26.0505 | -3.6566 | 143.3093 | 25.9986 | -13.4159 | 138.581 | 25.1408 | -23.4944 | 128.9472 | 43.6226 | 48.0513 | 129.5129 | 40.5192 | 33.7906 | 130.4128 | 37.4842 | 25.4254 | 131.4559 | 35.0191 | 18.5708 | 132.7235 | 32.0438 | 11.3393 | 134.2563 | 28.603 | 5.652 | 136.1328 | 25.9415 | 4.2635 | 134.6541 | 24.4284 | 2.8606 | 129.4783 | 23.4894 | 0.90453 | 124.6253 | 22.609 | -1.2667 | 103.5773 | 18.7906 | -15.4319 | 81.8604 | 14.8508 | -35.5778 | 68.9131 | 12.5019 | -49.6969 | 61.1809 | 11.0992 | -62.8329 | 51.9948 | 9.4327 | -72.4899 | 128.9475 | 43.6226 | 48.0513 | 129.0712 | 41.5273 | 39.0508 | 129.6634 | 39.9637 | 31.8523 | 130.3837 | 38.5287 | 25.2106 | 131.3954 | 36.9723 | 18.0176 | 132.9078 | 35.6454 | 12.1313 | 134.9528 | 34.0396 | 9.5435 | 139.9033 | 31.9615 | 1.6877 | 146.0593 | 30.1261 | -8.0615 | 148.1304 | 28.1027 | -14.1449 | 132.2754 | 23.9969 | -32.2682 | 112.8435 | 20.4716 | -49.186 | 95.7391 | 17.3686 | -61.5384 | 86.119 | 15.6234 | -68.8705 | 76.7094 | 13.9163 | -64.0164 | 128.9033 | 43.6226 | 48.0513 | 129.3525 | 41.6516 | 39.1439 | 130.0012 | 39.0114 | 34.1052 | 130.6555 | 36.7904 | 30.8281 | 131.4669 | 34.0038 | 27.5242 | 132.6821 | 30.7116 | 24.42 | 134.3138 | 28.05 | 22.9543 | 136.2479 | 26.6333 | 21.306 | 138.294 | 25.7072 | 18.6716 | 137.1495 | 24.8811 | 15.9204 | 121.4508 | 22.0331 | 4.7716 | 109.5239 | 19.8694 | -5.0207 | 103.8031 | 18.8315 | -11.5376 | 104.3853 | 18.9372 | -16.778 | 103.7648 | 18.8246 | -18.8844 | 128.9033 | 43.6226 | 48.0513 | 129.1432 | 40.3763 | 32.9687 | 129.9393 | 38.5559 | 24.2408 | 130.8897 | 37.046 | 17.0044 | 132.0495 | 35.1501 | 7.4583 | 133.4366 | 33.5817 | 0.40204 | 135.2148 | 31.7889 | -3.3748 | 139.9939 | 29.5068 | -12.5651 | 146.0028 | 27.6353 | -22.8708 | 141.1973 | 25.6154 | -29.2081 | 118.4741 | 21.4931 | -48.6095 | 98.496 | 17.8687 | -67.248 | 80.7607 | 14.6513 | -81.2921 | 69.1398 | 12.5431 | -90.2463 | 58.8907 | 10.6837 | -86.8493
LONGSIGHT | BREDBURY | 385592 | 396016 | 149.6259 | 51.4442 | 51.5719 | 149.9812 | 48.6377 | 39.3221 | 150.6034 | 42.7635 | 28.39 | 151.1333 | 37.458 | 18.7006 | 151.6377 | 32.8437 | 8.7747 | 147.525 | 26.7634 | 2.5173 | 122.8499 | 22.2869 | -1.9762 | 112.5953 | 20.4266 | -7.8487 | 103.3031 | 18.7408 | -9.2713 | 94.0732 | 17.0664 | -10.633 | 81.037 | 14.7014 | -19.5924 | 72.2831 | 13.1133 | -30.7337 | 77.0919 | 13.9857 | -38.9298 | 98.1787 | 17.8112 | -46.4274 | 108.6182 | 19.7051 | -51.4774 | 149.5666 | 51.4442 | 51.5719 | 149.8404 | 50.3499 | 45.7724 | 150.3755 | 44.8955 | 36.9429 | 150.7824 | 40.1003 | 27.7313 | 151.1571 | 35.4921 | 18.5294 | 151.6046 | 30.9288 | 13.1181 | 119.5848 | 21.6946 | 9.0415 | 116.7357 | 21.1777 | 4.6004 | 114.1903 | 20.7159 | 3.2286 | 112.8655 | 20.4756 | 1.8314 | 109.4629 | 19.8583 | -2.3294 | 118.423 | 21.4838 | -6.6197 | 129.2995 | 23.457 | -10.4943 | 148.1332 | 26.8737 | -14.6873 | 158.7118 | 28.7929 | -18.1957 | 149.6507 | 51.4442 | 51.5719 | 150.1092 | 48.1546 | 37.6599 | 150.8515 | 42.0432 | 26.0393 | 151.5328 | 36.7247 | 15.9753 | 152.1672 | 31.7507 | 5.5555 | 142.877 | 25.9202 | -1.2242 | 117.5149 | 21.3191 | -6.2006 | 106.3185 | 19.2879 | -12.5159 | 95.9153 | 17.4006 | -14.2506 | 85.9139 | 15.5862 | -16.0008 | 70.9606 | 12.8734 | -26.1576 | 60.6485 | 11.0026 | -38.3238 | 65.0807 | 11.8067 | -45.2534 | 85.8745 | 15.579 | -50.4965 | 97.8346 | 17.7487 | -51.8334 | 149.6508 | 51.4442 | 51.5719 | 149.7949 | 48.8435 | 41.5006 | 150.3553 | 46.7445 | 30.7439 | 150.8413 | 44.7287 | 20.8175 | 151.3374 | 43.1935 | 10.4621 | 151.8511 | 42.0255 | 3.7066 | 152.4679 | 41.2621 | -1.8777 | 156.9419 | 39.7457 | -12.7287 | 159.106 | 38.5695 | -18.4066 | 159.6453 | 37.2642 | -22.2721 | 161.5012 | 33.6222 | -33.1366 | 163.0599 | 30.1769 | -42.1562 | 151.4495 | 27.4754 | -47.304 | 140.4101 | 25.4726 | -48.8873 | 132.3923 | 24.0181 | -44.841 | 149.6258 | 51.4442 | 51.5719 | 149.9466 | 49.5889 | 43.5939 | 150.4861 | 43.9089 | 33.6112 | 150.8864 | 38.6247 | 24.131 | 151.2428 | 34.088 | 14.6219 | 151.7279 | 28.0997 | 8.8873 | 130.5193 | 23.6783 | 4.7635 | 120.4825 | 21.8575 | -0.94811 | 111.2052 | 20.1744 | -2.3922 | 101.8881 | 18.4841 | -3.9022 | 91.2824 | 16.5601 | -10.4507 | 88.5576 | 16.0658 | -15.4278 | 98.4757 | 17.8651 | -18.6759 | 124.838 | 22.6476 | -21.7499 | 139.9621 | 25.3914 | -23.1926 | 149.6258 | 51.4442 | 51.5719 | 149.8526 | 47.8949 | 37.0949 | 150.5314 | 45.5462 | 25.2314 | 151.1567 | 43.4766 | 15.0214 | 151.7677 | 41.8748 | 4.4025 | 152.3054 | 40.6032 | -2.5481 | 152.9175 | 39.7873 | -8.3654 | 157.4457 | 38.2169 | -19.5266 | 159.6152 | 37.0076 | -25.3234 | 160.1511 | 35.6838 | -29.4137 | 162.0246 | 31.9313 | -40.9128 | 156.3976 | 28.373 | -50.5123 | 140.9477 | 25.5702 | -56.2742 | 129.2191 | 23.4424 | -58.6402 | 120.492 | 21.8592 | -55.5559
LOWER DARWEN | ROCHDALE | 369695 | 424981 | 64.9439 | 11.7819 | 62.317 | 60.5656 | 10.9876 | 56.0422 | 57.6968 | 10.4671 | 53.8585 | 55.1443 | 10.0041 | 52.4929 | 52.5775 | 9.5384 | 50.868 | 47.4435 | 8.607 | 47.4435 | 41.4818 | 7.5255 | 41.4818 | 37.3853 | 6.7823 | 37.3853 | 32.5843 | 5.9113 | 32.5843 | 29.3136 | 5.318 | 29.3136 | 16.8665 | 3.0599 | 16.8665 | 16.1879 | 2.9367 | 11.651 | 40.0934 | 7.2736 | -1.9084 | 85.3361 | 15.4813 | -14.3838 | 86.6578 | 17.0693 | -23.383 | 64.9439 | 11.7819 | 62.317 | 65.1797 | 11.8246 | 59.9234 | 66.5392 | 12.0713 | 59.059 | 66.5262 | 12.0689 | 58.3702 | 63.949 | 11.6014 | 57.5022 | 61.1834 | 11.0996 | 56.5229 | 39.0704 | 7.088 | 39.0704 | 36.2767 | 6.5812 | 36.2767 | 33.4579 | 6.0698 | 33.4579 | 31.4537 | 5.7062 | 31.4537 | 25.912 | 4.7008 | 25.912 | 28.3075 | 5.1354 | 28.3075 | 51.4845 | 9.3401 | 34.9802 | 86.3028 | 15.6567 | 29.9229 | 93.2628 | 16.9194 | 26.7284 | 64.9439 | 11.7819 | 62.317 | 59.1779 | 10.7358 | 55.0256 | 54.9976 | 9.9774 | 52.4463 | 51.4023 | 9.3252 | 50.9002 | 48.0402 | 8.7153 | 48.0402 | 42.2776 | 7.6698 | 42.2776 | 35.7609 | 6.4876 | 35.7609 | 30.8801 | 5.6021 | 30.8801 | 25.5144 | 4.6287 | 25.5144 | 21.6071 | 3.9199 | 21.6071 | 6.0843 | 1.1038 | 6.0843 | 2.4657 | 0.44731 | 2.4657 | 29.1334 | 5.2853 | -3.2659 | 74.2201 | 13.4647 | -13.4913 | 79.0938 | 14.9145 | -19.1258 | 64.9439 | 11.7819 | 62.317 | 61.6303 | 11.1807 | 58.0675 | 60.079 | 10.8993 | 56.0691 | 57.3325 | 10.401 | 54.7111 | 52.4725 | 9.5193 | 52.4725 | 46.9481 | 8.5171 | 46.9481 | 40.2589 | 7.3036 | 40.2589 | 41.7184 | 7.5684 | 39.3557 | 42.5369 | 7.7169 | 33.3345 | 44.7551 | 8.1193 | 26.2837 | 108.4597 | 23.6416 | 8.8517 | 98.6118 | 20.2277 | -4.9787 | 91.2761 | 17.7329 | -14.6142 | 85.5507 | 16.7502 | -19.1105 | 81.1347 | 15.6473 | -12.689 | 64.9439 | 11.7819 | 62.317 | 62.5125 | 11.3408 | 58.0651 | 60.1951 | 10.9204 | 56.4052 | 58.0044 | 10.5229 | 55.3889 | 56.0614 | 10.1704 | 54.4761 | 51.4382 | 9.3317 | 51.4382 | 45.6708 | 8.2854 | 45.6708 | 41.6661 | 7.5589 | 41.6661 | 37.0002 | 6.7124 | 37.0002 | 33.7304 | 6.1192 | 33.7304 | 24.068 | 4.3663 | 24.068 | 29.2101 | 5.2992 | 29.2101 | 61.5977 | 11.1748 | 26.3934 | 102.4969 | 21.1362 | 23.0761 | 104.1509 | 23.8298 | 21.6762 | 64.9439 | 11.7819 | 62.317 | 59.013 | 10.7059 | 55.2666 | 56.7364 | 10.2929 | 52.4305 | 53.791 | 9.7585 | 50.6255 | 48.7542 | 8.8448 | 48.4692 | 43.2167 | 7.8402 | 43.2167 | 35.6363 | 6.465 | 35.6363 | 36.092 | 6.5477 | 33.8886 | 35.9742 | 6.5263 | 27.6283 | 38.315 | 6.951 | 20.3283 | 105.5152 | 22.4569 | 1.9002 | 95.1799 | 18.8874 | -13.1287 | 87.3392 | 16.2462 | -24.0625 | 81.0701 | 15.0842 | -29.9993 | 76.2345 | 13.8301 | -25.1078
LYTHAM | PENWORTHAM WEST / STANAH | 335361 | 429316 | 19.0678 | 19.0678 | -3.0454 | 19.3756 | 19.3756 | -5.1867 | 19.8285 | 19.8285 | -6.0483 | 20.3948 | 20.3948 | -6.7015 | 21.0245 | 21.0245 | -7.505 | 21.4479 | 21.4479 | -8.3317 | 21.9166 | 21.9166 | -9.1033 | 22.4571 | 22.4571 | -9.7925 | 22.8774 | 22.8774 | -10.4132 | 23.273 | 23.273 | -10.9378 | 24.7685 | 24.7685 | -15.0609 | 26.4915 | 26.4915 | -22.645 | 27.4598 | 27.4598 | -28.7751 | 28.276 | 27.2634 | -35.3945 | 28.8057 | 25.3831 | -41.2773 | 18.9602 | 18.9602 | -3.0454 | 19.185 | 19.185 | -4.1514 | 19.4259 | 19.4259 | -4.9235 | 19.7296 | 19.7296 | -5.585 | 20.1398 | 20.1398 | -6.3487 | 20.6428 | 20.6428 | -7.0447 | 21.235 | 21.235 | -7.9131 | 21.9 | 21.9 | -9.0007 | 22.3103 | 22.3103 | -9.8125 | 22.7346 | 22.7346 | -10.6191 | 23.6223 | 23.6223 | -12.988 | 24.4385 | 24.4385 | -15.327 | 25.1808 | 25.1808 | -17.4305 | 25.9653 | 25.9653 | -19.7209 | 26.5556 | 26.5556 | -21.4157 | 19.1173 | 19.1173 | -3.0454 | 19.468 | 19.468 | -5.3932 | 19.9913 | 19.9913 | -6.239 | 20.6617 | 20.6617 | -6.781 | 21.1664 | 21.1664 | -7.4797 | 21.6422 | 21.6422 | -8.1883 | 22.1751 | 22.1751 | -8.7811 | 22.7918 | 22.7918 | -9.2915 | 23.2433 | 23.2433 | -9.6398 | 23.6635 | 23.6635 | -9.9525 | 25.2442 | 25.2442 | -13.4074 | 26.7974 | 26.7974 | -20.4116 | 27.9217 | 27.9217 | -25.9989 | 28.8193 | 26.0539 | -31.9065 | 29.2611 | 24.2679 | -36.9644 | 19.1173 | 19.1173 | -3.0454 | 19.1502 | 19.1502 | -4.0675 | 19.4006 | 19.4006 | -4.5737 | 19.7459 | 19.7459 | -4.9914 | 20.2488 | 20.2488 | -5.6344 | 20.8664 | 20.8664 | -6.3419 | 21.3939 | 21.3939 | -7.3848 | 22.0455 | 22.0455 | -9.7964 | 22.5612 | 22.5612 | -12.1744 | 23.0637 | 23.0637 | -14.5581 | 24.5795 | 24.5795 | -21.4225 | 26.0633 | 26.0633 | -28.0712 | 26.9568 | 26.9568 | -33.1774 | 27.6118 | 27.6118 | -36.3497 | 27.6381 | 26.8405 | -33.8138 | 19.0678 | 19.0678 | -3.0454 | 19.331 | 19.331 | -4.487 | 19.6412 | 19.6412 | -5.1414 | 19.9907 | 19.9907 | -5.6358 | 20.4425 | 20.4425 | -6.1694 | 21.0602 | 21.0602 | -6.6887 | 21.4843 | 21.4843 | -7.1913 | 21.9444 | 21.9444 | -7.706 | 22.311 | 22.311 | -8.2778 | 22.6731 | 22.6731 | -8.8188 | 23.8206 | 23.8206 | -10.6565 | 25.0306 | 25.0306 | -12.7661 | 25.8965 | 25.8965 | -14.121 | 26.5713 | 26.5713 | -15.4509 | 26.9058 | 26.9058 | -16.1082 | 19.0678 | 19.0678 | -3.0454 | 19.2171 | 19.2171 | -5.046 | 19.6468 | 19.6468 | -5.9181 | 20.2075 | 20.2075 | -6.587 | 20.8798 | 20.8798 | -7.4629 | 21.3084 | 21.3084 | -8.34 | 21.8382 | 21.8382 | -9.5953 | 22.6144 | 22.6144 | -12.2767 | 23.1597 | 23.1597 | -14.8191 | 23.6826 | 23.6826 | -17.3701 | 25.193 | 25.193 | -24.7564 | 26.5399 | 26.5399 | -31.8417 | 27.372 | 27.372 | -37.4357 | 27.9432 | 26.8002 | -41.1967 | 27.9746 | 25.6709 | -39.3175
MACCLESFIELD | MACCLESFIELD | 392047 | 374564 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | -5.7485 | 10.6707 | 1.9358 | -16.7772 | 10.6707 | 1.9358 | -28.4274 | 10.6707 | 1.9358 | -38.7553 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 6.7326 | 10.6707 | 1.9358 | 1.79 | 10.6707 | 1.9358 | -3.4955 | 10.6707 | 1.9358 | -7.921 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | -15.039 | 10.6707 | 1.9358 | -25.0349 | 10.6707 | 1.9358 | -35.7036 | 10.6707 | 1.9358 | -44.8701 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 5.7351 | 10.6707 | 1.9358 | -9.4085 | 10.6707 | 1.9358 | -21.3008 | 10.6707 | 1.9358 | -30.6991 | 10.6707 | 1.9358 | -36.8514 | 10.6707 | 1.9358 | -33.6341 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 7.274 | 10.6707 | 1.9358 | 3.2122 | 10.6707 | 1.9358 | -0.72159 | 10.6707 | 1.9358 | -2.8233 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 2.2861 | 10.6707 | 1.9358 | -13.8619 | 10.6707 | 1.9358 | -26.6414 | 10.6707 | 1.9358 | -36.9089 | 10.6707 | 1.9358 | -44.0812 | 10.6707 | 1.9358 | -42.0074
MOSS NOOK | SOUTH MANCHESTER | 384073 | 385068 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 2.5505 | 1.0476 | 2.5505 | -4.2134 | -1.7306 | -4.2134 | -11.0901 | -4.5552 | -11.0901 | -18.0456 | -7.4121 | -18.0456 | -27.3184 | -11.2208 | -27.3184 | -38.1407 | -15.666 | -38.1407 | -46.6998 | -19.1816 | -46.6998 | -50.1599 | -20.6028 | -50.1599 | -58.3667 | -23.9737 | -58.3667 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 8.4262 | 1.9358 | 8.4262 | 6.6339 | 1.9358 | 6.6339 | 5.0269 | 1.9358 | 5.0269 | 3.7169 | 1.5267 | 3.7169 | 0.88815 | 0.3648 | 0.88815 | 3.5779 | 1.4696 | 3.5779 | 3.7787 | 1.5521 | 3.7787 | 5.2836 | 1.9358 | 5.2836 | 5.9004 | 1.9358 | 5.9004 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 8.4224 | 1.9358 | 8.4224 | -0.53315 | -0.21899 | -0.53315 | -7.5502 | -3.1012 | -7.5502 | -14.7287 | -6.0497 | -14.7287 | -22.0457 | -9.0551 | -22.0457 | -32.3518 | -13.2882 | -32.3518 | -43.717 | -17.9564 | -43.717 | -52.9941 | -21.7669 | -52.9941 | -57.1088 | -23.457 | -57.1088 | -65.4959 | -26.902 | -65.4959 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 8.9649 | 1.9358 | 8.9649 | 0.43885 | 0.18026 | 0.43885 | -14.6925 | -6.0348 | -14.6925 | -29.5231 | -12.1264 | -29.5231 | -42.2868 | -17.369 | -42.2868 | -49.1338 | -20.1813 | -49.1338 | -58.4802 | -24.0203 | -58.4802 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 5.1674 | 1.9358 | 5.1674 | -1.4472 | -0.59444 | -1.4472 | -8.2514 | -3.3892 | -8.2514 | -15.1806 | -6.2353 | -15.1806 | -22.7993 | -9.3646 | -22.7993 | -29.6601 | -12.1827 | -29.6601 | -34.7879 | -14.2889 | -34.7879 | -34.26 | -14.0721 | -34.26 | -38.0191 | -15.6161 | -38.0191 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.0013 | 1.9358 | 10.0013 | 6.2583 | 1.9358 | 6.2583 | -2.4327 | -0.99922 | -2.4327 | -18.2069 | -7.4783 | -18.2069 | -33.5652 | -13.7866 | -33.5652 | -46.7532 | -19.2035 | -46.7532 | -54.1761 | -22.2524 | -54.1761 | -63.9372 | -26.2617 | -63.9372
NELSON | PADIHAM | 385989 | 438643 | 43.5951 | 7.9088 | 33.7728 | 38.9644 | 7.0688 | 30.3313 | 25.1468 | 4.562 | 25.1468 | 3.0825 | 0.55922 | 3.0825 | -11.5218 | -2.0902 | -11.5218 | -23.488 | -4.2611 | -23.488 | -37.4798 | -6.7994 | -37.4798 | -45.9059 | -8.3281 | -45.9059 | -49.1525 | -8.917 | -49.1525 | -51.8232 | -9.4016 | -51.8232 | -63.9418 | -11.6001 | -63.9418 | -78.5528 | -14.2507 | -78.5528 | -86.9581 | -15.7756 | -86.9581 | -95.4496 | -17.3161 | -95.4496 | -113.1727 | -20.5313 | -113.1727 | 43.5951 | 7.9088 | 33.7728 | 41.9482 | 7.6101 | 32.5993 | 33.5101 | 6.0793 | 31.7739 | 25.8197 | 4.6841 | 25.8197 | 18.0773 | 3.2795 | 18.0773 | 10.7111 | 1.9432 | 10.7111 | -10.5332 | -1.9109 | -10.5332 | -13.6676 | -2.4795 | -13.6676 | -16.319 | -2.9605 | -16.319 | -18.5447 | -3.3643 | -18.5447 | -24.986 | -4.5329 | -24.986 | -24.8059 | -4.5002 | -24.8059 | -26.7626 | -4.8552 | -26.7626 | -27.0783 | -4.9124 | -27.0783 | -27.9773 | -5.0755 | -27.9773 | 43.5951 | 7.9088 | 33.7728 | 37.9091 | 6.8773 | 29.8301 | 22.5689 | 4.0944 | 22.5689 | -2.2247 | -0.4036 | -2.2247 | -12.533 | -2.2737 | -12.533 | -26.4711 | -4.8023 | -26.4711 | -41.2142 | -7.4769 | -41.2142 | -50.0727 | -9.084 | -50.0727 | -53.5507 | -9.7149 | -53.5507 | -57.18 | -10.3734 | -57.18 | -71.2472 | -12.9254 | -71.2472 | -86.2183 | -15.6414 | -86.2183 | -94.4457 | -17.134 | -94.4457 | -108.9822 | -19.7711 | -108.9822 | -116.8652 | -21.2012 | -116.8652 | 43.5951 | 7.9088 | 33.7728 | 39.5075 | 7.1673 | 31.785 | 34.9941 | 6.3485 | 30.8555 | 27.2659 | 4.9465 | 27.2659 | 25.2495 | 4.5807 | 25.2495 | 21.7978 | 3.9545 | 21.7978 | 15.3336 | 2.7818 | 15.3336 | -5.2417 | -0.95092 | -5.2417 | -15.8605 | -2.8773 | -15.8605 | -29.7609 | -5.3991 | -29.7609 | -50.2711 | -9.12 | -50.2711 | -63.2123 | -11.4677 | -63.2123 | -80.9173 | -14.6797 | -80.9173 | -94.6008 | -17.1621 | -94.6008 | -99.1335 | -17.9844 | -99.1335 | 43.5951 | 7.9088 | 33.7728 | 40.6571 | 7.3759 | 32.1419 | 27.2252 | 4.9391 | 27.2252 | 5.2941 | 0.96044 | 5.2941 | -8.5767 | -1.556 | -8.5767 | -20.2205 | -3.6683 | -20.2205 | -34.1141 | -6.1888 | -34.1141 | -42.4845 | -7.7074 | -42.4845 | -45.7787 | -8.305 | -45.7787 | -48.5587 | -8.8093 | -48.5587 | -58.0312 | -10.5278 | -58.0312 | -66.0448 | -11.9816 | -66.0448 | -65.049 | -11.8009 | -65.049 | -67.6204 | -12.2674 | -67.6204 | -69.5574 | -12.6188 | -69.5574 | 43.5951 | 7.9088 | 33.7728 | 37.8872 | 6.8733 | 30.0961 | 32.8491 | 5.9593 | 28.6167 | 24.6044 | 4.4636 | 24.6044 | 22.319 | 4.049 | 22.319 | 18.7143 | 3.3951 | 18.7143 | 12.1654 | 2.207 | 12.1654 | -9.3719 | -1.7002 | -9.3719 | -19.6671 | -3.5679 | -19.6671 | -33.2873 | -6.0388 | -33.2873 | -54.5657 | -9.8991 | -54.5657 | -68.0833 | -12.3514 | -68.0833 | -86.0879 | -15.6177 | -86.0879 | -102.6437 | -18.6212 | -102.6437 | -107.6348 | -19.5267 | -107.6348 | Switchgear to be replaced in RIIO-ED2
NEW MILLS | STALYBRIDGE | 401141 | 383916 | 52.8888 | 52.8888 | 24.9959 | 53.029 | 53.029 | 24.1554 | 53.2275 | 53.2275 | 23.6722 | 53.475 | 53.475 | 23.3722 | 53.7861 | 53.7861 | 22.9095 | 54.1562 | 54.1562 | 22.4253 | 54.7546 | 54.7546 | 21.8437 | 55.3011 | 55.3011 | 21.4472 | 55.7708 | 55.7708 | 20.8575 | 56.2452 | 56.2452 | 20.3103 | 57.5889 | 57.5889 | 16.6467 | 58.7578 | 57.2656 | 10.3511 | 59.6003 | 56.7391 | 5.149 | 60.3316 | 56.8575 | -0.17989 | 60.8493 | 55.5469 | -4.62 | 52.8231 | 52.8231 | 24.9959 | 52.997 | 52.997 | 24.5404 | 53.1661 | 53.1661 | 24.0981 | 53.3731 | 53.3731 | 23.7136 | 53.6431 | 53.6431 | 23.265 | 53.9806 | 53.9806 | 22.7818 | 54.3895 | 54.3895 | 22.1558 | 54.867 | 54.867 | 21.3511 | 55.1048 | 55.1048 | 20.6368 | 55.3609 | 55.3609 | 19.9136 | 56.3597 | 56.3597 | 17.5878 | 57.2988 | 57.2988 | 15.376 | 58.1866 | 58.1866 | 13.2886 | 59.0979 | 59.0979 | 10.8659 | 59.6081 | 59.6081 | 9.1946 | 52.9046 | 52.9046 | 24.9959 | 53.056 | 53.056 | 24.115 | 53.2738 | 53.2738 | 23.6679 | 53.5494 | 53.5494 | 23.4698 | 54.0591 | 54.0591 | 22.9335 | 54.4583 | 54.4583 | 22.5754 | 54.9368 | 54.9368 | 22.3327 | 55.531 | 55.531 | 22.1222 | 56.0101 | 56.0101 | 21.8004 | 56.4927 | 56.4927 | 21.4641 | 60.647 | 57.8591 | 15.2073 | 61.9477 | 56.9289 | 9.311 | 62.8601 | 56.2232 | 4.5096 | 63.5752 | 55.7606 | -0.25117 | 64.0149 | 54.2637 | -3.9944 | 52.9046 | 52.9046 | 24.9959 | 52.879 | 52.879 | 24.86 | 53.1525 | 53.1525 | 24.4302 | 53.2782 | 53.2782 | 24.2933 | 53.4844 | 53.4844 | 23.9739 | 57.4163 | 57.4163 | 19.8108 | 57.6905 | 56.4379 | 19.3311 | 58.0723 | 53.9613 | 17.6866 | 58.4649 | 53.6438 | 15.8318 | 58.8743 | 53.3492 | 13.9536 | 60.3676 | 52.7342 | 8.2381 | 61.6777 | 51.2465 | 2.6898 | 62.4894 | 49.2361 | -1.6243 | 63.01 | 47.1358 | -4.1868 | 62.996 | 46.5191 | -1.982 | 52.8888 | 52.8888 | 24.9959 | 53.0072 | 53.0072 | 24.5023 | 53.1466 | 53.1466 | 24.154 | 53.3031 | 53.3031 | 23.9768 | 53.5126 | 53.5126 | 23.7827 | 53.8335 | 53.8335 | 23.5424 | 54.4161 | 54.4161 | 23.0735 | 54.8991 | 54.8991 | 22.6908 | 55.3019 | 55.3019 | 22.0467 | 55.7222 | 55.7222 | 21.3982 | 57.1215 | 57.1215 | 19.1711 | 58.1166 | 58.1166 | 16.6713 | 58.812 | 58.3021 | 14.6515 | 59.3732 | 58.7703 | 12.9239 | 59.6142 | 57.921 | 12.2974 | 52.8888 | 52.8888 | 24.9959 | 52.928 | 52.928 | 24.4406 | 53.2925 | 53.2925 | 23.7755 | 53.5242 | 53.5242 | 23.4401 | 53.819 | 53.819 | 22.939 | 57.7635 | 57.7635 | 18.6496 | 58.0214 | 56.1594 | 18.0188 | 58.4355 | 53.6633 | 16.1701 | 58.8258 | 53.3295 | 14.1851 | 59.2284 | 53.0248 | 12.1751 | 60.7199 | 52.4085 | 6.0092 | 62.0709 | 50.8539 | 0.0071226 | 62.9207 | 48.8287 | -4.7693 | 63.4501 | 46.5766 | -7.8952 | 63.4669 | 45.709 | -6.3006
ORRELL | WASHWAY FARM / KIRKBY | 352784 | 404565 | 100.4695 | 58.0726 | 51.5262 | 100.6815 | 57.2643 | 46.9232 | 100.9403 | 56.3131 | 44.6014 | 101.2786 | 55.4772 | 43.1225 | 101.7544 | 53.3421 | 41.4232 | 102.3191 | 51.2835 | 39.6021 | 102.9187 | 49.287 | 38.0806 | 103.6365 | 47.6776 | 36.8262 | 108.7808 | 45.2871 | 30.6957 | 109.3754 | 44.766 | 29.1849 | 115.9062 | 39.854 | 17.7231 | 118.4273 | 36.1496 | 6.7377 | 120.8637 | 34.715 | -2.9805 | 122.3993 | 40.3032 | -11.5995 | 122.9944 | 41.3613 | -18.1089 | 100.2793 | 58.0726 | 51.5262 | 100.5986 | 57.8193 | 50.1491 | 100.7658 | 57.152 | 49.2883 | 100.9646 | 56.5376 | 48.6639 | 101.2372 | 55.8223 | 47.922 | 101.5767 | 55.1228 | 47.0308 | 101.9978 | 50.3367 | 45.9416 | 102.5023 | 49.9677 | 44.6553 | 102.8982 | 49.5885 | 43.1769 | 103.3363 | 49.3657 | 41.6189 | 104.7705 | 48.8359 | 36.8075 | 106.3933 | 49.9472 | 31.976 | 108.8038 | 50.4328 | 26.6379 | 110.476 | 54.8985 | 21.9448 | 111.5412 | 59.4714 | 19.097 | 100.4838 | 58.0726 | 51.5262 | 100.6951 | 57.1503 | 46.3428 | 100.9632 | 56.1024 | 43.9731 | 101.3129 | 55.2203 | 42.6654 | 101.7979 | 52.9811 | 41.0808 | 102.3505 | 50.8101 | 39.4098 | 102.9425 | 48.7105 | 38.1203 | 103.6654 | 46.96 | 37.1788 | 108.705 | 44.4643 | 31.6064 | 109.2247 | 43.8784 | 30.5088 | 116.5703 | 38.4325 | 19.1234 | 119.2186 | 34.1962 | 8.704 | 120.8791 | 32.9609 | 0.26227 | 122.4663 | 38.9123 | -7.7358 | 123.0297 | 40.5606 | -13.3251 | 100.484 | 58.0726 | 51.5262 | 100.4897 | 57.3975 | 48.3436 | 100.6335 | 56.8241 | 46.601 | 100.8986 | 56.5626 | 45.4889 | 101.2963 | 54.0886 | 44.0135 | 101.8345 | 51.7182 | 42.2076 | 102.5706 | 43.2335 | 40.1878 | 113.6171 | 33.1134 | 27.0353 | 114.3381 | 24.6303 | 23.9077 | 97.9241 | 17.765 | 20.6426 | 79.1911 | 14.3665 | 10.5277 | 77.5754 | 14.0734 | 0.66244 | 66.5372 | 12.0709 | -6.9943 | 88.4856 | 16.0527 | -11.6961 | 81.3893 | 14.7653 | -8.303 | 100.4688 | 58.0726 | 51.5262 | 100.6417 | 57.6043 | 49.223 | 100.8195 | 56.7392 | 47.6116 | 101.0192 | 55.9492 | 46.5777 | 101.2947 | 53.8952 | 45.5456 | 101.7096 | 51.914 | 44.206 | 102.2478 | 49.9536 | 42.9579 | 102.8668 | 48.3629 | 41.9467 | 107.9219 | 45.9732 | 35.9971 | 108.4532 | 45.4428 | 34.58 | 114.4033 | 40.9484 | 25.6298 | 116.5687 | 38.0744 | 20.3208 | 118.8901 | 37.4919 | 15.8847 | 120.2496 | 44.3578 | 12.8942 | 120.3083 | 46.4424 | 12.5518 | 100.4688 | 58.0726 | 51.5262 | 100.533 | 57.0906 | 46.0459 | 100.7709 | 56.4164 | 43.5001 | 101.1445 | 56.1101 | 41.951 | 101.6223 | 53.6161 | 40.1205 | 102.171 | 51.2216 | 38.2014 | 102.8664 | 42.7003 | 36.0978 | 113.9173 | 32.5284 | 22.7 | 114.6807 | 24.0324 | 19.3809 | 94.5649 | 17.1556 | 15.9293 | 75.1222 | 13.6284 | 5.0042 | 72.7917 | 13.2056 | -5.8851 | 61.3274 | 11.1258 | -14.3664 | 83.0256 | 15.0622 | -19.8304 | 75.8293 | 13.7566 | -17.1999
PADIHAM | PADIHAM | 378571 | 433224 | 136.5197 | 47.5217 | 65.6904 | 136.9596 | 46.4521 | 61.6388 | 138.8156 | 44.8232 | 58.554 | 139.6522 | 42.0805 | 57.3821 | 140.6267 | 38.9668 | 56.1316 | 141.7806 | 35.7529 | 54.866 | 146.0581 | 32.0683 | 50.6423 | 147.3248 | 29.9262 | 49.5852 | 148.4165 | 29.1394 | 47.7274 | 153.8169 | 28.4499 | 41.5732 | 141.8885 | 25.7408 | 32.2486 | 126.1465 | 22.885 | 17.0267 | 107.5392 | 19.5093 | -1.1299 | 100.0016 | 18.1419 | -9.5797 | 83.8644 | 15.2143 | -16.2851 | 136.4017 | 47.5217 | 65.6904 | 136.8089 | 46.9939 | 63.8711 | 137.3787 | 46.4368 | 62.6787 | 138 | 45.8907 | 61.7117 | 138.7434 | 45.2539 | 60.6978 | 139.6606 | 44.6434 | 59.636 | 140.7886 | 39.0831 | 58.264 | 142.0678 | 38.5226 | 56.5152 | 142.8506 | 38.0138 | 54.7154 | 143.6975 | 37.7028 | 52.8946 | 147.8383 | 36.5824 | 45.6236 | 149.9761 | 37.5948 | 40.0558 | 152.2042 | 37.6067 | 34.7372 | 162.4198 | 37.2834 | 20.9584 | 164.868 | 36.6887 | 16.3376 | 136.5692 | 47.5217 | 65.6904 | 137.0469 | 46.2259 | 61.0609 | 138.9545 | 44.3804 | 57.8864 | 139.8843 | 41.3976 | 56.6728 | 140.9618 | 38.1153 | 55.3976 | 142.2268 | 34.8336 | 54.1165 | 143.7605 | 31.5356 | 52.9085 | 144.8253 | 29.2814 | 51.7112 | 145.5945 | 28.4549 | 50.59 | 146.3793 | 27.6707 | 49.5752 | 130.2609 | 23.6314 | 31.9857 | 111.6794 | 20.2604 | 17.5926 | 96.1402 | 17.4414 | 9.172 | 86.7659 | 15.7407 | 1.9831 | 75.3698 | 13.6733 | -3.072 | 136.5692 | 47.5217 | 65.6904 | 136.6946 | 46.654 | 62.7709 | 138.2742 | 45.809 | 60.0355 | 138.8475 | 40.8995 | 58.9229 | 142.7623 | 39.8729 | 54.5191 | 144.0152 | 38.8364 | 53.0988 | 147.0518 | 35.6735 | 49.7469 | 148.7036 | 30.2498 | 46.7952 | 140.8899 | 25.5597 | 43.3023 | 109.3464 | 19.8372 | 30.6233 | 85.6953 | 15.5465 | 15.31 | 76.8799 | 13.9472 | 6.1401 | 58.5759 | 10.6266 | -0.74673 | 45.9739 | 8.3404 | -4.5848 | 35.7866 | 6.4923 | -0.5834 | 136.5196 | 47.5217 | 65.6904 | 136.8942 | 46.7369 | 62.6495 | 138.5785 | 45.2129 | 59.8428 | 139.1468 | 42.4981 | 58.8784 | 139.8234 | 39.4955 | 58.0456 | 140.8245 | 36.3916 | 57.1558 | 145.0305 | 32.7183 | 53.2248 | 146.5035 | 30.6048 | 52.3931 | 147.6516 | 29.8188 | 50.7608 | 152.9585 | 29.1316 | 44.5678 | 147.7245 | 26.7996 | 37.6365 | 136.9989 | 24.8538 | 28.0842 | 122.0212 | 22.1366 | 14.9211 | 119.6412 | 21.7048 | 12.0381 | 109.3897 | 19.845 | 11.3454 | 136.5196 | 47.5217 | 65.6904 | 136.8077 | 46.1898 | 60.9396 | 138.6272 | 45.2116 | 57.695 | 139.4812 | 40.2287 | 56.3335 | 143.623 | 39.1245 | 51.7193 | 144.8741 | 38.0482 | 50.2256 | 147.8148 | 34.8519 | 46.8351 | 149.4019 | 29.4027 | 43.7339 | 135.9101 | 24.6563 | 39.78 | 104.4211 | 18.9436 | 26.3939 | 80.4172 | 14.589 | 9.7205 | 71.1564 | 12.9089 | -0.40593 | 51.9587 | 9.4261 | -8.228 | 38.8384 | 7.0459 | -13.0557 | 28.1146 | 5.1004 | -10.0408
PEEL | PENWORTHAM WEST / STANAH | 335644 | 432080 | 19.8496 | 19.8496 | 15.0919 | 20.1034 | 20.1034 | 11.9344 | 20.5021 | 20.5021 | 7.4205 | 20.9418 | 20.9418 | 3.3453 | 21.4969 | 21.4969 | -0.9645 | 22.1632 | 22.1632 | -5.3395 | 22.7872 | 22.7872 | -6.362 | 23.4708 | 23.4708 | -7.2033 | 24.1046 | 24.1046 | -8.1097 | 24.7171 | 24.7171 | -8.958 | 27.2637 | 27.2637 | -12.8386 | 29.6121 | 29.6121 | -18.8699 | 30.9203 | 30.9203 | -24.0153 | 31.7283 | 31.7283 | -29.0829 | 32.2334 | 32.2334 | -33.6998 | 19.8154 | 19.8154 | 15.0919 | 19.9707 | 19.9707 | 13.8241 | 20.1736 | 20.1736 | 13.0125 | 20.3724 | 20.3724 | 12.4488 | 20.6006 | 20.6006 | 11.8783 | 20.8265 | 20.8265 | 11.2963 | 21.1315 | 21.1315 | 10.5538 | 21.5987 | 21.5987 | 9.5255 | 22.0575 | 22.0575 | 8.4962 | 22.5263 | 22.5263 | 7.4744 | 23.9882 | 23.9882 | 4.4046 | 25.6139 | 25.6139 | 1.0902 | 27.1473 | 27.1473 | -1.9226 | 28.9107 | 28.9107 | -5.2643 | 31.4821 | 31.4821 | -9.0671 | 19.864 | 19.864 | 15.0919 | 20.1316 | 20.1316 | 11.5204 | 20.55 | 20.55 | 6.9692 | 21.0933 | 21.0933 | 2.8666 | 21.6803 | 21.6803 | -1.3666 | 22.3175 | 22.3175 | -5.5767 | 22.9899 | 22.9899 | -6.4944 | 23.7303 | 23.7303 | -7.1966 | 24.3747 | 24.3747 | -7.8925 | 24.9885 | 24.9885 | -8.5146 | 28.8206 | 28.8206 | -13.056 | 30.9139 | 30.9139 | -18.437 | 32.1885 | 32.1885 | -22.9158 | 32.8496 | 32.8496 | -27.0031 | 33.1094 | 33.1094 | -30.4862 | 19.8641 | 19.8641 | 15.0919 | 19.9519 | 19.9519 | 12.9174 | 20.3431 | 20.3431 | 8.6169 | 20.7347 | 20.7347 | 4.6673 | 21.2487 | 21.2487 | 0.4752 | 23.3421 | 23.3421 | -5.321 | 24.0894 | 24.0894 | -6.4799 | 25.7365 | 25.7365 | -8.8349 | 26.8735 | 26.8735 | -10.7478 | 27.9903 | 27.9903 | -12.605 | 29.5949 | 29.5949 | -17.9015 | 30.8517 | 30.8517 | -22.988 | 31.643 | 31.643 | -26.7411 | 32.1034 | 32.1034 | -29.0073 | 31.832 | 31.832 | -27.5721 | 19.8496 | 19.8496 | 15.0919 | 20.0566 | 20.0566 | 13.0186 | 20.3956 | 20.3956 | 8.7566 | 20.7319 | 20.7319 | 4.8088 | 21.1156 | 21.1156 | 0.74359 | 21.6401 | 21.6401 | -3.4069 | 22.1727 | 22.1727 | -4.2723 | 22.7919 | 22.7919 | -5.0599 | 23.4271 | 23.4271 | -6.0452 | 24.0736 | 24.0736 | -7.0217 | 26.1666 | 26.1666 | -9.914 | 28.4413 | 28.4413 | -13.0214 | 30.0406 | 30.0406 | -15.4354 | 30.7065 | 30.7065 | -17.3999 | 30.9548 | 30.9548 | -18.3981 | 19.8496 | 19.8496 | 15.0919 | 19.9817 | 19.9817 | 11.5005 | 20.4463 | 20.4463 | 6.7981 | 20.9263 | 20.9263 | 2.6471 | 21.5093 | 21.5093 | -1.729 | 23.5923 | 23.5923 | -7.652 | 24.2998 | 24.2998 | -8.9413 | 25.9604 | 25.9604 | -11.502 | 27.111 | 27.111 | -13.5462 | 28.238 | 28.238 | -15.5277 | 29.9667 | 29.9667 | -21.1843 | 31.2282 | 31.2282 | -26.6256 | 32.0015 | 32.0015 | -30.7116 | 32.403 | 32.403 | -33.3857 | 32.223 | 32.223 | -32.5051
PENRITH & SHAP | HARKER / HUTTON | 349996 | 530398 | 11.07 | 11.07 | 2.0585 | 12.0729 | 12.0729 | -4.5098 | 13.2004 | 13.2004 | -6.5608 | 14.3815 | 14.3815 | -7.9015 | 15.9867 | 15.9867 | -10.2303 | 17.885 | 17.885 | -12.6741 | 20.1349 | 20.1349 | -15.3082 | 22.6202 | 22.6202 | -18.2576 | 25.3792 | 25.3792 | -22.3964 | 28.0804 | 28.0804 | -27.1917 | 42.4125 | 31.6146 | -51.8554 | 49.0357 | 27.8903 | -71.3817 | 58.5266 | 24.2156 | -90.3234 | 61.4407 | 20.4732 | -101.1115 | 62.6043 | 15.6929 | -109.7557 | 11.0717 | 11.0717 | 2.0585 | 12.0725 | 12.0725 | -0.27145 | 12.9092 | 12.9092 | -1.6835 | 13.8073 | 13.8073 | -3.2283 | 14.9335 | 14.9335 | -5.1589 | 16.3423 | 16.3423 | -6.9087 | 18.083 | 18.083 | -9.1854 | 19.7111 | 19.7111 | -14.4563 | 20.9284 | 20.9284 | -15.7812 | 22.3635 | 22.3635 | -17.2592 | 27.6125 | 27.6125 | -23.1955 | 33.8966 | 33.8966 | -33.1455 | 39.3801 | 38.9359 | -44.56 | 47.7538 | 35.901 | -61.9247 | 58.7321 | 31.9147 | -79.9912 | 11.0713 | 11.0713 | 2.0585 | 12.0066 | 12.0066 | -5.3209 | 13.2376 | 13.2376 | -7.4302 | 14.4228 | 14.4228 | -8.5348 | 15.9948 | 15.9948 | -10.5875 | 17.7571 | 17.7571 | -12.654 | 19.728 | 19.728 | -14.7232 | 21.9111 | 21.9111 | -17.5817 | 24.2216 | 24.2216 | -21.2267 | 26.5902 | 26.5902 | -25.267 | 42.1474 | 28.3726 | -50.5837 | 54.9144 | 23.1266 | -77.0047 | 60.9498 | 19.0506 | -93.4268 | 64.1326 | 13.8022 | -104.7875 | 46.1883 | 8.3793 | -112.5653 | 11.0718 | 11.0718 | 2.0585 | 11.4137 | 11.4137 | -2.3599 | 12.1458 | 12.1458 | -3.8862 | 13.2485 | 13.2485 | -5.441 | 16.1064 | 16.1064 | -8.9756 | 18.478 | 18.478 | -11.7283 | 20.7544 | 20.7544 | -14.7169 | 24.5176 | 24.5176 | -20.8964 | 38.6504 | 16.0724 | -38.9507 | 40.9216 | 9.2256 | -45.531 | 0.27434 | 0.049769 | -67.9197 | 10.6707 | 1.9358 | -86.5055 | 7.2348 | 1.9358 | -98.6012 | 6.7308 | 1.9358 | -105.3208 | 6.7308 | 1.9358 | -103.5612 | 11.0695 | 11.0695 | 2.0585 | 11.8963 | 11.8963 | -0.97925 | 12.8497 | 12.8497 | -2.3713 | 13.7296 | 13.7296 | -3.5764 | 14.8841 | 14.8841 | -5.2303 | 16.6081 | 16.6081 | -6.6553 | 18.6428 | 18.6428 | -8.3435 | 20.6088 | 20.6088 | -10.4828 | 22.7538 | 22.7538 | -13.6312 | 25.2062 | 25.2062 | -17.6668 | 39.2412 | 32.96 | -39.1561 | 45.5397 | 29.5901 | -54.541 | 54.6973 | 26.2665 | -70.0367 | 57.3913 | 22.7384 | -78.5455 | 58.0269 | 18.1393 | -82.5024 | 11.0695 | 11.0695 | 2.0585 | 11.7351 | 11.7351 | -5.4084 | 12.8868 | 12.8868 | -7.8617 | 13.9983 | 13.9983 | -9.8093 | 16.7578 | 16.7578 | -13.682 | 18.9476 | 18.9476 | -16.6226 | 20.9195 | 20.9195 | -19.7695 | 24.3829 | 24.0681 | -26.1348 | 38.4893 | 15.4903 | -43.6627 | 40.426 | 8.811 | -49.2227 | 10.6707 | 1.9358 | -70.7107 | 10.6707 | 1.9358 | -91.2208 | 4.8119 | 1.9358 | -105.4541 | 6.7308 | 1.9358 | -113.6106 | 6.7308 | 1.9358 | -112.5686
PRESTON EAST | PENWORTHAM EAST / ROCHDALE | 356774 | 432942 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 4.6817 | 10.6707 | 1.9358 | -9.2992 | 10.6707 | 1.9358 | -14.1871 | 10.6707 | 1.9358 | -18.0019 | 10.6707 | 1.9358 | -22.3154 | 10.6707 | 1.9358 | -26.7568 | 10.6707 | 1.9358 | -31.1505 | 10.6707 | 1.9358 | -41.101 | 10.6707 | 1.9358 | -52.2483 | 10.6707 | 1.9358 | -61.1679 | 10.6707 | 1.9358 | -69.5592 | 10.6707 | 1.9358 | -77.0113 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 2.8601 | 10.6707 | 1.9358 | 1.6858 | 10.6707 | 1.9358 | 0.50125 | 10.6707 | 1.9358 | -1.0087 | 10.6707 | 1.9358 | -2.1041 | 10.6707 | 1.9358 | -3.223 | 10.6707 | 1.9358 | -6.7683 | 10.6707 | 1.9358 | -10.5026 | 10.6707 | 1.9358 | -14.2949 | 10.6707 | 1.9358 | -18.7254 | 10.6707 | 1.9358 | -21.8031 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 0.77416 | 10.6707 | 1.9358 | -14.7834 | 10.6707 | 1.9358 | -20.755 | 10.6707 | 1.9358 | -24.5732 | 10.6707 | 1.9358 | -28.8719 | 10.6707 | 1.9358 | -33.1871 | 10.6707 | 1.9358 | -37.44 | 10.6707 | 1.9358 | -47.0538 | 10.6707 | 1.9358 | -56.4412 | 10.6707 | 1.9358 | -64.7845 | 10.6707 | 1.9358 | -72.3442 | 10.6707 | 1.9358 | -78.586 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 4.4124 | 10.6707 | 1.9358 | -12.4219 | 10.6707 | 1.9358 | -18.3139 | 10.6707 | 1.9358 | -22.5453 | 10.6707 | 1.9358 | -28.6573 | 10.6707 | 1.9358 | -34.9888 | 10.6707 | 1.9358 | -41.7171 | 10.6707 | 1.9358 | -54.9594 | 10.6707 | 1.9358 | -64.9791 | 10.6707 | 1.9358 | -72.4258 | 10.6707 | 1.9358 | -76.3522 | 10.6707 | 1.9358 | -73.354 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | -3.3697 | 10.6707 | 1.9358 | -7.826 | 10.6707 | 1.9358 | -11.3611 | 10.6707 | 1.9358 | -15.508 | 10.6707 | 1.9358 | -19.906 | 10.6707 | 1.9358 | -24.3323 | 10.6707 | 1.9358 | -32.3423 | 10.6707 | 1.9358 | -37.253 | 10.6707 | 1.9358 | -40.5487 | 10.6707 | 1.9358 | -43.0085 | 10.6707 | 1.9358 | -43.8917 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 0.060236 | 10.6707 | 1.9358 | -17.4395 | 10.6707 | 1.9358 | -23.6474 | 10.6707 | 1.9358 | -28.1615 | 10.6707 | 1.9358 | -34.8507 | 10.6707 | 1.9358 | -41.94 | 10.6707 | 1.9358 | -48.7671 | 10.6707 | 1.9358 | -62.4705 | 10.6707 | 1.9358 | -73.1966 | 10.6707 | 1.9358 | -81.3833 | 10.6707 | 1.9358 | -86.1149 | 10.6707 | 1.9358 | -83.9365
RED BANK | WHITEGATE | 384542 | 399276 | 152.6466 | 40.5673 | 63.2487 | 152.9781 | 38.1469 | 51.3638 | 153.5509 | 36.7642 | 46.1291 | 154.1186 | 35.4836 | 41.3545 | 154.7014 | 34.7889 | 39.2718 | 155.3549 | 34.0694 | 36.9335 | 156.0933 | 33.4969 | 35.3467 | 156.8103 | 33.0816 | 33.8105 | 157.3864 | 32.5824 | 32.013 | 157.9551 | 32.1243 | 30.441 | 159.6646 | 30.4335 | 23.8496 | 157.8356 | 28.6339 | 14.3413 | 151.3445 | 27.4563 | 7.0438 | 144.6389 | 26.2398 | -0.077289 | 133.1597 | 24.1573 | -6.368 | 152.591 | 40.5673 | 63.2487 | 152.9531 | 39.8127 | 59.6161 | 153.5011 | 38.7655 | 56.7122 | 154.0393 | 37.4623 | 52.1387 | 154.6164 | 36.8486 | 50.8959 | 155.2493 | 36.3245 | 49.5752 | 155.8459 | 30.6885 | 48.2129 | 156.4902 | 30.147 | 46.5725 | 157.0009 | 29.6384 | 45.138 | 157.5261 | 29.3418 | 43.6889 | 157.9665 | 28.6576 | 39.548 | 160.6526 | 29.9461 | 35.561 | 162.0162 | 30.5403 | 31.6466 | 163.4431 | 30.5493 | 27.3181 | 164.6068 | 30.1738 | 23.5377 | 152.67 | 40.5673 | 63.2487 | 153.0555 | 37.7627 | 49.5707 | 153.6943 | 36.1963 | 40.7636 | 154.3526 | 34.7722 | 33.1629 | 155.0364 | 33.9312 | 30.4883 | 155.8034 | 33.0978 | 27.891 | 156.6332 | 32.5166 | 26.1149 | 157.2793 | 31.9895 | 24.3448 | 157.8639 | 31.423 | 22.6712 | 158.4313 | 30.8904 | 21.0818 | 159.4599 | 28.9286 | 14.4948 | 148.3857 | 26.9195 | 5.4037 | 140.9863 | 25.5772 | -1.0996 | 131.957 | 23.9391 | -6.9192 | 120.0299 | 21.7753 | -11.1853 | 152.67 | 40.5673 | 63.2487 | 152.7559 | 38.6532 | 53.8881 | 153.164 | 37.6118 | 46.0783 | 153.5672 | 36.4345 | 38.457 | 154.0166 | 35.7585 | 36.0396 | 154.6476 | 35.0744 | 33.4758 | 155.4142 | 34.5047 | 31.3042 | 156.249 | 33.7064 | 27.8084 | 156.8445 | 32.9114 | 24.2896 | 157.4332 | 31.7135 | 20.8871 | 158.8801 | 28.8234 | 11.7647 | 141.1886 | 25.6139 | 3.5678 | 125.8929 | 22.839 | -1.9438 | 114.3827 | 20.7508 | -4.949 | 103.8414 | 18.8385 | -3.6465 | 152.6466 | 40.5673 | 63.2487 | 152.9495 | 39.2842 | 56.9033 | 153.4312 | 38.1398 | 52.8867 | 153.8556 | 36.9061 | 48.1863 | 154.2833 | 36.3056 | 46.4956 | 154.8681 | 35.6587 | 44.7907 | 155.5919 | 35.134 | 43.5155 | 156.3641 | 34.7425 | 42.1193 | 156.9794 | 34.2509 | 40.3042 | 157.5099 | 33.774 | 38.6355 | 159.1183 | 32.4139 | 33.8744 | 160.6545 | 31.4191 | 29.023 | 161.7165 | 31.019 | 25.7194 | 162.6122 | 30.5914 | 22.4508 | 161.7106 | 29.3369 | 20.2352 | 152.6466 | 40.5673 | 63.2487 | 152.8553 | 37.5674 | 48.5478 | 153.4342 | 36.2726 | 39.4143 | 154.0325 | 35.0249 | 31.7407 | 154.6499 | 34.2997 | 28.7658 | 155.3305 | 33.5849 | 25.9829 | 156.107 | 32.9518 | 23.5361 | 156.9228 | 32.1158 | 19.7096 | 157.5317 | 31.2839 | 16.0237 | 158.1276 | 30.0718 | 12.4471 | 148.8087 | 26.9963 | 2.7507 | 130.9385 | 23.7543 | -5.8638 | 115.43 | 20.9408 | -11.7843 | 103.678 | 18.8088 | -15.2716 | 92.5516 | 16.7903 | -14.5829
RIBBLE | PENWORTHAM EAST / ROCHDALE | 351794 | 429241 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 8.3053 | 1.9358 | 8.3053 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 1.6121 | 6.7308 | 1.9358 | -17.8207 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 1.0733 | 0.44083 | 1.0733 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | -2.0922 | 6.7308 | 1.9358 | -18.5325 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 7.7189 | 1.9358 | 7.7189 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | -2.6155 | 6.7308 | 1.9358 | -13.7815 | 6.7308 | 1.9358 | -5.4604 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 6.5527 | 1.9358 | 6.5527 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 1.1614 | 0.47705 | 1.1614 | 6.7308 | 1.9358 | -1.8214 | 6.7308 | 1.9358 | -22.27 | 6.7308 | 1.9358 | -35.6029 | 6.7308 | 1.9358 | -29.5215
ROCHDALE CENTRAL | ROCHDALE | 389111 | 413393 | 92.9159 | 42.8558 | 61.181 | 93.2846 | 42.515 | 60.3191 | 93.695 | 42.2691 | 59.7963 | 94.2217 | 42.0489 | 59.2269 | 94.8725 | 41.6436 | 58.5942 | 95.5542 | 41.1725 | 57.9331 | 96.0933 | 40.653 | 57.2573 | 96.7472 | 40.2299 | 56.5377 | 97.2882 | 39.7766 | 55.8159 | 97.829 | 39.4012 | 55.1195 | 99.9028 | 37.7137 | 49.4564 | 102.3947 | 35.6366 | 41.0108 | 104.0838 | 33.8641 | 34.4816 | 105.5106 | 32.1911 | 27.3861 | 106.467 | 30.045 | 21.1611 | 92.8508 | 42.8558 | 61.181 | 93.0957 | 42.6746 | 60.5872 | 93.3147 | 42.2946 | 59.9909 | 93.5962 | 41.8899 | 59.3762 | 93.9726 | 41.4809 | 58.6402 | 94.4429 | 41.086 | 57.7586 | 95.0045 | 37.6338 | 56.7023 | 95.6132 | 37.2304 | 55.3598 | 95.9866 | 36.8885 | 54.8436 | 96.3925 | 36.647 | 54.3177 | 97.7981 | 36.2789 | 51.9256 | 99.1013 | 37.1559 | 49.1199 | 100.2741 | 37.4987 | 46.67 | 101.4681 | 37.3673 | 44.338 | 102.2958 | 37.0882 | 42.8745 | 92.9428 | 42.8558 | 61.181 | 93.2948 | 42.461 | 60.2436 | 93.7184 | 42.1552 | 59.7307 | 94.2696 | 41.8385 | 59.1003 | 94.9484 | 41.3248 | 58.4222 | 95.5881 | 40.7502 | 57.7298 | 96.1293 | 40.2002 | 57.0349 | 96.7647 | 39.6887 | 56.2993 | 97.263 | 39.2253 | 55.5249 | 97.7746 | 38.7565 | 54.7848 | 99.8755 | 36.8836 | 49.9733 | 102.5042 | 34.6261 | 41.6694 | 104.5263 | 32.6883 | 35.123 | 105.6689 | 30.6821 | 28.5814 | 106.3447 | 28.7786 | 23.3317 | 92.9432 | 42.8558 | 61.181 | 93.1289 | 42.6672 | 60.8813 | 93.3973 | 42.6374 | 60.6458 | 93.7656 | 42.7856 | 60.2185 | 94.2905 | 42.3943 | 59.7003 | 95.0464 | 41.9971 | 59.0972 | 95.72 | 40.2208 | 58.3065 | 96.5511 | 38.3555 | 56.0333 | 97.3512 | 36.3684 | 52.966 | 98.1684 | 34.2114 | 49.9117 | 100.636 | 31.4896 | 41.3085 | 102.9157 | 29.2645 | 33.4459 | 104.3776 | 27.4747 | 27.4458 | 105.1008 | 26.098 | 23.4999 | 105.0479 | 25.6656 | 25.4896 | 92.9156 | 42.8558 | 61.181 | 93.2102 | 42.6786 | 60.6678 | 93.4914 | 42.4807 | 60.3042 | 93.824 | 42.2944 | 59.8817 | 94.2554 | 41.9668 | 59.4417 | 94.8846 | 41.5639 | 58.8999 | 95.5461 | 41.0769 | 58.2669 | 96.0811 | 40.6658 | 57.592 | 96.5878 | 40.2216 | 56.8993 | 97.1073 | 39.8398 | 56.1971 | 98.7605 | 38.5748 | 53.6643 | 100.4491 | 37.489 | 49.5622 | 101.664 | 36.5844 | 46.9086 | 102.6963 | 35.6631 | 43.4675 | 103.1843 | 34.8248 | 41.5696 | 92.9156 | 42.8558 | 61.181 | 93.1388 | 42.5063 | 60.4382 | 93.5051 | 42.393 | 59.9158 | 93.9911 | 42.49 | 59.2272 | 94.5928 | 42.0505 | 58.4661 | 95.2842 | 41.6183 | 57.6932 | 95.8928 | 39.8388 | 56.7357 | 96.7115 | 37.8818 | 54.2087 | 97.4818 | 35.8957 | 50.9971 | 98.2747 | 33.7637 | 47.7934 | 100.762 | 30.8406 | 38.6422 | 103.1221 | 28.5125 | 30.1843 | 104.869 | 26.6233 | 23.5766 | 105.7419 | 25.1524 | 18.9106 | 105.7505 | 24.6152 | 20.1365
ROSSENDALE | PADIHAM | 380261 | 422010 | 106.576 | 72.0836 | 70.4374 | 107.0392 | 71.6332 | 69.1583 | 107.7684 | 68.8889 | 67.634 | 108.4741 | 65.0031 | 66.5655 | 108.873 | 61.2259 | 65.4825 | 109.3558 | 57.5417 | 64.3733 | 112.8857 | 53.5058 | 60.0611 | 113.4453 | 51.6355 | 59.031 | 114.0952 | 50.9646 | 57.5498 | 114.7679 | 50.382 | 56.085 | 117.1706 | 47.9979 | 48.061 | 119.6804 | 45.5531 | 35.814 | 121.3844 | 44.6194 | 25.1436 | 122.8805 | 44.3008 | 12.9025 | 123.8316 | 42.2969 | 3.1555 | 106.4241 | 72.0836 | 70.4374 | 106.7659 | 71.8121 | 69.5765 | 107.1726 | 69.9344 | 68.4991 | 107.6701 | 68.1612 | 67.7813 | 108.334 | 66.4282 | 67.0885 | 109.1799 | 64.7342 | 66.0767 | 110.1348 | 58.8473 | 64.7842 | 110.8999 | 58.3027 | 63.1548 | 111.335 | 57.8221 | 61.7955 | 111.8029 | 57.5016 | 60.4051 | 113.3105 | 56.5406 | 56.1156 | 114.95 | 57.2428 | 51.6606 | 116.5075 | 57.9411 | 47.4961 | 118.0487 | 58.2761 | 43.016 | 121.0798 | 57.203 | 37.6809 | 106.6459 | 72.0836 | 70.4374 | 107.1838 | 71.5303 | 68.9615 | 108.0301 | 68.5503 | 67.1903 | 108.5756 | 64.5193 | 65.8769 | 109.0114 | 60.6417 | 64.5567 | 109.5299 | 56.7801 | 63.2139 | 112.9432 | 52.5249 | 58.83 | 113.5301 | 50.4242 | 57.5837 | 114.1407 | 49.5514 | 56.0788 | 114.7705 | 48.7504 | 54.5969 | 121.6956 | 45.5419 | 41.5571 | 124.2959 | 42.9708 | 29.6707 | 125.9052 | 41.702 | 20.7664 | 126.9477 | 40.6941 | 12.1015 | 127.4482 | 38.0576 | 4.7015 | 106.6459 | 72.0836 | 70.4374 | 106.7218 | 71.7406 | 70.0419 | 107.1578 | 71.031 | 68.6412 | 107.7527 | 65.2244 | 67.5346 | 111.0082 | 63.9789 | 63.2164 | 111.2536 | 63.159 | 62.0853 | 111.6999 | 60.1971 | 60.2171 | 112.4136 | 54.7319 | 56.2443 | 113.4247 | 49.7473 | 51.7515 | 114.2685 | 44.9759 | 47.5301 | 117.3864 | 39.3959 | 34.7522 | 119.6547 | 37.7306 | 23.0975 | 121.1408 | 34.2552 | 13.5945 | 121.9597 | 30.8498 | 8.1436 | 121.7754 | 29.0348 | 12.6999 | 106.576 | 72.0836 | 70.4374 | 106.97 | 71.733 | 69.4346 | 107.4822 | 69.0669 | 68.1033 | 108.0628 | 65.2392 | 67.3099 | 108.5047 | 61.5723 | 66.7315 | 108.9064 | 57.9622 | 66.0489 | 112.4014 | 53.9668 | 61.9745 | 112.8706 | 52.1345 | 61.1257 | 113.42 | 51.4929 | 59.7312 | 114.0082 | 50.9106 | 58.2834 | 116.111 | 49.1214 | 53.3263 | 118.1428 | 47.9589 | 48.133 | 119.4691 | 48.1365 | 44.6705 | 120.5358 | 48.9629 | 41.6506 | 120.9175 | 48.1168 | 40.4412 | 106.576 | 72.0836 | 70.4374 | 106.8258 | 71.601 | 69.5928 | 107.5328 | 70.8014 | 67.8769 | 108.2411 | 64.911 | 66.4714 | 111.5326 | 63.6201 | 61.8977 | 111.8229 | 62.7695 | 60.6653 | 112.2782 | 59.7792 | 58.7408 | 113.0602 | 54.272 | 54.5885 | 114.0623 | 49.2821 | 50.013 | 114.8914 | 44.4831 | 45.717 | 118.1119 | 38.823 | 31.7181 | 120.4685 | 36.9922 | 18.0932 | 122.073 | 33.385 | 7.5884 | 122.9451 | 29.6583 | 0.93504 | 122.8435 | 27.6766 | 4.1729
ROYTON | WHITEGATE | 392426 | 407533 | -24.7098 | -4.4827 | -24.7098 | -27.9162 | -5.0644 | -27.9162 | -30.2048 | -5.4796 | -30.2048 | -32.2375 | -5.8484 | -32.2375 | -35.1371 | -6.3744 | -35.1371 | -37.8534 | -6.8672 | -37.8534 | -40.8419 | -7.4094 | -40.8419 | -42.3216 | -7.6778 | -42.3216 | -44.0413 | -7.9898 | -44.0413 | -44.2742 | -8.032 | -44.2742 | -47.1784 | -8.5589 | -47.1784 | -39.5754 | -7.1796 | -39.5754 | -6.2889 | -1.1409 | -6.2889 | 34.6237 | 6.2813 | 34.6237 | 39.7677 | 7.2145 | 39.7677 | -24.7098 | -4.4827 | -24.7098 | -25.8556 | -4.6906 | -25.8556 | -27.0491 | -4.9071 | -27.0491 | -28.4058 | -5.1533 | -28.4058 | -30.1295 | -5.466 | -30.1295 | -31.494 | -5.7135 | -31.494 | -46.6441 | -8.462 | -46.6441 | -48.2568 | -8.7546 | -48.2568 | -49.6418 | -9.0058 | -49.6418 | -50.5069 | -9.1628 | -50.5069 | -53.4226 | -9.6917 | -53.4226 | -51.6121 | -9.3633 | -51.6121 | -27.5017 | -4.9893 | -27.5017 | 7.6738 | 1.3922 | 7.6738 | 15.3017 | 2.776 | 15.3017 | -24.7098 | -4.4827 | -24.7098 | -28.4572 | -5.1626 | -28.4572 | -31.1837 | -5.6572 | -31.1837 | -33.9031 | -6.1506 | -33.9031 | -37.6471 | -6.8298 | -37.6471 | -41.1974 | -7.4739 | -41.1974 | -44.7213 | -8.1132 | -44.7213 | -46.7025 | -8.4726 | -46.7025 | -48.73 | -8.8404 | -48.73 | -49.575 | -8.9937 | -49.575 | -54.7255 | -9.9281 | -54.7255 | -48.5394 | -8.8058 | -48.5394 | -15.7549 | -2.8582 | -15.7549 | 23.3488 | 4.2358 | 23.3488 | 28.7729 | 5.2199 | 28.7729 | -24.7098 | -4.4827 | -24.7098 | -26.7426 | -4.8515 | -26.7426 | -27.6475 | -5.0157 | -27.6475 | -29.2863 | -5.313 | -29.2863 | -32.2422 | -5.8493 | -32.2422 | -35.4071 | -6.4234 | -35.4071 | -39.0967 | -7.0928 | -39.0967 | -33.8585 | -6.1425 | -33.8585 | -31.4389 | -5.7035 | -31.4389 | -26.0034 | -4.7174 | -26.0034 | 61.227 | 11.1076 | 61.227 | 47.7403 | 8.6609 | 47.7403 | 36.5196 | 6.6252 | 36.5196 | 26.7072 | 4.8451 | 26.7072 | 21.4326 | 3.8882 | 21.4326 | -24.7098 | -4.4827 | -24.7098 | -26.1419 | -4.7426 | -26.1419 | -27.9421 | -5.0691 | -27.9421 | -29.763 | -5.3995 | -29.763 | -32.2658 | -5.8535 | -32.2658 | -34.5917 | -6.2755 | -34.5917 | -37.4552 | -6.795 | -37.4552 | -38.7246 | -7.0253 | -38.7246 | -40.2759 | -7.3067 | -40.2759 | -40.4726 | -7.3424 | -40.4726 | -41.0855 | -7.4536 | -41.0855 | -28.7275 | -5.2116 | -28.7275 | 8.6844 | 1.5755 | 8.6844 | 53.7324 | 9.7479 | 53.7324 | 62.4476 | 11.329 | 62.4476 | -24.7098 | -4.4827 | -24.7098 | -28.2235 | -5.1202 | -28.2235 | -29.6667 | -5.382 | -29.6667 | -31.5904 | -5.731 | -31.5904 | -34.7441 | -6.3031 | -34.7441 | -38.0151 | -6.8965 | -38.0151 | -41.9755 | -7.615 | -41.9755 | -36.8896 | -6.6924 | -36.8896 | -34.6326 | -6.2829 | -34.6326 | -29.2789 | -5.3117 | -29.2789 | 56.9809 | 10.3372 | 56.9809 | 43.1418 | 7.8266 | 43.1418 | 31.4208 | 5.7002 | 31.4208 | 21.1758 | 3.8416 | 21.1758 | 15.0959 | 2.7386 | 15.0959 | Switchgear to be replaced in RIIO-ED2
SALE | CARRINGTON | 378726 | 392892 | 78.0704 | 60.3469 | 28.7689 | 78.4042 | 59.7132 | 26.5499 | 78.8398 | 58.9637 | 25.4637 | 79.368 | 58.2966 | 24.6059 | 80.0174 | 57.561 | 23.3234 | 80.7529 | 56.8273 | 21.944 | 81.6262 | 56.105 | 20.5276 | 82.6601 | 55.6538 | 19.2198 | 83.4325 | 55.136 | 17.7547 | 84.0904 | 54.6134 | 16.1592 | 86.2655 | 52.6518 | 8.5656 | 88.4922 | 50.3838 | -2.4877 | 90.0524 | 48.8327 | -10.817 | 91.3423 | 48.8412 | -18.3652 | 92.123 | 48.0218 | -24.3216 | 77.9556 | 60.3469 | 28.7689 | 78.2092 | 60.1252 | 27.8382 | 78.4443 | 59.6171 | 27.202 | 78.7262 | 59.0932 | 26.55 | 79.1039 | 58.5133 | 25.653 | 79.5676 | 57.9163 | 24.7222 | 80.1362 | 53.5354 | 23.5126 | 80.798 | 53.1179 | 22.0559 | 81.2777 | 52.756 | 20.889 | 81.7977 | 52.5224 | 19.6692 | 83.5638 | 51.9907 | 15.4161 | 85.4484 | 53.0007 | 11.122 | 87.0633 | 53.3718 | 7.1824 | 88.7365 | 54.0868 | 3.1705 | 89.738 | 54.7029 | 0.47613 | 78.1024 | 60.3469 | 28.7689 | 78.5009 | 59.5764 | 26.1454 | 79.0197 | 58.6934 | 24.8434 | 79.6251 | 57.9374 | 23.8546 | 80.3482 | 57.1445 | 22.3896 | 81.1906 | 56.3289 | 20.8436 | 82.1826 | 55.5179 | 19.1465 | 83.2213 | 54.9621 | 17.5394 | 83.8981 | 54.3293 | 15.8594 | 84.5789 | 53.6798 | 13.9449 | 86.9421 | 51.3173 | 5.4797 | 89.3737 | 48.9163 | -5.4378 | 91.0494 | 47.2904 | -13.3688 | 92.3284 | 47.1963 | -20.0408 | 92.8983 | 46.5743 | -23.6004 | 78.1026 | 60.3469 | 28.7689 | 78.1409 | 59.818 | 27.8806 | 78.4149 | 59.3845 | 27.0561 | 78.7528 | 58.8359 | 26.2313 | 79.2442 | 58.1937 | 24.8007 | 79.9869 | 57.5002 | 23.1643 | 80.9335 | 55.3351 | 20.7733 | 82.04 | 52.9967 | 16.6159 | 82.8887 | 50.6169 | 12.3732 | 83.7544 | 48.2609 | 8.1521 | 86.224 | 44.7079 | -3.2757 | 88.401 | 41.9337 | -12.6188 | 89.8187 | 39.8476 | -18.6007 | 90.7446 | 39.6387 | -21.0638 | 90.7851 | 38.5231 | -18.3727 | 78.0703 | 60.3469 | 28.7689 | 78.347 | 59.9254 | 27.4829 | 78.6514 | 59.2503 | 26.7728 | 78.9747 | 58.6557 | 26.2906 | 79.3946 | 58.04 | 25.6628 | 80.0184 | 57.3987 | 24.8936 | 80.8266 | 56.7495 | 23.9471 | 81.7352 | 56.346 | 22.9282 | 82.5406 | 55.8693 | 21.6389 | 83.229 | 55.3514 | 20.1739 | 85.1946 | 53.8471 | 15.2844 | 87.1401 | 52.532 | 10.2215 | 88.5288 | 51.737 | 6.5493 | 89.6952 | 52.4616 | 2.9838 | 90.2749 | 52.3635 | 0.91796 | 78.0703 | 60.3469 | 28.7689 | 78.1999 | 59.6005 | 26.8815 | 78.652 | 59.0484 | 25.5383 | 79.1969 | 58.4241 | 24.3035 | 79.8436 | 57.7111 | 22.513 | 80.5859 | 56.9743 | 20.6568 | 81.4742 | 54.7709 | 17.9936 | 82.6349 | 52.3664 | 13.4545 | 83.479 | 49.9433 | 8.9219 | 84.3374 | 47.5388 | 4.4294 | 86.8287 | 43.859 | -7.9034 | 89.0407 | 40.9441 | -18.0716 | 90.5278 | 38.7667 | -24.8362 | 91.4738 | 38.4378 | -28.152 | 91.5899 | 37.2705 | -26.1799
BARROW & SANDGATE | HARKER / HUTTON | 321492 | 468870 | 159.1463 | 29.9465 | 92.2962 | 159.4913 | 29.351 | 90.5277 | 154.918 | 28.1046 | 88.9006 | 148.88 | 27.0092 | 72.5647 | 140.9802 | 25.576 | 55.8205 | 132.8113 | 24.0941 | 53.3535 | 125.2075 | 22.7146 | 48.804 | 120.3127 | 21.8266 | 47.2399 | 116.1256 | 21.067 | 45.7341 | 111.5374 | 20.2347 | 44.2803 | 95.2024 | 17.2712 | 36.7614 | 76.0112 | 13.7896 | 15.9642 | 57.4518 | 10.4227 | 8.4793 | 42.9966 | 7.8003 | 2.8176 | 30.9601 | 5.6167 | -1.5646 | 159.0783 | 29.9465 | 92.2962 | 146.9277 | 26.655 | 91.3945 | 128.0077 | 23.2226 | 90.3224 | 108.991 | 19.7727 | 74.3192 | 89.3127 | 16.2027 | 58.2295 | 69.4179 | 12.5935 | 57.4745 | 34.1057 | 6.1873 | 34.1057 | 30.6224 | 5.5554 | 30.6224 | 27.8711 | 5.0563 | 27.8711 | 26.2387 | 4.7601 | 26.2387 | 22.5724 | 4.095 | 22.5724 | 30.744 | 5.5775 | 30.744 | 31.2325 | 5.6661 | 31.2325 | 28.2569 | 5.1263 | 28.2569 | 18.0921 | 3.2822 | 18.0921 | 159.1747 | 29.9465 | 92.2962 | 159.5257 | 29.2321 | 90.3619 | 153.2978 | 27.8107 | 88.7717 | 146.2002 | 26.523 | 72.4835 | 137.6729 | 24.9761 | 55.8806 | 129.7005 | 23.5297 | 53.593 | 122.0907 | 22.1492 | 49.199 | 116.7318 | 21.177 | 47.8366 | 111.1881 | 20.1713 | 46.5738 | 106.668 | 19.3513 | 45.3633 | 78.6363 | 14.2659 | 26.1133 | 57.9068 | 10.5052 | 7.725 | 38.3916 | 6.9648 | 1.4258 | 31.0367 | 5.6305 | -3.0038 | 17.5433 | 3.1826 | -5.6007 | 159.175 | 29.9465 | 92.2962 | 159.213 | 29.3496 | 91.8745 | 153.7295 | 27.889 | 90.0722 | 146.0569 | 26.497 | 74.0249 | 129.7954 | 23.5469 | 48.7745 | 119.2739 | 21.6382 | 46.8302 | 81.7374 | 14.8285 | 42.2158 | 52.2558 | 9.48 | 39.0992 | 24.6969 | 4.4804 | 22.8229 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 3.7952 | 10.6707 | 1.9358 | -1.7906 | 10.6707 | 1.9358 | -3.7485 | 10.6707 | 1.9358 | 2.3819 | 159.1461 | 29.9465 | 92.2962 | 159.4221 | 29.4654 | 91.0517 | 155.9293 | 28.2881 | 89.6102 | 149.9872 | 27.2101 | 73.4767 | 142.6054 | 25.8709 | 57.1842 | 134.8376 | 24.4617 | 55.2761 | 127.3769 | 23.1082 | 50.9261 | 122.6129 | 22.2439 | 49.5289 | 118.2216 | 21.4473 | 48.1314 | 113.5553 | 20.6007 | 46.6931 | 99.6288 | 18.0742 | 41.5045 | 87.0162 | 15.7861 | 26.1855 | 73.8572 | 13.3989 | 23.542 | 71.083 | 12.8956 | 23.0895 | 66.0821 | 11.9884 | 24.5257 | 159.1461 | 29.9465 | 92.2962 | 159.2662 | 29.1637 | 90.9236 | 152.1824 | 27.6083 | 88.7345 | 144.3421 | 26.186 | 72.401 | 127.8551 | 23.195 | 46.8848 | 117.2024 | 21.2624 | 44.9498 | 79.6546 | 14.4506 | 40.2605 | 49.1059 | 8.9086 | 36.891 | 21.5904 | 3.9168 | 20.4282 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 8.2022 | 10.6707 | 1.9358 | -0.038721 | 10.6707 | 1.9358 | -6.7372 | 10.6707 | 1.9358 | -9.6319 | 10.6707 | 1.9358 | -3.8663
PENRITH & SHAP | HARKER / HUTTON | 356910 | 513357 | 11.07 | 11.07 | 2.0585 | 12.0729 | 12.0729 | -4.5098 | 13.2004 | 13.2004 | -6.5608 | 14.3815 | 14.3815 | -7.9015 | 15.9867 | 15.9867 | -10.2303 | 17.885 | 17.885 | -12.6741 | 20.1349 | 20.1349 | -15.3082 | 22.6202 | 22.6202 | -18.2576 | 25.3792 | 25.3792 | -22.3964 | 28.0804 | 28.0804 | -27.1917 | 42.4125 | 31.6146 | -51.8554 | 49.0357 | 27.8903 | -71.3817 | 58.5266 | 24.2156 | -90.3234 | 61.4407 | 20.4732 | -101.1115 | 62.6043 | 15.6929 | -109.7557 | 11.0717 | 11.0717 | 2.0585 | 12.0725 | 12.0725 | -0.27145 | 12.9092 | 12.9092 | -1.6835 | 13.8073 | 13.8073 | -3.2283 | 14.9335 | 14.9335 | -5.1589 | 16.3423 | 16.3423 | -6.9087 | 18.083 | 18.083 | -9.1854 | 19.7111 | 19.7111 | -14.4563 | 20.9284 | 20.9284 | -15.7812 | 22.3635 | 22.3635 | -17.2592 | 27.6125 | 27.6125 | -23.1955 | 33.8966 | 33.8966 | -33.1455 | 39.3801 | 38.9359 | -44.56 | 47.7538 | 35.901 | -61.9247 | 58.7321 | 31.9147 | -79.9912 | 11.0713 | 11.0713 | 2.0585 | 12.0066 | 12.0066 | -5.3209 | 13.2376 | 13.2376 | -7.4302 | 14.4228 | 14.4228 | -8.5348 | 15.9948 | 15.9948 | -10.5875 | 17.7571 | 17.7571 | -12.654 | 19.728 | 19.728 | -14.7232 | 21.9111 | 21.9111 | -17.5817 | 24.2216 | 24.2216 | -21.2267 | 26.5902 | 26.5902 | -25.267 | 42.1474 | 28.3726 | -50.5837 | 54.9144 | 23.1266 | -77.0047 | 60.9498 | 19.0506 | -93.4268 | 64.1326 | 13.8022 | -104.7875 | 46.1883 | 8.3793 | -112.5653 | 11.0718 | 11.0718 | 2.0585 | 11.4137 | 11.4137 | -2.3599 | 12.1458 | 12.1458 | -3.8862 | 13.2485 | 13.2485 | -5.441 | 16.1064 | 16.1064 | -8.9756 | 18.478 | 18.478 | -11.7283 | 20.7544 | 20.7544 | -14.7169 | 24.5176 | 24.5176 | -20.8964 | 38.6504 | 16.0724 | -38.9507 | 40.9216 | 9.2256 | -45.531 | 0.27434 | 0.049769 | -67.9197 | 10.6707 | 1.9358 | -86.5055 | 7.2348 | 1.9358 | -98.6012 | -11.3593 | -4.6657 | -105.3208 | -27.7225 | -11.3868 | -103.5612 | 11.0695 | 11.0695 | 2.0585 | 11.8963 | 11.8963 | -0.97925 | 12.8497 | 12.8497 | -2.3713 | 13.7296 | 13.7296 | -3.5764 | 14.8841 | 14.8841 | -5.2303 | 16.6081 | 16.6081 | -6.6553 | 18.6428 | 18.6428 | -8.3435 | 20.6088 | 20.6088 | -10.4828 | 22.7538 | 22.7538 | -13.6312 | 25.2062 | 25.2062 | -17.6668 | 39.2412 | 32.96 | -39.1561 | 45.5397 | 29.5901 | -54.541 | 54.6973 | 26.2665 | -70.0367 | 57.3913 | 22.7384 | -78.5455 | 58.0269 | 18.1393 | -82.5024 | 11.0695 | 11.0695 | 2.0585 | 11.7351 | 11.7351 | -5.4084 | 12.8868 | 12.8868 | -7.8617 | 13.9983 | 13.9983 | -9.8093 | 16.7578 | 16.7578 | -13.682 | 18.9476 | 18.9476 | -16.6226 | 20.9195 | 20.9195 | -19.7695 | 24.3829 | 24.0681 | -26.1348 | 38.4893 | 15.4903 | -43.6627 | 40.426 | 8.811 | -49.2227 | 10.6707 | 1.9358 | -70.7107 | 10.6707 | 1.9358 | -91.2208 | 4.8119 | 1.9358 | -105.4541 | -13.9796 | -5.742 | -113.6106 | -30.3856 | -12.4807 | -112.5686
STAINBURN & SIDDICK | HARKER / HUTTON | 300332 | 530823 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.079 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.1526 | 6.7308 | 1.9358 | 6.7308
SKELMERSDALE | WASHWAY FARM / KIRKBY | 347172 | 407455 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 5.4628 | 10.6707 | 1.9358 | -5.2134 | 10.6707 | 1.9358 | -12.9975 | 52.7225 | 22.2806 | -19.5068 | 53.1029 | 27.2299 | -23.768 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 6.7387 | 49.5267 | 11.5506 | 2.2504 | 51.0611 | 18.1502 | -0.794 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 3.284 | 10.6707 | 1.9358 | -7.0514 | 10.6707 | 1.9358 | -14.1502 | 52.8696 | 16.6666 | -19.2328 | 52.6547 | 22.5689 | -21.0186 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 34.1926 | 34.1926 | 22.5439 | 34.7495 | 34.7495 | 21.069 | 35.6294 | 33.2637 | 19.5515 | 36.8258 | 29.6713 | 17.6282 | 38.3379 | 29.9194 | 14.08 | 39.9385 | 26.9661 | 10.3255 | 41.3175 | 23.6312 | 6.5397 | 45.4982 | 19.6602 | -4.1477 | 48.9656 | 16.6959 | -12.9244 | 50.8764 | 13.777 | -18.0837 | 51.4191 | 12.9295 | -19.3182 | 50.6932 | 10.6678 | -16.0058 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 6.4921 | 8.6467 | 1.5686 | 2.684 | 50.782 | 25.0453 | -0.88442 | 50.9177 | 30.3612 | -2.1968 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 34.5825 | 34.5825 | 20.0239 | 35.2574 | 34.481 | 18.253 | 36.0902 | 32.7592 | 16.5615 | 37.1529 | 29.1741 | 14.4464 | 38.5822 | 29.4136 | 10.6464 | 40.0295 | 26.4463 | 6.7914 | 41.418 | 23.1092 | 2.8982 | 45.5331 | 19.0157 | -8.4254 | 49.3285 | 15.926 | -18.069 | 51.7115 | 12.8998 | -24.1754 | 52.4326 | 11.9836 | -26.2184 | 51.7894 | 9.6658 | -23.1236
STAINBURN & SIDDICK | HARKER / HUTTON | 302535 | 529330 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.079 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.7308 | 6.7308 | 1.9358 | 6.1526 | 6.7308 | 1.9358 | 6.7308
STRETFORD | SOUTH MANCHESTER | 380069 | 395104 | 133.7021 | 37.9336 | 73.116 | 134.0798 | 36.7643 | 66.3151 | 135.4405 | 35.2492 | 61.3185 | 136.0679 | 34.2305 | 58.1861 | 136.8755 | 33.2283 | 55.0483 | 137.8704 | 31.4009 | 51.7839 | 139.0574 | 29.7328 | 48.7148 | 140.4659 | 28.6143 | 46.0917 | 142.0535 | 27.3687 | 43.0707 | 143.3199 | 26.3622 | 40.002 | 136.8555 | 24.8278 | 24.1553 | 141.5929 | 25.6872 | 9.3511 | 166.8206 | 31.3755 | -4.0848 | 168.605 | 42.5632 | -12.8296 | 168.9171 | 47.0591 | -19.0421 | 133.6332 | 37.9336 | 73.116 | 133.8662 | 37.8742 | 71.1377 | 134.2441 | 37.2177 | 69.8465 | 134.5785 | 36.7831 | 68.8068 | 134.9165 | 36.2567 | 67.6861 | 135.2615 | 35.2206 | 66.5154 | 135.7192 | 30.2541 | 65.1595 | 136.3463 | 29.8437 | 63.6901 | 137.1251 | 29.4233 | 62.2102 | 138.0125 | 29.1551 | 60.6321 | 141.2882 | 28.4048 | 55.4073 | 146.2189 | 29.3259 | 48.5892 | 154.0495 | 33.7377 | 38.6019 | 157.4529 | 42.7575 | 32.1378 | 164.6433 | 47.3119 | 22.2884 | 133.7208 | 37.9336 | 73.116 | 134.2216 | 36.5074 | 65.1118 | 135.706 | 34.7515 | 55.6054 | 136.4783 | 33.5094 | 47.9909 | 137.4224 | 32.2868 | 44.0998 | 138.538 | 30.54 | 40.2373 | 139.8228 | 28.5895 | 35.96 | 140.8366 | 27.2059 | 32.172 | 141.767 | 25.7188 | 28.1131 | 134.8749 | 24.4685 | 24.0102 | 122.76 | 22.2706 | 1.5513 | 125.0214 | 22.6809 | -16.8628 | 156.3071 | 28.3566 | -25.9 | 170.9014 | 39.6459 | -32.883 | 170.4914 | 44.3604 | -36.6536 | 133.7209 | 37.9336 | 73.116 | 133.9637 | 36.9672 | 67.7408 | 135.3417 | 36.0043 | 58.9226 | 136.0767 | 35.6163 | 51.3472 | 137.0249 | 35.4036 | 47.4689 | 138.6094 | 34.6598 | 43.1336 | 141.3115 | 33.573 | 36.5637 | 148.7367 | 34.2957 | 23.9377 | 158.5454 | 34.2509 | 8.6977 | 159.5384 | 34.4976 | 2.9499 | 163.9494 | 50.435 | -11.6807 | 166.8444 | 47.3096 | -22.6494 | 168.48 | 45.1542 | -30.3394 | 169.5229 | 47.3733 | -34.0685 | 168.4011 | 46.2305 | -31.1965 | 133.702 | 37.9336 | 73.116 | 134.0325 | 37.5007 | 69.812 | 135.322 | 36.1473 | 65.5573 | 135.8017 | 35.1681 | 62.651 | 136.3486 | 34.2367 | 59.9206 | 137.0594 | 32.4655 | 57.063 | 137.9535 | 30.8545 | 54.3263 | 139.0489 | 29.7805 | 51.9587 | 140.3998 | 28.5635 | 49.0936 | 141.9174 | 27.5703 | 46.1165 | 145.8898 | 26.4667 | 32.7919 | 155.8256 | 28.2692 | 23.46 | 164.2204 | 34.7613 | 14.6064 | 165.9586 | 46.8667 | 10.628 | 165.9025 | 52.2928 | 9.2169 | 133.702 | 37.9336 | 73.116 | 134.0015 | 36.3326 | 64.5972 | 135.453 | 35.1943 | 54.9324 | 136.2604 | 34.7469 | 47.3421 | 137.2412 | 34.488 | 43.2504 | 138.7521 | 33.717 | 38.8085 | 141.5378 | 32.6079 | 32.1629 | 148.8689 | 33.3021 | 19.392 | 158.4871 | 33.2477 | 4.1266 | 159.2977 | 33.4798 | -1.6467 | 163.6155 | 49.3252 | -16.6479 | 167.578 | 46.1018 | -28.3996 | 169.5519 | 43.8445 | -36.9064 | 170.7822 | 45.9774 | -41.6933 | 169.7685 | 44.7097 | -39.5252
STUART ST | STALYBRIDGE | 387247 | 398875 | 20.1439 | 3.6544 | 20.1439 | 10.6707 | 1.9358 | 5.6598 | 10.6707 | 1.9358 | -4.701 | 10.6707 | 1.9358 | -10.6526 | 10.6707 | 1.9358 | -17.1065 | 10.6707 | 1.9358 | -23.6641 | 10.6707 | 1.9358 | -29.5154 | 10.6707 | 1.9358 | -33.9617 | 10.6707 | 1.9358 | -37.6296 | 10.6707 | 1.9358 | -41.4439 | 10.6707 | 1.9358 | -54.5332 | 10.6707 | 1.9358 | -70.7625 | 10.6707 | 1.9358 | -83.2833 | 10.6707 | 1.9358 | -98.5328 | 10.6707 | 1.9358 | -108.7376 | 20.1439 | 3.6544 | 20.1439 | 8.7847 | 1.5937 | 8.7847 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 7.1927 | 10.6707 | 1.9358 | 2.6466 | 10.6707 | 1.9358 | -2.1437 | 10.6707 | 1.9358 | -5.4593 | 10.6707 | 1.9358 | -8.5681 | 10.6707 | 1.9358 | -11.7388 | 10.6707 | 1.9358 | -21.1021 | 10.6707 | 1.9358 | -30.4958 | 10.6707 | 1.9358 | -39.1905 | 10.6707 | 1.9358 | -49.6911 | 10.6707 | 1.9358 | -56.8881 | 20.1439 | 3.6544 | 20.1439 | 10.6707 | 1.9358 | 1.7612 | 10.6707 | 1.9358 | -10.1287 | 10.6707 | 1.9358 | -16.9246 | 10.6707 | 1.9358 | -24.2346 | 10.6707 | 1.9358 | -31.6699 | 10.6707 | 1.9358 | -38.3768 | 10.6707 | 1.9358 | -42.7367 | 10.6707 | 1.9358 | -47.1594 | 10.6707 | 1.9358 | -51.5744 | 10.6707 | 1.9358 | -67.0849 | 10.6707 | 1.9358 | -83.9877 | 10.6707 | 1.9358 | -97.4088 | 10.6707 | 1.9358 | -111.8142 | 10.6707 | 1.9358 | -119.5325 | 20.1439 | 3.6544 | 20.1439 | 10.6707 | 1.9358 | 9.8855 | 10.6707 | 1.9358 | -0.19042 | 10.6707 | 1.9358 | -6.7434 | 10.6707 | 1.9358 | -13.868 | 10.6707 | 1.9358 | -21.208 | 10.6707 | 1.9358 | -28.3421 | 10.6707 | 1.9358 | -34.6101 | 10.6707 | 1.9358 | -41.0142 | 10.6707 | 1.9358 | -47.3245 | 10.6707 | 1.9358 | -65.1898 | 10.6707 | 1.9358 | -81.6521 | 10.6707 | 1.9358 | -95.2781 | 10.6707 | 1.9358 | -105.7073 | 9.2518 | 1.9358 | -106.8448 | 20.1439 | 3.6544 | 20.1439 | 1.5798 | 0.2866 | 1.5798 | 10.6707 | 1.9358 | 8.3507 | 10.6707 | 1.9358 | 2.8681 | 10.6707 | 1.9358 | -2.9188 | 10.6707 | 1.9358 | -8.9951 | 10.6707 | 1.9358 | -14.5482 | 10.6707 | 1.9358 | -18.8802 | 10.6707 | 1.9358 | -22.594 | 10.6707 | 1.9358 | -26.5434 | 10.6707 | 1.9358 | -37.7748 | 10.6707 | 1.9358 | -49.1735 | 10.6707 | 1.9358 | -57.6426 | 10.6707 | 1.9358 | -67.2647 | 10.6707 | 1.9358 | -71.6122 | 20.1439 | 3.6544 | 20.1439 | 10.6707 | 1.9358 | -1.0573 | 10.6707 | 1.9358 | -13.5889 | 10.6707 | 1.9358 | -20.449 | 10.6707 | 1.9358 | -27.8465 | 10.6707 | 1.9358 | -35.3279 | 10.6707 | 1.9358 | -42.5735 | 10.6707 | 1.9358 | -49.0652 | 10.6707 | 1.9358 | -55.5542 | 10.6707 | 1.9358 | -61.9409 | 10.6707 | 1.9358 | -80.0729 | 10.6707 | 1.9358 | -97.556 | 10.6707 | 1.9358 | -112.0587 | 9.3175 | 1.9358 | -123.3355 | 0.61367 | 0.25206 | -125.3863
THORNTON | PENWORTHAM WEST / STANAH | 334559 | 443368 | 25.4306 | 16.5588 | 25.4306 | 25.8654 | 15.9981 | 25.8654 | 26.235 | 15.4771 | 26.235 | 26.594 | 14.9278 | 26.594 | 27.0282 | 13.3598 | 27.0282 | 27.4816 | 11.6175 | 27.4816 | 27.9613 | 9.2692 | 27.9613 | 28.4979 | 7.1235 | 28.4979 | 29.006 | 5.3015 | 29.006 | 19.743 | 3.5817 | 19.743 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 4.3293 | 9.3337 | 1.6933 | -3.8482 | 12.6501 | 2.2949 | -11.5131 | 25.4947 | 16.5588 | 25.4947 | 26.1383 | 16.3002 | 26.1383 | 26.659 | 16.0352 | 26.659 | 27.3068 | 15.712 | 27.3068 | 28.0063 | 14.9492 | 28.0063 | 28.4771 | 14.2232 | 28.4771 | 29.0439 | 11.3682 | 29.0439 | 29.702 | 10.6353 | 29.702 | 30.1979 | 9.9624 | 29.7632 | 30.7193 | 9.3423 | 28.5845 | 32.4215 | 7.8872 | 25.0615 | 34.0881 | 7.329 | 21.2416 | 35.4723 | 8.4602 | 17.6337 | 38.2486 | 12.6811 | 12.1309 | 39.2237 | 15.0624 | 9.1923 | 25.3955 | 16.5588 | 25.3955 | 25.8055 | 15.8872 | 25.8055 | 26.0897 | 15.1925 | 26.0897 | 26.3492 | 14.4796 | 26.3492 | 26.6616 | 12.5391 | 26.6616 | 26.9669 | 10.3788 | 26.9669 | 27.2495 | 7.5309 | 27.2495 | 27.0281 | 4.9033 | 22.936 | 14.2153 | 2.5789 | 14.2153 | 2.105 | 0.38189 | 2.105 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 4.8727 | 10.6707 | 1.9358 | -2.4114 | 10.6707 | 1.9358 | -9.8201 | 10.6707 | 1.9358 | -16.5713 | 25.3956 | 16.5588 | 25.3956 | 25.2568 | 16.145 | 25.2568 | 25.2603 | 15.6242 | 25.2603 | 25.2733 | 14.889 | 25.2733 | 25.397 | 12.6546 | 25.397 | 25.595 | 10.3737 | 25.595 | 25.8376 | 6.9635 | 25.8376 | 23.1251 | 4.1953 | 23.1251 | 8.6493 | 1.5691 | 8.6493 | 10.6707 | 1.9358 | 10.6707 | 19.7403 | 3.5812 | 6.9614 | 10.6707 | 1.9358 | -1.6594 | 10.6707 | 1.9358 | -8.2614 | 10.6707 | 1.9358 | -12.4589 | 10.6707 | 1.9358 | -10.5018 | 25.4305 | 16.5588 | 25.4305 | 25.8145 | 16.1923 | 25.8145 | 26.0647 | 15.733 | 26.0647 | 26.2631 | 15.2249 | 26.2631 | 26.5402 | 13.744 | 26.5402 | 26.9525 | 12.0424 | 26.9525 | 27.4858 | 9.7246 | 27.4858 | 28.058 | 7.587 | 28.058 | 28.5595 | 5.741 | 28.5595 | 21.987 | 3.9888 | 21.987 | 2.8387 | 0.51499 | 2.8387 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 25.1968 | 4.5711 | 15.1579 | 35.6514 | 6.4677 | 13.5838 | 25.4305 | 16.5588 | 25.4305 | 25.5214 | 15.9403 | 25.5214 | 25.8041 | 15.3364 | 25.8041 | 26.1416 | 14.5383 | 26.1416 | 26.572 | 12.2702 | 26.572 | 27.0045 | 9.9655 | 27.0045 | 27.5121 | 6.5266 | 27.5121 | 20.5613 | 3.7302 | 20.5613 | 5.1448 | 0.93334 | 5.1448 | 10.6707 | 1.9358 | 10.6707 | 13.4322 | 2.4368 | 0.13511 | 10.6707 | 1.9358 | -10.9433 | 10.6707 | 1.9358 | -19.9783 | 10.6707 | 1.9358 | -27.3274 | 10.6707 | 1.9358 | -29.2224
ULVERSTON | HARKER / HUTTON | 327495 | 477808 | 40.814 | 40.814 | 37.8293 | 41.3191 | 40.1158 | 36.2213 | 42.082 | 39.1029 | 35.3845 | 42.9963 | 38.1347 | 34.7967 | 44.028 | 36.8013 | 33.7009 | 45.1382 | 35.6305 | 32.5647 | 45.8599 | 34.4896 | 31.71 | 46.6767 | 33.664 | 30.9607 | 47.3476 | 32.8826 | 30.0555 | 47.9097 | 32.11 | 29.2745 | 51.0436 | 29.0848 | 21.7153 | 54.6214 | 25.5103 | 9.0033 | 56.0745 | 22.5098 | -0.432 | 60.7073 | 21.1293 | -13.3952 | 61.3879 | 20.2525 | -21.6048 | 40.8163 | 40.8163 | 37.8293 | 41.3501 | 40.4759 | 36.9898 | 41.9701 | 40.042 | 36.3036 | 42.7821 | 39.5453 | 35.6223 | 43.8787 | 38.7798 | 34.7848 | 44.3692 | 37.9985 | 33.9435 | 44.7918 | 34.0146 | 32.8596 | 45.2901 | 33.26 | 30.4993 | 45.6952 | 32.614 | 29.8486 | 46.1049 | 32.0813 | 29.2023 | 47.3518 | 30.6299 | 26.8196 | 49.392 | 30.4701 | 23.3008 | 50.6682 | 29.7355 | 20.7376 | 56.1658 | 29.2745 | 13.435 | 57.7411 | 29.3245 | 9.9395 | 40.8156 | 40.8156 | 37.8293 | 41.3263 | 39.9683 | 36.1154 | 42.0931 | 38.7614 | 35.3291 | 43.0148 | 37.6997 | 34.8903 | 44.0508 | 36.2417 | 33.9431 | 45.0091 | 35.023 | 32.9802 | 45.8009 | 33.7633 | 32.378 | 46.6971 | 32.8781 | 31.8966 | 47.7824 | 31.9553 | 31.2323 | 48.3454 | 31.1104 | 30.7494 | 55.861 | 27.0692 | 19.6835 | 59.0987 | 23.2003 | 8.1123 | 60.4568 | 19.5962 | -0.54703 | 61.4504 | 17.8531 | -9.1129 | 61.8178 | 15.8626 | -16.2242 | 40.8156 | 40.8156 | 37.8293 | 40.7704 | 40.1735 | 37.4962 | 41.0651 | 39.0902 | 37.0468 | 41.5354 | 37.8503 | 36.508 | 42.1124 | 36.33 | 35.5996 | 43.8591 | 34.7813 | 33.7871 | 46.3437 | 28.4778 | 30.903 | 50.7501 | 21.7922 | 23.9166 | 51.9681 | 15.5875 | 20.0538 | 50.7427 | 9.2055 | 15.6654 | 7.9436 | 1.4411 | 4.7017 | 10.6707 | 1.9358 | -4.9582 | 10.6707 | 1.9358 | -12.7012 | 10.6707 | 1.9358 | -17.1297 | 10.6707 | 1.9358 | -13.0149 | 40.814 | 40.814 | 37.8293 | 41.2319 | 40.371 | 37.011 | 41.7394 | 39.4237 | 36.388 | 42.2874 | 38.4842 | 35.9597 | 42.962 | 37.2175 | 35.3558 | 43.9782 | 36.1163 | 34.7496 | 45.2057 | 35.0135 | 34.1682 | 45.9858 | 34.1944 | 33.4673 | 46.6466 | 33.4061 | 32.4552 | 47.2384 | 32.6189 | 31.4563 | 50.2078 | 30.0205 | 26.482 | 53.2213 | 27.5703 | 20.7915 | 54.1786 | 25.5373 | 17.8682 | 58.3527 | 25.1123 | 11.5989 | 58.4539 | 24.8853 | 10.5066 | 40.814 | 40.814 | 37.8293 | 41.0755 | 39.9291 | 36.7048 | 41.8061 | 38.7575 | 35.85 | 42.7888 | 37.4778 | 34.9599 | 43.8179 | 35.9097 | 33.72 | 45.7559 | 34.3333 | 31.6625 | 48.0937 | 28.002 | 28.4824 | 52.5182 | 21.2629 | 21.1047 | 53.4772 | 15.0729 | 16.9898 | 48.1218 | 8.7301 | 12.3483 | 3.6454 | 0.66133 | 0.60771 | 10.6707 | 1.9358 | -9.7137 | 10.6707 | 1.9358 | -18.1232 | 10.6707 | 1.9358 | -23.4095 | 10.6707 | 1.9358 | -20.2753
VERNON PARK | BREDBURY | 391131 | 390929 | 84.6186 | 19.6845 | 16.2219 | 85.103 | 17.0891 | 9.5984 | 79.1571 | 14.3604 | 6.3861 | 63.9985 | 11.6104 | 3.5423 | 48.2326 | 8.7502 | 0.38394 | 23.132 | 4.1965 | -5.4425 | 6.6996 | 1.2154 | -8.5609 | 10.6707 | 1.9358 | -11.7433 | 10.6707 | 1.9358 | -16.727 | 10.6707 | 1.9358 | -19.7507 | 10.6707 | 1.9358 | -37.8314 | 10.6707 | 1.9358 | -56.949 | 10.6707 | 1.9358 | -71.1642 | 10.6707 | 1.9358 | -86.5474 | 10.6707 | 1.9358 | -97.3739 | 84.4446 | 19.6845 | 16.2219 | 84.9938 | 17.8136 | 12.2834 | 83.9939 | 15.2378 | 10.0054 | 69.4749 | 12.6039 | 7.8495 | 54.4556 | 9.8791 | 5.498 | 38.571 | 6.9974 | 3.0594 | 10.6707 | 1.9358 | 0.24646 | 10.6707 | 1.9358 | -2.9399 | 10.6707 | 1.9358 | -5.6062 | 10.6707 | 1.9358 | -8.3134 | 10.6707 | 1.9358 | -15.6347 | 10.6707 | 1.9358 | -23.9656 | 10.6707 | 1.9358 | -31.4067 | 10.6707 | 1.9358 | -40.7876 | 10.6707 | 1.9358 | -46.0805 | 84.6562 | 19.6845 | 16.2219 | 85.179 | 16.8301 | 8.7771 | 76.2017 | 13.8242 | 5.192 | 59.6538 | 10.8222 | 2.0633 | 42.7302 | 7.7519 | -1.3937 | 16.6052 | 3.0125 | -7.5289 | 10.6707 | 1.9358 | -13.021 | 10.6707 | 1.9358 | -16.6968 | 10.6707 | 1.9358 | -21.9392 | 10.6707 | 1.9358 | -25.2009 | 10.6707 | 1.9358 | -42.548 | 10.6707 | 1.9358 | -60.868 | 10.6707 | 1.9358 | -74.6823 | 10.6707 | 1.9358 | -87.293 | 10.6707 | 1.9358 | -96.084 | 84.6563 | 19.6845 | 16.2219 | 84.6528 | 17.3638 | 11.2768 | 83.993 | 15.2377 | 8.4528 | 66.5547 | 12.0741 | 1.0201 | 53.9225 | 9.7824 | -1.9119 | 37.7783 | 6.8536 | -7.7161 | 29.4878 | 5.3496 | -11.888 | 17.6204 | 3.1966 | -21.3774 | 6.1995 | 1.1247 | -30.265 | 10.6707 | 1.9358 | -36.6991 | 10.6707 | 1.9358 | -53.5201 | 10.6707 | 1.9358 | -70.3725 | 10.6707 | 1.9358 | -82.1832 | 10.6707 | 1.9358 | -89.4346 | 10.6707 | 1.9358 | -86.4826 | 84.6181 | 19.6845 | 16.2219 | 85.036 | 17.5968 | 11.4624 | 82.8834 | 15.0364 | 8.8452 | 68.299 | 12.3905 | 6.4617 | 53.3998 | 9.6876 | 4.0058 | 29.1413 | 5.2867 | -1.2161 | 13.2669 | 2.4068 | -3.9305 | 1.4622 | 0.26526 | -6.8148 | 10.6707 | 1.9358 | -11.6834 | 10.6707 | 1.9358 | -14.7146 | 10.6707 | 1.9358 | -27.2909 | 10.6707 | 1.9358 | -37.1758 | 10.6707 | 1.9358 | -43.6603 | 10.6707 | 1.9358 | -51.1203 | 10.6707 | 1.9358 | -54.3325 | 84.6181 | 19.6845 | 16.2219 | 84.7656 | 16.8462 | 9.3729 | 79.965 | 14.5069 | 5.8015 | 61.8217 | 11.2154 | -2.135 | 48.6 | 8.8168 | -5.4754 | 32.0554 | 5.8154 | -11.4526 | 23.4187 | 4.2485 | -15.7385 | 11.042 | 2.0032 | -25.5503 | 10.6707 | 1.9358 | -34.6274 | 10.6707 | 1.9358 | -41.1562 | 10.6707 | 1.9358 | -61.0918 | 10.6707 | 1.9358 | -79.0814 | 10.6707 | 1.9358 | -92.0353 | 10.6707 | 1.9358 | -100.452 | 10.6707 | 1.9358 | -98.8484
WEST DIDSBURY | SOUTH MANCHESTER | 382900 | 393269 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 5.5366 | 1.9358 | 5.5366 | -1.4196 | -0.5831 | -1.4196 | -8.3653 | -3.436 | -8.3653 | -15.3156 | -6.2908 | -15.3156 | -27.1214 | -11.1399 | -27.1214 | -40.2874 | -16.5478 | -40.2874 | -51.1469 | -21.0082 | -51.1469 | -58.3879 | -23.9824 | -58.3879 | -65.251 | -26.8014 | -65.251 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 9.317 | 1.9358 | 9.317 | 7.0489 | 1.9358 | 7.0489 | 5.1101 | 1.9358 | 5.1101 | 0.10171 | 0.041778 | 0.10171 | -0.11336 | -0.046561 | -0.11336 | -2.2125 | -0.90877 | -2.2125 | -3.6738 | -1.509 | -3.6738 | -5.7528 | -2.3629 | -5.7528 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.1224 | 1.9358 | 10.1224 | 1.07 | 0.4395 | 1.07 | -6.4354 | -2.6433 | -6.4354 | -13.9231 | -5.7188 | -13.9231 | -21.4608 | -8.8149 | -21.4608 | -35.5876 | -14.6174 | -35.5876 | -50.388 | -20.6965 | -50.388 | -64.3406 | -26.4274 | -64.3406 | -76.2906 | -31.3358 | -76.2906 | -87.4001 | -35.8989 | -87.4001 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 8.4546 | 1.9358 | 8.4546 | -0.65065 | -0.26725 | -0.65065 | -20.3958 | -8.3774 | -20.3958 | -37.1926 | -15.2766 | -37.1926 | -52.9716 | -21.7577 | -52.9716 | -66.3177 | -27.2395 | -66.3177 | -80.0095 | -32.8633 | -80.0095 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 9.2032 | 1.9358 | 9.2032 | 2.49 | 1.0227 | 2.49 | -4.3553 | -1.7889 | -4.3553 | -11.1615 | -4.5845 | -11.1615 | -20.8047 | -8.5454 | -20.8047 | -29.2456 | -12.0124 | -29.2456 | -36.3644 | -14.9364 | -36.3644 | -40.1081 | -16.4741 | -40.1081 | -43.8898 | -18.0274 | -43.8898 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.6707 | 1.9358 | 10.6707 | 10.3311 | 1.9358 | 10.3311 | 4.9971 | 1.9358 | 4.9971 | -4.3297 | -1.7784 | -4.3297 | -24.6675 | -10.132 | -24.6675 | -42.1589 | -17.3165 | -42.1589 | -58.5658 | -24.0554 | -58.5658 | -72.5537 | -29.8009 | -72.5537 | -86.7932 | -35.6496 | -86.7932
WESTHOUGHTON | KEARSLEY | 365831 | 407025 | 88.7474 | 39.7544 | 52.4555 | 89.0795 | 33.2904 | 46.7101 | 89.5421 | 26.3373 | 44.2376 | 89.9958 | 19.5362 | 39.6527 | 69.6933 | 12.6435 | 34.6925 | 31.0521 | 5.6333 | 31.0521 | 22.6942 | 4.1171 | 22.6942 | 19.4788 | 3.5338 | 19.4788 | 15.9427 | 2.8923 | 15.9427 | 13.863 | 2.515 | 13.863 | 4.4866 | 0.81394 | 4.4866 | 10.6707 | 1.9358 | -5.814 | 7.8355 | 1.4215 | -16.731 | 109.5676 | 24.113 | -27.193 | 110.7842 | 22.4475 | -35.3699 | 88.6341 | 39.7544 | 52.4555 | 88.9346 | 34.0156 | 50.434 | 89.2903 | 27.4396 | 49.9047 | 89.5809 | 20.8113 | 46.4833 | 78.1496 | 14.1776 | 42.8717 | 41.4198 | 7.5142 | 41.4198 | 5.8175 | 1.0554 | 5.8175 | 3.898 | 0.70716 | 3.898 | 1.5759 | 0.28589 | 1.5759 | 0.28523 | 0.051746 | 0.28523 | 10.6707 | 1.9358 | 10.6707 | 4.8761 | 0.88459 | 4.8761 | 13.665 | 2.479 | 13.665 | 92.8663 | 16.8474 | 8.0004 | 107.1024 | 30.7899 | 3.538 | 88.7779 | 39.7544 | 52.4555 | 89.1354 | 33.0869 | 45.8854 | 89.6076 | 25.9987 | 42.9835 | 90.094 | 19.0936 | 38.0976 | 66.462 | 12.0573 | 32.8457 | 27.8364 | 5.05 | 27.8364 | 19.0352 | 3.4533 | 19.0352 | 15.4278 | 2.7988 | 15.4278 | 11.6188 | 2.1078 | 11.6188 | 9.1872 | 1.6667 | 9.1872 | 10.6707 | 1.9358 | 8.7097 | 10.6707 | 1.9358 | -6.1005 | 10.6707 | 1.9358 | -16.5987 | 110.0028 | 22.4204 | -25.5648 | 110.7769 | 21.5662 | -31.2156 | 88.7781 | 39.7544 | 52.4555 | 88.7999 | 33.6093 | 48.6261 | 89.0977 | 27.0952 | 46.4283 | 89.4326 | 20.5611 | 41.7111 | 69.5339 | 12.6146 | 36.4927 | 28.2434 | 5.1238 | 28.2434 | 16.0198 | 2.9063 | 16.0198 | 8.9796 | 1.629 | 8.9796 | 3.991 | 0.72403 | 3.991 | 9.6934 | 1.7585 | 9.6934 | 101.1346 | 23.8439 | -1.9356 | 104.9653 | 20.1336 | -14.8064 | 94.5579 | 17.1543 | -23.3831 | 82.5765 | 14.9807 | -28.0993 | 75.4888 | 13.6949 | -24.7327 | 88.7473 | 39.7544 | 52.4555 | 89.0157 | 33.8064 | 49.3222 | 89.384 | 27.0119 | 47.6709 | 89.6632 | 20.256 | 43.4652 | 74.3912 | 13.4957 | 39.1473 | 36.2922 | 6.584 | 36.2922 | 28.188 | 5.1138 | 28.188 | 25.1662 | 4.5655 | 25.1662 | 21.7257 | 3.9414 | 21.7257 | 19.6639 | 3.5673 | 19.6639 | 13.1307 | 2.3821 | 13.1307 | 13.4892 | 2.4472 | 9.4044 | 28.3427 | 5.1418 | 3.5787 | 107.0962 | 28.7659 | -1.0459 | 107.7938 | 28.8703 | -3.1554 | 88.7473 | 39.7544 | 52.4555 | 88.8711 | 33.0807 | 45.9189 | 89.2996 | 26.401 | 42.8399 | 89.766 | 19.7813 | 37.6957 | 64.8734 | 11.7691 | 32.1147 | 23.4504 | 4.2543 | 23.4504 | 11.1315 | 2.0194 | 11.1315 | 3.8785 | 0.70362 | 3.8785 | 10.6707 | 1.9358 | 10.6707 | 4.3711 | 0.79299 | 4.3711 | 101.3448 | 22.551 | -8.3019 | 103.4219 | 18.7624 | -22.4308 | 85.2108 | 15.4586 | -32.2543 | 73.0689 | 13.2559 | -38.178 | 65.3492 | 11.8554 | -35.9214
WIGAN | WASHWAY FARM / KIRKBY | 358343 | 404626 | 88.6502 | 74.5137 | 57.2167 | 89.2281 | 73.0528 | 51.9383 | 89.7702 | 71.6426 | 50.324 | 90.4549 | 70.3547 | 49.3407 | 91.5701 | 67.8445 | 47.8927 | 92.7646 | 65.4862 | 46.3597 | 93.8934 | 63.185 | 44.9128 | 94.9978 | 61.5028 | 43.5421 | 96.045 | 59.7782 | 41.9277 | 97.0711 | 59.2695 | 40.3739 | 102.8159 | 54.915 | 31.4081 | 105.8041 | 51.3401 | 17.772 | 107.8228 | 50.8507 | 5.6941 | 109.3493 | 51.0972 | -7.0252 | 110.1498 | 48.9657 | -18.2143 | 88.6434 | 74.5137 | 57.2167 | 89.0677 | 74.0239 | 55.452 | 89.3594 | 73.232 | 54.4927 | 89.7 | 72.471 | 53.7718 | 90.1631 | 71.6504 | 52.8705 | 90.6388 | 70.848 | 51.8398 | 91.2641 | 65.8275 | 50.4971 | 92.1092 | 65.3071 | 48.7855 | 92.9077 | 64.8558 | 47.4256 | 93.7509 | 64.567 | 46.0142 | 96.3292 | 63.7791 | 41.7113 | 99.1085 | 64.7006 | 37.2346 | 101.8709 | 65.9353 | 32.945 | 104.9742 | 67.1413 | 28.2393 | 107.2922 | 66.924 | 24.9798 | 88.6531 | 74.5137 | 57.2167 | 89.2477 | 72.8227 | 51.2679 | 89.7966 | 71.2301 | 40.6446 | 90.4959 | 69.8254 | 30.8888 | 91.6187 | 67.2519 | 29.3392 | 92.8166 | 64.833 | 27.7401 | 93.9519 | 62.4633 | 26.2738 | 95.0729 | 60.7183 | 24.887 | 96.0855 | 58.9751 | 23.5505 | 97.0418 | 58.416 | 22.2991 | 102.5957 | 53.9257 | 15.1514 | 105.6766 | 50.1529 | 1.6028 | 107.8464 | 49.4938 | -9.7308 | 109.4715 | 49.5691 | -21.3592 | 110.2122 | 47.4527 | -31.2617 | 88.6531 | 74.5137 | 57.2167 | 88.7021 | 73.3205 | 54.0224 | 89.0564 | 72.3478 | 44.098 | 89.7204 | 71.5605 | 34.4841 | 90.8277 | 69.6699 | 32.9878 | 92.1187 | 67.7421 | 31.3206 | 94.1196 | 60.9175 | 28.8905 | 96.6961 | 54.4488 | 23.8239 | 97.6939 | 48.021 | 18.6602 | 98.7196 | 42.5105 | 13.5722 | 101.8615 | 41.1832 | 0.2284 | 104.7206 | 40.7081 | -12.5478 | 106.5757 | 37.4331 | -22.8782 | 107.6933 | 34.4751 | -29.3854 | 107.4973 | 33.1419 | -25.3455 | 88.6502 | 74.5137 | 57.2167 | 89.1298 | 73.6416 | 54.6177 | 89.5427 | 72.3699 | 53.7108 | 89.955 | 71.1507 | 53.0855 | 90.4918 | 68.7531 | 52.3317 | 91.1472 | 66.4745 | 51.4258 | 91.9397 | 64.2222 | 50.3751 | 92.8788 | 62.5775 | 49.2109 | 93.9146 | 60.855 | 47.6368 | 95.0182 | 60.3402 | 46.019 | 98.7773 | 56.5472 | 39.6548 | 102.9915 | 54.3344 | 32.6362 | 105.6554 | 55.165 | 27.7438 | 106.9621 | 56.9957 | 23.7827 | 107.3806 | 56.4049 | 22.142 | 88.6502 | 74.5137 | 57.2167 | 88.8045 | 72.7402 | 51.4419 | 89.3242 | 71.5988 | 40.6735 | 90.1824 | 70.7459 | 30.6373 | 91.4473 | 68.7885 | 28.7562 | 92.7626 | 66.8253 | 26.8351 | 94.7471 | 59.9646 | 24.1049 | 97.3905 | 53.4442 | 18.6292 | 98.3553 | 46.974 | 13.2118 | 99.3486 | 41.4152 | 7.8638 | 102.5056 | 39.9244 | -6.3863 | 105.4609 | 39.3736 | -20.0461 | 107.4691 | 35.984 | -31.2813 | 108.6515 | 32.8766 | -38.8663 | 108.5432 | 31.3983 | -36.0161
WRIGHTINGTON | PENWORTHAM WEST / STANAH | 354460 | 413610 | 79.8381 | 38.9553 | 9.179 | 80.5433 | 37.3801 | -1.2551 | 81.6491 | 35.0655 | -7.5674 | 83.0413 | 32.9105 | -9.1576 | 84.6432 | 29.6564 | -11.5035 | 86.3109 | 26.0683 | -13.9872 | 87.8619 | 23.5561 | -16.1561 | 89.6233 | 22.1547 | -18.4602 | 91.4344 | 21.094 | -21.4136 | 93.3308 | 20.0188 | -24.2971 | 87.975 | 15.9601 | -38.9671 | 63.8794 | 11.5887 | -61.0097 | 46.3652 | 8.4114 | -78.3967 | 37.8841 | 6.8728 | -95.9248 | 26.5665 | 4.8196 | -111.1189 | 79.6272 | 38.9553 | 9.179 | 80.1326 | 38.3465 | 6.9008 | 80.7652 | 37.3584 | 5.4585 | 81.5201 | 36.3466 | 4.111 | 82.5104 | 35.0847 | 2.3745 | 83.7709 | 33.7746 | 0.47086 | 85.3056 | 29.0341 | -2.0234 | 87.1055 | 28.0817 | -5.3681 | 88.5331 | 27.2338 | -8.3176 | 90.1063 | 26.4983 | -11.3449 | 94.5374 | 24.4277 | -20.8262 | 98.7828 | 23.7218 | -30.8849 | 102.9294 | 22.509 | -40.6301 | 107.2744 | 21.1747 | -51.7422 | 110.1702 | 21.2363 | -58.8856 | 79.927 | 38.9553 | 9.179 | 80.6878 | 37.0699 | -1.9812 | 81.9006 | 34.3731 | -8.4771 | 83.3899 | 31.8759 | -9.9399 | 85.0455 | 28.2754 | -12.2392 | 86.6377 | 24.8374 | -14.585 | 88.0173 | 22.021 | -16.4106 | 89.7481 | 20.3638 | -18.0271 | 91.3894 | 19.0985 | -20.143 | 93.1148 | 17.8161 | -22.3364 | 71.3713 | 12.9479 | -35.0237 | 41.4743 | 7.5241 | -55.8412 | 21.2858 | 3.8616 | -72.2592 | 10.9807 | 1.9921 | -88.3565 | 0.78011 | 0.14152 | -101.6401 | 79.9271 | 38.9553 | 9.179 | 80.0259 | 37.6516 | 1.746 | 80.6917 | 35.6732 | -3.7936 | 81.5606 | 33.1718 | -5.0258 | 82.7369 | 31.3149 | -7.2288 | 84.5016 | 29.5822 | -9.7232 | 86.2972 | 27.2301 | -12.9019 | 88.1847 | 25.2906 | -19.3088 | 90.1509 | 23.5947 | -26.2904 | 92.2222 | 21.4655 | -33.3714 | 98.6182 | 18.2304 | -53.794 | 72.8221 | 13.2111 | -73.2547 | 53.0584 | 9.6256 | -87.8551 | 51.1323 | 9.2762 | -97.144 | 34.7742 | 6.3086 | -92.6958 | 79.8379 | 38.9553 | 9.179 | 80.419 | 38.0384 | 2.2858 | 81.2039 | 35.863 | -3.1204 | 82.0913 | 33.7807 | -4.1916 | 83.2575 | 30.6224 | -5.607 | 84.9533 | 27.2831 | -7.2939 | 86.748 | 24.8262 | -9.0005 | 88.2577 | 23.4664 | -11.0616 | 89.7808 | 22.4166 | -14.0052 | 91.42 | 21.3221 | -17.0349 | 96.9999 | 17.8349 | -27.4629 | 80.5214 | 14.6079 | -38.8496 | 68.5173 | 12.4301 | -47.511 | 66.3559 | 12.038 | -55.2427 | 62.5854 | 11.354 | -58.723 | 79.8379 | 38.9553 | 9.179 | 80.1634 | 37.0839 | -1.4803 | 81.1946 | 34.9514 | -8.1791 | 82.5357 | 32.4277 | -10.1689 | 84.0866 | 30.2758 | -13.0389 | 85.6642 | 28.5201 | -15.9361 | 87.1873 | 26.1409 | -19.5703 | 89.1062 | 24.1282 | -26.6257 | 90.9785 | 22.407 | -34.0036 | 92.9505 | 20.2513 | -41.485 | 92.9056 | 16.8546 | -63.519 | 64.5777 | 11.7154 | -84.8559 | 43.6017 | 7.91 | -101.2772 | 40.4395 | 7.3364 | -112.4015 | 23.9925 | 4.3526 | -109.7101