## BAU Scenario
General information |  |  |  | Input data for assessment | [12 empty] | Intermediate data | [6 empty] | Output
Substation Number | Substation | Manufacturer | Grid Reference | Power Rating (kVA) | HV | LV | Transformer Age (till 2015) | Indoor/Outdoor | Number of customers | [7 empty] | Peak load (p.u.) |  | Moisture |  | Peak hot-spot temperature (°C) |  | Bubbling inception temperature (°C) | Loss-of-life (year per year) | Expected lifetime (p.u.) | Failure probability (%)
[9 empty] | PC1 | PC2 | PC3 | PC4 | PC5 | PC6 | PC7 | PC8 | No EVs | With EVs | In oil (ppm) | In paper (%) | No EVs | With EVs
165002 | LANCASTER RD SALFORD 6 | ABB | SD78720037 | 500 | 6.6 KV | LV | 13 | INDOOR | 372 | 15 | 5 | 2 | 0 | 0 | 0 | 0 | 0.99198 | N/A | 8.2455 | 5.2642 | 81.1897 | N/A | 114.0666 | 0.015405 | 1111.3322 | 0
165080 | ST MARGARETS RD, PRESTWICH | PAUWELS | SD82210493 | 800 | 6.6 KV | LV | 16 | INDOOR | 320 | 20 | 8 | 0 | 0 | 0 | 0 | 0 | 0.54738 | N/A | 8.9376 | 5.5613 | 51.0614 | N/A | 112.2814 | 0.0015315 | 11178.8207 | 0
165083 | NAZARETH HS, PRESTWICH | ABB | SD82260317 | 500 | 6.6 KV | LV | 14 | OUTDOOR | 212 | 7 | 7 | 0 | 0 | 1 | 0 | 0 | 0.6099 | N/A | 10.1006 | 6.0184 | 43.6167 | N/A | 110.0615 | 0.00058637 | 29196.8251 | 0
165133 | MANTON CL, BROUGHTON | FERRANTI | SD83620078 | 750 | 6.6 KV | LV | 50 | INDOOR | 75 | 82 | 1 | 2 | 0 | 0 | 0 | 0 | 0.27314 | N/A | 16.399 | 8.4146 | 36.7376 | N/A | 99.0988 | 0.00063152 | 27109.1302 | 0
165528 | BISHOP RD, PENDLETON | CROMPTON PARKINSON | SJ78889962 | 1000 | 6.6 KV | LV | 52 | INDOOR | 216 | 26 | 2 | 0 | 0 | 0 | 0 | 0 | 0.30159 | N/A | 16.836 | 8.5638 | 38.739 | N/A | 98.5734 | 0.00071216 | 24039.4779 | 0
165647 | HEATH AVE, SALFORD 7 | CROMPTON PARKINSON | SJ82429945 | 1000 | 6.6 KV | LV | 51 | INDOOR | 299 | 3 | 14 | 2 | 0 | 0 | 0 | 0 | 0.41697 | N/A | 16.593 | 8.4782 | 44.3649 | N/A | 98.8882 | 0.001024 | 16719.38 | 0
165756 | ALBANY CT URMSTON | ABB | SJ75999500 | 800 | 6.6 KV | LV | 13 | OUTDOOR | 153 | 39 | 3 | 0 | 0 | 0 | 0 | 0 | 0.30434 | N/A | 9.786 | 5.879 | 27.7636 | N/A | 110.9841 | 0.00020554 | 83293.3951 | 0
166355 | TRAFFORD RD 181 | BRUSH | SJ76769802 | 500 | 6.6 KV | LV | 30 | OUTDOOR | 369 | 6 | 7 | 1 | 1 | 0 | 0 | 1 | 1.0585 | N/A | 15.4781 | 8.0559 | 77.2891 | N/A | 100.7671 | 0.0096152 | 1780.5139 | 0
166499 | THE HAWTHORNS | SOUTH WALES SWITCHGEAR | SJ80509420 | 800 | 6.6 KV | LV | 27 | INDOOR | 27 | 75 | 2 | 1 | 0 | 0 | 0 | 0 | 0.18338 | N/A | 11.299 | 6.5344 | 34.8905 | N/A | 106.9609 | 0.00059513 | 28766.866 | 0
166588 | MONTON MILL GDN | SOUTH WALES SWITCHGEAR | SJ76319942 | 1000 | 6.6 KV | LV | 25 | INDOOR | 152 | 71 | 13 | 0 | 0 | 0 | 0 | 0 | 0.30959 | N/A | 10.5433 | 6.2278 | 39.5059 | N/A | 108.5866 | 0.00078641 | 21769.9095 | 0
166825 | DEEPDALE CT, NORTHWOLD DR M9 | HACKBRIDGE AND HEWITTIC | SD87850342 | 1000 | 6.6 KV | LV | 21 | OUTDOOR | 167 | 6 | 0 | 0 | 0 | 0 | 0 | 1 | 0.23986 | N/A | 12.5473 | 6.9829 | 25.6199 | N/A | 105.2416 | 0.00018143 | 94362.0974 | 0
171440 | CLOUGH RD, DROYLSDEN | LINDLEY THOMPSON | SJ90519893 | 750 | 6.6 KV | LV | 50 | INDOOR | 186 | 15 | 2 | 0 | 0 | 0 | 0 | 0 | 0.33512 | N/A | 16.4706 | 8.4417 | 38.9558 | N/A | 98.9811 | 0.00067462 | 25377.2193 | 0
171459 | LONGDEN RD LEVENSHULME, LONGDEN RD | BABCOCK | SJ87709485 | 800 | 6.6 KV | LV | 22 | OUTDOOR | 148 | 7 | 3 | 0 | 0 | 0 | 0 | 0 | 0.24726 | N/A | 12.7404 | 7.0507 | 25.8264 | N/A | 105.0066 | 0.0001823 | 93909.7129 | 0
171643 | RAMILLIES AVE, CHEADLE HULME | DISTRIBUTION TRANSFORMERS LTD | SJ87848631 | 500 | 11 KV | LV | 42 | INDOOR | 329 | 18 | 10 | 2 | 1 | 0 | 0 | 0 | 0.95932 | N/A | 14.6973 | 7.8119 | 80.1809 | N/A | 101.3934 | 0.015562 | 1100.1028 | 0
171832 | HOLLAND ST | EFACEC | SJ91789558 | 750 | 6.6 KV | LV | 2 | INDOOR | 241 | 13 | 8 | 1 | 1 | 1 | 1 | 0 | 0.53015 | N/A | 6.451 | 4.4666 | 50.2282 | N/A | 119.235 | 0.0015317 | 11177.3057 | 0
171852 | WESTBURY AVE 37 SALE, SALE | BONAR LONG | SJ76109039 | 500 | 11 KV | LV | 38 | OUTDOOR | 280 | 9 | 3 | 1 | 0 | 0 | 0 | 0 | 0.73216 | N/A | 18.3653 | 9.0594 | 50.3435 | N/A | 96.9956 | 0.00087213 | 19630.03 | 0
171966 | PARKFIELD RD S | BRUSH | SJ84259165 | 500 | 6.6 KV | LV | 33 | INDOOR | 188 | 19 | 12 | 1 | 0 | 0 | 0 | 0 | 0.58209 | N/A | 12.4831 | 6.9904 | 51.8338 | N/A | 104.8706 | 0.0015753 | 10867.4817 | 0
172014 | SCHOOL LN DIDSBURY | PAUWELS | SJ85339100 | 800 | 6.6 KV | LV | 16 | INDOOR | 225 | 64 | 9 | 0 | 0 | 1 | 0 | 0 | 0.49607 | N/A | 8.8939 | 5.5491 | 48.6474 | N/A | 112.2616 | 0.0014099 | 12143.0678 | 0
172242 | CARRGATE RD, DENTON | LINDLEY THOMPSON | SJ93939422 | 500 | 6.6 KV | LV | 53 | INDOOR | 179 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0.45222 | N/A | 17.282 | 8.7157 | 43.0328 | N/A | 98.0482 | 0.00079025 | 21663.974 | 0
172344 | FAIRFIELD RD 222, REAR 90 SILVERDAL ST | SOUTH WALES SWITCHGEAR | SJ89729760 | 500 | 6.6 KV | LV | 17 | OUTDOOR | 281 | 27 | 7 | 4 | 1 | 0 | 0 | 1 | 0.92259 | N/A | 11.0591 | 6.4037 | 66.8438 | N/A | 108.0483 | 0.0040018 | 4278.1156 | 0
172448 | ST WILFREDS ST HULME, OFF ST WILFRED'S S | SOUTH WALES SWITCHGEAR | SJ83189686 | 500 | 6.6 KV | LV | 21 | INDOOR | 306 | 20 | 21 | 4 | 0 | 0 | 0 | 0 | 0.95138 | N/A | 9.8032 | 5.9205 | 81.1518 | N/A | 110.2683 | 0.018277 | 936.7079 | 0
172508 | BRIARFIELDS,BOUNDARY LN, OPP BONSALL ST, | ABB | SJ84059683 | 800 | 6.6 KV | LV | 20 | OUTDOOR | 223 | 72 | 7 | 0 | 0 | 2 | 0 | 0 | 0.52074 | N/A | 11.8034 | 6.6889 | 38.4423 | N/A | 106.7666 | 0.00043088 | 39733.0644 | 0
172607 | BRITANNIA MILL, HULME HALL RD,HULME | SOUTH WALES SWITCHGEAR | SJ82599721 | 1000 | 6.6 KV | LV | 16 | INDOOR | 0 | 108 | 0 | 3 | 0 | 0 | 0 | 0 | 0.19629 | N/A | 8.464 | 5.3585 | 35.0945 | N/A | 113.4792 | 0.00058308 | 29361.5682 | 0
211326 | BEECH TREES S, OPP 113 (SKELM) | BRENTFORD TRANSFORMERS | SD49540503 | 1000 | 11 KV | LV | 24 | OUTDOOR | 189 | 59 | 1 | 0 | 0 | 0 | 1 | 0 | 0.32971 | N/A | 13.3452 | 7.2778 | 28.7692 | N/A | 104.0179 | 0.00021977 | 77899.2864 | 0
211505 | SMETHURST RD, OPP 2 ORRELL | FERRANTI | SD52630306 | 750 | 11 KV | LV | 50 | OUTDOOR | 326 | 20 | 12 | 3 | 0 | 0 | 0 | 0 | 0.6266 | N/A | 22.5084 | 10.3981 | 44.3679 | N/A | 92.6514 | 0.00060803 | 28156.3108 | 0
211944 | JENNET HEY, ADJ 12 ASHTON | ENGLISH ELECTRIC | SD56610065 | 500 | 6.6 KV | LV | 50 | INDOOR | 285 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0.75198 | N/A | 16.478 | 8.4373 | 62.0788 | N/A | 99.0524 | 0.0030433 | 5625.4235 | 0
211948 | PRIORY RD, ADJ 2 ASHTON | BRUSH | SD56940017 | 500 | 6.6 KV | LV | 46 | INDOOR | 289 | 6 | 1 | 1 | 0 | 0 | 0 | 0 | 0.73562 | N/A | 15.6494 | 8.148 | 60.3989 | N/A | 100.1274 | 0.0025857 | 6621.113 | 0
212333 | HORNE GR, OPP 18 W/MESNES | BONAR LONG | SD56950441 | 750 | 6.6 KV | LV | 47 | INDOOR | 117 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21037 | N/A | 15.8829 | 8.2341 | 34.5494 | N/A | 99.7679 | 0.00052856 | 32389.9752 | 0
212620 | MOSS LN, ADJ 31 PLATT BRIDGE | ENGLISH ELECTRIC | SD60390324 | 500 | 11 KV | LV | 51 | INDOOR | 321 | 22 | 9 | 3 | 0 | 0 | 0 | 0 | 0.91596 | N/A | 16.5383 | 8.4574 | 75.7066 | N/A | 98.985 | 0.0099536 | 1719.9766 | 0
212649 | ABINGDON DRIVE (ABRAM), OPP 13 ABINGDON | S&C ELECTRIC | SD64140212 | 500 | 11 KV | LV | 42 | OUTDOOR | 349 | 8 | 0 | 1 | 0 | 0 | 0 | 0 | 0.88162 | N/A | 19.6419 | 9.4804 | 60.5308 | N/A | 95.5822 | 0.0018864 | 9075.3331 | 0
212806 | CHURCH ST N, CHURCH ST WESTH'TON | ABB | SD65380671 | 500 | 11 KV | LV | 20 | OUTDOOR | 249 | 22 | 18 | 7 | 2 | 1 | 1 | 0 | 1.0058 | N/A | 12.1156 | 6.8165 | 77.4273 | N/A | 106.0431 | 0.013741 | 1245.929 | 0
212904 | WESTSIDE AVE, OFF WEST END RD | LINDLEY THOMPSON | SJ54089687 | 500 | 11 KV | LV | 49 | OUTDOOR | 167 | 2 | 9 | 1 | 0 | 0 | 0 | 0 | 0.47208 | N/A | 22.4559 | 10.3818 | 35.7671 | N/A | 92.6921 | 0.00034089 | 50220.9969 | 0
212944 | PENNY LN, ADJ 223 HAYDOCK | ABB | SJ57449737 | 500 | 11 KV | LV | 13 | INDOOR | 191 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0.48029 | N/A | 8.456 | 5.3584 | 44.6435 | N/A | 113.4149 | 0.00087988 | 19457.2078 | 0
213807 | WOTTON DR, FRONT 19/21 WOTTON D | ABB | SJ58929951 | 500 | 6.6 KV | LV | 20 | OUTDOOR | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.81368 | N/A | 11.9632 | 6.7615 | 55.4013 | N/A | 106.2591 | 0.0012289 | 13931.3661 | 0
216118 | BELVEDERE RD, NEWTON LE WILLOWS | ABB | SJ57739573 | 500 | 11 KV | LV | 20 | OUTDOOR | 125 | 6 | 8 | 2 | 0 | 0 | 0 | 0 | 0.38323 | N/A | 12.019 | 6.7776 | 31.5896 | N/A | 106.2444 | 0.0002659 | 64384.7002 | 0
216276 | CROFT ST, LITTLE HULTON | LINDLEY THOMPSON | SD71880410 | 500 | 11 KV | LV | 52 | INDOOR | 228 | 3 | 2 | 1 | 0 | 1 | 0 | 0 | 0.6204 | N/A | 17.0643 | 8.6414 | 53.5099 | N/A | 98.3002 | 0.0016718 | 10240.5377 | 0
216543 | GOWER ST, SWINTON | FERRANTI | SD78380224 | 750 | 11 KV | LV | 50 | INDOOR | 180 | 4 | 14 | 5 | 0 | 0 | 0 | 1 | 0.4233 | N/A | 16.5075 | 8.4414 | 44.3018 | N/A | 99.0821 | 0.0010423 | 16424.508 | 0
216664 | HUTTON AVE, BOOTHSTOWN | ENGLISH ELECTRIC | SD71720083 | 750 | 11 KV | LV | 51 | INDOOR | 381 | 17 | 1 | 0 | 0 | 0 | 0 | 0 | 0.65237 | N/A | 16.8364 | 8.5656 | 55.8439 | N/A | 98.5519 | 0.0019311 | 8865.3656 | 0
216674 | HULME RD, LEIGH | SOUTH WALES SWITCHGEAR | SD64270060 | 800 | 11 KV | LV | 20 | OUTDOOR | 125 | 0 | 3 | 0 | 1 | 0 | 0 | 0 | 0.22457 | N/A | 12.2404 | 6.8605 | 25.3477 | N/A | 105.8561 | 0.00018026 | 94971.9682 | 0
217117 | LAWSON AVE, WESTLEIGH LANE LEIGH | PARSONS | SD65050220 | 500 | 11 KV | LV | 37 | OUTDOOR | 185 | 12 | 1 | 1 | 0 | 0 | 0 | 0 | 0.49634 | N/A | 18.2854 | 9.0305 | 36.1903 | N/A | 97.1103 | 0.00033165 | 51621.06 | 0
217521 | WESTWOOD METHS, BOLTON ROAD SWINTON | DENIS FERRANTI | SD79450076 | 500 | 11 KV | LV | 52 | OUTDOOR | 170 | 9 | 6 | 1 | 0 | 0 | 0 | 0 | 0.48005 | N/A | 23.0591 | 10.5743 | 35.8193 | N/A | 92.0888 | 0.00033665 | 50853.3011 | 0
218214 | BLACKBERRY DR | ABB | SD61500399 | 500 | 11 KV | LV | 12 | OUTDOOR | 207 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.51487 | N/A | 9.4302 | 5.7422 | 37.0337 | N/A | 111.5717 | 0.00034286 | 49933.5539 | 0
231594 | MIDDLEBROOK HOUSING, MIDDLEBROOK LOSTOCK | SOUTH WALES SWITCHGEAR | SD64771013 | 500 | 11 KV | LV | 16 | INDOOR | 277 | 0 | 2 | 3 | 0 | 0 | 0 | 0 | 0.71516 | N/A | 9.0853 | 5.6223 | 59.3976 | N/A | 111.9454 | 0.0024598 | 6959.9387 | 0
231670 | LITTLE OAKS | EFACEC | SD73021210 | 500 | 11 KV | LV | 2 | OUTDOOR | 101 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26657 | N/A | 7.2559 | 4.8079 | 26.3463 | N/A | 117.2551 | 0.00018604 | 92024.0372 | 0
232046 | DOROTHY ST, RAMSBOTTOM | ABB | SD78731612 | 500 | 11 KV | LV | 14 | OUTDOOR | 291 | 11 | 13 | 1 | 0 | 0 | 0 | 0 | 0.81954 | N/A | 10.0837 | 5.9916 | 57.8228 | N/A | 110.4691 | 0.0017062 | 10033.757 | 0
232164 | DORIS MILL, ADJ 90 BURY N RD HEY | SOUTH WALES SWITCHGEAR | SD84201080 | 500 | 6.6 KV | LV | 18 | OUTDOOR | 363 | 16 | 13 | 1 | 0 | 0 | 2 | 1 | 1.157 | N/A | 11.6665 | 6.6371 | 87.9 | N/A | 106.9588 | 0.028543 | 599.8027 | 0
232373 | THATCHLEACH LN W, WHITEFIELD | BRUCE PEEBLES | SD81070514 | 750 | 11 KV | LV | 51 | OUTDOOR | 310 | 37 | 19 | 3 | 1 | 0 | 0 | 0 | 0.67988 | N/A | 22.8113 | 10.4913 | 48.9595 | N/A | 92.3577 | 0.0009249 | 18510.0939 | 0
232384 | WINGATE DR, WHITEFIELD | LINDLEY THOMPSON | SD80060637 | 500 | 11 KV | LV | 57 | INDOOR | 205 | 9 | 3 | 1 | 0 | 1 | 0 | 0 | 0.58459 | N/A | 17.9927 | 8.9601 | 51.417 | N/A | 97.1668 | 0.0014725 | 11626.5404 | 0
232432 | BOOTH RD, OPP 30 BOOTH RD | CROMPTON PARKINSON | SD75960696 | 500 | 11 KV | LV | 53 | INDOOR | 250 | 29 | 5 | 1 | 1 | 0 | 0 | 0 | 0.75664 | N/A | 17.2193 | 8.6971 | 63.2602 | N/A | 98.0821 | 0.0036075 | 4745.6351 | 0
232488 | LONGTON ST, BURY RR 660 MCR RD | BABCOCK | SD80630794 | 500 | 11 KV | LV | 21 | INDOOR | 212 | 7 | 4 | 0 | 1 | 1 | 1 | 0 | 0.67662 | N/A | 9.9357 | 5.9819 | 58.7641 | N/A | 109.8598 | 0.002746 | 6234.6155 | 0
232553 | MARKET ST BURY, BURY | ABB | SD80740983 | 800 | 6.6 KV | LV | 13 | OUTDOOR | 149 | 3 | 6 | 1 | 1 | 0 | 0 | 0 | 0.28195 | N/A | 9.8816 | 5.9203 | 27.3754 | N/A | 110.731 | 0.00020463 | 83664.9762 | 0
232576 | ABINGDON CL, ADJ 1 ABINGDON CLOSE | ENGLISH ELECTRIC | SD80730688 | 500 | 11 KV | LV | 50 | INDOOR | 231 | 8 | 1 | 1 | 0 | 0 | 0 | 0 | 0.59885 | N/A | 16.6356 | 8.4939 | 51.4237 | N/A | 98.8286 | 0.0013694 | 12502.1443 | 0
310448 | HALFWAY HS, REAR OF PUB ROYTON | FERRANTI | SD91380886 | 750 | 6.6 KV | LV | 56 | INDOOR | 142 | 5 | 1 | 1 | 0 | 0 | 0 | 0 | 0.24931 | N/A | 17.9191 | 8.9308 | 35.8028 | N/A | 97.3003 | 0.00056664 | 30213.2834 | 0
310534 | WHITEGATE AVE, CHADDERTON | SOUTH WALES SWITCHGEAR | SD89910378 | 800 | 6.6 KV | LV | 17 | OUTDOOR | 370 | 10 | 4 | 0 | 0 | 0 | 0 | 0 | 0.5944 | N/A | 11.188 | 6.4643 | 41.5575 | N/A | 107.6259 | 0.00046459 | 36849.7836 | 0
311103 | MIDDLEGATE, RR 43 MIDGATE HOLINS | BRUSH | SD92260271 | 500 | 6.6 KV | LV | 32 | OUTDOOR | 255 | 7 | 0 | 1 | 0 | 0 | 0 | 0 | 0.64946 | N/A | 15.7441 | 8.1539 | 44.7014 | N/A | 100.3152 | 0.00056831 | 30124.2897 | 0
312270 | HOLLY ST, MALHAM CLOSE ROYTON | DENIS FERRANTI | SD91720797 | 750 | 6.6 KV | LV | 50 | INDOOR | 321 | 17 | 4 | 2 | 0 | 0 | 0 | 0 | 0.57783 | N/A | 16.4597 | 8.4339 | 51.5907 | N/A | 99.0442 | 0.0014915 | 11478.5966 | 0
312895 | MERTON AVE, ADJ HERON MILL O/HAM | FERRANTI | SD91740307 | 750 | 6.6 KV | LV | 50 | OUTDOOR | 332 | 20 | 4 | 0 | 1 | 0 | 0 | 0 | 0.61342 | N/A | 22.5375 | 10.4064 | 43.0941 | N/A | 92.6284 | 0.00053689 | 31887.2341 | 0
313307 | GREENSIDE AVE, OFF HAVEN LN OLDHAM | FERRANTI | SD95050697 | 500 | 6.6 KV | LV | 48 | INDOOR | 232 | 5 | 6 | 2 | 1 | 0 | 0 | 0 | 0.66794 | N/A | 16.2186 | 8.3499 | 57.3246 | N/A | 99.3487 | 0.0023154 | 7393.9268 | 0
314107 | KIRKLAND YARNS, OFF JOWETT ST OLDHAM | SOUTH WALES SWITCHGEAR | SD94430650 | 800 | 6.6 KV | LV | 44 | INDOOR | 184 | 6 | 3 | 2 | 0 | 0 | 0 | 0 | 0.31203 | N/A | 15.0483 | 7.9381 | 39.2858 | N/A | 100.8933 | 0.0007395 | 23150.8402 | 0
314325 | BELLSHILL CRES, ROCHDALE | PAUWELS | SD91261409 | 500 | 6.6 KV | LV | 16 | OUTDOOR | 311 | 1 | 5 | 1 | 0 | 0 | 0 | 0 | 0.79924 | N/A | 10.7611 | 6.2749 | 55.1833 | N/A | 108.819 | 0.0012723 | 13456.4268 | 0
314378 | CROFTHEAD | EFACEC | SD93521716 | 750 | 6.6 KV | LV | 1 | INDOOR | 292 | 4 | 1 | 1 | 0 | 0 | 0 | 0 | 0.49201 | N/A | 6.1254 | 4.3081 | 46.3822 | N/A | 120.4829 | 0.0010355 | 16532.5061 | 0
314400 | DURN | SCHNEIDER ELECTRIC | SD94211644 | 750 | 6.6 KV | LV | 1 | INDOOR | 241 | 5 | 8 | 2 | 0 | 0 | 0 | 0 | 0.44255 | N/A | 6.2692 | 4.3674 | 44.3328 | N/A | 120.199 | 0.00095613 | 17905.4819 | 0
314436 | HAUGH LANE, HAUGH LN NEWHEY | ABB | SD94121170 | 500 | 6.6 KV | LV | 20 | OUTDOOR | 311 | 12 | 2 | 2 | 0 | 0 | 0 | 0 | 0.81884 | N/A | 11.9817 | 6.758 | 56.3726 | N/A | 106.423 | 0.0013868 | 12345.3058 | 0
314606 | DUNLOP AVE, QUEENSWAY RDALE | ENGLISH ELECTRIC | SD89331143 | 750 | 6.6 KV | LV | 54 | OUTDOOR | 129 | 17 | 6 | 1 | 0 | 0 | 0 | 0 | 0.26643 | N/A | 24.0061 | 10.8616 | 26.6297 | N/A | 91.2245 | 0.00019414 | 88182.8055 | 0
314974 | NORDEN RD, BAMFORD | LINDLEY THOMPSON | SD86311311 | 750 | 6.6 KV | LV | 50 | INDOOR | 186 | 9 | 12 | 5 | 0 | 0 | 0 | 0 | 0.39378 | N/A | 16.3751 | 8.4047 | 42.4754 | N/A | 99.1453 | 0.00089045 | 19226.2766 | 0
320939 | FLEET ST | EFACEC | SJ95229533 | 500 | 6.6 KV | LV | 2 | OUTDOOR | 192 | 9 | 2 | 0 | 0 | 0 | 0 | 0 | 0.50251 | N/A | 7.0989 | 4.7316 | 36.483 | N/A | 117.8796 | 0.00033599 | 50954.4287 | 0
322939 | KINGS RD, OLD PEOPLES HOST AUL | FERRANTI | SD95090040 | 750 | 6.6 KV | LV | 51 | INDOOR | 274 | 10 | 4 | 0 | 1 | 0 | 0 | 0 | 0.50245 | N/A | 16.9532 | 8.6044 | 47.4429 | N/A | 98.4366 | 0.0011582 | 14781.8291 | 0
323779 | CALVER MEWS, CAR PARK GAMESLEY | SOUTH WALES SWITCHGEAR | SK01029484 | 1000 | 11 KV | LV | 26 | OUTDOOR | 100 | 75 | 2 | 0 | 0 | 0 | 0 | 0 | 0.22045 | N/A | 13.8889 | 7.4849 | 25.0359 | N/A | 103.0525 | 0.00017878 | 95758.3144 | 0
326139 | WILTSHIRE DR, GLOSSOP | HAWKER SIDDELEY | SK04259335 | 500 | 11 KV | LV | 18 | OUTDOOR | 278 | 16 | 0 | 0 | 1 | 0 | 0 | 0 | 0.75606 | N/A | 11.361 | 6.5143 | 52.1222 | N/A | 107.6104 | 0.0010161 | 16849.4527 | 0
327085 | OLDHAM ATHLETIC, SHEEPFOOT LN OLDHAM | FERRANTI | SD91500646 | 750 | 6.6 KV | LV | 23 | OUTDOOR | 134 | 7 | 2 | 0 | 0 | 0 | 0 | 0 | 0.23723 | N/A | 10.3288 | 6.1404 | 35.4107 | N/A | 109.0269 | 0.00055501 | 30846.3223 | 0
327098 | E WHITTAKER, OLDHAM | SOUTH WALES SWITCHGEAR | SD92160607 | 500 | 6.6 KV | LV | 26 | OUTDOOR | 114 | 1 | 4 | 1 | 0 | 0 | 0 | 0 | 0.31232 | N/A | 14.0679 | 7.5627 | 28.2529 | N/A | 102.5875 | 0.00021125 | 81039.8274 | 0
327479 | ARMITAGE CL, OFF HERON ST | ABB | SD91320350 | 500 | 6.6 KV | LV | 22 | OUTDOOR | 305 | 48 | 19 | 4 | 0 | 3 | 0 | 0 | 1.1196 | N/A | 12.7472 | 7.0558 | 86.8187 | N/A | 104.9453 | 0.029788 | 574.7241 | 0
330093 | BIRKETT AND BOSTOCK, HR HILLGATE STOCKPR | FERRANTI | SJ89968953 | 750 | 6.6 KV | LV | 51 | INDOOR | 100 | 0 | 2 | 1 | 1 | 0 | 0 | 1 | 0.23945 | N/A | 16.7995 | 8.5498 | 35.9474 | N/A | 98.633 | 0.00059762 | 28646.7404 | 0
330180 | HEMPSHAW LN OFFERTON STOCKPORT | ABB | SJ90788941 | 500 | 6.6 KV | LV | 13 | OUTDOOR | 220 | 5 | 10 | 4 | 0 | 1 | 0 | 0 | 0.67813 | N/A | 9.815 | 5.8957 | 48.9603 | N/A | 110.799 | 0.00092356 | 18536.922 | 0
330222 | NORRIS BANK, HEATON NORRIS | ABB | SJ87839059 | 800 | 6.6 KV | LV | 21 | OUTDOOR | 347 | 3 | 1 | 1 | 0 | 0 | 0 | 0 | 0.54371 | N/A | 12.5835 | 6.9951 | 38.5913 | N/A | 105.2203 | 0.00037889 | 45184.037 | 0
330225 | OSBORNE ST, BREDBURY | SOUTH WALES SWITCHGEAR | SJ91469112 | 800 | 11 KV | LV | 15 | INDOOR | 228 | 35 | 10 | 2 | 0 | 0 | 0 | 0 | 0.44834 | N/A | 8.6184 | 5.4217 | 45.9091 | N/A | 113.1568 | 0.001146 | 14939.3757 | 0
330276 | TATTON RD, HEATON MOOR | FERRANTI | SJ88179210 | 1000 | 6.6 KV | LV | 50 | INDOOR | 250 | 62 | 17 | 10 | 0 | 1 | 0 | 0 | 0.49553 | N/A | 16.3541 | 8.4018 | 49.5 | N/A | 99.1242 | 0.0015918 | 10755.3211 | 0
330300 | WOODLANDS DR, OFFERTON | ABB | SJ91658969 | 500 | 6.6 KV | LV | 15 | INDOOR | 273 | 15 | 2 | 0 | 0 | 0 | 0 | 0 | 0.71527 | N/A | 8.6788 | 5.4508 | 58.9887 | N/A | 112.926 | 0.0023424 | 7308.5928 | 0
330305 | YORK ST STOCKPORT | ABB | SJ89108971 | 1000 | 6.6 KV | LV | 12 | OUTDOOR | 212 | 8 | 11 | 0 | 0 | 0 | 1 | 0 | 0.32254 | N/A | 9.2272 | 5.6547 | 28.8553 | N/A | 112.1303 | 0.00022238 | 76984.5523 | 0
331769 | HULLEY RD, MACCLESFIELD | SOUTH WALES SWITCHGEAR | SJ92737461 | 500 | 11 KV | LV | 18 | OUTDOOR | 331 | 54 | 6 | 4 | 0 | 0 | 0 | 0 | 1.0119 | N/A | 11.5695 | 6.608 | 72.3684 | N/A | 107.02 | 0.0058617 | 2920.6303 | 0
331890 | GRANGE RD, BRAMHALL | YORKSHIRE ELECTRICAL TRANSFORMERS | SJ89728707 | 500 | 11 KV | LV | 48 | INDOOR | 169 | 14 | 3 | 0 | 0 | 0 | 0 | 0 | 0.46423 | N/A | 16.0877 | 8.3021 | 43.9311 | N/A | 99.5489 | 0.00085952 | 19918.1529 | 0
331994 | POWNALL FM, STYAL | LINDLEY THOMPSON | SJ84018349 | 500 | 11 KV | LV | 49 | INDOOR | 91 | 12 | 8 | 1 | 0 | 0 | 1 | 0 | 0.35631 | N/A | 16.3665 | 8.4015 | 39.7206 | N/A | 99.1637 | 0.00072169 | 23722.159 | 0
331997 | QUEENS AVE, MACCLESFIELD | TRANSFORMERS (WALES) | SJ92197455 | 800 | 11 KV | LV | 18 | INDOOR | 144 | 14 | 7 | 1 | 3 | 3 | 0 | 0 | 0.42656 | N/A | 9.1809 | 5.6695 | 46.4724 | N/A | 111.5613 | 0.0013624 | 12565.9621 | 0
332456 | PARKGATE WAY, SPATH LNG6 HANDFORTH | LINDLEY THOMPSON | SJ85948362 | 500 | 11 KV | LV | 51 | INDOOR | 119 | 11 | 3 | 0 | 0 | 0 | 0 | 0 | 0.33464 | N/A | 16.6102 | 8.4825 | 37.9341 | N/A | 98.8915 | 0.00060432 | 28329.3927 | 0
332587 | REDHOUSE LN, DISLEY | UNIDAIRE LTD | SJ98048467 | 500 | 11 KV | LV | 22 | OUTDOOR | 113 | 10 | 4 | 1 | 0 | 0 | 0 | 0 | 0.33213 | N/A | 12.6612 | 7.0219 | 29.012 | N/A | 105.1343 | 0.00022206 | 77095.0439 | 0
332821 | CHESTER WALKS, BREDBURY | CROMPTON PARKINSON | SJ93329018 | 500 | 11 KV | LV | 51 | INDOOR | 210 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0.53291 | N/A | 16.7908 | 8.544 | 47.3238 | N/A | 98.6758 | 0.0010297 | 16626.0738 | 0
332876 | LADYBROOK RD, BRAMHALL | PAUWELS | SJ88338631 | 750 | 11 KV | LV | 16 | OUTDOOR | 137 | 8 | 5 | 2 | 0 | 0 | 0 | 0 | 0.26697 | N/A | 11.0793 | 6.4059 | 26.6464 | N/A | 108.132 | 0.00019368 | 88392.3561 | 0
333103 | QUEENS RD FLATS, WILMSLOW | ABB | SJ84268087 | 500 | 11 KV | LV | 13 | INDOOR | 136 | 24 | 8 | 1 | 0 | 2 | 0 | 2 | 0.63792 | N/A | 8.0606 | 5.1877 | 57.325 | N/A | 114.4855 | 0.0029263 | 5850.3199 | 0
333883 | HIGHFIELD AVE, BREDBURY | SOUTH WALES SWITCHGEAR | SJ92879085 | 750 | 11 KV | LV | 45 | INDOOR | 191 | 6 | 1 | 0 | 0 | 1 | 0 | 0 | 0.34852 | N/A | 15.4714 | 8.0892 | 39.7234 | N/A | 100.3105 | 0.00071627 | 23901.65 | 0
333962 | DIXON DRIVE 29, CHELFORD | SOUTH WALES SWITCHGEAR | SJ81377512 | 1000 | 11 KV | LV | 26 | INDOOR | 130 | 61 | 7 | 5 | 0 | 0 | 0 | 0 | 0.27636 | N/A | 10.8367 | 6.3451 | 38.2161 | N/A | 107.9861 | 0.00072866 | 23495.3136 | 0
334173 | ALDERWOOD AVE, HEATON MERSEY | BRUSH | SJ87059030 | 500 | 6.6 KV | LV | 33 | INDOOR | 318 | 17 | 1 | 0 | 0 | 0 | 0 | 0 | 0.82461 | N/A | 12.4016 | 6.9573 | 66.7448 | N/A | 105.0408 | 0.0042389 | 4038.797 | 0
334195 | CORBAR RD(STOCKPORT), STOCKPORT | DENIS FERRANTI | SJ90568835 | 750 | 6.6 KV | LV | 49 | OUTDOOR | 40 | 85 | 2 | 0 | 0 | 1 | 0 | 0 | 0.23743 | N/A | 21.9614 | 10.2202 | 25.7342 | N/A | 93.2272 | 0.00019436 | 88084.016 | 0
336478 | LOWER BENTS LN, BREDBURY | BRUSH | SJ92599166 | 500 | 11 KV | LV | 29 | OUTDOOR | 217 | 15 | 10 | 3 | 0 | 0 | 0 | 0 | 0.65009 | N/A | 15.3122 | 7.9985 | 46.2768 | N/A | 100.9687 | 0.00071635 | 23899.0578 | 0
336998 | ST GEORGES ST, MACCLESFIELD | SOUTH WALES SWITCHGEAR | SJ91857303 | 500 | 11 KV | LV | 26 | OUTDOOR | 81 | 31 | 6 | 1 | 1 | 0 | 0 | 0 | 0.35653 | N/A | 14.0877 | 7.5574 | 30.6477 | N/A | 102.7442 | 0.00026237 | 65250.4647 | 0
337081 | DORCHESTER WAY, DORCHESTER WAY,MACC | HAWKER SIDDELEY | SJ91097579 | 500 | 11 KV | LV | 25 | OUTDOOR | 230 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0.57497 | N/A | 13.7802 | 7.4467 | 40.2884 | N/A | 103.195 | 0.00042129 | 40636.7289 | 0
337724 | DIDSBURY ROAD, OPP 218 | ABB | SJ87409070 | 500 | 6.6 KV | LV | 20 | OUTDOOR | 228 | 16 | 1 | 1 | 0 | 0 | 0 | 0 | 0.6113 | N/A | 11.894 | 6.7242 | 42.537 | N/A | 106.5657 | 0.00049935 | 34284.2618 | 0
410398 | ROBINSON ST, PRESTON | SOUTH WALES SWITCHGEAR | SD52913133 | 500 | 6.6 KV | LV | 25 | OUTDOOR | 229 | 17 | 15 | 3 | 0 | 0 | 1 | 0 | 0.76181 | N/A | 13.5103 | 7.348 | 54.9692 | N/A | 103.6014 | 0.0015103 | 11335.3507 | 0
410460 | CEMETERY (PRESTON), PRESTON | ABB | SD56333023 | 500 | 6.6 KV | LV | 16 | INDOOR | 278 | 7 | 22 | 4 | 0 | 0 | 1 | 0 | 0.9086 | N/A | 8.7306 | 5.4836 | 78.1699 | N/A | 112.5794 | 0.014993 | 1141.8655 | 0
410579 | HARBOUR LN (WARTON), WARTON | BABCOCK | SD41292865 | 800 | 6.6 KV | LV | 22 | INDOOR | 343 | 14 | 13 | 5 | 1 | 0 | 1 | 0 | 0.67105 | N/A | 10.3296 | 6.147 | 60.7256 | N/A | 108.9202 | 0.0034159 | 5011.7997 | 0
410611 | WATERLOO RD, PRESTON | BONAR LONG | SD51793064 | 500 | 6.6 KV | LV | 55 | INDOOR | 193 | 24 | 10 | 4 | 0 | 0 | 0 | 0 | 0.62277 | N/A | 17.5255 | 8.8001 | 54.5861 | N/A | 97.7365 | 0.0019536 | 8763.3629 | 0
410842 | BROWNING RD, PRESTON | BABCOCK | SD55633065 | 500 | 6.6 KV | LV | 22 | OUTDOOR | 126 | 5 | 7 | 1 | 0 | 0 | 0 | 0 | 0.3682 | N/A | 12.6795 | 7.0337 | 30.7447 | N/A | 105.0011 | 0.0002488 | 68810.4419 | 0
414508 | JUNCTION LN, BURSCOUGH | FERRANTI | SD44401155 | 750 | 11 KV | LV | 52 | INDOOR | 102 | 8 | 3 | 1 | 0 | 0 | 0 | 0 | 0.1965 | N/A | 17.041 | 8.6337 | 34.2925 | N/A | 98.3342 | 0.00052732 | 32466.1183 | 0
414539 | HENNEL LN SW HS, WALTON LE DALE | BONAR LONG | SD54752702 | 500 | 11 KV | LV | 29 | OUTDOOR | 180 | 7 | 3 | 0 | 0 | 0 | 0 | 0 | 0.4738 | N/A | 14.7399 | 7.7988 | 35.1147 | N/A | 101.696 | 0.00031099 | 55050.8717 | 0
414613 | BALCARRES RD, LEYLAND | ABB | SD54242163 | 500 | 11 KV | LV | 14 | INDOOR | 181 | 5 | 9 | 4 | 0 | 0 | 0 | 1 | 0.59834 | N/A | 8.4753 | 5.3714 | 53.446 | N/A | 113.2595 | 0.0018659 | 9175.1879 | 0
414615 | MOSSY LEA, WRIGHTINGTON | ABB | SD53651254 | 500 | 11 KV | LV | 14 | OUTDOOR | 174 | 5 | 4 | 0 | 1 | 1 | 0 | 0 | 0.53266 | N/A | 10.3845 | 6.1258 | 39.4881 | N/A | 109.6147 | 0.00045543 | 37590.9573 | 0
414674 | COW MOSS | EFACEC | SD56501397 | 500 | 11 KV | LV | 1 | INDOOR | 261 | 14 | 3 | 0 | 0 | 0 | 1 | 0 | 0.73519 | N/A | 6.2175 | 4.3455 | 61.0861 | N/A | 120.3291 | 0.002883 | 5938.2754 | 0
414844 | ROAD SPRINGS, LEYLAND | PAUWELS | SD52302184 | 500 | 11 KV | LV | 14 | OUTDOOR | 139 | 7 | 3 | 5 | 0 | 0 | 0 | 0 | 0.41897 | N/A | 10.2557 | 6.0763 | 33.0246 | N/A | 109.8078 | 0.00028808 | 59427.2683 | 0
415028 | CLOVER RD, CHORLEY | FERRANTI | SD57121619 | 500 | 11 KV | LV | 49 | INDOOR | 117 | 7 | 6 | 1 | 0 | 2 | 0 | 0 | 0.4231 | N/A | 16.1392 | 8.3202 | 43.2046 | N/A | 99.4786 | 0.0009328 | 18353.334 | 0
415087 | ALDERBROOK DR, PARBOLD | LINDLEY THOMPSON | SD49231083 | 500 | 11 KV | LV | 51 | INDOOR | 119 | 5 | 8 | 2 | 0 | 0 | 0 | 0 | 0.36648 | N/A | 16.3763 | 8.4044 | 39.9398 | N/A | 99.1502 | 0.00070991 | 24115.7753 | 0
415293 | BLACKGATE LN, TARLETON | SOUTH WALES SWITCHGEAR | SD44892033 | 500 | 11 KV | LV | 27 | INDOOR | 112 | 44 | 7 | 4 | 0 | 0 | 0 | 0 | 0.4577 | N/A | 11.1462 | 6.4671 | 44.5894 | N/A | 107.3773 | 0.0010029 | 17069.7631 | 0
415504 | CLAUGHTON AVE, CLAYTON-LE-WOODS | PARSONS | SD56342239 | 500 | 11 KV | LV | 31 | INDOOR | 366 | 23 | 2 | 0 | 0 | 0 | 0 | 0 | 0.96229 | N/A | 12.1771 | 6.8735 | 77.8453 | N/A | 105.3977 | 0.011043 | 1550.2456 | 0
415540 | WYRESDALE DR | ABB | SD54732098 | 500 | 11 KV | LV | 12 | INDOOR | 228 | 7 | 1 | 0 | 0 | 0 | 0 | 0 | 0.57998 | N/A | 7.9254 | 5.117 | 50.1506 | N/A | 115.1017 | 0.0012442 | 13759.8406 | 0
417073 | RIPON ST, RIPON STREET PRESTON | BRUSH | SD53403071 | 800 | 6.6 KV | LV | 29 | OUTDOOR | 138 | 9 | 3 | 0 | 0 | 0 | 0 | 0 | 0.23507 | N/A | 15.2287 | 7.9766 | 25.4598 | N/A | 100.9882 | 0.00017896 | 95662.5336 | 0
418214 | BRITANNIA DR, PRESTON | SOUTH WALES SWITCHGEAR | SD51712948 | 800 | 6.6 KV | LV | 17 | OUTDOOR | 42 | 177 | 1 | 6 | 0 | 0 | 0 | 0 | 0.43109 | N/A | 11.1724 | 6.4537 | 32.5918 | N/A | 107.7148 | 0.00029352 | 58326.1751 | 0
423267 | QUEENS PK EST, ST ANNES | PARSONS | SD33852875 | 500 | 6.6 KV | LV | 35 | INDOOR | 222 | 18 | 4 | 0 | 0 | 0 | 0 | 0 | 0.60918 | N/A | 13.055 | 7.212 | 52.2949 | N/A | 103.8262 | 0.0014891 | 11496.8912 | 0
423313 | SOUTH HEY, ST ANNES | BONAR LONG | SD34502860 | 750 | 6.6 KV | LV | 47 | INDOOR | 238 | 108 | 0 | 4 | 0 | 0 | 0 | 0 | 0.58992 | N/A | 15.9728 | 8.2634 | 52.3726 | N/A | 99.6761 | 0.0016977 | 10083.9697 | 0
423928 | HOLYOAKE AVE, OPP NO1 HOLYOAKE | PARSONS | SD32323837 | 500 | 6.6 KV | LV | 35 | OUTDOOR | 101 | 7 | 4 | 2 | 2 | 0 | 0 | 0 | 0.38366 | N/A | 17.4739 | 8.7531 | 32.1949 | N/A | 98.1131 | 0.00029202 | 58626.3544 | 0
427236 | HERITAGE WAY | BABCOCK | SD32704224 | 800 | 6.6 KV | LV | 22 | OUTDOOR | 121 | 48 | 2 | 0 | 0 | 0 | 0 | 0 | 0.26591 | N/A | 12.4587 | 6.9427 | 26.4183 | N/A | 105.5358 | 0.0001914 | 89447.2838 | 0
428275 | KINGSWAY, OLD FLATS ENTRANCE | PAUWELS | SD31304270 | 800 | 6.6 KV | LV | 16 | INDOOR | 57 | 68 | 2 | 3 | 0 | 0 | 0 | 0 | 0.21609 | N/A | 8.704 | 5.4656 | 36.0297 | N/A | 112.7859 | 0.00064258 | 26642.6017 | 0
429617 | PEACE PL, GAMBLE RD THORNTON | ABB | SD33464390 | 800 | 11 KV | LV | 15 | INDOOR | 334 | 13 | 6 | 0 | 1 | 0 | 1 | 0 | 0.60311 | N/A | 8.6664 | 5.448 | 55.0182 | N/A | 112.9056 | 0.0020916 | 8185.3107 | 0
429948 | LITTLE POULTON GDNS | ABB | SD35703910 | 500 | 6.6 KV | LV | 12 | INDOOR | 48 | 76 | 6 | 0 | 0 | 0 | 0 | 0 | 0.33854 | N/A | 8.0661 | 5.1854 | 38.4539 | N/A | 114.5568 | 0.00069258 | 24719.2846 | 0
450050 | STANSFELD ST, BLACKBURN BB18 I | BRUSH | SD67422706 | 800 | 6.6 KV | LV | 31 | OUTDOOR | 120 | 4 | 7 | 1 | 1 | 0 | 0 | 0 | 0.24394 | N/A | 15.7424 | 8.148 | 26.1256 | N/A | 100.3963 | 0.00019147 | 89412.128 | 0
450074 | GUIDE, CARPARK OF ENSOR | SOUTH WALES SWITCHGEAR | SD70562579 | 500 | 6.6 KV | LV | 19 | OUTDOOR | 108 | 2 | 3 | 0 | 0 | 0 | 0 | 0 | 0.28551 | N/A | 11.7888 | 6.6972 | 27.1345 | N/A | 106.5367 | 0.00019635 | 87189.4386 | 0
450105 | WILWORTH CRES, PLECKGATE Z4 0 | ABB | SD68043043 | 500 | 6.6 KV | LV | 15 | OUTDOOR | 89 | 4 | 6 | 0 | 0 | 1 | 0 | 1 | 0.35771 | N/A | 10.215 | 6.0709 | 30.8687 | N/A | 109.6879 | 0.00026934 | 63562.399 | 0
450183 | OAK HILL, ACCRINGTON R22 I | SOUTH WALES SWITCHGEAR | SD76642772 | 500 | 6.6 KV | LV | 24 | INDOOR | 190 | 12 | 7 | 0 | 0 | 0 | 0 | 0 | 0.53282 | N/A | 10.3684 | 6.1544 | 48.0643 | N/A | 108.9947 | 0.00115 | 14886.9412 | 0
450388 | HASTON LEE MILL, BLACKBURN AA6 I | ABB | SD68643057 | 500 | 6.6 KV | LV | 17 | INDOOR | 178 | 2 | 12 | 2 | 0 | 0 | 0 | 0 | 0.52544 | N/A | 9.0727 | 5.6253 | 48.565 | N/A | 111.8079 | 0.0012572 | 13617.2216 | 0
450584 | BLACKBURN RD (OSW), OSWALDTWISTLE L17 I | BABCOCK | SD73032830 | 800 | 6.6 KV | LV | 21 | INDOOR | 154 | 12 | 8 | 1 | 0 | 0 | 0 | 0 | 0.28718 | N/A | 10.1905 | 6.0781 | 38.5361 | N/A | 109.453 | 0.00072102 | 23744.2297 | 0
450784 | BROADFIELD, ACCRINGTON Q21 I | LINDLEY THOMPSON | SD75502727 | 500 | 6.6 KV | LV | 48 | INDOOR | 149 | 29 | 2 | 0 | 0 | 0 | 0 | 0 | 0.44689 | N/A | 15.9909 | 8.2733 | 42.9923 | N/A | 99.6074 | 0.00081925 | 20897.1568 | 0
451828 | BRANTWOOD | ABB | SD74233092 | 500 | 6.6 KV | LV | 14 | OUTDOOR | 176 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.435 | N/A | 10.0914 | 6.0176 | 32.9947 | N/A | 110.0413 | 0.00026725 | 64059.3039 | 0
451866 | MILNSHAW GDNS | SOUTH WALES SWITCHGEAR | SD75472905 | 800 | 6.6 KV | LV | 25 | OUTDOOR | 41 | 57 | 5 | 0 | 0 | 0 | 0 | 0 | 0.16806 | N/A | 14.232 | 7.6162 | 23.784 | N/A | 102.4334 | 0.00016831 | 101714.9969 | 0
453049 | FOREST MILL, LUMB A18 I | SOUTH WALES SWITCHGEAR | SD84072561 | 500 | 6.6 KV | LV | 17 | INDOOR | 175 | 8 | 4 | 1 | 0 | 0 | 0 | 0 | 0.47868 | N/A | 9.0046 | 5.5896 | 44.8833 | N/A | 112.0952 | 0.00092264 | 18555.3774 | 0
455007 | WADDINGTON, WADDINGTON C2 I6 | CROMPTON PARKINSON | SD72864394 | 500 | 11 KV | LV | 53 | OUTDOOR | 133 | 20 | 9 | 4 | 0 | 1 | 0 | 0 | 0.50054 | N/A | 23.4497 | 10.6852 | 38.1253 | N/A | 91.7868 | 0.0004403 | 38882.3475 | 0
458190 | GRETNA, BURNLEY B3 B3 | FERRANTI | SD82693146 | 750 | 6.6 KV | LV | 53 | OUTDOOR | 220 | 5 | 3 | 1 | 0 | 0 | 0 | 0 | 0.38378 | N/A | 23.2196 | 10.6208 | 30.927 | N/A | 91.9603 | 0.00024228 | 70663.385 | 0
458556 | GERTRUDE ST, NELSON N1 F14 | LINDLEY THOMPSON | SD87023875 | 500 | 6.6 KV | LV | 55 | INDOOR | 317 | 34 | 15 | 0 | 1 | 0 | 1 | 0 | 1.0254 | N/A | 17.5459 | 8.8031 | 87.4747 | N/A | 97.7486 | 0.032599 | 525.1706 | 0
458558 | OXFORD RD | ALSTOM | SD87253869 | 500 | 6.6 KV | LV | 11 | INDOOR | 193 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0.48951 | N/A | 7.8305 | 5.0819 | 45.0441 | N/A | 115.2188 | 0.00089794 | 19065.7565 | 0
458748 | BACK RUTLAND AVE, BURNLEY B1 B13 | FERRANTI | SD81463288 | 750 | 6.6 KV | LV | 51 | INDOOR | 119 | 6 | 5 | 0 | 0 | 0 | 1 | 0 | 0.25322 | N/A | 16.6843 | 8.5087 | 36.2478 | N/A | 98.7877 | 0.00059586 | 28731.6253 | 0
616017 | TWEED RISE, WALNEY BARROW | SOUTH WALES SWITCHGEAR | SD17796893 | 500 | 11 KV | LV | 58 | OUTDOOR | 244 | 17 | 0 | 2 | 1 | 0 | 0 | 0 | 0.6936 | N/A | 25.3828 | 11.2767 | 48.266 | N/A | 89.9767 | 0.00078447 | 21823.6194 | 0
616120 | HEST VIEW, ULVERSTON | BONAR LONG | SD28787649 | 500 | 11 KV | LV | 45 | OUTDOOR | 261 | 22 | 1 | 1 | 0 | 0 | 0 | 0 | 0.70677 | N/A | 20.9287 | 9.9002 | 48.47 | N/A | 94.2137 | 0.00075746 | 22601.7705 | 0
620293 | THE ARCHES, MARYPORT | SOUTH WALES SWITCHGEAR | NY03783549 | 500 | 11 KV | LV | 17 | INDOOR | 242 | 5 | 2 | 0 | 0 | 0 | 0 | 0 | 0.61479 | N/A | 8.8875 | 5.544 | 52.3779 | N/A | 112.3212 | 0.0014531 | 11781.5942 | 0
620717 | DERWENT RD, MOSS BAY WORKINGTON | SOUTH WALES SWITCHGEAR | NX99282733 | 500 | 11 KV | LV | 17 | OUTDOOR | 327 | 20 | 30 | 6 | 0 | 0 | 0 | 0 | 1.078 | N/A | 11.1412 | 6.4412 | 82.4831 | N/A | 107.8154 | 0.018863 | 907.5851 | 0
636100 | CHESTERHOLM, ADJ 69 CHESTERHOLM | BONAR LONG | NY37025553 | 500 | 11 KV | LV | 39 | OUTDOOR | 252 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65037 | N/A | 18.6321 | 9.15 | 44.6453 | N/A | 96.6726 | 0.00056415 | 30346.6769 | 0
636173 | TODDS | ABB | NY39565561 | 800 | 11 KV | LV | 12 | OUTDOOR | 134 | 12 | 12 | 2 | 0 | 0 | 0 | 0 | 0.27794 | N/A | 9.4945 | 5.7668 | 27.2827 | N/A | 111.464 | 0.00020534 | 83371.9433 | 0
636385 | QUEENSWAY, BES NO 10 QUEENSWAY | YORKSHIRE SWITCHGEAR AND ENGINEERING | NY37905480 | 500 | 11 KV | LV | 44 | INDOOR | 240 | 16 | 6 | 1 | 0 | 0 | 0 | 0 | 0.6684 | N/A | 15.458 | 8.0849 | 56.4877 | N/A | 100.3239 | 0.0020508 | 8347.7609 | 0
642320 | CONISTON AVENUE HAMBLETON | SOUTH WALES SWITCHGEAR | SD37064267 | 500 | 11 KV | LV | 17 | INDOOR | 137 | 25 | 3 | 1 | 0 | 0 | 0 | 0 | 0.42231 | N/A | 9.018 | 5.5955 | 41.9703 | N/A | 112.0927 | 0.00078092 | 21922.7312 | 0
642344 | BEECHFIELD AVE, PREESALL | ABB | SD36414838 | 500 | 6.6 KV | LV | 15 | INDOOR | 168 | 25 | 2 | 0 | 0 | 0 | 0 | 0 | 0.48343 | N/A | 8.5623 | 5.3991 | 44.8622 | N/A | 113.2792 | 0.00091332 | 18744.7244 | 0
643270 | ULSTER ROAD, BOWERHAM LANCASTER | HAWKER SIDDELEY | SD48466041 | 1000 | 11 KV | LV | 27 | INDOOR | 343 | 29 | 5 | 2 | 0 | 0 | 0 | 0 | 0.47787 | N/A | 11.2135 | 6.4928 | 47.0359 | N/A | 107.2515 | 0.001177 | 14545.1787 | 0
643285 | DALTON ROAD (LANCASTER), LANCASTER | SOUTH WALES SWITCHGEAR | SD48486185 | 500 | 11 KV | LV | 27 | OUTDOOR | 321 | 30 | 6 | 0 | 0 | 0 | 0 | 0 | 0.89187 | N/A | 14.4535 | 7.6889 | 62.0433 | N/A | 102.2107 | 0.0022589 | 7578.9537 | 0
643286 | MOORGATE, LANCASTER | HAWKER SIDDELEY | SD48306164 | 500 | 11 KV | LV | 27 | INDOOR | 292 | 35 | 14 | 4 | 0 | 0 | 0 | 0 | 0.9141 | N/A | 11.0403 | 6.4282 | 76.6796 | N/A | 107.5441 | 0.011677 | 1466.1619 | 0
643293 | RIDGE LANE | NITRAN | SD48236224 | 800 | 11 KV | 6.6 KV | 23 | OUTDOOR | 90 | 26 | 1 | 5 | 0 | 0 | 0 | 0 | 0.20944 | N/A | 13.2704 | 7.2468 | 24.8669 | N/A | 104.1865 | 0.00017706 | 96691.1765 | 0
666035 | RAISELANDS CROFT, ADJ.7 RAISELANDS CFT | DISTRIBUTION TRANSFORMERS LTD | NY51103120 | 500 | 11 KV | LV | 36 | OUTDOOR | 308 | 14 | 4 | 1 | 1 | 0 | 0 | 0 | 0.85572 | N/A | 17.6323 | 8.8156 | 59.9219 | N/A | 97.8243 | 0.0019598 | 8735.6967 | 0

## Mapping - BAU
Mapping of failure probability of demonstrated distribution transformers

## Mid-range Scenario
General information |  |  |  | Input data for assessment | [12 empty] | Intermediate data | [6 empty] | Output
Substation Number | Substation | Manufacturer | Grid Reference | Power Rating (kVA) | HV | LV | Transformer Age (till 2015) | Indoor/Outdoor | Number of customers | [7 empty] | Peak load (p.u.) |  | Moisture |  | Peak hot-spot temperature (°C) |  | Bubbling inception temperature (°C) | Loss-of-life (year per year) | Expected lifetime (p.u.) | Failure probability (%)
[9 empty] | PC1 | PC2 | PC3 | PC4 | PC5 | PC6 | PC7 | PC8 | No EVs | With EVs | In oil (ppm) | In paper (%) | No EVs | With EVs
165002 | LANCASTER RD SALFORD 6 | ABB | SD78720037 | 500 | 6.6 KV | LV | 13 | INDOOR | 372 | 15 | 5 | 2 | 0 | 0 | 0 | 0 | 0.99198 | 1.3049 | 8.2455 | 5.2642 | 81.1897 | 101.7018 | 114.0666 | 0.045741 | 374.278 | 4.2
165080 | ST MARGARETS RD, PRESTWICH | PAUWELS | SD82210493 | 800 | 6.6 KV | LV | 16 | INDOOR | 320 | 20 | 8 | 0 | 0 | 0 | 0 | 0 | 0.54738 | 0.71717 | 8.9376 | 5.5613 | 51.0614 | 58.6971 | 112.2814 | 0.0018174 | 9419.8202 | 0
165083 | NAZARETH HS, PRESTWICH | ABB | SD82260317 | 500 | 6.6 KV | LV | 14 | OUTDOOR | 212 | 7 | 7 | 0 | 0 | 1 | 0 | 0 | 0.6099 | 0.79318 | 10.1006 | 6.0184 | 43.6167 | 51.7437 | 110.0615 | 0.00070503 | 24282.6358 | 0
165133 | MANTON CL, BROUGHTON | FERRANTI | SD83620078 | 750 | 6.6 KV | LV | 50 | INDOOR | 75 | 82 | 1 | 2 | 0 | 0 | 0 | 0 | 0.27314 | 0.36103 | 16.399 | 8.4146 | 36.7376 | 39.0666 | 99.0988 | 0.00065066 | 26311.5654 | 0
165528 | BISHOP RD, PENDLETON | CROMPTON PARKINSON | SJ78889962 | 1000 | 6.6 KV | LV | 52 | INDOOR | 216 | 26 | 2 | 0 | 0 | 0 | 0 | 0 | 0.30159 | 0.40097 | 16.836 | 8.5638 | 38.739 | 41.6587 | 98.5734 | 0.00074177 | 23079.7841 | 0
165647 | HEATH AVE, SALFORD 7 | CROMPTON PARKINSON | SJ82429945 | 1000 | 6.6 KV | LV | 51 | INDOOR | 299 | 3 | 14 | 2 | 0 | 0 | 0 | 0 | 0.41697 | 0.54138 | 16.593 | 8.4782 | 44.3649 | 49.0157 | 98.8882 | 0.0011081 | 15449.5004 | 0
165756 | ALBANY CT URMSTON | ABB | SJ75999500 | 800 | 6.6 KV | LV | 13 | OUTDOOR | 153 | 39 | 3 | 0 | 0 | 0 | 0 | 0 | 0.30434 | 0.40313 | 9.786 | 5.879 | 27.7636 | 30.5281 | 110.9841 | 0.00021328 | 80268.5935 | 0
166355 | TRAFFORD RD 181 | BRUSH | SJ76769802 | 500 | 6.6 KV | LV | 30 | OUTDOOR | 369 | 6 | 7 | 1 | 1 | 0 | 0 | 1 | 1.0585 | 1.3608 | 15.4781 | 8.0559 | 77.2891 | 96.9792 | 100.7671 | 0.026903 | 636.3695 | 28
166499 | THE HAWTHORNS | SOUTH WALES SWITCHGEAR | SJ80509420 | 800 | 6.6 KV | LV | 27 | INDOOR | 27 | 75 | 2 | 1 | 0 | 0 | 0 | 0 | 0.18338 | 0.22759 | 11.299 | 6.5344 | 34.8905 | 35.7699 | 106.9609 | 0.00060211 | 28433.3401 | 0
166588 | MONTON MILL GDN | SOUTH WALES SWITCHGEAR | SJ76319942 | 1000 | 6.6 KV | LV | 25 | INDOOR | 152 | 71 | 13 | 0 | 0 | 0 | 0 | 0 | 0.30959 | 0.40316 | 10.5433 | 6.2278 | 39.5059 | 42.2957 | 108.5866 | 0.00081721 | 20949.3225 | 0
166825 | DEEPDALE CT, NORTHWOLD DR M9 | HACKBRIDGE AND HEWITTIC | SD87850342 | 1000 | 6.6 KV | LV | 21 | OUTDOOR | 167 | 6 | 0 | 0 | 0 | 0 | 0 | 1 | 0.23986 | 0.3132 | 12.5473 | 6.9829 | 25.6199 | 27.3162 | 105.2416 | 0.00018528 | 92400.3551 | 0
171440 | CLOUGH RD, DROYLSDEN | LINDLEY THOMPSON | SJ90519893 | 750 | 6.6 KV | LV | 50 | INDOOR | 186 | 15 | 2 | 0 | 0 | 0 | 0 | 0 | 0.33512 | 0.44538 | 16.4706 | 8.4417 | 38.9558 | 42.3987 | 98.9811 | 0.00070994 | 24114.8649 | 0
171459 | LONGDEN RD LEVENSHULME, LONGDEN RD | BABCOCK | SJ87709485 | 800 | 6.6 KV | LV | 22 | OUTDOOR | 148 | 7 | 3 | 0 | 0 | 0 | 0 | 0 | 0.24726 | 0.32921 | 12.7404 | 7.0507 | 25.8264 | 27.7606 | 105.0066 | 0.00018681 | 91645.0074 | 0
171643 | RAMILLIES AVE, CHEADLE HULME | DISTRIBUTION TRANSFORMERS LTD | SJ87848631 | 500 | 11 KV | LV | 42 | INDOOR | 329 | 18 | 10 | 2 | 1 | 0 | 0 | 0 | 0.95932 | 1.241 | 14.6973 | 7.8119 | 80.1809 | 98.217 | 101.3934 | 0.036082 | 474.4716 | 23.8
171832 | HOLLAND ST | EFACEC | SJ91789558 | 750 | 6.6 KV | LV | 2 | INDOOR | 241 | 13 | 8 | 1 | 1 | 1 | 1 | 0 | 0.53015 | 0.66995 | 6.451 | 4.4666 | 50.2282 | 56.1573 | 119.235 | 0.0017235 | 9933.0787 | 0
171852 | WESTBURY AVE 37 SALE, SALE | BONAR LONG | SJ76109039 | 500 | 11 KV | LV | 38 | OUTDOOR | 280 | 9 | 3 | 1 | 0 | 0 | 0 | 0 | 0.73216 | 0.96768 | 18.3653 | 9.0594 | 50.3435 | 62.3754 | 96.9956 | 0.0012763 | 13413.4039 | 0
171966 | PARKFIELD RD S | BRUSH | SJ84259165 | 500 | 6.6 KV | LV | 33 | INDOOR | 188 | 19 | 12 | 1 | 0 | 0 | 0 | 0 | 0.58209 | 0.75652 | 12.4831 | 6.9904 | 51.8338 | 59.5951 | 104.8706 | 0.0018711 | 9149.5442 | 0
172014 | SCHOOL LN DIDSBURY | PAUWELS | SJ85339100 | 800 | 6.6 KV | LV | 16 | INDOOR | 225 | 64 | 9 | 0 | 0 | 1 | 0 | 0 | 0.49607 | 0.64118 | 8.8939 | 5.5491 | 48.6474 | 54.7254 | 112.2616 | 0.0015809 | 10829.3113 | 0
172242 | CARRGATE RD, DENTON | LINDLEY THOMPSON | SJ93939422 | 500 | 6.6 KV | LV | 53 | INDOOR | 179 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0.45222 | 0.60653 | 17.282 | 8.7157 | 43.0328 | 48.9016 | 98.0482 | 0.00087762 | 19507.2938 | 0
172344 | FAIRFIELD RD 222, REAR 90 SILVERDAL ST | SOUTH WALES SWITCHGEAR | SJ89729760 | 500 | 6.6 KV | LV | 17 | OUTDOOR | 281 | 27 | 7 | 4 | 1 | 0 | 0 | 1 | 0.92259 | 1.1752 | 11.0591 | 6.4037 | 66.8438 | 81.5663 | 108.0483 | 0.0071304 | 2400.9984 | 0
172448 | ST WILFREDS ST HULME, OFF ST WILFRED'S S | SOUTH WALES SWITCHGEAR | SJ83189686 | 500 | 6.6 KV | LV | 21 | INDOOR | 306 | 20 | 21 | 4 | 0 | 0 | 0 | 0 | 0.95138 | 1.2243 | 9.8032 | 5.9205 | 81.1518 | 98.1665 | 110.2683 | 0.039005 | 438.9196 | 2
172508 | BRIARFIELDS,BOUNDARY LN, OPP BONSALL ST, | ABB | SJ84059683 | 800 | 6.6 KV | LV | 20 | OUTDOOR | 223 | 72 | 7 | 0 | 0 | 2 | 0 | 0 | 0.52074 | 0.66882 | 11.8034 | 6.6889 | 38.4423 | 44.469 | 106.7666 | 0.00048332 | 35421.3884 | 0
172607 | BRITANNIA MILL, HULME HALL RD,HULME | SOUTH WALES SWITCHGEAR | SJ82599721 | 1000 | 6.6 KV | LV | 16 | INDOOR | 0 | 108 | 0 | 3 | 0 | 0 | 0 | 0 | 0.19629 | 0.20026 | 8.464 | 5.3585 | 35.0945 | 35.1952 | 113.4792 | 0.00058779 | 29126.0504 | 0
211326 | BEECH TREES S, OPP 113 (SKELM) | BRENTFORD TRANSFORMERS | SD49540503 | 1000 | 11 KV | LV | 24 | OUTDOOR | 189 | 59 | 1 | 0 | 0 | 0 | 1 | 0 | 0.32971 | 0.43058 | 13.3452 | 7.2778 | 28.7692 | 31.8312 | 104.0179 | 0.00022936 | 74640.9668 | 0
211505 | SMETHURST RD, OPP 2 ORRELL | FERRANTI | SD52630306 | 750 | 11 KV | LV | 50 | OUTDOOR | 326 | 20 | 12 | 3 | 0 | 0 | 0 | 0 | 0.6266 | 0.81492 | 22.5084 | 10.3981 | 44.3679 | 53.2465 | 92.6514 | 0.00075211 | 22762.6747 | 0
211944 | JENNET HEY, ADJ 12 ASHTON | ENGLISH ELECTRIC | SD56610065 | 500 | 6.6 KV | LV | 50 | INDOOR | 285 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0.75198 | 0.9941 | 16.478 | 8.4373 | 62.0788 | 75.2596 | 99.0524 | 0.0047825 | 3579.7056 | 0
211948 | PRIORY RD, ADJ 2 ASHTON | BRUSH | SD56940017 | 500 | 6.6 KV | LV | 46 | INDOOR | 289 | 6 | 1 | 1 | 0 | 0 | 0 | 0 | 0.73562 | 0.97316 | 15.6494 | 8.148 | 60.3989 | 73.1042 | 100.1274 | 0.0039717 | 4310.4925 | 0
212333 | HORNE GR, OPP 18 W/MESNES | BONAR LONG | SD56950441 | 750 | 6.6 KV | LV | 47 | INDOOR | 117 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21037 | 0.28735 | 15.8829 | 8.2341 | 34.5494 | 36.2244 | 99.7679 | 0.00053906 | 31758.8693 | 0
212620 | MOSS LN, ADJ 31 PLATT BRIDGE | ENGLISH ELECTRIC | SD60390324 | 500 | 11 KV | LV | 51 | INDOOR | 321 | 22 | 9 | 3 | 0 | 0 | 0 | 0 | 0.91596 | 1.1925 | 16.5383 | 8.4574 | 75.7066 | 92.9795 | 98.985 | 0.021658 | 790.4631 | 8
212649 | ABINGDON DRIVE (ABRAM), OPP 13 ABINGDON | S&C ELECTRIC | SD64140212 | 500 | 11 KV | LV | 42 | OUTDOOR | 349 | 8 | 0 | 1 | 0 | 0 | 0 | 0 | 0.88162 | 1.1681 | 19.6419 | 9.4804 | 60.5308 | 77.0446 | 95.5822 | 0.0038301 | 4469.8757 | 0
212806 | CHURCH ST N, CHURCH ST WESTH'TON | ABB | SD65380671 | 500 | 11 KV | LV | 20 | OUTDOOR | 249 | 22 | 18 | 7 | 2 | 1 | 1 | 0 | 1.0058 | 1.211 | 12.1156 | 6.8165 | 77.4273 | 90.0873 | 106.0431 | 0.021548 | 794.5165 | 0
212904 | WESTSIDE AVE, OFF WEST END RD | LINDLEY THOMPSON | SJ54089687 | 500 | 11 KV | LV | 49 | OUTDOOR | 167 | 2 | 9 | 1 | 0 | 0 | 0 | 0 | 0.47208 | 0.61387 | 22.4559 | 10.3818 | 35.7671 | 40.9727 | 92.6921 | 0.00037363 | 45821.2867 | 0
212944 | PENNY LN, ADJ 223 HAYDOCK | ABB | SJ57449737 | 500 | 11 KV | LV | 13 | INDOOR | 191 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0.48029 | 0.6392 | 8.456 | 5.3584 | 44.6435 | 50.9702 | 113.4149 | 0.00099103 | 17275.0067 | 0
213807 | WOTTON DR, FRONT 19/21 WOTTON D | ABB | SJ58929951 | 500 | 6.6 KV | LV | 20 | OUTDOOR | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.81368 | 1.0781 | 11.9632 | 6.7615 | 55.4013 | 69.982 | 106.2591 | 0.002134 | 8022.4184 | 0
216118 | BELVEDERE RD, NEWTON LE WILLOWS | ABB | SJ57739573 | 500 | 11 KV | LV | 20 | OUTDOOR | 125 | 6 | 8 | 2 | 0 | 0 | 0 | 0 | 0.38323 | 0.50047 | 12.019 | 6.7776 | 31.5896 | 35.2509 | 106.2444 | 0.00028087 | 60952.5427 | 0
216276 | CROFT ST, LITTLE HULTON | LINDLEY THOMPSON | SD71880410 | 500 | 11 KV | LV | 52 | INDOOR | 228 | 3 | 2 | 1 | 0 | 1 | 0 | 0 | 0.6204 | 0.81095 | 17.0643 | 8.6414 | 53.5099 | 62.5155 | 98.3002 | 0.0020886 | 8196.9566 | 0
216543 | GOWER ST, SWINTON | FERRANTI | SD78380224 | 750 | 11 KV | LV | 50 | INDOOR | 180 | 4 | 14 | 5 | 0 | 0 | 0 | 1 | 0.4233 | 0.52556 | 16.5075 | 8.4414 | 44.3018 | 47.9503 | 99.0821 | 0.0011069 | 15466.4368 | 0
216664 | HUTTON AVE, BOOTHSTOWN | ENGLISH ELECTRIC | SD71720083 | 750 | 11 KV | LV | 51 | INDOOR | 381 | 17 | 1 | 0 | 0 | 0 | 0 | 0 | 0.65237 | 0.85966 | 16.8364 | 8.5656 | 55.8439 | 66.3548 | 98.5519 | 0.0026107 | 6557.5651 | 0
216674 | HULME RD, LEIGH | SOUTH WALES SWITCHGEAR | SD64270060 | 800 | 11 KV | LV | 20 | OUTDOOR | 125 | 0 | 3 | 0 | 1 | 0 | 0 | 0 | 0.22457 | 0.29493 | 12.2404 | 6.8605 | 25.3477 | 26.8419 | 105.8561 | 0.00018353 | 93281.4567 | 0
217117 | LAWSON AVE, WESTLEIGH LANE LEIGH | PARSONS | SD65050220 | 500 | 11 KV | LV | 37 | OUTDOOR | 185 | 12 | 1 | 1 | 0 | 0 | 0 | 0 | 0.49634 | 0.66408 | 18.2854 | 9.0305 | 36.1903 | 42.701 | 97.1103 | 0.00037468 | 45692.2493 | 0
217521 | WESTWOOD METHS, BOLTON ROAD SWINTON | DENIS FERRANTI | SD79450076 | 500 | 11 KV | LV | 52 | OUTDOOR | 170 | 9 | 6 | 1 | 0 | 0 | 0 | 0 | 0.48005 | 0.62854 | 23.0591 | 10.5743 | 35.8193 | 41.4291 | 92.0888 | 0.00037292 | 45907.8358 | 0
218214 | BLACKBERRY DR | ABB | SD61500399 | 500 | 11 KV | LV | 12 | OUTDOOR | 207 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.51487 | 0.68859 | 9.4302 | 5.7422 | 37.0337 | 43.9311 | 111.5717 | 0.00039368 | 43487.2326 | 0
231594 | MIDDLEBROOK HOUSING, MIDDLEBROOK LOSTOCK | SOUTH WALES SWITCHGEAR | SD64771013 | 500 | 11 KV | LV | 16 | INDOOR | 277 | 0 | 2 | 3 | 0 | 0 | 0 | 0 | 0.71516 | 0.93751 | 9.0853 | 5.6223 | 59.3976 | 71.0466 | 111.9454 | 0.0035382 | 4838.6466 | 0
231670 | LITTLE OAKS | EFACEC | SD73021210 | 500 | 11 KV | LV | 2 | OUTDOOR | 101 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26657 | 0.36049 | 7.2559 | 4.8079 | 26.3463 | 28.6268 | 117.2551 | 0.00019132 | 89481.4742 | 0
232046 | DOROTHY ST, RAMSBOTTOM | ABB | SD78731612 | 500 | 11 KV | LV | 14 | OUTDOOR | 291 | 11 | 13 | 1 | 0 | 0 | 0 | 0 | 0.81954 | 1.0627 | 10.0837 | 5.9916 | 57.8228 | 71.2001 | 110.4691 | 0.0027405 | 6247.1295 | 0
232164 | DORIS MILL, ADJ 90 BURY N RD HEY | SOUTH WALES SWITCHGEAR | SD84201080 | 500 | 6.6 KV | LV | 18 | OUTDOOR | 363 | 16 | 13 | 1 | 0 | 0 | 2 | 1 | 1.157 | 1.4596 | 11.6665 | 6.6371 | 87.9 | 108.4637 | 106.9588 | 0.090743 | 188.6641 | 64.4
232373 | THATCHLEACH LN W, WHITEFIELD | BRUCE PEEBLES | SD81070514 | 750 | 11 KV | LV | 51 | OUTDOOR | 310 | 37 | 19 | 3 | 1 | 0 | 0 | 0 | 0.67988 | 0.87085 | 22.8113 | 10.4913 | 48.9595 | 58.1477 | 92.3577 | 0.0011656 | 14688.2967 | 0
232384 | WINGATE DR, WHITEFIELD | LINDLEY THOMPSON | SD80060637 | 500 | 11 KV | LV | 57 | INDOOR | 205 | 9 | 3 | 1 | 0 | 1 | 0 | 0 | 0.58459 | 0.76283 | 17.9927 | 8.9601 | 51.417 | 59.47 | 97.1668 | 0.0017682 | 9682.0206 | 0
232432 | BOOTH RD, OPP 30 BOOTH RD | CROMPTON PARKINSON | SD75960696 | 500 | 11 KV | LV | 53 | INDOOR | 250 | 29 | 5 | 1 | 1 | 0 | 0 | 0 | 0.75664 | 0.98583 | 17.2193 | 8.6971 | 63.2602 | 75.7189 | 98.0821 | 0.0053826 | 3180.6207 | 0
232488 | LONGTON ST, BURY RR 660 MCR RD | BABCOCK | SD80630794 | 500 | 11 KV | LV | 21 | INDOOR | 212 | 7 | 4 | 0 | 1 | 1 | 1 | 0 | 0.67662 | 0.85874 | 9.9357 | 5.9819 | 58.7641 | 67.6156 | 109.8598 | 0.0034495 | 4963.0096 | 0
232553 | MARKET ST BURY, BURY | ABB | SD80740983 | 800 | 6.6 KV | LV | 13 | OUTDOOR | 149 | 3 | 6 | 1 | 1 | 0 | 0 | 0 | 0.28195 | 0.3623 | 9.8816 | 5.9203 | 27.3754 | 29.3835 | 110.731 | 0.00021028 | 81414.6488 | 0
232576 | ABINGDON CL, ADJ 1 ABINGDON CLOSE | ENGLISH ELECTRIC | SD80730688 | 500 | 11 KV | LV | 50 | INDOOR | 231 | 8 | 1 | 1 | 0 | 0 | 0 | 0 | 0.59885 | 0.79971 | 16.6356 | 8.4939 | 51.4237 | 60.7567 | 98.8286 | 0.0017192 | 9958.2009 | 0
310448 | HALFWAY HS, REAR OF PUB ROYTON | FERRANTI | SD91380886 | 750 | 6.6 KV | LV | 56 | INDOOR | 142 | 5 | 1 | 1 | 0 | 0 | 0 | 0 | 0.24931 | 0.33391 | 17.9191 | 8.9308 | 35.8028 | 37.8993 | 97.3003 | 0.00058189 | 29421.3342 | 0
310534 | WHITEGATE AVE, CHADDERTON | SOUTH WALES SWITCHGEAR | SD89910378 | 800 | 6.6 KV | LV | 17 | OUTDOOR | 370 | 10 | 4 | 0 | 0 | 0 | 0 | 0 | 0.5944 | 0.78117 | 11.188 | 6.4643 | 41.5575 | 50.0497 | 107.6259 | 0.00056856 | 30111.1808 | 0
311103 | MIDDLEGATE, RR 43 MIDGATE HOLINS | BRUSH | SD92260271 | 500 | 6.6 KV | LV | 32 | OUTDOOR | 255 | 7 | 0 | 1 | 0 | 0 | 0 | 0 | 0.64946 | 0.85928 | 15.7441 | 8.1539 | 44.7014 | 54.5931 | 100.3152 | 0.00074017 | 23129.8517 | 0
312270 | HOLLY ST, MALHAM CLOSE ROYTON | DENIS FERRANTI | SD91720797 | 750 | 6.6 KV | LV | 50 | INDOOR | 321 | 17 | 4 | 2 | 0 | 0 | 0 | 0 | 0.57783 | 0.76216 | 16.4597 | 8.4339 | 51.5907 | 60.136 | 99.0442 | 0.0018225 | 9393.454 | 0
312895 | MERTON AVE, ADJ HERON MILL O/HAM | FERRANTI | SD91740307 | 750 | 6.6 KV | LV | 50 | OUTDOOR | 332 | 20 | 4 | 0 | 1 | 0 | 0 | 0 | 0.61342 | 0.79917 | 22.5375 | 10.4064 | 43.0941 | 51.6178 | 92.6284 | 0.00065985 | 25945.3774 | 0
313307 | GREENSIDE AVE, OFF HAVEN LN OLDHAM | FERRANTI | SD95050697 | 500 | 6.6 KV | LV | 48 | INDOOR | 232 | 5 | 6 | 2 | 1 | 0 | 0 | 0 | 0.66794 | 0.86194 | 16.2186 | 8.3499 | 57.3246 | 66.9375 | 99.3487 | 0.0029914 | 5723.1235 | 0
314107 | KIRKLAND YARNS, OFF JOWETT ST OLDHAM | SOUTH WALES SWITCHGEAR | SD94430650 | 800 | 6.6 KV | LV | 44 | INDOOR | 184 | 6 | 3 | 2 | 0 | 0 | 0 | 0 | 0.31203 | 0.41135 | 15.0483 | 7.9381 | 39.2858 | 42.2249 | 100.8933 | 0.00077038 | 22222.6802 | 0
314325 | BELLSHILL CRES, ROCHDALE | PAUWELS | SD91261409 | 500 | 6.6 KV | LV | 16 | OUTDOOR | 311 | 1 | 5 | 1 | 0 | 0 | 0 | 0 | 0.79924 | 1.0554 | 10.7611 | 6.2749 | 55.1833 | 69.1453 | 108.819 | 0.0020881 | 8198.8813 | 0
314378 | CROFTHEAD | EFACEC | SD93521716 | 750 | 6.6 KV | LV | 1 | INDOOR | 292 | 4 | 1 | 1 | 0 | 0 | 0 | 0 | 0.49201 | 0.64961 | 6.1254 | 4.3081 | 46.3822 | 52.9468 | 120.4829 | 0.0011798 | 14510.3566 | 0
314400 | DURN | SCHNEIDER ELECTRIC | SD94211644 | 750 | 6.6 KV | LV | 1 | INDOOR | 241 | 5 | 8 | 2 | 0 | 0 | 0 | 0 | 0.44255 | 0.57699 | 6.2692 | 4.3674 | 44.3328 | 49.494 | 120.199 | 0.0010457 | 16371.2907 | 0
314436 | HAUGH LANE, HAUGH LN NEWHEY | ABB | SD94121170 | 500 | 6.6 KV | LV | 20 | OUTDOOR | 311 | 12 | 2 | 2 | 0 | 0 | 0 | 0 | 0.81884 | 1.0792 | 11.9817 | 6.758 | 56.3726 | 70.8123 | 106.423 | 0.0023903 | 7162.3921 | 0
314606 | DUNLOP AVE, QUEENSWAY RDALE | ENGLISH ELECTRIC | SD89331143 | 750 | 6.6 KV | LV | 54 | OUTDOOR | 129 | 17 | 6 | 1 | 0 | 0 | 0 | 0 | 0.26643 | 0.35049 | 24.0061 | 10.8616 | 26.6297 | 28.7044 | 91.2245 | 0.00019921 | 85937.8152 | 0
314974 | NORDEN RD, BAMFORD | LINDLEY THOMPSON | SD86311311 | 750 | 6.6 KV | LV | 50 | INDOOR | 186 | 9 | 12 | 5 | 0 | 0 | 0 | 0 | 0.39378 | 0.50267 | 16.3751 | 8.4047 | 42.4754 | 46.2113 | 99.1453 | 0.00094565 | 18103.9998 | 0
320939 | FLEET ST | EFACEC | SJ95229533 | 500 | 6.6 KV | LV | 2 | OUTDOOR | 192 | 9 | 2 | 0 | 0 | 0 | 0 | 0 | 0.50251 | 0.66871 | 7.0989 | 4.7316 | 36.483 | 42.9941 | 117.8796 | 0.00038026 | 45021.6493 | 0
322939 | KINGS RD, OLD PEOPLES HOST AUL | FERRANTI | SD95090040 | 750 | 6.6 KV | LV | 51 | INDOOR | 274 | 10 | 4 | 0 | 1 | 0 | 0 | 0 | 0.50245 | 0.65122 | 16.9532 | 8.6044 | 47.4429 | 53.7053 | 98.4366 | 0.0013135 | 13033.7792 | 0
323779 | CALVER MEWS, CAR PARK GAMESLEY | SOUTH WALES SWITCHGEAR | SK01029484 | 1000 | 11 KV | LV | 26 | OUTDOOR | 100 | 75 | 2 | 0 | 0 | 0 | 0 | 0 | 0.22045 | 0.29396 | 13.8889 | 7.4849 | 25.0359 | 26.6507 | 103.0525 | 0.00018221 | 93957.108 | 0
326139 | WILTSHIRE DR, GLOSSOP | HAWKER SIDDELEY | SK04259335 | 500 | 11 KV | LV | 18 | OUTDOOR | 278 | 16 | 0 | 0 | 1 | 0 | 0 | 0 | 0.75606 | 0.99188 | 11.361 | 6.5143 | 52.1222 | 64.479 | 107.6104 | 0.0015164 | 11290.2561 | 0
327085 | OLDHAM ATHLETIC, SHEEPFOOT LN OLDHAM | FERRANTI | SD91500646 | 750 | 6.6 KV | LV | 23 | OUTDOOR | 134 | 7 | 2 | 0 | 0 | 0 | 0 | 0 | 0.23723 | 0.31811 | 10.3288 | 6.1404 | 35.4107 | 37.3224 | 109.0269 | 0.00056803 | 30139.5152 | 0
327098 | E WHITTAKER, OLDHAM | SOUTH WALES SWITCHGEAR | SD92160607 | 500 | 6.6 KV | LV | 26 | OUTDOOR | 114 | 1 | 4 | 1 | 0 | 0 | 0 | 0 | 0.31232 | 0.41716 | 14.0679 | 7.5627 | 28.2529 | 31.1184 | 102.5875 | 0.00021964 | 77945.149 | 0
327479 | ARMITAGE CL, OFF HERON ST | ABB | SD91320350 | 500 | 6.6 KV | LV | 22 | OUTDOOR | 305 | 48 | 19 | 4 | 0 | 3 | 0 | 0 | 1.1196 | 1.4014 | 12.7472 | 7.0558 | 86.8187 | 105.45 | 104.9453 | 0.074066 | 231.1441 | 57.8
330093 | BIRKETT AND BOSTOCK, HR HILLGATE STOCKPR | FERRANTI | SJ89968953 | 750 | 6.6 KV | LV | 51 | INDOOR | 100 | 0 | 2 | 1 | 1 | 0 | 0 | 1 | 0.23945 | 0.29896 | 16.7995 | 8.5498 | 35.9474 | 37.2974 | 98.633 | 0.00060803 | 28156.3481 | 0
330180 | HEMPSHAW LN OFFERTON STOCKPORT | ABB | SJ90788941 | 500 | 6.6 KV | LV | 13 | OUTDOOR | 220 | 5 | 10 | 4 | 0 | 1 | 0 | 0 | 0.67813 | 0.87148 | 9.815 | 5.8957 | 48.9603 | 58.0405 | 110.799 | 0.0011621 | 14731.8075 | 0
330222 | NORRIS BANK, HEATON NORRIS | ABB | SJ87839059 | 800 | 6.6 KV | LV | 21 | OUTDOOR | 347 | 3 | 1 | 1 | 0 | 0 | 0 | 0 | 0.54371 | 0.72096 | 12.5835 | 6.9951 | 38.5913 | 46.1472 | 105.2203 | 0.00044585 | 38398.8621 | 0
330225 | OSBORNE ST, BREDBURY | SOUTH WALES SWITCHGEAR | SJ91469112 | 800 | 11 KV | LV | 15 | INDOOR | 228 | 35 | 10 | 2 | 0 | 0 | 0 | 0 | 0.44834 | 0.58545 | 8.6184 | 5.4217 | 45.9091 | 51.2666 | 113.1568 | 0.0012603 | 13584.5267 | 0
330276 | TATTON RD, HEATON MOOR | FERRANTI | SJ88179210 | 1000 | 6.6 KV | LV | 50 | INDOOR | 250 | 62 | 17 | 10 | 0 | 1 | 0 | 0 | 0.49553 | 0.62075 | 16.3541 | 8.4018 | 49.5 | 54.7204 | 99.1242 | 0.0017533 | 9764.4513 | 0
330300 | WOODLANDS DR, OFFERTON | ABB | SJ91658969 | 500 | 6.6 KV | LV | 15 | INDOOR | 273 | 15 | 2 | 0 | 0 | 0 | 0 | 0 | 0.71527 | 0.94666 | 8.6788 | 5.4508 | 58.9887 | 71.2256 | 112.926 | 0.0034582 | 4950.5154 | 0
330305 | YORK ST STOCKPORT | ABB | SJ89108971 | 1000 | 6.6 KV | LV | 12 | OUTDOOR | 212 | 8 | 11 | 0 | 0 | 0 | 1 | 0 | 0.32254 | 0.41591 | 9.2272 | 5.6547 | 28.8553 | 31.5309 | 112.1303 | 0.00023102 | 74104.9035 | 0
331769 | HULLEY RD, MACCLESFIELD | SOUTH WALES SWITCHGEAR | SJ92737461 | 500 | 11 KV | LV | 18 | OUTDOOR | 331 | 54 | 6 | 4 | 0 | 0 | 0 | 0 | 1.0119 | 1.3186 | 11.5695 | 6.608 | 72.3684 | 91.9927 | 107.02 | 0.016176 | 1058.3427 | 0.2
331890 | GRANGE RD, BRAMHALL | YORKSHIRE ELECTRICAL TRANSFORMERS | SJ89728707 | 500 | 11 KV | LV | 48 | INDOOR | 169 | 14 | 3 | 0 | 0 | 0 | 0 | 0 | 0.46423 | 0.61808 | 16.0877 | 8.3021 | 43.9311 | 49.8453 | 99.5489 | 0.00095552 | 17916.8576 | 0
331994 | POWNALL FM, STYAL | LINDLEY THOMPSON | SJ84018349 | 500 | 11 KV | LV | 49 | INDOOR | 91 | 12 | 8 | 1 | 0 | 0 | 1 | 0 | 0.35631 | 0.4478 | 16.3665 | 8.4015 | 39.7206 | 42.4678 | 99.1637 | 0.00075219 | 22760.2328 | 0
331997 | QUEENS AVE, MACCLESFIELD | TRANSFORMERS (WALES) | SJ92197455 | 800 | 11 KV | LV | 18 | INDOOR | 144 | 14 | 7 | 1 | 3 | 3 | 0 | 0 | 0.42656 | 0.49531 | 9.1809 | 5.6695 | 46.4724 | 48.7799 | 111.5613 | 0.0014232 | 12029.3142 | 0
332456 | PARKGATE WAY, SPATH LNG6 HANDFORTH | LINDLEY THOMPSON | SJ85948362 | 500 | 11 KV | LV | 51 | INDOOR | 119 | 11 | 3 | 0 | 0 | 0 | 0 | 0 | 0.33464 | 0.4485 | 16.6102 | 8.4825 | 37.9341 | 41.347 | 98.8915 | 0.00063462 | 26976.9046 | 0
332587 | REDHOUSE LN, DISLEY | UNIDAIRE LTD | SJ98048467 | 500 | 11 KV | LV | 22 | OUTDOOR | 113 | 10 | 4 | 1 | 0 | 0 | 0 | 0 | 0.33213 | 0.43783 | 12.6612 | 7.0219 | 29.012 | 32.0499 | 105.1343 | 0.00023144 | 73971.2243 | 0
332821 | CHESTER WALKS, BREDBURY | CROMPTON PARKINSON | SJ93329018 | 500 | 11 KV | LV | 51 | INDOOR | 210 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0.53291 | 0.71236 | 16.7908 | 8.544 | 47.3238 | 55.0287 | 98.6758 | 0.0012134 | 14108.8698 | 0
332876 | LADYBROOK RD, BRAMHALL | PAUWELS | SJ88338631 | 750 | 11 KV | LV | 16 | OUTDOOR | 137 | 8 | 5 | 2 | 0 | 0 | 0 | 0 | 0.26697 | 0.35004 | 11.0793 | 6.4059 | 26.6464 | 28.7001 | 108.132 | 0.0001988 | 86118.5769 | 0
333103 | QUEENS RD FLATS, WILMSLOW | ABB | SJ84268087 | 500 | 11 KV | LV | 13 | INDOOR | 136 | 24 | 8 | 1 | 0 | 2 | 0 | 2 | 0.63792 | 0.7717 | 8.0606 | 5.1877 | 57.325 | 63.4752 | 114.4855 | 0.0033314 | 5138.9528 | 0
333883 | HIGHFIELD AVE, BREDBURY | SOUTH WALES SWITCHGEAR | SJ92879085 | 750 | 11 KV | LV | 45 | INDOOR | 191 | 6 | 1 | 0 | 0 | 1 | 0 | 0 | 0.34852 | 0.45709 | 15.4714 | 8.0892 | 39.7234 | 43.1965 | 100.3105 | 0.00075475 | 22682.9781 | 0
333962 | DIXON DRIVE 29, CHELFORD | SOUTH WALES SWITCHGEAR | SJ81377512 | 1000 | 11 KV | LV | 26 | INDOOR | 130 | 61 | 7 | 5 | 0 | 0 | 0 | 0 | 0.27636 | 0.35795 | 10.8367 | 6.3451 | 38.2161 | 40.4139 | 107.9861 | 0.00074988 | 22830.4231 | 0
334173 | ALDERWOOD AVE, HEATON MERSEY | BRUSH | SJ87059030 | 500 | 6.6 KV | LV | 33 | INDOOR | 318 | 17 | 1 | 0 | 0 | 0 | 0 | 0 | 0.82461 | 1.0934 | 12.4016 | 6.9573 | 66.7448 | 82.3869 | 105.0408 | 0.0080161 | 2135.7101 | 0
334195 | CORBAR RD(STOCKPORT), STOCKPORT | DENIS FERRANTI | SJ90568835 | 750 | 6.6 KV | LV | 49 | OUTDOOR | 40 | 85 | 2 | 0 | 0 | 1 | 0 | 0 | 0.23743 | 0.30725 | 21.9614 | 10.2202 | 25.7342 | 27.3074 | 93.2272 | 0.00019795 | 86488.152 | 0
336478 | LOWER BENTS LN, BREDBURY | BRUSH | SJ92599166 | 500 | 11 KV | LV | 29 | OUTDOOR | 217 | 15 | 10 | 3 | 0 | 0 | 0 | 0 | 0.65009 | 0.84178 | 15.3122 | 7.9985 | 46.2768 | 55.2245 | 100.9687 | 0.00089188 | 19195.3569 | 0
336998 | ST GEORGES ST, MACCLESFIELD | SOUTH WALES SWITCHGEAR | SJ91857303 | 500 | 11 KV | LV | 26 | OUTDOOR | 81 | 31 | 6 | 1 | 1 | 0 | 0 | 0 | 0.35653 | 0.45885 | 14.0877 | 7.5574 | 30.6477 | 33.6301 | 102.7442 | 0.00027357 | 62580.902 | 0
337081 | DORCHESTER WAY, DORCHESTER WAY,MACC | HAWKER SIDDELEY | SJ91097579 | 500 | 11 KV | LV | 25 | OUTDOOR | 230 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0.57497 | 0.77079 | 13.7802 | 7.4467 | 40.2884 | 48.6641 | 103.195 | 0.00050866 | 33656.8611 | 0
337724 | DIDSBURY ROAD, OPP 218 | ABB | SJ87409070 | 500 | 6.6 KV | LV | 20 | OUTDOOR | 228 | 16 | 1 | 1 | 0 | 0 | 0 | 0 | 0.6113 | 0.81146 | 11.894 | 6.7242 | 42.537 | 51.471 | 106.5657 | 0.00062112 | 27563.2549 | 0
410398 | ROBINSON ST, PRESTON | SOUTH WALES SWITCHGEAR | SD52913133 | 500 | 6.6 KV | LV | 25 | OUTDOOR | 229 | 17 | 15 | 3 | 0 | 0 | 1 | 0 | 0.76181 | 0.96945 | 13.5103 | 7.348 | 54.9692 | 65.6372 | 103.6014 | 0.0020624 | 8301.1232 | 0
410460 | CEMETERY (PRESTON), PRESTON | ABB | SD56333023 | 500 | 6.6 KV | LV | 16 | INDOOR | 278 | 7 | 22 | 4 | 0 | 0 | 1 | 0 | 0.9086 | 1.1397 | 8.7306 | 5.4836 | 78.1699 | 92.1232 | 112.5794 | 0.025515 | 670.9692 | 0
410579 | HARBOUR LN (WARTON), WARTON | BABCOCK | SD41292865 | 800 | 6.6 KV | LV | 22 | INDOOR | 343 | 14 | 13 | 5 | 1 | 0 | 1 | 0 | 0.67105 | 0.8518 | 10.3296 | 6.147 | 60.7256 | 69.9329 | 108.9202 | 0.0043639 | 3923.1038 | 0
410611 | WATERLOO RD, PRESTON | BONAR LONG | SD51793064 | 500 | 6.6 KV | LV | 55 | INDOOR | 193 | 24 | 10 | 4 | 0 | 0 | 0 | 0 | 0.62277 | 0.81044 | 17.5255 | 8.8001 | 54.5861 | 63.4274 | 97.7365 | 0.0024032 | 7123.8265 | 0
410842 | BROWNING RD, PRESTON | BABCOCK | SD55633065 | 500 | 6.6 KV | LV | 22 | OUTDOOR | 126 | 5 | 7 | 1 | 0 | 0 | 0 | 0 | 0.3682 | 0.48553 | 12.6795 | 7.0337 | 30.7447 | 34.2971 | 105.0011 | 0.00026228 | 65274.1793 | 0
414508 | JUNCTION LN, BURSCOUGH | FERRANTI | SD44401155 | 750 | 11 KV | LV | 52 | INDOOR | 102 | 8 | 3 | 1 | 0 | 0 | 0 | 0 | 0.1965 | 0.26127 | 17.041 | 8.6337 | 34.2925 | 35.6141 | 98.3342 | 0.00053569 | 31958.7131 | 0
414539 | HENNEL LN SW HS, WALTON LE DALE | BONAR LONG | SD54752702 | 500 | 11 KV | LV | 29 | OUTDOOR | 180 | 7 | 3 | 0 | 0 | 0 | 0 | 0 | 0.4738 | 0.63291 | 14.7399 | 7.7988 | 35.1147 | 41.0848 | 101.696 | 0.00034655 | 49401.75 | 0
414613 | BALCARRES RD, LEYLAND | ABB | SD54242163 | 500 | 11 KV | LV | 14 | INDOOR | 181 | 5 | 9 | 4 | 0 | 0 | 0 | 1 | 0.59834 | 0.75695 | 8.4753 | 5.3714 | 53.446 | 60.5468 | 113.2595 | 0.0021827 | 7843.4787 | 0
414615 | MOSSY LEA, WRIGHTINGTON | ABB | SD53651254 | 500 | 11 KV | LV | 14 | OUTDOOR | 174 | 5 | 4 | 0 | 1 | 1 | 0 | 0 | 0.53266 | 0.68162 | 10.3845 | 6.1258 | 39.4881 | 45.3706 | 109.6147 | 0.00050968 | 33589.4607 | 0
414674 | COW MOSS | EFACEC | SD56501397 | 500 | 11 KV | LV | 1 | INDOOR | 261 | 14 | 3 | 0 | 0 | 0 | 1 | 0 | 0.73519 | 0.95501 | 6.2175 | 4.3455 | 61.0861 | 72.8507 | 120.3291 | 0.0041963 | 4079.7449 | 0
414844 | ROAD SPRINGS, LEYLAND | PAUWELS | SD52302184 | 500 | 11 KV | LV | 14 | OUTDOOR | 139 | 7 | 3 | 5 | 0 | 0 | 0 | 0 | 0.41897 | 0.55103 | 10.2557 | 6.0763 | 33.0246 | 37.4491 | 109.8078 | 0.00030909 | 55388.5256 | 0
415028 | CLOVER RD, CHORLEY | FERRANTI | SD57121619 | 500 | 11 KV | LV | 49 | INDOOR | 117 | 7 | 6 | 1 | 0 | 2 | 0 | 0 | 0.4231 | 0.52743 | 16.1392 | 8.3202 | 43.2046 | 46.7981 | 99.4786 | 0.00098822 | 17324.0961 | 0
415087 | ALDERBROOK DR, PARBOLD | LINDLEY THOMPSON | SD49231083 | 500 | 11 KV | LV | 51 | INDOOR | 119 | 5 | 8 | 2 | 0 | 0 | 0 | 0 | 0.36648 | 0.47571 | 16.3763 | 8.4044 | 39.9398 | 43.351 | 99.1502 | 0.00074727 | 22909.9615 | 0
415293 | BLACKGATE LN, TARLETON | SOUTH WALES SWITCHGEAR | SD44892033 | 500 | 11 KV | LV | 27 | INDOOR | 112 | 44 | 7 | 4 | 0 | 0 | 0 | 0 | 0.4577 | 0.59401 | 11.1462 | 6.4671 | 44.5894 | 49.6905 | 107.3773 | 0.0010928 | 15666.4154 | 0
415504 | CLAUGHTON AVE, CLAYTON-LE-WOODS | PARSONS | SD56342239 | 500 | 11 KV | LV | 31 | INDOOR | 366 | 23 | 2 | 0 | 0 | 0 | 0 | 0 | 0.96229 | 1.2674 | 12.1771 | 6.8735 | 77.8453 | 97.4916 | 105.3977 | 0.030747 | 556.8045 | 7
415540 | WYRESDALE DR | ABB | SD54732098 | 500 | 11 KV | LV | 12 | INDOOR | 228 | 7 | 1 | 0 | 0 | 0 | 0 | 0 | 0.57998 | 0.77176 | 7.9254 | 5.117 | 50.1506 | 58.8062 | 115.1017 | 0.0015332 | 11166.0903 | 0
417073 | RIPON ST, RIPON STREET PRESTON | BRUSH | SD53403071 | 800 | 6.6 KV | LV | 29 | OUTDOOR | 138 | 9 | 3 | 0 | 0 | 0 | 0 | 0 | 0.23507 | 0.31468 | 15.2287 | 7.9766 | 25.4598 | 27.261 | 100.9882 | 0.00018292 | 93594.5341 | 0
418214 | BRITANNIA DR, PRESTON | SOUTH WALES SWITCHGEAR | SD51712948 | 800 | 6.6 KV | LV | 17 | OUTDOOR | 42 | 177 | 1 | 6 | 0 | 0 | 0 | 0 | 0.43109 | 0.4917 | 11.1724 | 6.4537 | 32.5918 | 34.7408 | 107.7148 | 0.00030874 | 55451.7813 | 0
423267 | QUEENS PK EST, ST ANNES | PARSONS | SD33852875 | 500 | 6.6 KV | LV | 35 | INDOOR | 222 | 18 | 4 | 0 | 0 | 0 | 0 | 0 | 0.60918 | 0.80436 | 13.055 | 7.212 | 52.2949 | 61.5174 | 103.8262 | 0.0018767 | 9122.4976 | 0
423313 | SOUTH HEY, ST ANNES | BONAR LONG | SD34502860 | 750 | 6.6 KV | LV | 47 | INDOOR | 238 | 108 | 0 | 4 | 0 | 0 | 0 | 0 | 0.58992 | 0.77321 | 15.9728 | 8.2634 | 52.3726 | 61.0442 | 99.6761 | 0.0020709 | 8267.0018 | 0
423928 | HOLYOAKE AVE, OPP NO1 HOLYOAKE | PARSONS | SD32323837 | 500 | 6.6 KV | LV | 35 | OUTDOOR | 101 | 7 | 4 | 2 | 2 | 0 | 0 | 0 | 0.38366 | 0.47556 | 17.4739 | 8.7531 | 32.1949 | 34.9276 | 98.1131 | 0.00030427 | 56266.6666 | 0
427236 | HERITAGE WAY | BABCOCK | SD32704224 | 800 | 6.6 KV | LV | 22 | OUTDOOR | 121 | 48 | 2 | 0 | 0 | 0 | 0 | 0 | 0.26591 | 0.35855 | 12.4587 | 6.9427 | 26.4183 | 28.7616 | 105.5358 | 0.00019705 | 86881.1648 | 0
428275 | KINGSWAY, OLD FLATS ENTRANCE | PAUWELS | SD31304270 | 800 | 6.6 KV | LV | 16 | INDOOR | 57 | 68 | 2 | 3 | 0 | 0 | 0 | 0 | 0.21609 | 0.28748 | 8.704 | 5.4656 | 36.0297 | 37.6175 | 112.7859 | 0.00065451 | 26156.986 | 0
429617 | PEACE PL, GAMBLE RD THORNTON | ABB | SD33464390 | 800 | 11 KV | LV | 15 | INDOOR | 334 | 13 | 6 | 0 | 1 | 0 | 1 | 0 | 0.60311 | 0.77455 | 8.6664 | 5.448 | 55.0182 | 63.2641 | 112.9056 | 0.0025589 | 6690.2476 | 0
429948 | LITTLE POULTON GDNS | ABB | SD35703910 | 500 | 6.6 KV | LV | 12 | INDOOR | 48 | 76 | 6 | 0 | 0 | 0 | 0 | 0 | 0.33854 | 0.44893 | 8.0661 | 5.1854 | 38.4539 | 41.8329 | 114.5568 | 0.00072493 | 23616.2041 | 0
450050 | STANSFELD ST, BLACKBURN BB18 I | BRUSH | SD67422706 | 800 | 6.6 KV | LV | 31 | OUTDOOR | 120 | 4 | 7 | 1 | 1 | 0 | 0 | 0 | 0.24394 | 0.31097 | 15.7424 | 8.148 | 26.1256 | 27.6235 | 100.3963 | 0.00019517 | 87720.0231 | 0
450074 | GUIDE, CARPARK OF ENSOR | SOUTH WALES SWITCHGEAR | SD70562579 | 500 | 6.6 KV | LV | 19 | OUTDOOR | 108 | 2 | 3 | 0 | 0 | 0 | 0 | 0 | 0.28551 | 0.38586 | 11.7888 | 6.6972 | 27.1345 | 29.7174 | 106.5367 | 0.00020287 | 84388.9675 | 0
450105 | WILWORTH CRES, PLECKGATE Z4 0 | ABB | SD68043043 | 500 | 6.6 KV | LV | 15 | OUTDOOR | 89 | 4 | 6 | 0 | 0 | 1 | 0 | 1 | 0.35771 | 0.43695 | 10.215 | 6.0709 | 30.8687 | 33.1164 | 109.6879 | 0.00027824 | 61528.6752 | 0
450183 | OAK HILL, ACCRINGTON R22 I | SOUTH WALES SWITCHGEAR | SD76642772 | 500 | 6.6 KV | LV | 24 | INDOOR | 190 | 12 | 7 | 0 | 0 | 0 | 0 | 0 | 0.53282 | 0.703 | 10.3684 | 6.1544 | 48.0643 | 55.3004 | 108.9947 | 0.0013381 | 12794.0362 | 0
450388 | HASTON LEE MILL, BLACKBURN AA6 I | ABB | SD68643057 | 500 | 6.6 KV | LV | 17 | INDOOR | 178 | 2 | 12 | 2 | 0 | 0 | 0 | 0 | 0.52544 | 0.67991 | 9.0727 | 5.6253 | 48.565 | 54.8548 | 111.8079 | 0.0014228 | 12032.3288 | 0
450584 | BLACKBURN RD (OSW), OSWALDTWISTLE L17 I | BABCOCK | SD73032830 | 800 | 6.6 KV | LV | 21 | INDOOR | 154 | 12 | 8 | 1 | 0 | 0 | 0 | 0 | 0.28718 | 0.37784 | 10.1905 | 6.0781 | 38.5361 | 41.0169 | 109.453 | 0.0007456 | 22961.3608 | 0
450784 | BROADFIELD, ACCRINGTON Q21 I | LINDLEY THOMPSON | SD75502727 | 500 | 6.6 KV | LV | 48 | INDOOR | 149 | 29 | 2 | 0 | 0 | 0 | 0 | 0 | 0.44689 | 0.6002 | 15.9909 | 8.2733 | 42.9923 | 48.7638 | 99.6074 | 0.0009068 | 18879.5268 | 0
451828 | BRANTWOOD | ABB | SD74233092 | 500 | 6.6 KV | LV | 14 | OUTDOOR | 176 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.435 | 0.58165 | 10.0914 | 6.0176 | 32.9947 | 38.1772 | 110.0413 | 0.00029139 | 58753.0904 | 0
451866 | MILNSHAW GDNS | SOUTH WALES SWITCHGEAR | SD75472905 | 800 | 6.6 KV | LV | 25 | OUTDOOR | 41 | 57 | 5 | 0 | 0 | 0 | 0 | 0 | 0.16806 | 0.22578 | 14.232 | 7.6162 | 23.784 | 24.7896 | 102.4334 | 0.00017014 | 100622.8519 | 0
453049 | FOREST MILL, LUMB A18 I | SOUTH WALES SWITCHGEAR | SD84072561 | 500 | 6.6 KV | LV | 17 | INDOOR | 175 | 8 | 4 | 1 | 0 | 0 | 0 | 0 | 0.47868 | 0.62991 | 9.0046 | 5.5896 | 44.8833 | 50.8049 | 112.0952 | 0.0010314 | 16599.0158 | 0
455007 | WADDINGTON, WADDINGTON C2 I6 | CROMPTON PARKINSON | SD72864394 | 500 | 11 KV | LV | 53 | OUTDOOR | 133 | 20 | 9 | 4 | 0 | 1 | 0 | 0 | 0.50054 | 0.62996 | 23.4497 | 10.6852 | 38.1253 | 42.9962 | 91.7868 | 0.00048003 | 35664.1846 | 0
458190 | GRETNA, BURNLEY B3 B3 | FERRANTI | SD82693146 | 750 | 6.6 KV | LV | 53 | OUTDOOR | 220 | 5 | 3 | 1 | 0 | 0 | 0 | 0 | 0.38378 | 0.50604 | 23.2196 | 10.6208 | 30.927 | 34.9572 | 91.9603 | 0.000258 | 66356.7651 | 0
458556 | GERTRUDE ST, NELSON N1 F14 | LINDLEY THOMPSON | SD87023875 | 500 | 6.6 KV | LV | 55 | INDOOR | 317 | 34 | 15 | 0 | 1 | 0 | 1 | 0 | 1.0254 | 1.3097 | 17.5459 | 8.8031 | 87.4747 | 106.2742 | 97.7486 | 0.082266 | 208.1045 | 97.4
458558 | OXFORD RD | ALSTOM | SD87253869 | 500 | 6.6 KV | LV | 11 | INDOOR | 193 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0.48951 | 0.65755 | 7.8305 | 5.0819 | 45.0441 | 51.8246 | 115.2188 | 0.0010213 | 16763.5386 | 0
458748 | BACK RUTLAND AVE, BURNLEY B1 B13 | FERRANTI | SD81463288 | 750 | 6.6 KV | LV | 51 | INDOOR | 119 | 6 | 5 | 0 | 0 | 0 | 1 | 0 | 0.25322 | 0.32558 | 16.6843 | 8.5087 | 36.2478 | 38.02 | 98.7877 | 0.00060967 | 28080.8684 | 0
616017 | TWEED RISE, WALNEY BARROW | SOUTH WALES SWITCHGEAR | SD17796893 | 500 | 11 KV | LV | 58 | OUTDOOR | 244 | 17 | 0 | 2 | 1 | 0 | 0 | 0 | 0.6936 | 0.90218 | 25.3828 | 11.2767 | 48.266 | 58.5166 | 89.9767 | 0.0010424 | 16422.8972 | 0
616120 | HEST VIEW, ULVERSTON | BONAR LONG | SD28787649 | 500 | 11 KV | LV | 45 | OUTDOOR | 261 | 22 | 1 | 1 | 0 | 0 | 0 | 0 | 0.70677 | 0.94132 | 20.9287 | 9.9002 | 48.47 | 60.1995 | 94.2137 | 0.0010675 | 16038.1499 | 0
620293 | THE ARCHES, MARYPORT | SOUTH WALES SWITCHGEAR | NY03783549 | 500 | 11 KV | LV | 17 | INDOOR | 242 | 5 | 2 | 0 | 0 | 0 | 0 | 0 | 0.61479 | 0.81979 | 8.8875 | 5.544 | 52.3779 | 62.0474 | 112.3212 | 0.0018623 | 9193.1457 | 0
620717 | DERWENT RD, MOSS BAY WORKINGTON | SOUTH WALES SWITCHGEAR | NX99282733 | 500 | 11 KV | LV | 17 | OUTDOOR | 327 | 20 | 30 | 6 | 0 | 0 | 0 | 0 | 1.078 | 1.3563 | 11.1412 | 6.4412 | 82.4831 | 100.4426 | 107.8154 | 0.043999 | 389.1 | 16.4
636100 | CHESTERHOLM, ADJ 69 CHESTERHOLM | BONAR LONG | NY37025553 | 500 | 11 KV | LV | 39 | OUTDOOR | 252 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65037 | 0.86968 | 18.6321 | 9.15 | 44.6453 | 55.0145 | 96.6726 | 0.00074406 | 23008.9111 | 0
636173 | TODDS | ABB | NY39565561 | 800 | 11 KV | LV | 12 | OUTDOOR | 134 | 12 | 12 | 2 | 0 | 0 | 0 | 0 | 0.27794 | 0.35592 | 9.4945 | 5.7668 | 27.2827 | 29.2461 | 111.464 | 0.00021081 | 81209.771 | 0
636385 | QUEENSWAY, BES NO 10 QUEENSWAY | YORKSHIRE SWITCHGEAR AND ENGINEERING | NY37905480 | 500 | 11 KV | LV | 44 | INDOOR | 240 | 16 | 6 | 1 | 0 | 0 | 0 | 0 | 0.6684 | 0.87638 | 15.458 | 8.0849 | 56.4877 | 66.9689 | 100.3239 | 0.0027474 | 6231.2936 | 0
642320 | CONISTON AVENUE HAMBLETON | SOUTH WALES SWITCHGEAR | SD37064267 | 500 | 11 KV | LV | 17 | INDOOR | 137 | 25 | 3 | 1 | 0 | 0 | 0 | 0 | 0.42231 | 0.55938 | 9.018 | 5.5955 | 41.9703 | 46.9335 | 112.0927 | 0.00084783 | 20192.6585 | 0
642344 | BEECHFIELD AVE, PREESALL | ABB | SD36414838 | 500 | 6.6 KV | LV | 15 | INDOOR | 168 | 25 | 2 | 0 | 0 | 0 | 0 | 0 | 0.48343 | 0.64432 | 8.5623 | 5.3991 | 44.8622 | 51.2401 | 113.2792 | 0.0010285 | 16645.0923 | 0
643270 | ULSTER ROAD, BOWERHAM LANCASTER | HAWKER SIDDELEY | SD48466041 | 1000 | 11 KV | LV | 27 | INDOOR | 343 | 29 | 5 | 2 | 0 | 0 | 0 | 0 | 0.47787 | 0.62631 | 11.2135 | 6.4928 | 47.0359 | 53.2334 | 107.2515 | 0.0013255 | 12916.1006 | 0
643285 | DALTON ROAD (LANCASTER), LANCASTER | SOUTH WALES SWITCHGEAR | SD48486185 | 500 | 11 KV | LV | 27 | OUTDOOR | 321 | 30 | 6 | 0 | 0 | 0 | 0 | 0 | 0.89187 | 1.169 | 14.4535 | 7.6889 | 62.0433 | 78.3361 | 102.2107 | 0.0044989 | 3805.4111 | 0
643286 | MOORGATE, LANCASTER | HAWKER SIDDELEY | SD48306164 | 500 | 11 KV | LV | 27 | INDOOR | 292 | 35 | 14 | 4 | 0 | 0 | 0 | 0 | 0.9141 | 1.1847 | 11.0403 | 6.4282 | 76.6796 | 93.3504 | 107.5441 | 0.023723 | 721.6511 | 0.2
643293 | RIDGE LANE | NITRAN | SD48236224 | 800 | 11 KV | 6.6 KV | 23 | OUTDOOR | 90 | 26 | 1 | 5 | 0 | 0 | 0 | 0 | 0.20944 | 0.27665 | 13.2704 | 7.2468 | 24.8669 | 26.2255 | 104.1865 | 0.00017986 | 95185.7327 | 0
666035 | RAISELANDS CROFT, ADJ.7 RAISELANDS CFT | DISTRIBUTION TRANSFORMERS LTD | NY51103120 | 500 | 11 KV | LV | 36 | OUTDOOR | 308 | 14 | 4 | 1 | 1 | 0 | 0 | 0 | 0.85572 | 1.1127 | 17.6323 | 8.8156 | 59.9219 | 74.6295 | 97.8243 | 0.0034724 | 4930.3383 | 0

## Mapping - Mid-range
Mapping of failure probability of demonstrated distribution transformers

## High-range Scenario
General information |  |  |  | Input data for assessment | [12 empty] | Intermediate data | [6 empty] | Output
Substation Number | Substation | Manufacturer | Grid Reference | Power Rating (kVA) | HV | LV | Transformer Age (till 2015) | Indoor/Outdoor | Number of customers | [7 empty] | Peak load (p.u.) |  | Moisture |  | Peak hot-spot temperature (°C) |  | Bubbling inception temperature (°C) | Loss-of-life (year per year) | Expected lifetime (p.u.) | Failure probability (%)
[9 empty] | PC1 | PC2 | PC3 | PC4 | PC5 | PC6 | PC7 | PC8 | No EVs | With EVs | In oil (ppm) | In paper (%) | No EVs | With EVs
165002 | LANCASTER RD SALFORD 6 | ABB | SD78720037 | 500 | 6.6 KV | LV | 13 | INDOOR | 372 | 15 | 5 | 2 | 0 | 0 | 0 | 0 | 0.99198 | 1.8531 | 8.2455 | 5.2642 | 81.1897 | 144.9411 | 114.0666 | 2.97 | 5.7644 | 99.8
165080 | ST MARGARETS RD, PRESTWICH | PAUWELS | SD82210493 | 800 | 6.6 KV | LV | 16 | INDOOR | 320 | 20 | 8 | 0 | 0 | 0 | 0 | 0 | 0.54738 | 1.0247 | 8.9376 | 5.5613 | 51.0614 | 75.5496 | 112.2814 | 0.0036687 | 4666.5109 | 0
165083 | NAZARETH HS, PRESTWICH | ABB | SD82260317 | 500 | 6.6 KV | LV | 14 | OUTDOOR | 212 | 7 | 7 | 0 | 0 | 1 | 0 | 0 | 0.6099 | 1.1134 | 10.1006 | 6.0184 | 43.6167 | 69.2207 | 110.0615 | 0.0015078 | 11354.293 | 0
165133 | MANTON CL, BROUGHTON | FERRANTI | SD83620078 | 750 | 6.6 KV | LV | 50 | INDOOR | 75 | 82 | 1 | 2 | 0 | 0 | 0 | 0 | 0.27314 | 0.51847 | 16.399 | 8.4146 | 36.7376 | 44.3809 | 99.0988 | 0.00070738 | 24201.9804 | 0
165528 | BISHOP RD, PENDLETON | CROMPTON PARKINSON | SJ78889962 | 1000 | 6.6 KV | LV | 52 | INDOOR | 216 | 26 | 2 | 0 | 0 | 0 | 0 | 0 | 0.30159 | 0.57609 | 16.836 | 8.5638 | 38.739 | 48.141 | 98.5734 | 0.00083404 | 20526.4961 | 0
165647 | HEATH AVE, SALFORD 7 | CROMPTON PARKINSON | SJ82429945 | 1000 | 6.6 KV | LV | 51 | INDOOR | 299 | 3 | 14 | 2 | 0 | 0 | 0 | 0 | 0.41697 | 0.76436 | 16.593 | 8.4782 | 44.3649 | 59.0608 | 98.8882 | 0.0014303 | 11969.646 | 0
165756 | ALBANY CT URMSTON | ABB | SJ75999500 | 800 | 6.6 KV | LV | 13 | OUTDOOR | 153 | 39 | 3 | 0 | 0 | 0 | 0 | 0 | 0.30434 | 0.58005 | 9.786 | 5.879 | 27.7636 | 36.7023 | 110.9841 | 0.00023751 | 72082.1784 | 0
166355 | TRAFFORD RD 181 | BRUSH | SJ76769802 | 500 | 6.6 KV | LV | 30 | OUTDOOR | 369 | 6 | 7 | 1 | 1 | 0 | 0 | 1 | 1.0585 | 1.8932 | 15.4781 | 8.0559 | 77.2891 | 138.1561 | 100.7671 | 1.273 | 13.4485 | 100
166499 | THE HAWTHORNS | SOUTH WALES SWITCHGEAR | SJ80509420 | 800 | 6.6 KV | LV | 27 | INDOOR | 27 | 75 | 2 | 1 | 0 | 0 | 0 | 0 | 0.18338 | 0.32269 | 11.299 | 6.5344 | 34.8905 | 38.0264 | 106.9609 | 0.00061889 | 27662.3109 | 0
166588 | MONTON MILL GDN | SOUTH WALES SWITCHGEAR | SJ76319942 | 1000 | 6.6 KV | LV | 25 | INDOOR | 152 | 71 | 13 | 0 | 0 | 0 | 0 | 0 | 0.30959 | 0.57004 | 10.5433 | 6.2278 | 39.5059 | 48.4241 | 108.5866 | 0.00091185 | 18774.9814 | 0
166825 | DEEPDALE CT, NORTHWOLD DR M9 | HACKBRIDGE AND HEWITTIC | SD87850342 | 1000 | 6.6 KV | LV | 21 | OUTDOOR | 167 | 6 | 0 | 0 | 0 | 0 | 0 | 1 | 0.23986 | 0.43809 | 12.5473 | 6.9829 | 25.6199 | 30.938 | 105.2416 | 0.00019525 | 87684.4166 | 0
171440 | CLOUGH RD, DROYLSDEN | LINDLEY THOMPSON | SJ90519893 | 750 | 6.6 KV | LV | 50 | INDOOR | 186 | 15 | 2 | 0 | 0 | 0 | 0 | 0 | 0.33512 | 0.63498 | 16.4706 | 8.4417 | 38.9558 | 49.8079 | 98.9811 | 0.00082508 | 20749.5667 | 0
171459 | LONGDEN RD LEVENSHULME, LONGDEN RD | BABCOCK | SJ87709485 | 800 | 6.6 KV | LV | 22 | OUTDOOR | 148 | 7 | 3 | 0 | 0 | 0 | 0 | 0 | 0.24726 | 0.47378 | 12.7404 | 7.0507 | 25.8264 | 32.0604 | 105.0066 | 0.0001992 | 85942.6714 | 0
171643 | RAMILLIES AVE, CHEADLE HULME | DISTRIBUTION TRANSFORMERS LTD | SJ87848631 | 500 | 11 KV | LV | 42 | INDOOR | 329 | 18 | 10 | 2 | 1 | 0 | 0 | 0 | 0.95932 | 1.7385 | 14.6973 | 7.8119 | 80.1809 | 136.0328 | 101.3934 | 1.1406 | 15.0102 | 100
171832 | HOLLAND ST | EFACEC | SJ91789558 | 750 | 6.6 KV | LV | 2 | INDOOR | 241 | 13 | 8 | 1 | 1 | 1 | 1 | 0 | 0.53015 | 0.91765 | 6.451 | 4.4666 | 50.2282 | 68.7501 | 119.235 | 0.0026175 | 6540.5219 | 0
171852 | WESTBURY AVE 37 SALE, SALE | BONAR LONG | SJ76109039 | 500 | 11 KV | LV | 38 | OUTDOOR | 280 | 9 | 3 | 1 | 0 | 0 | 0 | 0 | 0.73216 | 1.3786 | 18.3653 | 9.0594 | 50.3435 | 87.8423 | 96.9956 | 0.006971 | 2455.8824 | 4.6
171966 | PARKFIELD RD S | BRUSH | SJ84259165 | 500 | 6.6 KV | LV | 33 | INDOOR | 188 | 19 | 12 | 1 | 0 | 0 | 0 | 0 | 0.58209 | 1.0691 | 12.4831 | 6.9904 | 51.8338 | 76.7267 | 104.8706 | 0.0039285 | 4357.8645 | 0
172014 | SCHOOL LN DIDSBURY | PAUWELS | SJ85339100 | 800 | 6.6 KV | LV | 16 | INDOOR | 225 | 64 | 9 | 0 | 0 | 1 | 0 | 0 | 0.49607 | 0.90798 | 8.8939 | 5.5491 | 48.6474 | 68.1027 | 112.2616 | 0.0024423 | 7009.8339 | 0
172242 | CARRGATE RD, DENTON | LINDLEY THOMPSON | SJ93939422 | 500 | 6.6 KV | LV | 53 | INDOOR | 179 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0.45222 | 0.8754 | 17.282 | 8.7157 | 43.0328 | 61.6115 | 98.0482 | 0.0012995 | 13174.7627 | 0
172344 | FAIRFIELD RD 222, REAR 90 SILVERDAL ST | SOUTH WALES SWITCHGEAR | SJ89729760 | 500 | 6.6 KV | LV | 17 | OUTDOOR | 281 | 27 | 7 | 4 | 1 | 0 | 0 | 1 | 0.92259 | 1.617 | 11.0591 | 6.4037 | 66.8438 | 112.6883 | 108.0483 | 0.088806 | 192.7803 | 73.8
172448 | ST WILFREDS ST HULME, OFF ST WILFRED'S S | SOUTH WALES SWITCHGEAR | SJ83189686 | 500 | 6.6 KV | LV | 21 | INDOOR | 306 | 20 | 21 | 4 | 0 | 0 | 0 | 0 | 0.95138 | 1.707 | 9.8032 | 5.9205 | 81.1518 | 134.4217 | 110.2683 | 0.97513 | 17.5566 | 99.2
172508 | BRIARFIELDS,BOUNDARY LN, OPP BONSALL ST, | ABB | SJ84059683 | 800 | 6.6 KV | LV | 20 | OUTDOOR | 223 | 72 | 7 | 0 | 0 | 2 | 0 | 0 | 0.52074 | 0.93605 | 11.8034 | 6.6889 | 38.4423 | 57.6542 | 106.7666 | 0.00073798 | 23198.5111 | 0
172607 | BRITANNIA MILL, HULME HALL RD,HULME | SOUTH WALES SWITCHGEAR | SJ82599721 | 1000 | 6.6 KV | LV | 16 | INDOOR | 0 | 108 | 0 | 3 | 0 | 0 | 0 | 0 | 0.19629 | 0.27764 | 8.464 | 5.3585 | 35.0945 | 36.7171 | 113.4792 | 0.00060016 | 28525.5708 | 0
211326 | BEECH TREES S, OPP 113 (SKELM) | BRENTFORD TRANSFORMERS | SD49540503 | 1000 | 11 KV | LV | 24 | OUTDOOR | 189 | 59 | 1 | 0 | 0 | 0 | 1 | 0 | 0.32971 | 0.60905 | 13.3452 | 7.2778 | 28.7692 | 38.3251 | 104.0179 | 0.00025898 | 66105.5965 | 0
211505 | SMETHURST RD, OPP 2 ORRELL | FERRANTI | SD52630306 | 750 | 11 KV | LV | 50 | OUTDOOR | 326 | 20 | 12 | 3 | 0 | 0 | 0 | 0 | 0.6266 | 1.1487 | 22.5084 | 10.3981 | 44.3679 | 71.973 | 92.6514 | 0.0018811 | 9101.1788 | 0
211944 | JENNET HEY, ADJ 12 ASHTON | ENGLISH ELECTRIC | SD56610065 | 500 | 6.6 KV | LV | 50 | INDOOR | 285 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0.75198 | 1.4125 | 16.478 | 8.4373 | 62.0788 | 102.9633 | 99.0524 | 0.034832 | 491.5021 | 78.2
211948 | PRIORY RD, ADJ 2 ASHTON | BRUSH | SD56940017 | 500 | 6.6 KV | LV | 46 | INDOOR | 289 | 6 | 1 | 1 | 0 | 0 | 0 | 0 | 0.73562 | 1.4017 | 15.6494 | 8.148 | 60.3989 | 100.9273 | 100.1274 | 0.028565 | 599.3395 | 60
212333 | HORNE GR, OPP 18 W/MESNES | BONAR LONG | SD56950441 | 750 | 6.6 KV | LV | 47 | INDOOR | 117 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21037 | 0.41059 | 15.8829 | 8.2341 | 34.5494 | 39.6717 | 99.7679 | 0.00056685 | 30201.9201 | 0
212620 | MOSS LN, ADJ 31 PLATT BRIDGE | ENGLISH ELECTRIC | SD60390324 | 500 | 11 KV | LV | 51 | INDOOR | 321 | 22 | 9 | 3 | 0 | 0 | 0 | 0 | 0.91596 | 1.6846 | 16.5383 | 8.4574 | 75.7066 | 129.2995 | 98.985 | 0.56019 | 30.561 | 100
212649 | ABINGDON DRIVE (ABRAM), OPP 13 ABINGDON | S&C ELECTRIC | SD64140212 | 500 | 11 KV | LV | 42 | OUTDOOR | 349 | 8 | 0 | 1 | 0 | 0 | 0 | 0 | 0.88162 | 1.6708 | 19.6419 | 9.4804 | 60.5308 | 112.5609 | 95.5822 | 0.080702 | 212.138 | 99.8
212806 | CHURCH ST N, CHURCH ST WESTH'TON | ABB | SD65380671 | 500 | 11 KV | LV | 20 | OUTDOOR | 249 | 22 | 18 | 7 | 2 | 1 | 1 | 0 | 1.0058 | 1.6312 | 12.1156 | 6.8165 | 77.4273 | 119.5801 | 106.0431 | 0.19769 | 86.601 | 93.6
212904 | WESTSIDE AVE, OFF WEST END RD | LINDLEY THOMPSON | SJ54089687 | 500 | 11 KV | LV | 49 | OUTDOOR | 167 | 2 | 9 | 1 | 0 | 0 | 0 | 0 | 0.47208 | 0.8772 | 22.4559 | 10.3818 | 35.7671 | 53.0366 | 92.6921 | 0.00052445 | 32643.452 | 0
212944 | PENNY LN, ADJ 223 HAYDOCK | ABB | SJ57449737 | 500 | 11 KV | LV | 13 | INDOOR | 191 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0.48029 | 0.92551 | 8.456 | 5.3584 | 44.6435 | 64.9517 | 113.4149 | 0.0015847 | 10803.5472 | 0
213807 | WOTTON DR, FRONT 19/21 WOTTON D | ABB | SJ58929951 | 500 | 6.6 KV | LV | 20 | OUTDOOR | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.81368 | 1.5458 | 11.9632 | 6.7615 | 55.4013 | 101.2038 | 106.2591 | 0.025218 | 678.888 | 28.4
216118 | BELVEDERE RD, NEWTON LE WILLOWS | ABB | SJ57739573 | 500 | 11 KV | LV | 20 | OUTDOOR | 125 | 6 | 8 | 2 | 0 | 0 | 0 | 0 | 0.38323 | 0.7088 | 12.019 | 6.7776 | 31.5896 | 43.4665 | 106.2444 | 0.0003328 | 51442.7498 | 0
216276 | CROFT ST, LITTLE HULTON | LINDLEY THOMPSON | SD71880410 | 500 | 11 KV | LV | 52 | INDOOR | 228 | 3 | 2 | 1 | 0 | 1 | 0 | 0 | 0.6204 | 1.1441 | 17.0643 | 8.6414 | 53.5099 | 81.6863 | 98.3002 | 0.0054503 | 3141.0944 | 0
216543 | GOWER ST, SWINTON | FERRANTI | SD78380224 | 750 | 11 KV | LV | 50 | INDOOR | 180 | 4 | 14 | 5 | 0 | 0 | 0 | 1 | 0.4233 | 0.72143 | 16.5075 | 8.4414 | 44.3018 | 56.3546 | 99.0821 | 0.0013373 | 12801.8882 | 0
216664 | HUTTON AVE, BOOTHSTOWN | ENGLISH ELECTRIC | SD71720083 | 750 | 11 KV | LV | 51 | INDOOR | 381 | 17 | 1 | 0 | 0 | 0 | 0 | 0 | 0.65237 | 1.2338 | 16.8364 | 8.5656 | 55.8439 | 89.228 | 98.5519 | 0.010243 | 1671.3291 | 1.2
216674 | HULME RD, LEIGH | SOUTH WALES SWITCHGEAR | SD64270060 | 800 | 11 KV | LV | 20 | OUTDOOR | 125 | 0 | 3 | 0 | 1 | 0 | 0 | 0 | 0.22457 | 0.40916 | 12.2404 | 6.8605 | 25.3477 | 29.9644 | 105.8561 | 0.00019175 | 89283.2722 | 0
217117 | LAWSON AVE, WESTLEIGH LANE LEIGH | PARSONS | SD65050220 | 500 | 11 KV | LV | 37 | OUTDOOR | 185 | 12 | 1 | 1 | 0 | 0 | 0 | 0 | 0.49634 | 0.9416 | 18.2854 | 9.0305 | 36.1903 | 56.0613 | 97.1103 | 0.00059032 | 29001.19 | 0
217521 | WESTWOOD METHS, BOLTON ROAD SWINTON | DENIS FERRANTI | SD79450076 | 500 | 11 KV | LV | 52 | OUTDOOR | 170 | 9 | 6 | 1 | 0 | 0 | 0 | 0 | 0.48005 | 0.89878 | 23.0591 | 10.5743 | 35.8193 | 53.9165 | 92.0888 | 0.00054256 | 31553.8957 | 0
218214 | BLACKBERRY DR | ABB | SD61500399 | 500 | 11 KV | LV | 12 | OUTDOOR | 207 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.51487 | 0.98248 | 9.4302 | 5.7422 | 37.0337 | 58.4646 | 111.5717 | 0.00067258 | 25454.3619 | 0
231594 | MIDDLEBROOK HOUSING, MIDDLEBROOK LOSTOCK | SOUTH WALES SWITCHGEAR | SD64771013 | 500 | 11 KV | LV | 16 | INDOOR | 277 | 0 | 2 | 3 | 0 | 0 | 0 | 0 | 0.71516 | 1.3424 | 9.0853 | 5.6223 | 59.3976 | 96.6861 | 111.9454 | 0.019346 | 884.9194 | 0.4
231670 | LITTLE OAKS | EFACEC | SD73021210 | 500 | 11 KV | LV | 2 | OUTDOOR | 101 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26657 | 0.52027 | 7.2559 | 4.8079 | 26.3463 | 33.6296 | 117.2551 | 0.00020726 | 82603.0179 | 0
232046 | DOROTHY ST, RAMSBOTTOM | ABB | SD78731612 | 500 | 11 KV | LV | 14 | OUTDOOR | 291 | 11 | 13 | 1 | 0 | 0 | 0 | 0 | 0.81954 | 1.5117 | 10.0837 | 5.9916 | 57.8228 | 100.794 | 110.4691 | 0.024977 | 685.4264 | 14.8
232164 | DORIS MILL, ADJ 90 BURY N RD HEY | SOUTH WALES SWITCHGEAR | SD84201080 | 500 | 6.6 KV | LV | 18 | OUTDOOR | 363 | 16 | 13 | 1 | 0 | 0 | 2 | 1 | 1.157 | 2.0041 | 11.6665 | 6.6371 | 87.9 | 152.2044 | 106.9588 | 6.4432 | 2.6571 | 100
232373 | THATCHLEACH LN W, WHITEFIELD | BRUCE PEEBLES | SD81070514 | 750 | 11 KV | LV | 51 | OUTDOOR | 310 | 37 | 19 | 3 | 1 | 0 | 0 | 0 | 0.67988 | 1.2114 | 22.8113 | 10.4913 | 48.9595 | 78.0073 | 92.3577 | 0.0032991 | 5189.2451 | 0
232384 | WINGATE DR, WHITEFIELD | LINDLEY THOMPSON | SD80060637 | 500 | 11 KV | LV | 57 | INDOOR | 205 | 9 | 3 | 1 | 0 | 1 | 0 | 0 | 0.58459 | 1.0771 | 17.9927 | 8.9601 | 51.417 | 76.7336 | 97.1668 | 0.0037744 | 4535.7763 | 0
232432 | BOOTH RD, OPP 30 BOOTH RD | CROMPTON PARKINSON | SD75960696 | 500 | 11 KV | LV | 53 | INDOOR | 250 | 29 | 5 | 1 | 1 | 0 | 0 | 0 | 0.75664 | 1.3796 | 17.2193 | 8.6971 | 63.2602 | 101.5279 | 98.0821 | 0.033009 | 518.6527 | 76.2
232488 | LONGTON ST, BURY RR 660 MCR RD | BABCOCK | SD80630794 | 500 | 11 KV | LV | 21 | INDOOR | 212 | 7 | 4 | 0 | 1 | 1 | 1 | 0 | 0.67662 | 1.1808 | 9.9357 | 5.9819 | 58.7641 | 86.3827 | 109.8598 | 0.0089896 | 1904.4282 | 0
232553 | MARKET ST BURY, BURY | ABB | SD80740983 | 800 | 6.6 KV | LV | 13 | OUTDOOR | 149 | 3 | 6 | 1 | 1 | 0 | 0 | 0 | 0.28195 | 0.50589 | 9.8816 | 5.9203 | 27.3754 | 33.9996 | 110.731 | 0.00022619 | 75688.5161 | 0
232576 | ABINGDON CL, ADJ 1 ABINGDON CLOSE | ENGLISH ELECTRIC | SD80730688 | 500 | 11 KV | LV | 50 | INDOOR | 231 | 8 | 1 | 1 | 0 | 0 | 0 | 0 | 0.59885 | 1.1376 | 16.6356 | 8.4939 | 51.4237 | 80.1125 | 98.8286 | 0.0045738 | 3743.0654 | 0
310448 | HALFWAY HS, REAR OF PUB ROYTON | FERRANTI | SD91380886 | 750 | 6.6 KV | LV | 56 | INDOOR | 142 | 5 | 1 | 1 | 0 | 0 | 0 | 0 | 0.24931 | 0.47692 | 17.9191 | 8.9308 | 35.8028 | 42.4034 | 97.3003 | 0.00062334 | 27464.8707 | 0
310534 | WHITEGATE AVE, CHADDERTON | SOUTH WALES SWITCHGEAR | SD89910378 | 800 | 6.6 KV | LV | 17 | OUTDOOR | 370 | 10 | 4 | 0 | 0 | 0 | 0 | 0 | 0.5944 | 1.1173 | 11.188 | 6.4643 | 41.5575 | 68.4666 | 107.6259 | 0.0013507 | 12674.8367 | 0
311103 | MIDDLEGATE, RR 43 MIDGATE HOLINS | BRUSH | SD92260271 | 500 | 6.6 KV | LV | 32 | OUTDOOR | 255 | 7 | 0 | 1 | 0 | 0 | 0 | 0 | 0.64946 | 1.2348 | 15.7441 | 8.1539 | 44.7014 | 76.244 | 100.3152 | 0.0024728 | 6923.3505 | 0
312270 | HOLLY ST, MALHAM CLOSE ROYTON | DENIS FERRANTI | SD91720797 | 750 | 6.6 KV | LV | 50 | INDOOR | 321 | 17 | 4 | 2 | 0 | 0 | 0 | 0 | 0.57783 | 1.0857 | 16.4597 | 8.4339 | 51.5907 | 78.2557 | 99.0442 | 0.0042641 | 4014.9362 | 0
312895 | MERTON AVE, ADJ HERON MILL O/HAM | FERRANTI | SD91740307 | 750 | 6.6 KV | LV | 50 | OUTDOOR | 332 | 20 | 4 | 0 | 1 | 0 | 0 | 0 | 0.61342 | 1.1363 | 22.5375 | 10.4064 | 43.0941 | 70.3821 | 92.6284 | 0.0015886 | 10776.5565 | 0
313307 | GREENSIDE AVE, OFF HAVEN LN OLDHAM | FERRANTI | SD95050697 | 500 | 6.6 KV | LV | 48 | INDOOR | 232 | 5 | 6 | 2 | 1 | 0 | 0 | 0 | 0.66794 | 1.2116 | 16.2186 | 8.3499 | 57.3246 | 87.7284 | 99.3487 | 0.009395 | 1822.2481 | 0.2
314107 | KIRKLAND YARNS, OFF JOWETT ST OLDHAM | SOUTH WALES SWITCHGEAR | SD94430650 | 800 | 6.6 KV | LV | 44 | INDOOR | 184 | 6 | 3 | 2 | 0 | 0 | 0 | 0 | 0.31203 | 0.587 | 15.0483 | 7.9381 | 39.2858 | 48.6718 | 100.8933 | 0.00087027 | 19671.9555 | 0
314325 | BELLSHILL CRES, ROCHDALE | PAUWELS | SD91261409 | 500 | 6.6 KV | LV | 16 | OUTDOOR | 311 | 1 | 5 | 1 | 0 | 0 | 0 | 0 | 0.79924 | 1.4955 | 10.7611 | 6.2749 | 55.1833 | 98.0072 | 108.819 | 0.018534 | 923.7225 | 10
314378 | CROFTHEAD | EFACEC | SD93521716 | 750 | 6.6 KV | LV | 1 | INDOOR | 292 | 4 | 1 | 1 | 0 | 0 | 0 | 0 | 0.49201 | 0.9299 | 6.1254 | 4.3081 | 46.3822 | 67.1906 | 120.4829 | 0.0019664 | 8706.2888 | 0
314400 | DURN | SCHNEIDER ELECTRIC | SD94211644 | 750 | 6.6 KV | LV | 1 | INDOOR | 241 | 5 | 8 | 2 | 0 | 0 | 0 | 0 | 0.44255 | 0.81716 | 6.2692 | 4.3674 | 44.3328 | 60.7139 | 120.199 | 0.0014358 | 11923.9282 | 0
314436 | HAUGH LANE, HAUGH LN NEWHEY | ABB | SD94121170 | 500 | 6.6 KV | LV | 20 | OUTDOOR | 311 | 12 | 2 | 2 | 0 | 0 | 0 | 0 | 0.81884 | 1.5379 | 11.9817 | 6.758 | 56.3726 | 101.4664 | 106.423 | 0.025477 | 671.9903 | 29.4
314606 | DUNLOP AVE, QUEENSWAY RDALE | ENGLISH ELECTRIC | SD89331143 | 750 | 6.6 KV | LV | 54 | OUTDOOR | 129 | 17 | 6 | 1 | 0 | 0 | 0 | 0 | 0.26643 | 0.49493 | 24.0061 | 10.8616 | 26.6297 | 33.2237 | 91.2245 | 0.00021393 | 80027.6317 | 0
314974 | NORDEN RD, BAMFORD | LINDLEY THOMPSON | SD86311311 | 750 | 6.6 KV | LV | 50 | INDOOR | 186 | 9 | 12 | 5 | 0 | 0 | 0 | 0 | 0.39378 | 0.70355 | 16.3751 | 8.4047 | 42.4754 | 54.6641 | 99.1453 | 0.0011398 | 15020.1208 | 0
320939 | FLEET ST | EFACEC | SJ95229533 | 500 | 6.6 KV | LV | 2 | OUTDOOR | 192 | 9 | 2 | 0 | 0 | 0 | 0 | 0 | 0.50251 | 0.95312 | 7.0989 | 4.7316 | 36.483 | 56.8794 | 117.8796 | 0.00061462 | 27854.7298 | 0
322939 | KINGS RD, OLD PEOPLES HOST AUL | FERRANTI | SD95090040 | 750 | 6.6 KV | LV | 51 | INDOOR | 274 | 10 | 4 | 0 | 1 | 0 | 0 | 0 | 0.50245 | 0.92954 | 16.9532 | 8.6044 | 47.4429 | 67.8007 | 98.4366 | 0.0021201 | 8075.1439 | 0
323779 | CALVER MEWS, CAR PARK GAMESLEY | SOUTH WALES SWITCHGEAR | SK01029484 | 1000 | 11 KV | LV | 26 | OUTDOOR | 100 | 75 | 2 | 0 | 0 | 0 | 0 | 0 | 0.22045 | 0.42087 | 13.8889 | 7.4849 | 25.0359 | 30.176 | 103.0525 | 0.0001915 | 89398.0209 | 0
326139 | WILTSHIRE DR, GLOSSOP | HAWKER SIDDELEY | SK04259335 | 500 | 11 KV | LV | 18 | OUTDOOR | 278 | 16 | 0 | 0 | 1 | 0 | 0 | 0 | 0.75606 | 1.4095 | 11.361 | 6.5143 | 52.1222 | 90.6152 | 107.6104 | 0.0092241 | 1856.0011 | 0.8
327085 | OLDHAM ATHLETIC, SHEEPFOOT LN OLDHAM | FERRANTI | SD91500646 | 750 | 6.6 KV | LV | 23 | OUTDOOR | 134 | 7 | 2 | 0 | 0 | 0 | 0 | 0 | 0.23723 | 0.45221 | 10.3288 | 6.1404 | 35.4107 | 41.4138 | 109.0269 | 0.00060546 | 28275.9097 | 0
327098 | E WHITTAKER, OLDHAM | SOUTH WALES SWITCHGEAR | SD92160607 | 500 | 6.6 KV | LV | 26 | OUTDOOR | 114 | 1 | 4 | 1 | 0 | 0 | 0 | 0 | 0.31232 | 0.59427 | 14.0679 | 7.5627 | 28.2529 | 37.1873 | 102.5875 | 0.00024408 | 70139.7157 | 0
327479 | ARMITAGE CL, OFF HERON ST | ABB | SD91320350 | 500 | 6.6 KV | LV | 22 | OUTDOOR | 305 | 48 | 19 | 4 | 0 | 3 | 0 | 0 | 1.1196 | 1.9302 | 12.7472 | 7.0558 | 86.8187 | 146.8593 | 104.9453 | 3.5305 | 4.8492 | 100
330093 | BIRKETT AND BOSTOCK, HR HILLGATE STOCKPR | FERRANTI | SJ89968953 | 750 | 6.6 KV | LV | 51 | INDOOR | 100 | 0 | 2 | 1 | 1 | 0 | 0 | 1 | 0.23945 | 0.4 | 16.7995 | 8.5498 | 35.9474 | 40.1391 | 98.633 | 0.00063279 | 27054.8407 | 0
330180 | HEMPSHAW LN OFFERTON STOCKPORT | ABB | SJ90788941 | 500 | 6.6 KV | LV | 13 | OUTDOOR | 220 | 5 | 10 | 4 | 0 | 1 | 0 | 0 | 0.67813 | 1.2037 | 9.815 | 5.8957 | 48.9603 | 77.1148 | 110.799 | 0.0030361 | 5638.7343 | 0
330222 | NORRIS BANK, HEATON NORRIS | ABB | SJ87839059 | 800 | 6.6 KV | LV | 21 | OUTDOOR | 347 | 3 | 1 | 1 | 0 | 0 | 0 | 0 | 0.54371 | 1.0276 | 12.5835 | 6.9951 | 38.5913 | 62.0751 | 105.2203 | 0.00083887 | 20408.4143 | 0
330225 | OSBORNE ST, BREDBURY | SOUTH WALES SWITCHGEAR | SJ91469112 | 800 | 11 KV | LV | 15 | INDOOR | 228 | 35 | 10 | 2 | 0 | 0 | 0 | 0 | 0.44834 | 0.82889 | 8.6184 | 5.4217 | 45.9091 | 62.7864 | 113.1568 | 0.0017541 | 9760.1019 | 0
330276 | TATTON RD, HEATON MOOR | FERRANTI | SJ88179210 | 1000 | 6.6 KV | LV | 50 | INDOOR | 250 | 62 | 17 | 10 | 0 | 1 | 0 | 0 | 0.49553 | 0.85894 | 16.3541 | 8.4018 | 49.5 | 66.4655 | 99.1242 | 0.0024708 | 6929.0497 | 0
330300 | WOODLANDS DR, OFFERTON | ABB | SJ91658969 | 500 | 6.6 KV | LV | 15 | INDOOR | 273 | 15 | 2 | 0 | 0 | 0 | 0 | 0 | 0.71527 | 1.3536 | 8.6788 | 5.4508 | 58.9887 | 97.0798 | 112.926 | 0.020343 | 841.5485 | 0.6
330305 | YORK ST STOCKPORT | ABB | SJ89108971 | 1000 | 6.6 KV | LV | 12 | OUTDOOR | 212 | 8 | 11 | 0 | 0 | 0 | 1 | 0 | 0.32254 | 0.57799 | 9.2272 | 5.6547 | 28.8553 | 37.3407 | 112.1303 | 0.00025647 | 66751.4136 | 0
331769 | HULLEY RD, MACCLESFIELD | SOUTH WALES SWITCHGEAR | SJ92737461 | 500 | 11 KV | LV | 18 | OUTDOOR | 331 | 54 | 6 | 4 | 0 | 0 | 0 | 0 | 1.0119 | 1.8745 | 11.5695 | 6.608 | 72.3684 | 133.9507 | 107.02 | 0.80203 | 21.3457 | 99
331890 | GRANGE RD, BRAMHALL | YORKSHIRE ELECTRICAL TRANSFORMERS | SJ89728707 | 500 | 11 KV | LV | 48 | INDOOR | 169 | 14 | 3 | 0 | 0 | 0 | 0 | 0 | 0.46423 | 0.88603 | 16.0877 | 8.3021 | 43.9311 | 62.7299 | 99.5489 | 0.0014215 | 12043.7545 | 0
331994 | POWNALL FM, STYAL | LINDLEY THOMPSON | SJ84018349 | 500 | 11 KV | LV | 49 | INDOOR | 91 | 12 | 8 | 1 | 0 | 0 | 1 | 0 | 0.35631 | 0.61126 | 16.3665 | 8.4015 | 39.7206 | 48.6247 | 99.1637 | 0.00084244 | 20321.8852 | 0
331997 | QUEENS AVE, MACCLESFIELD | TRANSFORMERS (WALES) | SJ92197455 | 800 | 11 KV | LV | 18 | INDOOR | 144 | 14 | 7 | 1 | 3 | 3 | 0 | 0 | 0.42656 | 0.64673 | 9.1809 | 5.6695 | 46.4724 | 54.9182 | 111.5613 | 0.0016003 | 10697.6893 | 0
332456 | PARKGATE WAY, SPATH LNG6 HANDFORTH | LINDLEY THOMPSON | SJ85948362 | 500 | 11 KV | LV | 51 | INDOOR | 119 | 11 | 3 | 0 | 0 | 0 | 0 | 0 | 0.33464 | 0.64154 | 16.6102 | 8.4825 | 37.9341 | 48.7245 | 98.8915 | 0.00073486 | 23296.8853 | 0
332587 | REDHOUSE LN, DISLEY | UNIDAIRE LTD | SJ98048467 | 500 | 11 KV | LV | 22 | OUTDOOR | 113 | 10 | 4 | 1 | 0 | 0 | 0 | 0 | 0.33213 | 0.6211 | 12.6612 | 7.0219 | 29.012 | 38.6602 | 105.1343 | 0.00026168 | 65422.9319 | 0
332821 | CHESTER WALKS, BREDBURY | CROMPTON PARKINSON | SJ93329018 | 500 | 11 KV | LV | 51 | INDOOR | 210 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0.53291 | 1.0233 | 16.7908 | 8.544 | 47.3238 | 71.4615 | 98.6758 | 0.0023762 | 7204.7577 | 0
332876 | LADYBROOK RD, BRAMHALL | PAUWELS | SJ88338631 | 750 | 11 KV | LV | 16 | OUTDOOR | 137 | 8 | 5 | 2 | 0 | 0 | 0 | 0 | 0.26697 | 0.49987 | 11.0793 | 6.4059 | 26.6464 | 33.3379 | 108.132 | 0.00021343 | 80212.6473 | 0
333103 | QUEENS RD FLATS, WILMSLOW | ABB | SJ84268087 | 500 | 11 KV | LV | 13 | INDOOR | 136 | 24 | 8 | 1 | 0 | 2 | 0 | 2 | 0.63792 | 1.0153 | 8.0606 | 5.1877 | 57.325 | 76.6135 | 114.4855 | 0.0053738 | 3185.7999 | 0
333883 | HIGHFIELD AVE, BREDBURY | SOUTH WALES SWITCHGEAR | SJ92879085 | 750 | 11 KV | LV | 45 | INDOOR | 191 | 6 | 1 | 0 | 0 | 1 | 0 | 0 | 0.34852 | 0.64677 | 15.4714 | 8.0892 | 39.7234 | 50.6569 | 100.3105 | 0.0008801 | 19452.4294 | 0
333962 | DIXON DRIVE 29, CHELFORD | SOUTH WALES SWITCHGEAR | SJ81377512 | 1000 | 11 KV | LV | 26 | INDOOR | 130 | 61 | 7 | 5 | 0 | 0 | 0 | 0 | 0.27636 | 0.50104 | 10.8367 | 6.3451 | 38.2161 | 45.2412 | 107.9861 | 0.0008103 | 21128.0524 | 0
334173 | ALDERWOOD AVE, HEATON MERSEY | BRUSH | SJ87059030 | 500 | 6.6 KV | LV | 33 | INDOOR | 318 | 17 | 1 | 0 | 0 | 0 | 0 | 0 | 0.82461 | 1.5569 | 12.4016 | 6.9573 | 66.7448 | 115.0607 | 105.0408 | 0.1251 | 136.8464 | 92.4
334195 | CORBAR RD(STOCKPORT), STOCKPORT | DENIS FERRANTI | SJ90568835 | 750 | 6.6 KV | LV | 49 | OUTDOOR | 40 | 85 | 2 | 0 | 0 | 1 | 0 | 0 | 0.23743 | 0.43158 | 21.9614 | 10.2202 | 25.7342 | 30.8114 | 93.2272 | 0.00020765 | 82445.494 | 0
336478 | LOWER BENTS LN, BREDBURY | BRUSH | SJ92599166 | 500 | 11 KV | LV | 29 | OUTDOOR | 217 | 15 | 10 | 3 | 0 | 0 | 0 | 0 | 0.65009 | 1.1917 | 15.3122 | 7.9985 | 46.2768 | 74.9528 | 100.9687 | 0.0024053 | 7117.7312 | 0
336998 | ST GEORGES ST, MACCLESFIELD | SOUTH WALES SWITCHGEAR | SJ91857303 | 500 | 11 KV | LV | 26 | OUTDOOR | 81 | 31 | 6 | 1 | 1 | 0 | 0 | 0 | 0.35653 | 0.62935 | 14.0877 | 7.5574 | 30.6477 | 39.869 | 102.7442 | 0.00030652 | 55853.0796 | 0
337081 | DORCHESTER WAY, DORCHESTER WAY,MACC | HAWKER SIDDELEY | SJ91097579 | 500 | 11 KV | LV | 25 | OUTDOOR | 230 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0.57497 | 1.0957 | 13.7802 | 7.4467 | 40.2884 | 66.0736 | 103.195 | 0.0011152 | 15351.3957 | 0
337724 | DIDSBURY ROAD, OPP 218 | ABB | SJ87409070 | 500 | 6.6 KV | LV | 20 | OUTDOOR | 228 | 16 | 1 | 1 | 0 | 0 | 0 | 0 | 0.6113 | 1.1607 | 11.894 | 6.7242 | 42.537 | 70.7556 | 106.5657 | 0.0016046 | 10669.2391 | 0
410398 | ROBINSON ST, PRESTON | SOUTH WALES SWITCHGEAR | SD52913133 | 500 | 6.6 KV | LV | 25 | OUTDOOR | 229 | 17 | 15 | 3 | 0 | 0 | 1 | 0 | 0.76181 | 1.3341 | 13.5103 | 7.348 | 54.9692 | 88.0503 | 103.6014 | 0.0080053 | 2138.5719 | 0
410460 | CEMETERY (PRESTON), PRESTON | ABB | SD56333023 | 500 | 6.6 KV | LV | 16 | INDOOR | 278 | 7 | 22 | 4 | 0 | 0 | 1 | 0 | 0.9086 | 1.5729 | 8.7306 | 5.4836 | 78.1699 | 122.8361 | 112.5794 | 0.29789 | 57.4714 | 91.2
410579 | HARBOUR LN (WARTON), WARTON | BABCOCK | SD41292865 | 800 | 6.6 KV | LV | 22 | INDOOR | 343 | 14 | 13 | 5 | 1 | 0 | 1 | 0 | 0.67105 | 1.1773 | 10.3296 | 6.147 | 60.7256 | 89.6165 | 108.9202 | 0.012524 | 1366.9825 | 0
410611 | WATERLOO RD, PRESTON | BONAR LONG | SD51793064 | 500 | 6.6 KV | LV | 55 | INDOOR | 193 | 24 | 10 | 4 | 0 | 0 | 0 | 0 | 0.62277 | 1.1353 | 17.5255 | 8.8001 | 54.5861 | 81.9653 | 97.7365 | 0.0057791 | 2962.4046 | 0
410842 | BROWNING RD, PRESTON | BABCOCK | SD55633065 | 500 | 6.6 KV | LV | 22 | OUTDOOR | 126 | 5 | 7 | 1 | 0 | 0 | 0 | 0 | 0.3682 | 0.68246 | 12.6795 | 7.0337 | 30.7447 | 41.9898 | 105.0011 | 0.0003063 | 55893.7198 | 0
414508 | JUNCTION LN, BURSCOUGH | FERRANTI | SD44401155 | 750 | 11 KV | LV | 52 | INDOOR | 102 | 8 | 3 | 1 | 0 | 0 | 0 | 0 | 0.1965 | 0.37376 | 17.041 | 8.6337 | 34.2925 | 38.5269 | 98.3342 | 0.00055714 | 30728.5071 | 0
414539 | HENNEL LN SW HS, WALTON LE DALE | BONAR LONG | SD54752702 | 500 | 11 KV | LV | 29 | OUTDOOR | 180 | 7 | 3 | 0 | 0 | 0 | 0 | 0 | 0.4738 | 0.89939 | 14.7399 | 7.7988 | 35.1147 | 53.5288 | 101.696 | 0.00050686 | 33776.5167 | 0
414613 | BALCARRES RD, LEYLAND | ABB | SD54242163 | 500 | 11 KV | LV | 14 | INDOOR | 181 | 5 | 9 | 4 | 0 | 0 | 0 | 1 | 0.59834 | 1.0458 | 8.4753 | 5.3714 | 53.446 | 76.3347 | 113.2595 | 0.0041115 | 4163.9388 | 0
414615 | MOSSY LEA, WRIGHTINGTON | ABB | SD53651254 | 500 | 11 KV | LV | 14 | OUTDOOR | 174 | 5 | 4 | 0 | 1 | 1 | 0 | 0 | 0.53266 | 0.95254 | 10.3845 | 6.1258 | 39.4881 | 58.4376 | 109.6147 | 0.00077404 | 22117.6538 | 0
414674 | COW MOSS | EFACEC | SD56501397 | 500 | 11 KV | LV | 1 | INDOOR | 261 | 14 | 3 | 0 | 0 | 0 | 1 | 0 | 0.73519 | 1.3538 | 6.2175 | 4.3455 | 61.0861 | 98.5301 | 120.3291 | 0.023577 | 726.1365 | 0.2
414844 | ROAD SPRINGS, LEYLAND | PAUWELS | SD52302184 | 500 | 11 KV | LV | 14 | OUTDOOR | 139 | 7 | 3 | 5 | 0 | 0 | 0 | 0 | 0.41897 | 0.76925 | 10.2557 | 6.0763 | 33.0246 | 46.6411 | 109.8078 | 0.00038482 | 44487.7927 | 0
415028 | CLOVER RD, CHORLEY | FERRANTI | SD57121619 | 500 | 11 KV | LV | 49 | INDOOR | 117 | 7 | 6 | 1 | 0 | 2 | 0 | 0 | 0.4231 | 0.71948 | 16.1392 | 8.3202 | 43.2046 | 54.8781 | 99.4786 | 0.001179 | 14520.4098 | 0
415087 | ALDERBROOK DR, PARBOLD | LINDLEY THOMPSON | SD49231083 | 500 | 11 KV | LV | 51 | INDOOR | 119 | 5 | 8 | 2 | 0 | 0 | 0 | 0 | 0.36648 | 0.67116 | 16.3763 | 8.4044 | 39.9398 | 51.0633 | 99.1502 | 0.00087266 | 19618.2281 | 0
415293 | BLACKGATE LN, TARLETON | SOUTH WALES SWITCHGEAR | SD44892033 | 500 | 11 KV | LV | 27 | INDOOR | 112 | 44 | 7 | 4 | 0 | 0 | 0 | 0 | 0.4577 | 0.83645 | 11.1462 | 6.4671 | 44.5894 | 60.8872 | 107.3773 | 0.0014699 | 11646.9084 | 0
415504 | CLAUGHTON AVE, CLAYTON-LE-WOODS | PARSONS | SD56342239 | 500 | 11 KV | LV | 31 | INDOOR | 366 | 23 | 2 | 0 | 0 | 0 | 0 | 0 | 0.96229 | 1.8218 | 12.1771 | 6.8735 | 77.8453 | 140.1113 | 105.3977 | 1.698 | 10.0822 | 100
415540 | WYRESDALE DR | ABB | SD54732098 | 500 | 11 KV | LV | 12 | INDOOR | 228 | 7 | 1 | 0 | 0 | 0 | 0 | 0 | 0.57998 | 1.1047 | 7.9254 | 5.117 | 50.1506 | 77.5721 | 115.1017 | 0.0037073 | 4617.876 | 0
417073 | RIPON ST, RIPON STREET PRESTON | BRUSH | SD53403071 | 800 | 6.6 KV | LV | 29 | OUTDOOR | 138 | 9 | 3 | 0 | 0 | 0 | 0 | 0 | 0.23507 | 0.45278 | 15.2287 | 7.9766 | 25.4598 | 31.2896 | 100.9882 | 0.00019369 | 88386.9001 | 0
418214 | BRITANNIA DR, PRESTON | SOUTH WALES SWITCHGEAR | SD51712948 | 800 | 6.6 KV | LV | 17 | OUTDOOR | 42 | 177 | 1 | 6 | 0 | 0 | 0 | 0 | 0.43109 | 0.69291 | 11.1724 | 6.4537 | 32.5918 | 42.7618 | 107.7148 | 0.00035947 | 47626.0762 | 0
423267 | QUEENS PK EST, ST ANNES | PARSONS | SD33852875 | 500 | 6.6 KV | LV | 35 | INDOOR | 222 | 18 | 4 | 0 | 0 | 0 | 0 | 0 | 0.60918 | 1.1556 | 13.055 | 7.212 | 52.2949 | 81.5982 | 103.8262 | 0.005282 | 3241.1682 | 0
423313 | SOUTH HEY, ST ANNES | BONAR LONG | SD34502860 | 750 | 6.6 KV | LV | 47 | INDOOR | 238 | 108 | 0 | 4 | 0 | 0 | 0 | 0 | 0.58992 | 1.1065 | 15.9728 | 8.2634 | 52.3726 | 80.0187 | 99.6761 | 0.0049925 | 3429.1397 | 0
423928 | HOLYOAKE AVE, OPP NO1 HOLYOAKE | PARSONS | SD32323837 | 500 | 6.6 KV | LV | 35 | OUTDOOR | 101 | 7 | 4 | 2 | 2 | 0 | 0 | 0 | 0.38366 | 0.6464 | 17.4739 | 8.7531 | 32.1949 | 41.2849 | 98.1131 | 0.00034188 | 50075.929 | 0
427236 | HERITAGE WAY | BABCOCK | SD32704224 | 800 | 6.6 KV | LV | 22 | OUTDOOR | 121 | 48 | 2 | 0 | 0 | 0 | 0 | 0 | 0.26591 | 0.50712 | 12.4587 | 6.9427 | 26.4183 | 33.5347 | 105.5358 | 0.00021228 | 80648.0064 | 0
428275 | KINGSWAY, OLD FLATS ENTRANCE | PAUWELS | SD31304270 | 800 | 6.6 KV | LV | 16 | INDOOR | 57 | 68 | 2 | 3 | 0 | 0 | 0 | 0 | 0.21609 | 0.40269 | 8.704 | 5.4656 | 36.0297 | 40.8545 | 112.7859 | 0.00068447 | 25012.0814 | 0
429617 | PEACE PL, GAMBLE RD THORNTON | ABB | SD33464390 | 800 | 11 KV | LV | 15 | INDOOR | 334 | 13 | 6 | 0 | 1 | 0 | 1 | 0 | 0.60311 | 1.0864 | 8.6664 | 5.448 | 55.0182 | 81.0973 | 112.9056 | 0.005882 | 2910.594 | 0
429948 | LITTLE POULTON GDNS | ABB | SD35703910 | 500 | 6.6 KV | LV | 12 | INDOOR | 48 | 76 | 6 | 0 | 0 | 0 | 0 | 0 | 0.33854 | 0.63858 | 8.0661 | 5.1854 | 38.4539 | 49.0388 | 114.5568 | 0.00082613 | 20723.085 | 0
450050 | STANSFELD ST, BLACKBURN BB18 I | BRUSH | SD67422706 | 800 | 6.6 KV | LV | 31 | OUTDOOR | 120 | 4 | 7 | 1 | 1 | 0 | 0 | 0 | 0.24394 | 0.43175 | 15.7424 | 8.148 | 26.1256 | 31.0271 | 100.3963 | 0.0002047 | 83635.9478 | 0
450074 | GUIDE, CARPARK OF ENSOR | SOUTH WALES SWITCHGEAR | SD70562579 | 500 | 6.6 KV | LV | 19 | OUTDOOR | 108 | 2 | 3 | 0 | 0 | 0 | 0 | 0 | 0.28551 | 0.55103 | 11.7888 | 6.6972 | 27.1345 | 35.1223 | 106.5367 | 0.00022207 | 77094.4818 | 0
450105 | WILWORTH CRES, PLECKGATE Z4 0 | ABB | SD68043043 | 500 | 6.6 KV | LV | 15 | OUTDOOR | 89 | 4 | 6 | 0 | 0 | 1 | 0 | 1 | 0.35771 | 0.58689 | 10.215 | 6.0709 | 30.8687 | 38.416 | 109.6879 | 0.0003045 | 56222.8788 | 0
450183 | OAK HILL, ACCRINGTON R22 I | SOUTH WALES SWITCHGEAR | SD76642772 | 500 | 6.6 KV | LV | 24 | INDOOR | 190 | 12 | 7 | 0 | 0 | 0 | 0 | 0 | 0.53282 | 0.99701 | 10.3684 | 6.1544 | 48.0643 | 70.7741 | 108.9947 | 0.0024029 | 7124.6892 | 0
450388 | HASTON LEE MILL, BLACKBURN AA6 I | ABB | SD68643057 | 500 | 6.6 KV | LV | 17 | INDOOR | 178 | 2 | 12 | 2 | 0 | 0 | 0 | 0 | 0.52544 | 0.95919 | 9.0727 | 5.6253 | 48.565 | 69.2467 | 111.8079 | 0.0023492 | 7287.6954 | 0
450584 | BLACKBURN RD (OSW), OSWALDTWISTLE L17 I | BABCOCK | SD73032830 | 800 | 6.6 KV | LV | 21 | INDOOR | 154 | 12 | 8 | 1 | 0 | 0 | 0 | 0 | 0.28718 | 0.53554 | 10.1905 | 6.0781 | 38.5361 | 46.5208 | 109.453 | 0.00081812 | 20925.9136 | 0
450784 | BROADFIELD, ACCRINGTON Q21 I | LINDLEY THOMPSON | SD75502727 | 500 | 6.6 KV | LV | 48 | INDOOR | 149 | 29 | 2 | 0 | 0 | 0 | 0 | 0 | 0.44689 | 0.85454 | 15.9909 | 8.2733 | 42.9923 | 60.6782 | 99.6074 | 0.0012798 | 13376.7239 | 0
451828 | BRANTWOOD | ABB | SD74233092 | 500 | 6.6 KV | LV | 14 | OUTDOOR | 176 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.435 | 0.83396 | 10.0914 | 6.0176 | 32.9947 | 49.3586 | 110.0413 | 0.00039751 | 43068.258 | 0
451866 | MILNSHAW GDNS | SOUTH WALES SWITCHGEAR | SD75472905 | 800 | 6.6 KV | LV | 25 | OUTDOOR | 41 | 57 | 5 | 0 | 0 | 0 | 0 | 0 | 0.16806 | 0.31522 | 14.232 | 7.6162 | 23.784 | 26.7934 | 102.4334 | 0.00017438 | 98176.3499 | 0
453049 | FOREST MILL, LUMB A18 I | SOUTH WALES SWITCHGEAR | SD84072561 | 500 | 6.6 KV | LV | 17 | INDOOR | 175 | 8 | 4 | 1 | 0 | 0 | 0 | 0 | 0.47868 | 0.9067 | 9.0046 | 5.5896 | 44.8833 | 64.3374 | 112.0952 | 0.0015878 | 10781.9647 | 0
455007 | WADDINGTON, WADDINGTON C2 I6 | CROMPTON PARKINSON | SD72864394 | 500 | 11 KV | LV | 53 | OUTDOOR | 133 | 20 | 9 | 4 | 0 | 1 | 0 | 0 | 0.50054 | 0.87273 | 23.4497 | 10.6852 | 38.1253 | 54.1511 | 91.7868 | 0.00064716 | 26454.0364 | 0
458190 | GRETNA, BURNLEY B3 B3 | FERRANTI | SD82693146 | 750 | 6.6 KV | LV | 53 | OUTDOOR | 220 | 5 | 3 | 1 | 0 | 0 | 0 | 0 | 0.38378 | 0.72811 | 23.2196 | 10.6208 | 30.927 | 43.9929 | 91.9603 | 0.00031551 | 54260.9453 | 0
458556 | GERTRUDE ST, NELSON N1 F14 | LINDLEY THOMPSON | SD87023875 | 500 | 6.6 KV | LV | 55 | INDOOR | 317 | 34 | 15 | 0 | 1 | 0 | 1 | 0 | 1.0254 | 1.8131 | 17.5459 | 8.8031 | 87.4747 | 145.5894 | 97.7486 | 3.4099 | 5.0207 | 100
458558 | OXFORD RD | ALSTOM | SD87253869 | 500 | 6.6 KV | LV | 11 | INDOOR | 193 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0.48951 | 0.93618 | 7.8305 | 5.0819 | 45.0441 | 65.7536 | 115.2188 | 0.0016645 | 10285.4479 | 0
458748 | BACK RUTLAND AVE, BURNLEY B1 B13 | FERRANTI | SD81463288 | 750 | 6.6 KV | LV | 51 | INDOOR | 119 | 6 | 5 | 0 | 0 | 0 | 1 | 0 | 0.25322 | 0.45111 | 16.6843 | 8.5087 | 36.2478 | 41.7908 | 98.7877 | 0.00064538 | 26526.9648 | 0
616017 | TWEED RISE, WALNEY BARROW | SOUTH WALES SWITCHGEAR | SD17796893 | 500 | 11 KV | LV | 58 | OUTDOOR | 244 | 17 | 0 | 2 | 1 | 0 | 0 | 0 | 0.6936 | 1.2808 | 25.3828 | 11.2767 | 48.266 | 80.8946 | 89.9767 | 0.0038267 | 4473.857 | 2.4
616120 | HEST VIEW, ULVERSTON | BONAR LONG | SD28787649 | 500 | 11 KV | LV | 45 | OUTDOOR | 261 | 22 | 1 | 1 | 0 | 0 | 0 | 0 | 0.70677 | 1.3391 | 20.9287 | 9.9002 | 48.47 | 84.4222 | 94.2137 | 0.0050558 | 3386.1997 | 2.4
620293 | THE ARCHES, MARYPORT | SOUTH WALES SWITCHGEAR | NY03783549 | 500 | 11 KV | LV | 17 | INDOOR | 242 | 5 | 2 | 0 | 0 | 0 | 0 | 0 | 0.61479 | 1.1682 | 8.8875 | 5.544 | 52.3779 | 82.226 | 112.3212 | 0.0055194 | 3101.8049 | 0
620717 | DERWENT RD, MOSS BAY WORKINGTON | SOUTH WALES SWITCHGEAR | NX99282733 | 500 | 11 KV | LV | 17 | OUTDOOR | 327 | 20 | 30 | 6 | 0 | 0 | 0 | 0 | 1.078 | 1.8893 | 11.1412 | 6.4412 | 82.4831 | 141.6377 | 107.8154 | 1.8611 | 9.1988 | 100
636100 | CHESTERHOLM, ADJ 69 CHESTERHOLM | BONAR LONG | NY37025553 | 500 | 11 KV | LV | 39 | OUTDOOR | 252 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65037 | 1.2451 | 18.6321 | 9.15 | 44.6453 | 76.8222 | 96.6726 | 0.0025671 | 6668.9872 | 0
636173 | TODDS | ABB | NY39565561 | 800 | 11 KV | LV | 12 | OUTDOOR | 134 | 12 | 12 | 2 | 0 | 0 | 0 | 0 | 0.27794 | 0.50362 | 9.4945 | 5.7668 | 27.2827 | 33.86 | 111.464 | 0.00022633 | 75640.6631 | 0
636385 | QUEENSWAY, BES NO 10 QUEENSWAY | YORKSHIRE SWITCHGEAR AND ENGINEERING | NY37905480 | 500 | 11 KV | LV | 44 | INDOOR | 240 | 16 | 6 | 1 | 0 | 0 | 0 | 0 | 0.6684 | 1.257 | 15.458 | 8.0849 | 56.4877 | 90.1164 | 100.3239 | 0.010506 | 1629.556 | 1.6
642320 | CONISTON AVENUE HAMBLETON | SOUTH WALES SWITCHGEAR | SD37064267 | 500 | 11 KV | LV | 17 | INDOOR | 137 | 25 | 3 | 1 | 0 | 0 | 0 | 0 | 0.42231 | 0.80254 | 9.018 | 5.5955 | 41.9703 | 57.8332 | 112.0927 | 0.0011278 | 15180.4248 | 0
642344 | BEECHFIELD AVE, PREESALL | ABB | SD36414838 | 500 | 6.6 KV | LV | 15 | INDOOR | 168 | 25 | 2 | 0 | 0 | 0 | 0 | 0 | 0.48343 | 0.92486 | 8.5623 | 5.3991 | 44.8622 | 65.0158 | 113.2792 | 0.0016442 | 10412.4007 | 0
643270 | ULSTER ROAD, BOWERHAM LANCASTER | HAWKER SIDDELEY | SD48466041 | 1000 | 11 KV | LV | 27 | INDOOR | 343 | 29 | 5 | 2 | 0 | 0 | 0 | 0 | 0.47787 | 0.89153 | 11.2135 | 6.4928 | 47.0359 | 66.5134 | 107.2515 | 0.0020693 | 8273.3041 | 0
643285 | DALTON ROAD (LANCASTER), LANCASTER | SOUTH WALES SWITCHGEAR | SD48486185 | 500 | 11 KV | LV | 27 | OUTDOOR | 321 | 30 | 6 | 0 | 0 | 0 | 0 | 0 | 0.89187 | 1.6753 | 14.4535 | 7.6889 | 62.0433 | 113.9725 | 102.2107 | 0.093778 | 182.5589 | 92.6
643286 | MOORGATE, LANCASTER | HAWKER SIDDELEY | SD48306164 | 500 | 11 KV | LV | 27 | INDOOR | 292 | 35 | 14 | 4 | 0 | 0 | 0 | 0 | 0.9141 | 1.6667 | 11.0403 | 6.4282 | 76.6796 | 128.9523 | 107.5441 | 0.50559 | 33.8615 | 99.4
643293 | RIDGE LANE | NITRAN | SD48236224 | 800 | 11 KV | 6.6 KV | 23 | OUTDOOR | 90 | 26 | 1 | 5 | 0 | 0 | 0 | 0 | 0.20944 | 0.38908 | 13.2704 | 7.2468 | 24.8669 | 29.1737 | 104.1865 | 0.00018693 | 91584.0282 | 0
666035 | RAISELANDS CROFT, ADJ.7 RAISELANDS CFT | DISTRIBUTION TRANSFORMERS LTD | NY51103120 | 500 | 11 KV | LV | 36 | OUTDOOR | 308 | 14 | 4 | 1 | 1 | 0 | 0 | 0 | 0.85572 | 1.5738 | 17.6323 | 8.8156 | 59.9219 | 105.6492 | 97.8243 | 0.040021 | 427.7763 | 91.6

## Mapping - High-range
Mapping of failure probability of demonstrated distribution transformers

## Extreme-range Sceanrio
General information |  |  |  | Input data for assessment | [12 empty] | Intermediate data | [6 empty] | Output
Substation Number | Substation | Manufacturer | Grid Reference | Power Rating (kVA) | HV | LV | Transformer Age (till 2015) | Indoor/Outdoor | Number of customers | [7 empty] | Peak load (p.u.) |  | Moisture |  | Peak hot-spot temperature (°C) |  | Bubbling inception temperature (°C) | Loss-of-life (year per year) | Expected lifetime (p.u.) | Failure probability (%)
[9 empty] | PC1 | PC2 | PC3 | PC4 | PC5 | PC6 | PC7 | PC8 | No EVs | With EVs | In oil (ppm) | In paper (%) | No EVs | With EVs
165002 | LANCASTER RD SALFORD 6 | ABB | SD78720037 | 500 | 6.6 KV | LV | 13 | INDOOR | 372 | 15 | 5 | 2 | 0 | 0 | 0 | 0 | 0.99198 | 2.5807 | 8.2455 | 5.2642 | 81.1897 | 214.6912 | 114.0666 | 5399.8801 | 0.0031704 | 100
165080 | ST MARGARETS RD, PRESTWICH | PAUWELS | SD82210493 | 800 | 6.6 KV | LV | 16 | INDOOR | 320 | 20 | 8 | 0 | 0 | 0 | 0 | 0 | 0.54738 | 1.4178 | 8.9376 | 5.5613 | 51.0614 | 102.087 | 112.2814 | 0.03169 | 540.2255 | 7.6
165083 | NAZARETH HS, PRESTWICH | ABB | SD82260317 | 500 | 6.6 KV | LV | 14 | OUTDOOR | 212 | 7 | 7 | 0 | 0 | 1 | 0 | 0 | 0.6099 | 1.5379 | 10.1006 | 6.0184 | 43.6167 | 97.1596 | 110.0615 | 0.015725 | 1088.745 | 6
165133 | MANTON CL, BROUGHTON | FERRANTI | SD83620078 | 750 | 6.6 KV | LV | 50 | INDOOR | 75 | 82 | 1 | 2 | 0 | 0 | 0 | 0 | 0.27314 | 0.71908 | 16.399 | 8.4146 | 36.7376 | 52.809 | 99.0988 | 0.00086679 | 19751.0427 | 0
165528 | BISHOP RD, PENDLETON | CROMPTON PARKINSON | SJ78889962 | 1000 | 6.6 KV | LV | 52 | INDOOR | 216 | 26 | 2 | 0 | 0 | 0 | 0 | 0 | 0.30159 | 0.79887 | 16.836 | 8.5638 | 38.739 | 58.3107 | 98.5734 | 0.0011373 | 15053.0116 | 0
165647 | HEATH AVE, SALFORD 7 | CROMPTON PARKINSON | SJ82429945 | 1000 | 6.6 KV | LV | 51 | INDOOR | 299 | 3 | 14 | 2 | 0 | 0 | 0 | 0 | 0.41697 | 1.0571 | 16.593 | 8.4782 | 44.3649 | 75.5352 | 98.8882 | 0.0032539 | 5261.3456 | 0
165756 | ALBANY CT URMSTON | ABB | SJ75999500 | 800 | 6.6 KV | LV | 13 | OUTDOOR | 153 | 39 | 3 | 0 | 0 | 0 | 0 | 0 | 0.30434 | 0.8007 | 9.786 | 5.879 | 27.7636 | 46.4277 | 110.9841 | 0.00031231 | 54817.6899 | 0
166355 | TRAFFORD RD 181 | BRUSH | SJ76769802 | 500 | 6.6 KV | LV | 30 | OUTDOOR | 369 | 6 | 7 | 1 | 1 | 0 | 0 | 1 | 1.0585 | 2.601 | 15.4781 | 8.0559 | 77.2891 | 203.7222 | 100.7671 | 1530.9808 | 0.011182 | 100
166499 | THE HAWTHORNS | SOUTH WALES SWITCHGEAR | SJ80509420 | 800 | 6.6 KV | LV | 27 | INDOOR | 27 | 75 | 2 | 1 | 0 | 0 | 0 | 0 | 0.18338 | 0.44955 | 11.299 | 6.5344 | 34.8905 | 41.8246 | 106.9609 | 0.00065452 | 26156.4832 | 0
166588 | MONTON MILL GDN | SOUTH WALES SWITCHGEAR | SJ76319942 | 1000 | 6.6 KV | LV | 25 | INDOOR | 152 | 71 | 13 | 0 | 0 | 0 | 0 | 0 | 0.30959 | 0.79364 | 10.5433 | 6.2278 | 39.5059 | 58.6859 | 108.5866 | 0.0012188 | 14046.8609 | 0
166825 | DEEPDALE CT, NORTHWOLD DR M9 | HACKBRIDGE AND HEWITTIC | SD87850342 | 1000 | 6.6 KV | LV | 21 | OUTDOOR | 167 | 6 | 0 | 0 | 0 | 0 | 0 | 1 | 0.23986 | 0.6016 | 12.5473 | 6.9829 | 25.6199 | 36.8477 | 105.2416 | 0.00021881 | 78240.443 | 0
171440 | CLOUGH RD, DROYLSDEN | LINDLEY THOMPSON | SJ90519893 | 750 | 6.6 KV | LV | 50 | INDOOR | 186 | 15 | 2 | 0 | 0 | 0 | 0 | 0 | 0.33512 | 0.89301 | 16.4706 | 8.4417 | 38.9558 | 62.4024 | 98.9811 | 0.0012793 | 13382.4472 | 0
171459 | LONGDEN RD LEVENSHULME, LONGDEN RD | BABCOCK | SJ87709485 | 800 | 6.6 KV | LV | 22 | OUTDOOR | 148 | 7 | 3 | 0 | 0 | 0 | 0 | 0 | 0.24726 | 0.66131 | 12.7404 | 7.0507 | 25.8264 | 39.206 | 105.0066 | 0.00023191 | 73820.3615 | 0
171643 | RAMILLIES AVE, CHEADLE HULME | DISTRIBUTION TRANSFORMERS LTD | SJ87848631 | 500 | 11 KV | LV | 42 | INDOOR | 329 | 18 | 10 | 2 | 1 | 0 | 0 | 0 | 0.95932 | 2.4185 | 14.6973 | 7.8119 | 80.1809 | 198.1611 | 101.3934 | 855.3247 | 0.020016 | 100
171832 | HOLLAND ST | EFACEC | SJ91789558 | 750 | 6.6 KV | LV | 2 | INDOOR | 241 | 13 | 8 | 1 | 1 | 1 | 1 | 0 | 0.53015 | 1.2465 | 6.451 | 4.4666 | 50.2282 | 89.0181 | 119.235 | 0.0098363 | 1740.4861 | 0
171852 | WESTBURY AVE 37 SALE, SALE | BONAR LONG | SJ76109039 | 500 | 11 KV | LV | 38 | OUTDOOR | 280 | 9 | 3 | 1 | 0 | 0 | 0 | 0 | 0.73216 | 1.9194 | 18.3653 | 9.0594 | 50.3435 | 129.242 | 96.9956 | 0.43292 | 39.5454 | 100
171966 | PARKFIELD RD S | BRUSH | SJ84259165 | 500 | 6.6 KV | LV | 33 | INDOOR | 188 | 19 | 12 | 1 | 0 | 0 | 0 | 0 | 0.58209 | 1.4737 | 12.4831 | 6.9904 | 51.8338 | 104.2637 | 104.8706 | 0.036997 | 462.7422 | 47
172014 | SCHOOL LN DIDSBURY | PAUWELS | SJ85339100 | 800 | 6.6 KV | LV | 16 | INDOOR | 225 | 64 | 9 | 0 | 0 | 1 | 0 | 0 | 0.49607 | 1.2551 | 8.8939 | 5.5491 | 48.6474 | 89.7493 | 112.2616 | 0.010277 | 1665.9209 | 0
172242 | CARRGATE RD, DENTON | LINDLEY THOMPSON | SJ93939422 | 500 | 6.6 KV | LV | 53 | INDOOR | 179 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0.45222 | 1.215 | 17.282 | 8.7157 | 43.0328 | 81.709 | 98.0482 | 0.0045193 | 3788.2168 | 0
172344 | FAIRFIELD RD 222, REAR 90 SILVERDAL ST | SOUTH WALES SWITCHGEAR | SJ89729760 | 500 | 6.6 KV | LV | 17 | OUTDOOR | 281 | 27 | 7 | 4 | 1 | 0 | 0 | 1 | 0.92259 | 2.2255 | 11.0591 | 6.4037 | 66.8438 | 163.4695 | 108.0483 | 17.5559 | 0.97517 | 100
172448 | ST WILFREDS ST HULME, OFF ST WILFRED'S S | SOUTH WALES SWITCHGEAR | SJ83189686 | 500 | 6.6 KV | LV | 21 | INDOOR | 306 | 20 | 21 | 4 | 0 | 0 | 0 | 0 | 0.95138 | 2.3484 | 9.8032 | 5.9205 | 81.1518 | 193.082 | 110.2683 | 512.1303 | 0.033429 | 100
172508 | BRIARFIELDS,BOUNDARY LN, OPP BONSALL ST, | ABB | SJ84059683 | 800 | 6.6 KV | LV | 20 | OUTDOOR | 223 | 72 | 7 | 0 | 0 | 2 | 0 | 0 | 0.52074 | 1.2956 | 11.8034 | 6.6889 | 38.4423 | 79.1341 | 106.7666 | 0.002971 | 5762.4631 | 0
172607 | BRITANNIA MILL, HULME HALL RD,HULME | SOUTH WALES SWITCHGEAR | SJ82599721 | 1000 | 6.6 KV | LV | 16 | INDOOR | 0 | 108 | 0 | 3 | 0 | 0 | 0 | 0 | 0.19629 | 0.38438 | 8.464 | 5.3585 | 35.0945 | 39.6235 | 113.4792 | 0.00062426 | 27424.6045 | 0
211326 | BEECH TREES S, OPP 113 (SKELM) | BRENTFORD TRANSFORMERS | SD49540503 | 1000 | 11 KV | LV | 24 | OUTDOOR | 189 | 59 | 1 | 0 | 0 | 0 | 1 | 0 | 0.32971 | 0.83925 | 13.3452 | 7.2778 | 28.7692 | 48.8407 | 104.0179 | 0.00035628 | 48052.5869 | 0
211505 | SMETHURST RD, OPP 2 ORRELL | FERRANTI | SD52630306 | 750 | 11 KV | LV | 50 | OUTDOOR | 326 | 20 | 12 | 3 | 0 | 0 | 0 | 0 | 0.6266 | 1.5934 | 22.5084 | 10.3981 | 44.3679 | 102.2366 | 92.6514 | 0.026512 | 645.7416 | 95.8
211944 | JENNET HEY, ADJ 12 ASHTON | ENGLISH ELECTRIC | SD56610065 | 500 | 6.6 KV | LV | 50 | INDOOR | 285 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0.75198 | 1.9703 | 16.478 | 8.4373 | 62.0788 | 147.6786 | 99.0524 | 3.4089 | 5.0221 | 100
211948 | PRIORY RD, ADJ 2 ASHTON | BRUSH | SD56940017 | 500 | 6.6 KV | LV | 46 | INDOOR | 289 | 6 | 1 | 1 | 0 | 0 | 0 | 0 | 0.73562 | 1.939 | 15.6494 | 8.148 | 60.3989 | 144.1739 | 100.1274 | 2.4785 | 6.9073 | 100
212333 | HORNE GR, OPP 18 W/MESNES | BONAR LONG | SD56950441 | 750 | 6.6 KV | LV | 47 | INDOOR | 117 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21037 | 0.56851 | 15.8829 | 8.2341 | 34.5494 | 45.3906 | 99.7679 | 0.00063001 | 27174.2027 | 0
212620 | MOSS LN, ADJ 31 PLATT BRIDGE | ENGLISH ELECTRIC | SD60390324 | 500 | 11 KV | LV | 51 | INDOOR | 321 | 22 | 9 | 3 | 0 | 0 | 0 | 0 | 0.91596 | 2.3477 | 16.5383 | 8.4574 | 75.7066 | 189.1422 | 98.985 | 330.6119 | 0.051783 | 100
212649 | ABINGDON DRIVE (ABRAM), OPP 13 ABINGDON | S&C ELECTRIC | SD64140212 | 500 | 11 KV | LV | 42 | OUTDOOR | 349 | 8 | 0 | 1 | 0 | 0 | 0 | 0 | 0.88162 | 2.3236 | 19.6419 | 9.4804 | 60.5308 | 168.8391 | 95.5822 | 32.9437 | 0.51967 | 100
212806 | CHURCH ST N, CHURCH ST WESTH'TON | ABB | SD65380671 | 500 | 11 KV | LV | 20 | OUTDOOR | 249 | 22 | 18 | 7 | 2 | 1 | 1 | 0 | 1.0058 | 2.1807 | 12.1156 | 6.8165 | 77.4273 | 165.7645 | 106.0431 | 24.8376 | 0.68928 | 100
212904 | WESTSIDE AVE, OFF WEST END RD | LINDLEY THOMPSON | SJ54089687 | 500 | 11 KV | LV | 49 | OUTDOOR | 167 | 2 | 9 | 1 | 0 | 0 | 0 | 0 | 0.47208 | 1.2147 | 22.4559 | 10.3818 | 35.7671 | 72.1707 | 92.6921 | 0.0015633 | 10951.1024 | 0
212944 | PENNY LN, ADJ 223 HAYDOCK | ABB | SJ57449737 | 500 | 11 KV | LV | 13 | INDOOR | 191 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0.48029 | 1.2791 | 8.456 | 5.3584 | 44.6435 | 86.7667 | 113.4149 | 0.0070877 | 2415.4677 | 0
213807 | WOTTON DR, FRONT 19/21 WOTTON D | ABB | SJ58929951 | 500 | 6.6 KV | LV | 20 | OUTDOOR | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.81368 | 2.1655 | 11.9632 | 6.7615 | 55.4013 | 152.08 | 106.2591 | 5.2056 | 3.2888 | 100
216118 | BELVEDERE RD, NEWTON LE WILLOWS | ABB | SJ57739573 | 500 | 11 KV | LV | 20 | OUTDOOR | 125 | 6 | 8 | 2 | 0 | 0 | 0 | 0 | 0.38323 | 0.96973 | 12.019 | 6.7776 | 31.5896 | 56.2702 | 106.2444 | 0.00054169 | 31604.6287 | 0
216276 | CROFT ST, LITTLE HULTON | LINDLEY THOMPSON | SD71880410 | 500 | 11 KV | LV | 52 | INDOOR | 228 | 3 | 2 | 1 | 0 | 1 | 0 | 0 | 0.6204 | 1.5817 | 17.0643 | 8.6414 | 53.5099 | 112.3039 | 98.3002 | 0.083324 | 205.4628 | 99.2
216543 | GOWER ST, SWINTON | FERRANTI | SD78380224 | 750 | 11 KV | LV | 50 | INDOOR | 180 | 4 | 14 | 5 | 0 | 0 | 0 | 1 | 0.4233 | 0.97416 | 16.5075 | 8.4414 | 44.3018 | 69.5405 | 99.0821 | 0.0023038 | 7431.0587 | 0
216664 | HUTTON AVE, BOOTHSTOWN | ENGLISH ELECTRIC | SD71720083 | 750 | 11 KV | LV | 51 | INDOOR | 381 | 17 | 1 | 0 | 0 | 0 | 0 | 0 | 0.65237 | 1.7253 | 16.8364 | 8.5656 | 55.8439 | 126.0863 | 98.5519 | 0.36742 | 46.5957 | 100
216674 | HULME RD, LEIGH | SOUTH WALES SWITCHGEAR | SD64270060 | 800 | 11 KV | LV | 20 | OUTDOOR | 125 | 0 | 3 | 0 | 1 | 0 | 0 | 0 | 0.22457 | 0.55848 | 12.2404 | 6.8605 | 25.3477 | 35.0827 | 105.8561 | 0.00020983 | 81590.8069 | 0
217117 | LAWSON AVE, WESTLEIGH LANE LEIGH | PARSONS | SD65050220 | 500 | 11 KV | LV | 37 | OUTDOOR | 185 | 12 | 1 | 1 | 0 | 0 | 0 | 0 | 0.49634 | 1.3187 | 18.2854 | 9.0305 | 36.1903 | 78.6243 | 97.1103 | 0.002648 | 6465.2481 | 0
217521 | WESTWOOD METHS, BOLTON ROAD SWINTON | DENIS FERRANTI | SD79450076 | 500 | 11 KV | LV | 52 | OUTDOOR | 170 | 9 | 6 | 1 | 0 | 0 | 0 | 0 | 0.48005 | 1.2486 | 23.0591 | 10.5743 | 35.8193 | 74.1146 | 92.0888 | 0.0018366 | 9321.4591 | 0.2
218214 | BLACKBERRY DR | ABB | SD61500399 | 500 | 11 KV | LV | 12 | OUTDOOR | 207 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.51487 | 1.3684 | 9.4302 | 5.7422 | 37.0337 | 82.1182 | 111.5717 | 0.0037324 | 4586.8716 | 0
231594 | MIDDLEBROOK HOUSING, MIDDLEBROOK LOSTOCK | SOUTH WALES SWITCHGEAR | SD64771013 | 500 | 11 KV | LV | 16 | INDOOR | 277 | 0 | 2 | 3 | 0 | 0 | 0 | 0 | 0.71516 | 1.8648 | 9.0853 | 5.6223 | 59.3976 | 137.4719 | 111.9454 | 1.1908 | 14.3765 | 99.6
231670 | LITTLE OAKS | EFACEC | SD73021210 | 500 | 11 KV | LV | 2 | OUTDOOR | 101 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26657 | 0.73253 | 7.2559 | 4.8079 | 26.3463 | 42.1411 | 117.2551 | 0.00025246 | 67811.8912 | 0
232046 | DOROTHY ST, RAMSBOTTOM | ABB | SD78731612 | 500 | 11 KV | LV | 14 | OUTDOOR | 291 | 11 | 13 | 1 | 0 | 0 | 0 | 0 | 0.81954 | 2.0996 | 10.0837 | 5.9916 | 57.8228 | 148.4238 | 110.4691 | 3.3767 | 5.07 | 99.8
232164 | DORIS MILL, ADJ 90 BURY N RD HEY | SOUTH WALES SWITCHGEAR | SD84201080 | 500 | 6.6 KV | LV | 18 | OUTDOOR | 363 | 16 | 13 | 1 | 0 | 0 | 2 | 1 | 1.157 | 2.7472 | 11.6665 | 6.6371 | 87.9 | 223.7083 | 106.9588 | 14080.6181 | 0.0012159 | 100
232373 | THATCHLEACH LN W, WHITEFIELD | BRUCE PEEBLES | SD81070514 | 750 | 11 KV | LV | 51 | OUTDOOR | 310 | 37 | 19 | 3 | 1 | 0 | 0 | 0 | 0.67988 | 1.6643 | 22.8113 | 10.4913 | 48.9595 | 109.9999 | 92.3577 | 0.060012 | 285.2739 | 100
232384 | WINGATE DR, WHITEFIELD | LINDLEY THOMPSON | SD80060637 | 500 | 11 KV | LV | 57 | INDOOR | 205 | 9 | 3 | 1 | 0 | 1 | 0 | 0 | 0.58459 | 1.4769 | 17.9927 | 8.9601 | 51.417 | 103.7759 | 97.1668 | 0.035322 | 484.6836 | 90.8
232432 | BOOTH RD, OPP 30 BOOTH RD | CROMPTON PARKINSON | SD75960696 | 500 | 11 KV | LV | 53 | INDOOR | 250 | 29 | 5 | 1 | 1 | 0 | 0 | 0 | 0.75664 | 1.9134 | 17.2193 | 8.6971 | 63.2602 | 143.8906 | 98.0821 | 2.3224 | 7.3718 | 100
232488 | LONGTON ST, BURY RR 660 MCR RD | BABCOCK | SD80630794 | 500 | 11 KV | LV | 21 | INDOOR | 212 | 7 | 4 | 0 | 1 | 1 | 1 | 0 | 0.67662 | 1.6053 | 9.9357 | 5.9819 | 58.7641 | 116.9698 | 109.8598 | 0.13383 | 127.9248 | 82.8
232553 | MARKET ST BURY, BURY | ABB | SD80740983 | 800 | 6.6 KV | LV | 13 | OUTDOOR | 149 | 3 | 6 | 1 | 1 | 0 | 0 | 0 | 0.28195 | 0.69527 | 9.8816 | 5.9203 | 27.3754 | 41.5061 | 110.731 | 0.00026746 | 64010.0066 | 0
232576 | ABINGDON CL, ADJ 1 ABINGDON CLOSE | ENGLISH ELECTRIC | SD80730688 | 500 | 11 KV | LV | 50 | INDOOR | 231 | 8 | 1 | 1 | 0 | 0 | 0 | 0 | 0.59885 | 1.5752 | 16.6356 | 8.4939 | 51.4237 | 110.9946 | 98.8286 | 0.07473 | 229.0919 | 99
310448 | HALFWAY HS, REAR OF PUB ROYTON | FERRANTI | SD91380886 | 750 | 6.6 KV | LV | 56 | INDOOR | 142 | 5 | 1 | 1 | 0 | 0 | 0 | 0 | 0.24931 | 0.66379 | 17.9191 | 8.9308 | 35.8028 | 49.8014 | 97.3003 | 0.00073492 | 23295.1704 | 0
310534 | WHITEGATE AVE, CHADDERTON | SOUTH WALES SWITCHGEAR | SD89910378 | 800 | 6.6 KV | LV | 17 | OUTDOOR | 370 | 10 | 4 | 0 | 0 | 0 | 0 | 0 | 0.5944 | 1.5672 | 11.188 | 6.4643 | 41.5575 | 98.7659 | 107.6259 | 0.018255 | 937.8162 | 11.2
311103 | MIDDLEGATE, RR 43 MIDGATE HOLINS | BRUSH | SD92260271 | 500 | 6.6 KV | LV | 32 | OUTDOOR | 255 | 7 | 0 | 1 | 0 | 0 | 0 | 0 | 0.64946 | 1.7189 | 15.7441 | 8.1539 | 44.7014 | 110.4257 | 100.3152 | 0.061935 | 276.4195 | 91.4
312270 | HOLLY ST, MALHAM CLOSE ROYTON | DENIS FERRANTI | SD91720797 | 750 | 6.6 KV | LV | 50 | INDOOR | 321 | 17 | 4 | 2 | 0 | 0 | 0 | 0 | 0.57783 | 1.5077 | 16.4597 | 8.4339 | 51.5907 | 107.675 | 99.0442 | 0.051975 | 329.3886 | 94.8
312895 | MERTON AVE, ADJ HERON MILL O/HAM | FERRANTI | SD91740307 | 750 | 6.6 KV | LV | 50 | OUTDOOR | 332 | 20 | 4 | 0 | 1 | 0 | 0 | 0 | 0.61342 | 1.5773 | 22.5375 | 10.4064 | 43.0941 | 100.1687 | 92.6284 | 0.021396 | 800.1309 | 92.6
313307 | GREENSIDE AVE, OFF HAVEN LN OLDHAM | FERRANTI | SD95050697 | 500 | 6.6 KV | LV | 48 | INDOOR | 232 | 5 | 6 | 2 | 1 | 0 | 0 | 0 | 0.66794 | 1.6624 | 16.2186 | 8.3499 | 57.3246 | 120.762 | 99.3487 | 0.20609 | 83.0692 | 100
314107 | KIRKLAND YARNS, OFF JOWETT ST OLDHAM | SOUTH WALES SWITCHGEAR | SD94430650 | 800 | 6.6 KV | LV | 44 | INDOOR | 184 | 6 | 3 | 2 | 0 | 0 | 0 | 0 | 0.31203 | 0.80907 | 15.0483 | 7.9381 | 39.2858 | 59.1114 | 100.8933 | 0.0011937 | 14341.5547 | 0
314325 | BELLSHILL CRES, ROCHDALE | PAUWELS | SD91261409 | 500 | 6.6 KV | LV | 16 | OUTDOOR | 311 | 1 | 5 | 1 | 0 | 0 | 0 | 0 | 0.79924 | 2.087 | 10.7611 | 6.2749 | 55.1833 | 145.5965 | 108.819 | 2.5667 | 6.67 | 100
314378 | CROFTHEAD | EFACEC | SD93521716 | 750 | 6.6 KV | LV | 1 | INDOOR | 292 | 4 | 1 | 1 | 0 | 0 | 0 | 0 | 0.49201 | 1.2965 | 6.1254 | 4.3081 | 46.3822 | 90.0816 | 120.4829 | 0.0097873 | 1749.1978 | 0
314400 | DURN | SCHNEIDER ELECTRIC | SD94211644 | 750 | 6.6 KV | LV | 1 | INDOOR | 241 | 5 | 8 | 2 | 0 | 0 | 0 | 0 | 0.44255 | 1.1364 | 6.2692 | 4.3674 | 44.3328 | 79.003 | 120.199 | 0.0039664 | 4316.2518 | 0
314436 | HAUGH LANE, HAUGH LN NEWHEY | ABB | SD94121170 | 500 | 6.6 KV | LV | 20 | OUTDOOR | 311 | 12 | 2 | 2 | 0 | 0 | 0 | 0 | 0.81884 | 2.1485 | 11.9817 | 6.758 | 56.3726 | 150.9424 | 106.423 | 4.4748 | 3.8259 | 100
314606 | DUNLOP AVE, QUEENSWAY RDALE | ENGLISH ELECTRIC | SD89331143 | 750 | 6.6 KV | LV | 54 | OUTDOOR | 129 | 17 | 6 | 1 | 0 | 0 | 0 | 0 | 0.26643 | 0.69212 | 24.0061 | 10.8616 | 26.6297 | 40.8813 | 91.2245 | 0.00025343 | 67553.5755 | 0
314974 | NORDEN RD, BAMFORD | LINDLEY THOMPSON | SD86311311 | 750 | 6.6 KV | LV | 50 | INDOOR | 186 | 9 | 12 | 5 | 0 | 0 | 0 | 0 | 0.39378 | 0.96747 | 16.3751 | 8.4047 | 42.4754 | 68.335 | 99.1453 | 0.0019778 | 8656.1174 | 0
320939 | FLEET ST | EFACEC | SJ95229533 | 500 | 6.6 KV | LV | 2 | OUTDOOR | 192 | 9 | 2 | 0 | 0 | 0 | 0 | 0 | 0.50251 | 1.3382 | 7.0989 | 4.7316 | 36.483 | 80.0083 | 117.8796 | 0.0029807 | 5743.5935 | 0
322939 | KINGS RD, OLD PEOPLES HOST AUL | FERRANTI | SD95090040 | 750 | 6.6 KV | LV | 51 | INDOOR | 274 | 10 | 4 | 0 | 1 | 0 | 0 | 0 | 0.50245 | 1.2848 | 16.9532 | 8.6044 | 47.4429 | 89.9396 | 98.4366 | 0.010193 | 1679.532 | 1.4
323779 | CALVER MEWS, CAR PARK GAMESLEY | SOUTH WALES SWITCHGEAR | SK01029484 | 1000 | 11 KV | LV | 26 | OUTDOOR | 100 | 75 | 2 | 0 | 0 | 0 | 0 | 0 | 0.22045 | 0.5873 | 13.8889 | 7.4849 | 25.0359 | 36.0537 | 103.0525 | 0.00021344 | 80210.4872 | 0
326139 | WILTSHIRE DR, GLOSSOP | HAWKER SIDDELEY | SK04259335 | 500 | 11 KV | LV | 18 | OUTDOOR | 278 | 16 | 0 | 0 | 1 | 0 | 0 | 0 | 0.75606 | 1.9466 | 11.361 | 6.5143 | 52.1222 | 132.3636 | 107.6104 | 0.64539 | 26.5264 | 99.2
327085 | OLDHAM ATHLETIC, SHEEPFOOT LN OLDHAM | FERRANTI | SD91500646 | 750 | 6.6 KV | LV | 23 | OUTDOOR | 134 | 7 | 2 | 0 | 0 | 0 | 0 | 0 | 0.23723 | 0.63838 | 10.3288 | 6.1404 | 35.4107 | 48.5503 | 109.0269 | 0.00070204 | 24385.9832 | 0
327098 | E WHITTAKER, OLDHAM | SOUTH WALES SWITCHGEAR | SD92160607 | 500 | 6.6 KV | LV | 26 | OUTDOOR | 114 | 1 | 4 | 1 | 0 | 0 | 0 | 0 | 0.31232 | 0.81608 | 14.0679 | 7.5627 | 28.2529 | 46.8636 | 102.5875 | 0.00031977 | 53537.8923 | 0
327479 | ARMITAGE CL, OFF HERON ST | ABB | SD91320350 | 500 | 6.6 KV | LV | 22 | OUTDOOR | 305 | 48 | 19 | 4 | 0 | 3 | 0 | 0 | 1.1196 | 2.6294 | 12.7472 | 7.0558 | 86.8187 | 212.4015 | 104.9453 | 4153.8284 | 0.0041215 | 100
330093 | BIRKETT AND BOSTOCK, HR HILLGATE STOCKPR | FERRANTI | SJ89968953 | 750 | 6.6 KV | LV | 51 | INDOOR | 100 | 0 | 2 | 1 | 1 | 0 | 0 | 1 | 0.23945 | 0.53148 | 16.7995 | 8.5498 | 35.9474 | 44.7026 | 98.633 | 0.00068589 | 24960.3191 | 0
330180 | HEMPSHAW LN OFFERTON STOCKPORT | ABB | SJ90788941 | 500 | 6.6 KV | LV | 13 | OUTDOOR | 220 | 5 | 10 | 4 | 0 | 1 | 0 | 0 | 0.67813 | 1.6501 | 9.815 | 5.8957 | 48.9603 | 108.3658 | 110.799 | 0.052926 | 323.4713 | 42.8
330222 | NORRIS BANK, HEATON NORRIS | ABB | SJ87839059 | 800 | 6.6 KV | LV | 21 | OUTDOOR | 347 | 3 | 1 | 1 | 0 | 0 | 0 | 0 | 0.54371 | 1.4405 | 12.5835 | 6.9951 | 38.5913 | 88.2896 | 105.2203 | 0.0064788 | 2642.4682 | 0
330225 | OSBORNE ST, BREDBURY | SOUTH WALES SWITCHGEAR | SJ91469112 | 800 | 11 KV | LV | 15 | INDOOR | 228 | 35 | 10 | 2 | 0 | 0 | 0 | 0 | 0.44834 | 1.1427 | 8.6184 | 5.4217 | 45.9091 | 81.1504 | 113.1568 | 0.0049594 | 3452.0097 | 0
330276 | TATTON RD, HEATON MOOR | FERRANTI | SJ88179210 | 1000 | 6.6 KV | LV | 50 | INDOOR | 250 | 62 | 17 | 10 | 0 | 1 | 0 | 0 | 0.49553 | 1.1757 | 16.3541 | 8.4018 | 49.5 | 85.4542 | 99.1242 | 0.0073707 | 2322.7135 | 0
330300 | WOODLANDS DR, OFFERTON | ABB | SJ91658969 | 500 | 6.6 KV | LV | 15 | INDOOR | 273 | 15 | 2 | 0 | 0 | 0 | 0 | 0 | 0.71527 | 1.8843 | 8.6788 | 5.4508 | 58.9887 | 138.9475 | 112.926 | 1.5049 | 11.3761 | 99.6
330305 | YORK ST STOCKPORT | ABB | SJ89108971 | 1000 | 6.6 KV | LV | 12 | OUTDOOR | 212 | 8 | 11 | 0 | 0 | 0 | 1 | 0 | 0.32254 | 0.79357 | 9.2272 | 5.6547 | 28.8553 | 46.7345 | 112.1303 | 0.00033173 | 51608.4623 | 0
331769 | HULLEY RD, MACCLESFIELD | SOUTH WALES SWITCHGEAR | SJ92737461 | 500 | 11 KV | LV | 18 | OUTDOOR | 331 | 54 | 6 | 4 | 0 | 0 | 0 | 0 | 1.0119 | 2.6027 | 11.5695 | 6.608 | 72.3684 | 201.5383 | 107.02 | 1201.7431 | 0.014246 | 100
331890 | GRANGE RD, BRAMHALL | YORKSHIRE ELECTRICAL TRANSFORMERS | SJ89728707 | 500 | 11 KV | LV | 48 | INDOOR | 169 | 14 | 3 | 0 | 0 | 0 | 0 | 0 | 0.46423 | 1.2345 | 16.0877 | 8.3021 | 43.9311 | 83.532 | 99.5489 | 0.0052676 | 3250.0777 | 0
331994 | POWNALL FM, STYAL | LINDLEY THOMPSON | SJ84018349 | 500 | 11 KV | LV | 49 | INDOOR | 91 | 12 | 8 | 1 | 0 | 0 | 1 | 0 | 0.35631 | 0.82078 | 16.3665 | 8.4015 | 39.7206 | 58.3184 | 99.1637 | 0.0011131 | 15380.5657 | 0
331997 | QUEENS AVE, MACCLESFIELD | TRANSFORMERS (WALES) | SJ92197455 | 800 | 11 KV | LV | 18 | INDOOR | 144 | 14 | 7 | 1 | 3 | 3 | 0 | 0 | 0.42656 | 0.84753 | 9.1809 | 5.6695 | 46.4724 | 64.744 | 111.5613 | 0.0021336 | 8023.8308 | 0
332456 | PARKGATE WAY, SPATH LNG6 HANDFORTH | LINDLEY THOMPSON | SJ85948362 | 500 | 11 KV | LV | 51 | INDOOR | 119 | 11 | 3 | 0 | 0 | 0 | 0 | 0 | 0.33464 | 0.89287 | 16.6102 | 8.4825 | 37.9341 | 60.7543 | 98.8915 | 0.0011041 | 15505.9937 | 0
332587 | REDHOUSE LN, DISLEY | UNIDAIRE LTD | SJ98048467 | 500 | 11 KV | LV | 22 | OUTDOOR | 113 | 10 | 4 | 1 | 0 | 0 | 0 | 0 | 0.33213 | 0.87361 | 12.6612 | 7.0219 | 29.012 | 49.9142 | 105.1343 | 0.0003684 | 46471.7424 | 0
332821 | CHESTER WALKS, BREDBURY | CROMPTON PARKINSON | SJ93329018 | 500 | 11 KV | LV | 51 | INDOOR | 210 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0.53291 | 1.4341 | 16.7908 | 8.544 | 47.3238 | 98.331 | 98.6758 | 0.020126 | 850.6283 | 49
332876 | LADYBROOK RD, BRAMHALL | PAUWELS | SJ88338631 | 750 | 11 KV | LV | 16 | OUTDOOR | 137 | 8 | 5 | 2 | 0 | 0 | 0 | 0 | 0.26697 | 0.68653 | 11.0793 | 6.4059 | 26.6464 | 40.7142 | 108.132 | 0.00025183 | 67982.6678 | 0
333103 | QUEENS RD FLATS, WILMSLOW | ABB | SJ84268087 | 500 | 11 KV | LV | 13 | INDOOR | 136 | 24 | 8 | 1 | 0 | 2 | 0 | 2 | 0.63792 | 1.3437 | 8.0606 | 5.1877 | 57.325 | 97.5843 | 114.4855 | 0.021901 | 781.7132 | 0.8
333883 | HIGHFIELD AVE, BREDBURY | SOUTH WALES SWITCHGEAR | SJ92879085 | 750 | 11 KV | LV | 45 | INDOOR | 191 | 6 | 1 | 0 | 0 | 1 | 0 | 0 | 0.34852 | 0.89308 | 15.4714 | 8.0892 | 39.7234 | 62.918 | 100.3105 | 0.0013589 | 12598.633 | 0
333962 | DIXON DRIVE 29, CHELFORD | SOUTH WALES SWITCHGEAR | SJ81377512 | 1000 | 11 KV | LV | 26 | INDOOR | 130 | 61 | 7 | 5 | 0 | 0 | 0 | 0 | 0.27636 | 0.6915 | 10.8367 | 6.3451 | 38.2161 | 53.2153 | 107.9861 | 0.0009761 | 17539.2409 | 0
334173 | ALDERWOOD AVE, HEATON MERSEY | BRUSH | SJ87059030 | 500 | 6.6 KV | LV | 33 | INDOOR | 318 | 17 | 1 | 0 | 0 | 0 | 0 | 0 | 0.82461 | 2.1811 | 12.4016 | 6.9573 | 66.7448 | 168.6411 | 105.0408 | 32.8536 | 0.5211 | 100
334195 | CORBAR RD(STOCKPORT), STOCKPORT | DENIS FERRANTI | SJ90568835 | 750 | 6.6 KV | LV | 49 | OUTDOOR | 40 | 85 | 2 | 0 | 0 | 1 | 0 | 0 | 0.23743 | 0.59505 | 21.9614 | 10.2202 | 25.7342 | 36.6449 | 93.2272 | 0.0002306 | 74240.2993 | 0
336478 | LOWER BENTS LN, BREDBURY | BRUSH | SJ92599166 | 500 | 11 KV | LV | 29 | OUTDOOR | 217 | 15 | 10 | 3 | 0 | 0 | 0 | 0 | 0.65009 | 1.6403 | 15.3122 | 7.9985 | 46.2768 | 106.1103 | 100.9687 | 0.040305 | 424.756 | 77.2
336998 | ST GEORGES ST, MACCLESFIELD | SOUTH WALES SWITCHGEAR | SJ91857303 | 500 | 11 KV | LV | 26 | OUTDOOR | 81 | 31 | 6 | 1 | 1 | 0 | 0 | 0 | 0.35653 | 0.85443 | 14.0877 | 7.5574 | 30.6477 | 50.0194 | 102.7442 | 0.00040974 | 41782.9337 | 0
337081 | DORCHESTER WAY, DORCHESTER WAY,MACC | HAWKER SIDDELEY | SJ91097579 | 500 | 11 KV | LV | 25 | OUTDOOR | 230 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0.57497 | 1.5319 | 13.7802 | 7.4467 | 40.2884 | 94.8081 | 103.195 | 0.01207 | 1418.4351 | 13
337724 | DIDSBURY ROAD, OPP 218 | ABB | SJ87409070 | 500 | 6.6 KV | LV | 20 | OUTDOOR | 228 | 16 | 1 | 1 | 0 | 0 | 0 | 0 | 0.6113 | 1.6185 | 11.894 | 6.7242 | 42.537 | 101.9693 | 106.5657 | 0.025566 | 669.6275 | 32.8
410398 | ROBINSON ST, PRESTON | SOUTH WALES SWITCHGEAR | SD52913133 | 500 | 6.6 KV | LV | 25 | OUTDOOR | 229 | 17 | 15 | 3 | 0 | 0 | 1 | 0 | 0.76181 | 1.8332 | 13.5103 | 7.348 | 54.9692 | 125.1745 | 103.6014 | 0.28364 | 60.3581 | 98.8
410460 | CEMETERY (PRESTON), PRESTON | ABB | SD56333023 | 500 | 6.6 KV | LV | 16 | INDOOR | 278 | 7 | 22 | 4 | 0 | 0 | 1 | 0 | 0.9086 | 2.1569 | 8.7306 | 5.4836 | 78.1699 | 173.1849 | 112.5794 | 54.0011 | 0.31703 | 100
410579 | HARBOUR LN (WARTON), WARTON | BABCOCK | SD41292865 | 800 | 6.6 KV | LV | 22 | INDOOR | 343 | 14 | 13 | 5 | 1 | 0 | 1 | 0 | 0.67105 | 1.617 | 10.3296 | 6.147 | 60.7256 | 121.8633 | 108.9202 | 0.23862 | 71.7467 | 95.8
410611 | WATERLOO RD, PRESTON | BONAR LONG | SD51793064 | 500 | 6.6 KV | LV | 55 | INDOOR | 193 | 24 | 10 | 4 | 0 | 0 | 0 | 0 | 0.62277 | 1.5685 | 17.5255 | 8.8001 | 54.5861 | 112.341 | 97.7365 | 0.080811 | 211.8528 | 99.2
410842 | BROWNING RD, PRESTON | BABCOCK | SD55633065 | 500 | 6.6 KV | LV | 22 | OUTDOOR | 126 | 5 | 7 | 1 | 0 | 0 | 0 | 0 | 0.3682 | 0.94074 | 12.6795 | 7.0337 | 30.7447 | 54.3836 | 105.0011 | 0.00047964 | 35693.5775 | 0
414508 | JUNCTION LN, BURSCOUGH | FERRANTI | SD44401155 | 750 | 11 KV | LV | 52 | INDOOR | 102 | 8 | 3 | 1 | 0 | 0 | 0 | 0 | 0.1965 | 0.51767 | 17.041 | 8.6337 | 34.2925 | 43.359 | 98.3342 | 0.00060476 | 28308.932 | 0
414539 | HENNEL LN SW HS, WALTON LE DALE | BONAR LONG | SD54752702 | 500 | 11 KV | LV | 29 | OUTDOOR | 180 | 7 | 3 | 0 | 0 | 0 | 0 | 0 | 0.4738 | 1.2596 | 14.7399 | 7.7988 | 35.1147 | 74.3099 | 101.696 | 0.0018133 | 9441.2768 | 0
414613 | BALCARRES RD, LEYLAND | ABB | SD54242163 | 500 | 11 KV | LV | 14 | INDOOR | 181 | 5 | 9 | 4 | 0 | 0 | 0 | 1 | 0.59834 | 1.4081 | 8.4753 | 5.3714 | 53.446 | 100.2582 | 113.2595 | 0.026826 | 638.1886 | 3
414615 | MOSSY LEA, WRIGHTINGTON | ABB | SD53651254 | 500 | 11 KV | LV | 14 | OUTDOOR | 174 | 5 | 4 | 0 | 1 | 1 | 0 | 0 | 0.53266 | 1.2861 | 10.3845 | 6.1258 | 39.4881 | 78.4505 | 109.6147 | 0.0029437 | 5815.8623 | 0
414674 | COW MOSS | EFACEC | SD56501397 | 500 | 11 KV | LV | 1 | INDOOR | 261 | 14 | 3 | 0 | 0 | 0 | 1 | 0 | 0.73519 | 1.8698 | 6.2175 | 4.3455 | 61.0861 | 138.5475 | 120.3291 | 1.3688 | 12.5072 | 96.6
414844 | ROAD SPRINGS, LEYLAND | PAUWELS | SD52302184 | 500 | 11 KV | LV | 14 | OUTDOOR | 139 | 7 | 3 | 5 | 0 | 0 | 0 | 0 | 0.41897 | 1.0562 | 10.2557 | 6.0763 | 33.0246 | 61.4899 | 109.8078 | 0.00073947 | 23151.6655 | 0
415028 | CLOVER RD, CHORLEY | FERRANTI | SD57121619 | 500 | 11 KV | LV | 49 | INDOOR | 117 | 7 | 6 | 1 | 0 | 2 | 0 | 0 | 0.4231 | 0.96667 | 16.1392 | 8.3202 | 43.2046 | 67.7697 | 99.4786 | 0.0019526 | 8767.7779 | 0
415087 | ALDERBROOK DR, PARBOLD | LINDLEY THOMPSON | SD49231083 | 500 | 11 KV | LV | 51 | INDOOR | 119 | 5 | 8 | 2 | 0 | 0 | 0 | 0 | 0.36648 | 0.91917 | 16.3763 | 8.4044 | 39.9398 | 63.4351 | 99.1502 | 0.0013746 | 12454.7919 | 0
415293 | BLACKGATE LN, TARLETON | SOUTH WALES SWITCHGEAR | SD44892033 | 500 | 11 KV | LV | 27 | INDOOR | 112 | 44 | 7 | 4 | 0 | 0 | 0 | 0 | 0.4577 | 1.1452 | 11.1462 | 6.4671 | 44.5894 | 78.7251 | 107.3773 | 0.0037912 | 4515.7455 | 0
415504 | CLAUGHTON AVE, CLAYTON-LE-WOODS | PARSONS | SD56342239 | 500 | 11 KV | LV | 31 | INDOOR | 366 | 23 | 2 | 0 | 0 | 0 | 0 | 0 | 0.96229 | 2.5481 | 12.1771 | 6.8735 | 77.8453 | 209.0852 | 105.3977 | 2594.2837 | 0.0065991 | 100
415540 | WYRESDALE DR | ABB | SD54732098 | 500 | 11 KV | LV | 12 | INDOOR | 228 | 7 | 1 | 0 | 0 | 0 | 0 | 0 | 0.57998 | 1.5569 | 7.9254 | 5.117 | 50.1506 | 108.5435 | 115.1017 | 0.054282 | 315.3892 | 25
417073 | RIPON ST, RIPON STREET PRESTON | BRUSH | SD53403071 | 800 | 6.6 KV | LV | 29 | OUTDOOR | 138 | 9 | 3 | 0 | 0 | 0 | 0 | 0 | 0.23507 | 0.62439 | 15.2287 | 7.9766 | 25.4598 | 37.6157 | 100.9882 | 0.00022046 | 77656.7958 | 0
418214 | BRITANNIA DR, PRESTON | SOUTH WALES SWITCHGEAR | SD51712948 | 800 | 6.6 KV | LV | 17 | OUTDOOR | 42 | 177 | 1 | 6 | 0 | 0 | 0 | 0 | 0.43109 | 0.95601 | 11.1724 | 6.4537 | 32.5918 | 55.7844 | 107.7148 | 0.00056188 | 30469.0138 | 0
423267 | QUEENS PK EST, ST ANNES | PARSONS | SD33852875 | 500 | 6.6 KV | LV | 35 | INDOOR | 222 | 18 | 4 | 0 | 0 | 0 | 0 | 0 | 0.60918 | 1.6044 | 13.055 | 7.212 | 52.2949 | 113.5172 | 103.8262 | 0.092736 | 184.6104 | 92.8
423313 | SOUTH HEY, ST ANNES | BONAR LONG | SD34502860 | 750 | 6.6 KV | LV | 47 | INDOOR | 238 | 108 | 0 | 4 | 0 | 0 | 0 | 0 | 0.58992 | 1.5381 | 15.9728 | 8.2634 | 52.3726 | 110.0752 | 99.6761 | 0.069382 | 246.75 | 97.8
423928 | HOLYOAKE AVE, OPP NO1 HOLYOAKE | PARSONS | SD32323837 | 500 | 6.6 KV | LV | 35 | OUTDOOR | 101 | 7 | 4 | 2 | 2 | 0 | 0 | 0 | 0.38366 | 0.86692 | 17.4739 | 8.7531 | 32.1949 | 51.3516 | 98.1131 | 0.00045796 | 37383.4522 | 0
427236 | HERITAGE WAY | BABCOCK | SD32704224 | 800 | 6.6 KV | LV | 22 | OUTDOOR | 121 | 48 | 2 | 0 | 0 | 0 | 0 | 0 | 0.26591 | 0.70884 | 12.4587 | 6.9427 | 26.4183 | 41.5737 | 105.5358 | 0.00025583 | 66920.2236 | 0
428275 | KINGSWAY, OLD FLATS ENTRANCE | PAUWELS | SD31304270 | 800 | 6.6 KV | LV | 16 | INDOOR | 57 | 68 | 2 | 3 | 0 | 0 | 0 | 0 | 0.21609 | 0.55674 | 8.704 | 5.4656 | 36.0297 | 46.3771 | 112.7859 | 0.00075468 | 22685.1662 | 0
429617 | PEACE PL, GAMBLE RD THORNTON | ABB | SD33464390 | 800 | 11 KV | LV | 15 | INDOOR | 334 | 13 | 6 | 0 | 1 | 0 | 1 | 0 | 0.60311 | 1.4954 | 8.6664 | 5.448 | 55.0182 | 109.6044 | 112.9056 | 0.067983 | 251.8261 | 38.6
429948 | LITTLE POULTON GDNS | ABB | SD35703910 | 500 | 6.6 KV | LV | 12 | INDOOR | 48 | 76 | 6 | 0 | 0 | 0 | 0 | 0 | 0.33854 | 0.87651 | 8.0661 | 5.1854 | 38.4539 | 60.4365 | 114.5568 | 0.0011927 | 14353.8426 | 0
450050 | STANSFELD ST, BLACKBURN BB18 I | BRUSH | SD67422706 | 800 | 6.6 KV | LV | 31 | OUTDOOR | 120 | 4 | 7 | 1 | 1 | 0 | 0 | 0 | 0.24394 | 0.588 | 15.7424 | 8.148 | 26.1256 | 36.5918 | 100.3963 | 0.00022695 | 75436.5799 | 0
450074 | GUIDE, CARPARK OF ENSOR | SOUTH WALES SWITCHGEAR | SD70562579 | 500 | 6.6 KV | LV | 19 | OUTDOOR | 108 | 2 | 3 | 0 | 0 | 0 | 0 | 0 | 0.28551 | 0.76456 | 11.7888 | 6.6972 | 27.1345 | 43.9072 | 106.5367 | 0.00027675 | 61861.6896 | 0
450105 | WILWORTH CRES, PLECKGATE Z4 0 | ABB | SD68043043 | 500 | 6.6 KV | LV | 15 | OUTDOOR | 89 | 4 | 6 | 0 | 0 | 1 | 0 | 1 | 0.35771 | 0.77564 | 10.215 | 6.0709 | 30.8687 | 46.4783 | 109.6879 | 0.00037399 | 45776.8151 | 0
450183 | OAK HILL, ACCRINGTON R22 I | SOUTH WALES SWITCHGEAR | SD76642772 | 500 | 6.6 KV | LV | 24 | INDOOR | 190 | 12 | 7 | 0 | 0 | 0 | 0 | 0 | 0.53282 | 1.3935 | 10.3684 | 6.1544 | 48.0643 | 96.2027 | 108.9947 | 0.017083 | 1002.189 | 3.8
450388 | HASTON LEE MILL, BLACKBURN AA6 I | ABB | SD68643057 | 500 | 6.6 KV | LV | 17 | INDOOR | 178 | 2 | 12 | 2 | 0 | 0 | 0 | 0 | 0.52544 | 1.3201 | 9.0727 | 5.6253 | 48.565 | 91.7839 | 111.8079 | 0.011337 | 1510.0989 | 0
450584 | BLACKBURN RD (OSW), OSWALDTWISTLE L17 I | BABCOCK | SD73032830 | 800 | 6.6 KV | LV | 21 | INDOOR | 154 | 12 | 8 | 1 | 0 | 0 | 0 | 0 | 0.28718 | 0.74148 | 10.1905 | 6.0781 | 38.5361 | 55.4834 | 109.453 | 0.0010307 | 16609.9431 | 0
450784 | BROADFIELD, ACCRINGTON Q21 I | LINDLEY THOMPSON | SD75502727 | 500 | 6.6 KV | LV | 48 | INDOOR | 149 | 29 | 2 | 0 | 0 | 0 | 0 | 0 | 0.44689 | 1.1967 | 15.9909 | 8.2733 | 42.9923 | 80.6558 | 99.6074 | 0.0041269 | 4148.3429 | 0
451828 | BRANTWOOD | ABB | SD74233092 | 500 | 6.6 KV | LV | 14 | OUTDOOR | 176 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.435 | 1.1715 | 10.0914 | 6.0176 | 32.9947 | 67.8398 | 110.0413 | 0.0010886 | 15726.6838 | 0
451866 | MILNSHAW GDNS | SOUTH WALES SWITCHGEAR | SD75472905 | 800 | 6.6 KV | LV | 25 | OUTDOOR | 41 | 57 | 5 | 0 | 0 | 0 | 0 | 0 | 0.16806 | 0.4391 | 14.232 | 7.6162 | 23.784 | 30.3019 | 102.4334 | 0.00018343 | 93334.2808 | 0
453049 | FOREST MILL, LUMB A18 I | SOUTH WALES SWITCHGEAR | SD84072561 | 500 | 6.6 KV | LV | 17 | INDOOR | 175 | 8 | 4 | 1 | 0 | 0 | 0 | 0 | 0.47868 | 1.2507 | 9.0046 | 5.5896 | 44.8833 | 85.1132 | 112.0952 | 0.0061777 | 2771.2461 | 0
455007 | WADDINGTON, WADDINGTON C2 I6 | CROMPTON PARKINSON | SD72864394 | 500 | 11 KV | LV | 53 | OUTDOOR | 133 | 20 | 9 | 4 | 0 | 1 | 0 | 0 | 0.50054 | 1.1871 | 23.4497 | 10.6852 | 38.1253 | 71.8988 | 91.7868 | 0.0016541 | 10349.7314 | 0
458190 | GRETNA, BURNLEY B3 B3 | FERRANTI | SD82693146 | 750 | 6.6 KV | LV | 53 | OUTDOOR | 220 | 5 | 3 | 1 | 0 | 0 | 0 | 0 | 0.38378 | 1.0057 | 23.2196 | 10.6208 | 30.927 | 58.1701 | 91.9603 | 0.00057508 | 29769.9103 | 0
458556 | GERTRUDE ST, NELSON N1 F14 | LINDLEY THOMPSON | SD87023875 | 500 | 6.6 KV | LV | 55 | INDOOR | 317 | 34 | 15 | 0 | 1 | 0 | 1 | 0 | 1.0254 | 2.4924 | 17.5459 | 8.8031 | 87.4747 | 210.3106 | 97.7486 | 3406.8683 | 0.0050251 | 100
458558 | OXFORD RD | ALSTOM | SD87253869 | 500 | 6.6 KV | LV | 11 | INDOOR | 193 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0.48951 | 1.3179 | 7.8305 | 5.0819 | 45.0441 | 89.1683 | 115.2188 | 0.008389 | 2040.7585 | 0
458748 | BACK RUTLAND AVE, BURNLEY B1 B13 | FERRANTI | SD81463288 | 750 | 6.6 KV | LV | 51 | INDOOR | 119 | 6 | 5 | 0 | 0 | 0 | 1 | 0 | 0.25322 | 0.61826 | 16.6843 | 8.5087 | 36.2478 | 48.2627 | 98.7877 | 0.00073418 | 23318.5085 | 0
616017 | TWEED RISE, WALNEY BARROW | SOUTH WALES SWITCHGEAR | SD17796893 | 500 | 11 KV | LV | 58 | OUTDOOR | 244 | 17 | 0 | 2 | 1 | 0 | 0 | 0 | 0.6936 | 1.7741 | 25.3828 | 11.2767 | 48.266 | 116.5247 | 89.9767 | 0.11232 | 152.4178 | 100
616120 | HEST VIEW, ULVERSTON | BONAR LONG | SD28787649 | 500 | 11 KV | LV | 45 | OUTDOOR | 261 | 22 | 1 | 1 | 0 | 0 | 0 | 0 | 0.70677 | 1.8663 | 20.9287 | 9.9002 | 48.47 | 123.6643 | 94.2137 | 0.24697 | 69.3208 | 100
620293 | THE ARCHES, MARYPORT | SOUTH WALES SWITCHGEAR | NY03783549 | 500 | 11 KV | LV | 17 | INDOOR | 242 | 5 | 2 | 0 | 0 | 0 | 0 | 0 | 0.61479 | 1.6286 | 8.8875 | 5.544 | 52.3779 | 115.4807 | 112.3212 | 0.11313 | 151.3335 | 66.8
620717 | DERWENT RD, MOSS BAY WORKINGTON | SOUTH WALES SWITCHGEAR | NX99282733 | 500 | 11 KV | LV | 17 | OUTDOOR | 327 | 20 | 30 | 6 | 0 | 0 | 0 | 0 | 1.078 | 2.595 | 11.1412 | 6.4412 | 82.4831 | 206.3889 | 107.8154 | 2268.5867 | 0.0075465 | 100
636100 | CHESTERHOLM, ADJ 69 CHESTERHOLM | BONAR LONG | NY37025553 | 500 | 11 KV | LV | 39 | OUTDOOR | 252 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65037 | 1.7361 | 18.6321 | 9.15 | 44.6453 | 111.864 | 96.6726 | 0.06849 | 249.9642 | 99.2
636173 | TODDS | ABB | NY39565561 | 800 | 11 KV | LV | 12 | OUTDOOR | 134 | 12 | 12 | 2 | 0 | 0 | 0 | 0 | 0.27794 | 0.68851 | 9.4945 | 5.7668 | 27.2827 | 41.25 | 111.464 | 0.00026607 | 64343.5623 | 0
636385 | QUEENSWAY, BES NO 10 QUEENSWAY | YORKSHIRE SWITCHGEAR AND ENGINEERING | NY37905480 | 500 | 11 KV | LV | 44 | INDOOR | 240 | 16 | 6 | 1 | 0 | 0 | 0 | 0 | 0.6684 | 1.7325 | 15.458 | 8.0849 | 56.4877 | 125.6743 | 100.3239 | 0.34115 | 50.1837 | 100
642320 | CONISTON AVENUE HAMBLETON | SOUTH WALES SWITCHGEAR | SD37064267 | 500 | 11 KV | LV | 17 | INDOOR | 137 | 25 | 3 | 1 | 0 | 0 | 0 | 0 | 0.42231 | 1.1107 | 9.018 | 5.5955 | 41.9703 | 75.0114 | 112.0927 | 0.0027333 | 6263.5909 | 0
642344 | BEECHFIELD AVE, PREESALL | ABB | SD36414838 | 500 | 6.6 KV | LV | 15 | INDOOR | 168 | 25 | 2 | 0 | 0 | 0 | 0 | 0 | 0.48343 | 1.2846 | 8.5623 | 5.3991 | 44.8622 | 87.3597 | 113.2792 | 0.0074016 | 2313.0025 | 0
643270 | ULSTER ROAD, BOWERHAM LANCASTER | HAWKER SIDDELEY | SD48466041 | 1000 | 11 KV | LV | 27 | INDOOR | 343 | 29 | 5 | 2 | 0 | 0 | 0 | 0 | 0.47787 | 1.24 | 11.2135 | 6.4928 | 47.0359 | 88.1149 | 107.2515 | 0.0086694 | 1974.7535 | 0
643285 | DALTON ROAD (LANCASTER), LANCASTER | SOUTH WALES SWITCHGEAR | SD48486185 | 500 | 11 KV | LV | 27 | OUTDOOR | 321 | 30 | 6 | 0 | 0 | 0 | 0 | 0 | 0.89187 | 2.3274 | 14.4535 | 7.6889 | 62.0433 | 170.3305 | 102.2107 | 39.2955 | 0.43567 | 100
643286 | MOORGATE, LANCASTER | HAWKER SIDDELEY | SD48306164 | 500 | 11 KV | LV | 27 | INDOOR | 292 | 35 | 14 | 4 | 0 | 0 | 0 | 0 | 0.9141 | 2.3103 | 11.0403 | 6.4282 | 76.6796 | 186.3019 | 107.5441 | 224.2901 | 0.07633 | 100
643293 | RIDGE LANE | NITRAN | SD48236224 | 800 | 11 KV | 6.6 KV | 23 | OUTDOOR | 90 | 26 | 1 | 5 | 0 | 0 | 0 | 0 | 0.20944 | 0.52939 | 13.2704 | 7.2468 | 24.8669 | 33.7918 | 104.1865 | 0.00020197 | 84763.6861 | 0
666035 | RAISELANDS CROFT, ADJ.7 RAISELANDS CFT | DISTRIBUTION TRANSFORMERS LTD | NY51103120 | 500 | 11 KV | LV | 36 | OUTDOOR | 308 | 14 | 4 | 1 | 1 | 0 | 0 | 0 | 0.85572 | 2.1817 | 17.6323 | 8.8156 | 59.9219 | 156.3336 | 97.8243 | 8.1154 | 2.1096 | 100

## Mapping - Extreme-range
Mapping of failure probability of demonstrated distribution transformers

## Appendix
Definition
EV Scenario |  | BAU |  | Business as usual with EVs penetration level of 0
|  | Mid-range |  | EVs penetration level of 11.7 %
|  | High-range |  | EVs penetration level of 32%
|  | Extreme-range |  | EVs penetration level of 58.9%
Condition settings for intermediate calculation
Ambient temperature (for hot-spot temperature calculation) (°C) | [8 empty] | 13.4
Oil depth (for bubbling inception temperaure calculation) (m) | [8 empty] | 1.57
Gas content (for bubbling inception temperature calculation) (%) | [8 empty] | 9
Thermal parameters applied for assessment
R |  |  | H |  |  | x | y
8.7 | 50.6 | 16.8 | 1.1 | 180 | 11.4 | 0.8 | 1.6 | 1.1 | 1 | 2
〖∆𝜃〗_𝑜𝑟
𝑔_𝑟
𝜏_𝑜
𝜏_𝑤
𝑘_11
𝑘_21
𝑘_22